## Scenario_Summary
CandidateKey | GridID | SubstationID | CandidateLineID | BaseDCMW | ServiceTarget | ServedLoadMW | OutageDurationHours | PVCapacityMW | PVCapacityRatioToDC | PVOutageCreditEnabled | PVCanRechargeBatteryDuringOutage | HistoricalOutageWindowsEvaluated | BatteryPowerMW | BatteryInstalledMWh | UnmarginedBatteryPowerMW | UnmarginedBatteryInstalledMWh | BatteryUsableSOCWindowMWh | BatteryDeliverableFromStartMWh | P99EnergyOptimalBatteryInstalledMWhByHistoricalStart | P95EnergyOptimalBatteryInstalledMWhByHistoricalStart | P50EnergyOptimalBatteryInstalledMWhByHistoricalStart | MinimumEnergyOptimalBatteryInstalledMWhByHistoricalStart | WorstEnergyOptimalHistoricalStartMWh | CriticalHistoricalStartUTC | CriticalHistoricalStartLocal | CriticalWindowPVAvailableMWh | CriticalWindowPVUsedDirectMWh | CriticalWindowPVChargedToBatteryACMWh | CriticalWindowPVCurtailedMWh | CriticalWindowBatteryDeliveredMWh | CriticalWindowMinimumSOCFraction | ConstraintGenerationIterations | FinalCriticalWindowCount | FinalHistoricalViolationCount | FinalMinimumSOCMarginMWh | FinalMaximumPowerDeficitMW | BatteryStartSOCFraction | BatteryMinSOCFraction | BatteryMaxSOCFraction | BatteryChargeEfficiency | BatteryDischargeEfficiency | EnergyTermination | PowerTermination | BatteryOnlyPowerMW | BatteryOnlyInstalledMWh | BatteryOnlyP99InstalledMWh | BatteryOnlyP95InstalledMWh | BatteryOnlyP50InstalledMWh | RobustBatteryEnergySavingsFromPVMWh | RobustBatteryPowerSavingsFromPVMW | P99BatteryEnergySavingsFromPVMWh | P95BatteryEnergySavingsFromPVMWh | P50BatteryEnergySavingsFromPVMWh | ParetoEfficient
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 6.7548 | 1 | 0 | 0 | FALSE | TRUE | 105397 | 6.7548 | 8.8879 | 6.7548 | 8.8879 | 7.1103 | 6.7548 | 8.8879 | 8.8879 | 8.8879 | 8.8879 | 8.8879 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 6.7548 | 10% | 1 | 12 | 0 | 0 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 6.7548 | 8.8879 | 8.8879 | 8.8879 | 8.8879 | 0 | 0 | 0 | 0 | 0 | TRUE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 6.7548 | 1 | 3.3774 | 0.25 | TRUE | TRUE | 105397 | 6.7548 | 8.8879 | 6.7548 | 8.8879 | 7.1103 | 6.7548 | 8.8879 | 8.8879 | 8.7992 | 3.9996 | 8.8879 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 6.7548 | 10% | 1 | 12 | 0 | 0 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 6.7548 | 8.8879 | 8.8879 | 8.8879 | 8.8879 | 0 | 0 | 0 | 0 | 0.088688 | FALSE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 6.7548 | 1 | 6.7548 | 0.5 | TRUE | TRUE | 105397 | 6.7548 | 8.8879 | 6.7548 | 8.8879 | 7.1103 | 6.7548 | 8.8879 | 8.8879 | 8.7105 | 1.2934e-10 | 8.8879 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 6.7548 | 10% | 1 | 12 | 0 | 0 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 6.7548 | 8.8879 | 8.8879 | 8.8879 | 8.8879 | 0 | 0 | 0 | 0 | 0.17738 | FALSE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 6.7548 | 1 | 10.1322 | 0.75 | TRUE | TRUE | 105397 | 6.7548 | 8.8879 | 6.7548 | 8.8879 | 7.1103 | 6.7548 | 8.8879 | 8.8879 | 8.6218 | 1.2934e-10 | 8.8879 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 6.7548 | 10% | 1 | 12 | 0 | 0 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 6.7548 | 8.8879 | 8.8879 | 8.8879 | 8.8879 | 0 | 0 | 0 | 0 | 0.26606 | FALSE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 6.7548 | 1 | 13.5096 | 1 | TRUE | TRUE | 105397 | 6.7548 | 8.8879 | 6.7548 | 8.8879 | 7.1103 | 6.7548 | 8.8879 | 8.8879 | 8.5331 | 1.2934e-10 | 8.8879 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 6.7548 | 10% | 1 | 12 | 0 | 0 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 6.7548 | 8.8879 | 8.8879 | 8.8879 | 8.8879 | 0 | 0 | 0 | 0 | 0.35475 | FALSE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 6.7548 | 2 | 0 | 0 | FALSE | TRUE | 105385 | 6.7548 | 17.7758 | 6.7548 | 17.7758 | 14.2206 | 13.5096 | 17.7758 | 17.7758 | 17.7758 | 17.7758 | 17.7758 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 13.5096 | 10% | 1 | 12 | 0 | 0 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 6.7548 | 17.7758 | 17.7758 | 17.7758 | 17.7758 | 0 | 0 | 0 | 0 | 0 | TRUE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 6.7548 | 2 | 3.3774 | 0.25 | TRUE | TRUE | 105385 | 6.7548 | 17.7758 | 6.7548 | 17.7758 | 14.2206 | 13.5096 | 17.7758 | 17.7758 | 17.4751 | 8.9553 | 17.7758 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 13.5096 | 10% | 1 | 12 | 0 | 0 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 6.7548 | 17.7758 | 17.7758 | 17.7758 | 17.7758 | 0 | 0 | 0 | 0 | 0.30075 | FALSE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 6.7548 | 2 | 6.7548 | 0.5 | TRUE | TRUE | 105385 | 6.7548 | 17.7758 | 6.7548 | 17.7758 | 14.2206 | 13.5096 | 17.7758 | 17.7758 | 17.1743 | 0.36223 | 17.7758 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 13.5096 | 10% | 1 | 12 | 0 | 0 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 6.7548 | 17.7758 | 17.7758 | 17.7758 | 17.7758 | 0 | 0 | 0 | 0 | 0.6015 | FALSE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 6.7548 | 2 | 10.1322 | 0.75 | TRUE | TRUE | 105385 | 6.7548 | 17.7758 | 6.7548 | 17.7758 | 14.2206 | 13.5096 | 17.7758 | 17.7758 | 16.8736 | 2.5867e-10 | 17.7758 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 13.5096 | 10% | 1 | 12 | 0 | 0 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 6.7548 | 17.7758 | 17.7758 | 17.7758 | 17.7758 | 0 | 0 | 0 | 0 | 0.90225 | FALSE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 6.7548 | 2 | 13.5096 | 1 | TRUE | TRUE | 105385 | 6.7548 | 17.7758 | 6.7548 | 17.7758 | 14.2206 | 13.5096 | 17.7758 | 17.7758 | 16.5728 | 2.5867e-10 | 17.7758 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 13.5096 | 10% | 1 | 12 | 0 | 0 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 6.7548 | 17.7758 | 17.7758 | 17.7758 | 17.7758 | 0 | 0 | 0 | 0 | 1.203 | FALSE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 6.7548 | 4 | 0 | 0 | FALSE | TRUE | 105361 | 6.7548 | 35.5516 | 6.7548 | 35.5516 | 28.4413 | 27.0192 | 35.5516 | 35.5516 | 35.5516 | 35.5516 | 35.5516 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 27.0192 | 10% | 1 | 12 | 0 | 0 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 6.7548 | 35.5516 | 35.5516 | 35.5516 | 35.5516 | 0 | 0 | 0 | 0 | 0 | TRUE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 6.7548 | 4 | 3.3774 | 0.25 | TRUE | TRUE | 105361 | 6.7548 | 35.5516 | 6.7548 | 35.5516 | 28.4413 | 27.0192 | 35.5516 | 35.5516 | 34.3091 | 18.9174 | 35.5516 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 27.0192 | 10% | 1 | 12 | 0 | 0 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 6.7548 | 35.5516 | 35.5516 | 35.5516 | 35.5516 | 0 | 0 | 0 | 0 | 1.2425 | FALSE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 6.7548 | 4 | 6.7548 | 0.5 | TRUE | TRUE | 105361 | 6.7548 | 35.5516 | 6.7548 | 35.5516 | 28.4413 | 27.0192 | 35.5516 | 35.5516 | 33.0667 | 2.3699 | 35.5516 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 27.0192 | 10% | 1 | 12 | 0 | 0 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 6.7548 | 35.5516 | 35.5516 | 35.5516 | 35.5516 | 0 | 0 | 0 | 0 | 2.4849 | FALSE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 6.7548 | 4 | 10.1322 | 0.75 | TRUE | TRUE | 105361 | 6.7548 | 35.5516 | 6.7548 | 35.5516 | 28.4413 | 27.0192 | 35.5516 | 35.5516 | 31.8242 | 5.1734e-10 | 35.5516 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 27.0192 | 10% | 1 | 12 | 0 | 0 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 6.7548 | 35.5516 | 35.5516 | 35.5516 | 35.5516 | 0 | 0 | 0 | 0 | 3.7274 | FALSE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 6.7548 | 4 | 13.5096 | 1 | TRUE | TRUE | 105361 | 6.7548 | 35.5516 | 6.7548 | 35.5516 | 28.4413 | 27.0192 | 35.5516 | 35.5516 | 30.5818 | 5.1734e-10 | 35.5516 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 27.0192 | 10% | 1 | 12 | 0 | 0 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 6.7548 | 35.5516 | 35.5516 | 35.5516 | 35.5516 | 0 | 0 | 0 | 0 | 4.9698 | FALSE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 6.7548 | 8 | 0 | 0 | FALSE | TRUE | 105313 | 6.7548 | 71.1032 | 6.7548 | 71.1032 | 56.8826 | 54.0384 | 71.1032 | 71.1032 | 71.1032 | 71.1032 | 71.1032 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 54.0384 | 10% | 1 | 12 | 0 | 0 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 6.7548 | 71.1032 | 71.1032 | 71.1032 | 71.1032 | 0 | 0 | 0 | 0 | 0 | TRUE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 6.7548 | 8 | 3.3774 | 0.25 | TRUE | TRUE | 105313 | 6.7548 | 71.1032 | 6.7548 | 71.1032 | 56.8826 | 54.0384 | 71.1032 | 71.1032 | 65.9666 | 42.2587 | 71.1032 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 54.0384 | 10% | 1 | 12 | 0 | 0 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 6.7548 | 71.1032 | 71.1032 | 71.1032 | 71.1032 | 0 | 0 | 0 | 0 | 5.1366 | FALSE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 6.7548 | 8 | 6.7548 | 0.5 | TRUE | TRUE | 105313 | 6.7548 | 71.1032 | 6.7548 | 71.1032 | 56.8826 | 54.0384 | 71.1032 | 71.1032 | 60.8301 | 13.5009 | 71.1032 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 54.0384 | 10% | 1 | 12 | 0 | 0 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 6.7548 | 71.1032 | 71.1032 | 71.1032 | 71.1032 | 0 | 0 | 0 | 0 | 10.2731 | FALSE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 6.7548 | 8 | 10.1322 | 0.75 | TRUE | TRUE | 105313 | 6.7548 | 71.1032 | 6.7548 | 71.1032 | 56.8826 | 54.0384 | 71.1032 | 71.1032 | 55.703 | 0.71594 | 71.1032 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 54.0384 | 10% | 1 | 12 | 0 | 0 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 6.7548 | 71.1032 | 71.1032 | 71.1032 | 71.1032 | 0 | 0 | 0 | 0 | 15.4002 | FALSE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 6.7548 | 8 | 13.5096 | 1 | TRUE | TRUE | 105313 | 6.7548 | 71.1032 | 6.7548 | 71.1032 | 56.8826 | 54.0384 | 71.1032 | 71.1032 | 50.9397 | 1.0347e-09 | 71.1032 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 54.0384 | 10% | 1 | 12 | 0 | 0 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 6.7548 | 71.1032 | 71.1032 | 71.1032 | 71.1032 | 0 | 0 | 0 | 0 | 20.1635 | FALSE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 10.1322 | 1 | 0 | 0 | FALSE | TRUE | 105397 | 10.1322 | 13.3319 | 10.1322 | 13.3319 | 10.6655 | 10.1322 | 13.3319 | 13.3319 | 13.3319 | 13.3319 | 13.3319 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 10.1322 | 10% | 1 | 12 | 0 | 1.5543e-15 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 10.1322 | 13.3319 | 13.3319 | 13.3319 | 13.3319 | 0 | 0 | 0 | 0 | 0 | TRUE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 10.1322 | 1 | 3.3774 | 0.25 | TRUE | TRUE | 105397 | 10.1322 | 13.3319 | 10.1322 | 13.3319 | 10.6655 | 10.1322 | 13.3319 | 13.3319 | 13.2432 | 8.4435 | 13.3319 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 10.1322 | 10% | 1 | 12 | 0 | 1.5543e-15 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 10.1322 | 13.3319 | 13.3319 | 13.3319 | 13.3319 | 0 | 0 | 0 | 0 | 0.088688 | FALSE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 10.1322 | 1 | 6.7548 | 0.5 | TRUE | TRUE | 105397 | 10.1322 | 13.3319 | 10.1322 | 13.3319 | 10.6655 | 10.1322 | 13.3319 | 13.3319 | 13.1545 | 3.5552 | 13.3319 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 10.1322 | 10% | 1 | 12 | 0 | 1.5543e-15 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 10.1322 | 13.3319 | 13.3319 | 13.3319 | 13.3319 | 0 | 0 | 0 | 0 | 0.17738 | FALSE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 10.1322 | 1 | 10.1322 | 0.75 | TRUE | TRUE | 105397 | 10.1322 | 13.3319 | 10.1322 | 13.3319 | 10.6655 | 10.1322 | 13.3319 | 13.3319 | 13.0658 | 1.94e-10 | 13.3319 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 10.1322 | 10% | 1 | 12 | 0 | 1.5543e-15 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 10.1322 | 13.3319 | 13.3319 | 13.3319 | 13.3319 | 0 | 0 | 0 | 0 | 0.26606 | FALSE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 10.1322 | 1 | 13.5096 | 1 | TRUE | TRUE | 105397 | 10.1322 | 13.3319 | 10.1322 | 13.3319 | 10.6655 | 10.1322 | 13.3319 | 13.3319 | 12.9771 | 1.94e-10 | 13.3319 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 10.1322 | 10% | 1 | 12 | 0 | 1.5543e-15 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 10.1322 | 13.3319 | 13.3319 | 13.3319 | 13.3319 | 0 | 0 | 0 | 0 | 0.35475 | FALSE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 10.1322 | 2 | 0 | 0 | FALSE | TRUE | 105385 | 10.1322 | 26.6637 | 10.1322 | 26.6637 | 21.331 | 20.2644 | 26.6637 | 26.6637 | 26.6637 | 26.6637 | 26.6637 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 20.2644 | 10% | 1 | 12 | 0 | 3.1086e-15 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 10.1322 | 26.6637 | 26.6637 | 26.6637 | 26.6637 | 0 | 0 | 0 | 0 | 0 | TRUE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 10.1322 | 2 | 3.3774 | 0.25 | TRUE | TRUE | 105385 | 10.1322 | 26.6637 | 10.1322 | 26.6637 | 21.331 | 20.2644 | 26.6637 | 26.6637 | 26.363 | 17.8432 | 26.6637 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 20.2644 | 10% | 1 | 12 | 0 | 3.1086e-15 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 10.1322 | 26.6637 | 26.6637 | 26.6637 | 26.6637 | 0 | 0 | 0 | 0 | 0.30075 | FALSE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 10.1322 | 2 | 6.7548 | 0.5 | TRUE | TRUE | 105385 | 10.1322 | 26.6637 | 10.1322 | 26.6637 | 21.331 | 20.2644 | 26.6637 | 26.6637 | 26.0622 | 9.0227 | 26.6637 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 20.2644 | 10% | 1 | 12 | 0 | 3.1086e-15 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 10.1322 | 26.6637 | 26.6637 | 26.6637 | 26.6637 | 0 | 0 | 0 | 0 | 0.6015 | FALSE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 10.1322 | 2 | 10.1322 | 0.75 | TRUE | TRUE | 105385 | 10.1322 | 26.6637 | 10.1322 | 26.6637 | 21.331 | 20.2644 | 26.6637 | 26.6637 | 25.7615 | 0.54334 | 26.6637 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 20.2644 | 10% | 1 | 12 | 0 | 3.1086e-15 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 10.1322 | 26.6637 | 26.6637 | 26.6637 | 26.6637 | 0 | 0 | 0 | 0 | 0.90225 | FALSE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 10.1322 | 2 | 13.5096 | 1 | TRUE | TRUE | 105385 | 10.1322 | 26.6637 | 10.1322 | 26.6637 | 21.331 | 20.2644 | 26.6637 | 26.6637 | 25.4607 | 3.8801e-10 | 26.6637 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 20.2644 | 10% | 1 | 12 | 0 | 3.1086e-15 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 10.1322 | 26.6637 | 26.6637 | 26.6637 | 26.6637 | 0 | 0 | 0 | 0 | 1.203 | FALSE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 10.1322 | 4 | 0 | 0 | FALSE | TRUE | 105361 | 10.1322 | 53.3274 | 10.1322 | 53.3274 | 42.6619 | 40.5288 | 53.3274 | 53.3274 | 53.3274 | 53.3274 | 53.3274 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 40.5288 | 10% | 1 | 12 | 0 | -1.6875e-14 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 10.1322 | 53.3274 | 53.3274 | 53.3274 | 53.3274 | 0 | 0 | 0 | 0 | 0 | TRUE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 10.1322 | 4 | 3.3774 | 0.25 | TRUE | TRUE | 105361 | 10.1322 | 53.3274 | 10.1322 | 53.3274 | 42.6619 | 40.5288 | 53.3274 | 53.3274 | 52.0849 | 36.6932 | 53.3274 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 40.5288 | 10% | 1 | 12 | 0 | -1.6875e-14 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 10.1322 | 53.3274 | 53.3274 | 53.3274 | 53.3274 | 0 | 0 | 0 | 0 | 1.2425 | FALSE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 10.1322 | 4 | 6.7548 | 0.5 | TRUE | TRUE | 105361 | 10.1322 | 53.3274 | 10.1322 | 53.3274 | 42.6619 | 40.5288 | 53.3274 | 53.3274 | 50.8425 | 20.059 | 53.3274 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 40.5288 | 10% | 1 | 12 | 0 | -1.6875e-14 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 10.1322 | 53.3274 | 53.3274 | 53.3274 | 53.3274 | 0 | 0 | 0 | 0 | 2.4849 | FALSE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 10.1322 | 4 | 10.1322 | 0.75 | TRUE | TRUE | 105361 | 10.1322 | 53.3274 | 10.1322 | 53.3274 | 42.6619 | 40.5288 | 53.3274 | 53.3274 | 49.6 | 3.5548 | 53.3274 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 40.5288 | 10% | 1 | 12 | 0 | -1.6875e-14 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 10.1322 | 53.3274 | 53.3274 | 53.3274 | 53.3274 | 0 | 0 | 0 | 0 | 3.7274 | FALSE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 10.1322 | 4 | 13.5096 | 1 | TRUE | TRUE | 105361 | 10.1322 | 53.3274 | 10.1322 | 53.3274 | 42.6619 | 40.5288 | 53.3274 | 53.3274 | 48.3576 | 7.7602e-10 | 53.3274 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 40.5288 | 10% | 1 | 12 | 0 | -1.6875e-14 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 10.1322 | 53.3274 | 53.3274 | 53.3274 | 53.3274 | 0 | 0 | 0 | 0 | 4.9698 | FALSE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 10.1322 | 8 | 0 | 0 | FALSE | TRUE | 105313 | 10.1322 | 106.6548 | 10.1322 | 106.6548 | 85.3238 | 81.0576 | 106.6548 | 106.6548 | 106.6548 | 106.6548 | 106.6548 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 81.0576 | 10% | 1 | 12 | 0 | 4.6185e-14 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 10.1322 | 106.6548 | 106.6548 | 106.6548 | 106.6548 | 0 | 0 | 0 | 0 | 0 | TRUE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 10.1322 | 8 | 3.3774 | 0.25 | TRUE | TRUE | 105313 | 10.1322 | 106.6548 | 10.1322 | 106.6548 | 85.3238 | 81.0576 | 106.6548 | 106.6548 | 101.5182 | 77.8103 | 106.6548 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 81.0576 | 10% | 1 | 12 | 0 | 4.6185e-14 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 10.1322 | 106.6548 | 106.6548 | 106.6548 | 106.6548 | 0 | 0 | 0 | 0 | 5.1366 | FALSE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 10.1322 | 8 | 6.7548 | 0.5 | TRUE | TRUE | 105313 | 10.1322 | 106.6548 | 10.1322 | 106.6548 | 85.3238 | 81.0576 | 106.6548 | 106.6548 | 96.3817 | 48.9659 | 106.6548 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 81.0576 | 10% | 1 | 12 | 0 | 4.6185e-14 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 10.1322 | 106.6548 | 106.6548 | 106.6548 | 106.6548 | 0 | 0 | 0 | 0 | 10.2731 | FALSE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 10.1322 | 8 | 10.1322 | 0.75 | TRUE | TRUE | 105313 | 10.1322 | 106.6548 | 10.1322 | 106.6548 | 85.3238 | 81.0576 | 106.6548 | 106.6548 | 91.2451 | 20.2514 | 106.6548 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 81.0576 | 10% | 1 | 12 | 0 | 4.6185e-14 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 10.1322 | 106.6548 | 106.6548 | 106.6548 | 106.6548 | 0 | 0 | 0 | 0 | 15.4097 | FALSE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 10.1322 | 8 | 13.5096 | 1 | TRUE | TRUE | 105313 | 10.1322 | 106.6548 | 10.1322 | 106.6548 | 85.3238 | 81.0576 | 106.6548 | 106.6548 | 86.1086 | 2.0978 | 106.6548 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 81.0576 | 10% | 1 | 12 | 0 | 4.6185e-14 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 10.1322 | 106.6548 | 106.6548 | 106.6548 | 106.6548 | 0 | 0 | 0 | 0 | 20.5462 | FALSE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 12.1586 | 1 | 0 | 0 | FALSE | TRUE | 105397 | 12.1586 | 15.9982 | 12.1586 | 15.9982 | 12.7986 | 12.1586 | 15.9982 | 15.9982 | 15.9982 | 15.9982 | 15.9982 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 12.1586 | 10% | 1 | 12 | 0 | 4.4409e-16 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 12.1586 | 15.9982 | 15.9982 | 15.9982 | 15.9982 | 0 | 0 | 0 | 0 | 0 | TRUE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 12.1586 | 1 | 3.3774 | 0.25 | TRUE | TRUE | 105397 | 12.1586 | 15.9982 | 12.1586 | 15.9982 | 12.7986 | 12.1586 | 15.9982 | 15.9982 | 15.9095 | 11.1099 | 15.9982 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 12.1586 | 10% | 1 | 12 | 0 | 4.4409e-16 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 12.1586 | 15.9982 | 15.9982 | 15.9982 | 15.9982 | 0 | 0 | 0 | 0 | 0.088688 | FALSE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 12.1586 | 1 | 6.7548 | 0.5 | TRUE | TRUE | 105397 | 12.1586 | 15.9982 | 12.1586 | 15.9982 | 12.7986 | 12.1586 | 15.9982 | 15.9982 | 15.8208 | 6.2215 | 15.9982 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 12.1586 | 10% | 1 | 12 | 0 | 4.4409e-16 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 12.1586 | 15.9982 | 15.9982 | 15.9982 | 15.9982 | 0 | 0 | 0 | 0 | 0.17738 | FALSE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 12.1586 | 1 | 10.1322 | 0.75 | TRUE | TRUE | 105397 | 12.1586 | 15.9982 | 12.1586 | 15.9982 | 12.7986 | 12.1586 | 15.9982 | 15.9982 | 15.7322 | 1.3332 | 15.9982 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 12.1586 | 10% | 1 | 12 | 0 | 4.4409e-16 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 12.1586 | 15.9982 | 15.9982 | 15.9982 | 15.9982 | 0 | 0 | 0 | 0 | 0.26606 | FALSE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 12.1586 | 1 | 13.5096 | 1 | TRUE | TRUE | 105397 | 12.1586 | 15.9982 | 12.1586 | 15.9982 | 12.7986 | 12.1586 | 15.9982 | 15.9982 | 15.6435 | 2.328e-10 | 15.9982 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 12.1586 | 10% | 1 | 12 | 0 | 4.4409e-16 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 12.1586 | 15.9982 | 15.9982 | 15.9982 | 15.9982 | 0 | 0 | 0 | 0 | 0.35475 | FALSE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 12.1586 | 2 | 0 | 0 | FALSE | TRUE | 105385 | 12.1586 | 31.9964 | 12.1586 | 31.9964 | 25.5972 | 24.3173 | 31.9964 | 31.9964 | 31.9964 | 31.9964 | 31.9964 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 24.3173 | 10% | 1 | 12 | 0 | 2.2204e-15 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 12.1586 | 31.9964 | 31.9964 | 31.9964 | 31.9964 | 0 | 0 | 0 | 0 | 0 | TRUE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 12.1586 | 2 | 3.3774 | 0.25 | TRUE | TRUE | 105385 | 12.1586 | 31.9964 | 12.1586 | 31.9964 | 25.5972 | 24.3173 | 31.9964 | 31.9964 | 31.6957 | 23.1759 | 31.9964 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 24.3173 | 10% | 1 | 12 | 0 | 2.2204e-15 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 12.1586 | 31.9964 | 31.9964 | 31.9964 | 31.9964 | 0 | 0 | 0 | 0 | 0.30075 | FALSE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 12.1586 | 2 | 6.7548 | 0.5 | TRUE | TRUE | 105385 | 12.1586 | 31.9964 | 12.1586 | 31.9964 | 25.5972 | 24.3173 | 31.9964 | 31.9964 | 31.3949 | 14.3554 | 31.9964 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 24.3173 | 10% | 1 | 12 | 0 | 2.2204e-15 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 12.1586 | 31.9964 | 31.9964 | 31.9964 | 31.9964 | 0 | 0 | 0 | 0 | 0.6015 | FALSE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 12.1586 | 2 | 10.1322 | 0.75 | TRUE | TRUE | 105385 | 12.1586 | 31.9964 | 12.1586 | 31.9964 | 25.5972 | 24.3173 | 31.9964 | 31.9964 | 31.0942 | 5.5349 | 31.9964 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 24.3173 | 10% | 1 | 12 | 0 | 2.2204e-15 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 12.1586 | 31.9964 | 31.9964 | 31.9964 | 31.9964 | 0 | 0 | 0 | 0 | 0.90225 | FALSE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 12.1586 | 2 | 13.5096 | 1 | TRUE | TRUE | 105385 | 12.1586 | 31.9964 | 12.1586 | 31.9964 | 25.5972 | 24.3173 | 31.9964 | 31.9964 | 30.7934 | 4.6561e-10 | 31.9964 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 24.3173 | 10% | 1 | 12 | 0 | 2.2204e-15 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 12.1586 | 31.9964 | 31.9964 | 31.9964 | 31.9964 | 0 | 0 | 0 | 0 | 1.203 | FALSE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 12.1586 | 4 | 0 | 0 | FALSE | TRUE | 105361 | 12.1586 | 63.9929 | 12.1586 | 63.9929 | 51.1943 | 48.6346 | 63.9929 | 63.9929 | 63.9929 | 63.9929 | 63.9929 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 48.6346 | 10% | 1 | 12 | 0 | 1.4211e-14 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 12.1586 | 63.9929 | 63.9929 | 63.9929 | 63.9929 | 0 | 0 | 0 | 0 | 0 | TRUE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 12.1586 | 4 | 3.3774 | 0.25 | TRUE | TRUE | 105361 | 12.1586 | 63.9929 | 12.1586 | 63.9929 | 51.1943 | 48.6346 | 63.9929 | 63.9929 | 62.7504 | 47.3587 | 63.9929 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 48.6346 | 10% | 1 | 12 | 0 | 1.4211e-14 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 12.1586 | 63.9929 | 63.9929 | 63.9929 | 63.9929 | 0 | 0 | 0 | 0 | 1.2425 | FALSE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 12.1586 | 4 | 6.7548 | 0.5 | TRUE | TRUE | 105361 | 12.1586 | 63.9929 | 12.1586 | 63.9929 | 51.1943 | 48.6346 | 63.9929 | 63.9929 | 61.508 | 30.7245 | 63.9929 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 48.6346 | 10% | 1 | 12 | 0 | 1.4211e-14 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 12.1586 | 63.9929 | 63.9929 | 63.9929 | 63.9929 | 0 | 0 | 0 | 0 | 2.4849 | FALSE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 12.1586 | 4 | 10.1322 | 0.75 | TRUE | TRUE | 105361 | 12.1586 | 63.9929 | 12.1586 | 63.9929 | 51.1943 | 48.6346 | 63.9929 | 63.9929 | 60.2655 | 14.0903 | 63.9929 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 48.6346 | 10% | 1 | 12 | 0 | 1.4211e-14 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 12.1586 | 63.9929 | 63.9929 | 63.9929 | 63.9929 | 0 | 0 | 0 | 0 | 3.7274 | FALSE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 12.1586 | 4 | 13.5096 | 1 | TRUE | TRUE | 105361 | 12.1586 | 63.9929 | 12.1586 | 63.9929 | 51.1943 | 48.6346 | 63.9929 | 63.9929 | 59.023 | 0.27501 | 63.9929 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 48.6346 | 10% | 1 | 12 | 0 | 1.4211e-14 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 12.1586 | 63.9929 | 63.9929 | 63.9929 | 63.9929 | 0 | 0 | 0 | 0 | 4.9698 | FALSE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 12.1586 | 8 | 0 | 0 | FALSE | TRUE | 105313 | 12.1586 | 127.9858 | 12.1586 | 127.9858 | 102.3886 | 97.2692 | 127.9858 | 127.9858 | 127.9858 | 127.9858 | 127.9858 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 97.2692 | 10% | 1 | 12 | 0 | 3.0198e-14 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 12.1586 | 127.9858 | 127.9858 | 127.9858 | 127.9858 | 0 | 0 | 0 | 0 | 0 | TRUE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 12.1586 | 8 | 3.3774 | 0.25 | TRUE | TRUE | 105313 | 12.1586 | 127.9858 | 12.1586 | 127.9858 | 102.3886 | 97.2692 | 127.9858 | 127.9858 | 122.8492 | 99.1413 | 127.9858 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 97.2692 | 10% | 1 | 12 | 0 | 3.0198e-14 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 12.1586 | 127.9858 | 127.9858 | 127.9858 | 127.9858 | 0 | 0 | 0 | 0 | 5.1366 | FALSE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 12.1586 | 8 | 6.7548 | 0.5 | TRUE | TRUE | 105313 | 12.1586 | 127.9858 | 12.1586 | 127.9858 | 102.3886 | 97.2692 | 127.9858 | 127.9858 | 117.7126 | 70.2968 | 127.9858 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 97.2692 | 10% | 1 | 12 | 0 | 3.0198e-14 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 12.1586 | 127.9858 | 127.9858 | 127.9858 | 127.9858 | 0 | 0 | 0 | 0 | 10.2731 | FALSE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 12.1586 | 8 | 10.1322 | 0.75 | TRUE | TRUE | 105313 | 12.1586 | 127.9858 | 12.1586 | 127.9858 | 102.3886 | 97.2692 | 127.9858 | 127.9858 | 112.5761 | 41.4524 | 127.9858 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 97.2692 | 10% | 1 | 12 | 0 | 3.0198e-14 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 12.1586 | 127.9858 | 127.9858 | 127.9858 | 127.9858 | 0 | 0 | 0 | 0 | 15.4097 | FALSE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 12.1586 | 8 | 13.5096 | 1 | TRUE | TRUE | 105313 | 12.1586 | 127.9858 | 12.1586 | 127.9858 | 102.3886 | 97.2692 | 127.9858 | 127.9858 | 107.4395 | 12.9545 | 127.9858 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 97.2692 | 10% | 1 | 12 | 0 | 3.0198e-14 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 12.1586 | 127.9858 | 127.9858 | 127.9858 | 127.9858 | 0 | 0 | 0 | 0 | 20.5462 | FALSE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 13.5096 | 1 | 0 | 0 | FALSE | TRUE | 105397 | 13.5096 | 17.7758 | 13.5096 | 17.7758 | 14.2206 | 13.5096 | 17.7758 | 17.7758 | 17.7758 | 17.7758 | 17.7758 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 13.5096 | 10% | 1 | 12 | 0 | 0 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 13.5096 | 17.7758 | 17.7758 | 17.7758 | 17.7758 | 0 | 0 | 0 | 0 | 0 | TRUE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 13.5096 | 1 | 3.3774 | 0.25 | TRUE | TRUE | 105397 | 13.5096 | 17.7758 | 13.5096 | 17.7758 | 14.2206 | 13.5096 | 17.7758 | 17.7758 | 17.6871 | 12.8875 | 17.7758 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 13.5096 | 10% | 1 | 12 | 0 | 0 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 13.5096 | 17.7758 | 17.7758 | 17.7758 | 17.7758 | 0 | 0 | 0 | 0 | 0.088688 | FALSE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 13.5096 | 1 | 6.7548 | 0.5 | TRUE | TRUE | 105397 | 13.5096 | 17.7758 | 13.5096 | 17.7758 | 14.2206 | 13.5096 | 17.7758 | 17.7758 | 17.5984 | 7.9991 | 17.7758 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 13.5096 | 10% | 1 | 12 | 0 | 0 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 13.5096 | 17.7758 | 17.7758 | 17.7758 | 17.7758 | 0 | 0 | 0 | 0 | 0.17738 | FALSE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 13.5096 | 1 | 10.1322 | 0.75 | TRUE | TRUE | 105397 | 13.5096 | 17.7758 | 13.5096 | 17.7758 | 14.2206 | 13.5096 | 17.7758 | 17.7758 | 17.5097 | 3.1108 | 17.7758 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 13.5096 | 10% | 1 | 12 | 0 | 0 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 13.5096 | 17.7758 | 17.7758 | 17.7758 | 17.7758 | 0 | 0 | 0 | 0 | 0.26606 | FALSE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 13.5096 | 1 | 13.5096 | 1 | TRUE | TRUE | 105397 | 13.5096 | 17.7758 | 13.5096 | 17.7758 | 14.2206 | 13.5096 | 17.7758 | 17.7758 | 17.421 | 2.5867e-10 | 17.7758 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 13.5096 | 10% | 1 | 12 | 0 | 0 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 13.5096 | 17.7758 | 17.7758 | 17.7758 | 17.7758 | 0 | 0 | 0 | 0 | 0.35475 | FALSE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 13.5096 | 2 | 0 | 0 | FALSE | TRUE | 105385 | 13.5096 | 35.5516 | 13.5096 | 35.5516 | 28.4413 | 27.0192 | 35.5516 | 35.5516 | 35.5516 | 35.5516 | 35.5516 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 27.0192 | 10% | 1 | 12 | 0 | 0 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 13.5096 | 35.5516 | 35.5516 | 35.5516 | 35.5516 | 0 | 0 | 0 | 0 | 0 | TRUE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 13.5096 | 2 | 3.3774 | 0.25 | TRUE | TRUE | 105385 | 13.5096 | 35.5516 | 13.5096 | 35.5516 | 28.4413 | 27.0192 | 35.5516 | 35.5516 | 35.2509 | 26.7311 | 35.5516 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 27.0192 | 10% | 1 | 12 | 0 | 0 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 13.5096 | 35.5516 | 35.5516 | 35.5516 | 35.5516 | 0 | 0 | 0 | 0 | 0.30075 | FALSE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 13.5096 | 2 | 6.7548 | 0.5 | TRUE | TRUE | 105385 | 13.5096 | 35.5516 | 13.5096 | 35.5516 | 28.4413 | 27.0192 | 35.5516 | 35.5516 | 34.9501 | 17.9106 | 35.5516 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 27.0192 | 10% | 1 | 12 | 0 | 0 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 13.5096 | 35.5516 | 35.5516 | 35.5516 | 35.5516 | 0 | 0 | 0 | 0 | 0.6015 | FALSE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 13.5096 | 2 | 10.1322 | 0.75 | TRUE | TRUE | 105385 | 13.5096 | 35.5516 | 13.5096 | 35.5516 | 28.4413 | 27.0192 | 35.5516 | 35.5516 | 34.6494 | 9.09 | 35.5516 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 27.0192 | 10% | 1 | 12 | 0 | 0 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 13.5096 | 35.5516 | 35.5516 | 35.5516 | 35.5516 | 0 | 0 | 0 | 0 | 0.90225 | FALSE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 13.5096 | 2 | 13.5096 | 1 | TRUE | TRUE | 105385 | 13.5096 | 35.5516 | 13.5096 | 35.5516 | 28.4413 | 27.0192 | 35.5516 | 35.5516 | 34.3486 | 0.72446 | 35.5516 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 27.0192 | 10% | 1 | 12 | 0 | 0 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 13.5096 | 35.5516 | 35.5516 | 35.5516 | 35.5516 | 0 | 0 | 0 | 0 | 1.203 | FALSE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 13.5096 | 4 | 0 | 0 | FALSE | TRUE | 105361 | 13.5096 | 71.1032 | 13.5096 | 71.1032 | 56.8826 | 54.0384 | 71.1032 | 71.1032 | 71.1032 | 71.1032 | 71.1032 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 54.0384 | 10% | 1 | 12 | 0 | 0 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 13.5096 | 71.1032 | 71.1032 | 71.1032 | 71.1032 | 0 | 0 | 0 | 0 | 0 | TRUE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 13.5096 | 4 | 3.3774 | 0.25 | TRUE | TRUE | 105361 | 13.5096 | 71.1032 | 13.5096 | 71.1032 | 56.8826 | 54.0384 | 71.1032 | 71.1032 | 69.8607 | 54.469 | 71.1032 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 54.0384 | 10% | 1 | 12 | 0 | 0 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 13.5096 | 71.1032 | 71.1032 | 71.1032 | 71.1032 | 0 | 0 | 0 | 0 | 1.2425 | FALSE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 13.5096 | 4 | 6.7548 | 0.5 | TRUE | TRUE | 105361 | 13.5096 | 71.1032 | 13.5096 | 71.1032 | 56.8826 | 54.0384 | 71.1032 | 71.1032 | 68.6183 | 37.8348 | 71.1032 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 54.0384 | 10% | 1 | 12 | 0 | 0 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 13.5096 | 71.1032 | 71.1032 | 71.1032 | 71.1032 | 0 | 0 | 0 | 0 | 2.4849 | FALSE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 13.5096 | 4 | 10.1322 | 0.75 | TRUE | TRUE | 105361 | 13.5096 | 71.1032 | 13.5096 | 71.1032 | 56.8826 | 54.0384 | 71.1032 | 71.1032 | 67.3758 | 21.2006 | 71.1032 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 54.0384 | 10% | 1 | 12 | 0 | 0 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 13.5096 | 71.1032 | 71.1032 | 71.1032 | 71.1032 | 0 | 0 | 0 | 0 | 3.7274 | FALSE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 13.5096 | 4 | 13.5096 | 1 | TRUE | TRUE | 105361 | 13.5096 | 71.1032 | 13.5096 | 71.1032 | 56.8826 | 54.0384 | 71.1032 | 71.1032 | 66.1334 | 4.7397 | 71.1032 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 54.0384 | 10% | 1 | 12 | 0 | 0 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 13.5096 | 71.1032 | 71.1032 | 71.1032 | 71.1032 | 0 | 0 | 0 | 0 | 4.9698 | FALSE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 13.5096 | 8 | 0 | 0 | FALSE | TRUE | 105313 | 13.5096 | 142.2064 | 13.5096 | 142.2064 | 113.7651 | 108.0769 | 142.2064 | 142.2064 | 142.2064 | 142.2064 | 142.2064 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 108.0769 | 10% | 1 | 12 | 0 | 0 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 13.5096 | 142.2064 | 142.2064 | 142.2064 | 142.2064 | 0 | 0 | 0 | 0 | 0 | TRUE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 13.5096 | 8 | 3.3774 | 0.25 | TRUE | TRUE | 105313 | 13.5096 | 142.2064 | 13.5096 | 142.2064 | 113.7651 | 108.0769 | 142.2064 | 142.2064 | 137.0698 | 113.3619 | 142.2064 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 108.0769 | 10% | 1 | 12 | 0 | 0 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 13.5096 | 142.2064 | 142.2064 | 142.2064 | 142.2064 | 0 | 0 | 0 | 0 | 5.1366 | FALSE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 13.5096 | 8 | 6.7548 | 0.5 | TRUE | TRUE | 105313 | 13.5096 | 142.2064 | 13.5096 | 142.2064 | 113.7651 | 108.0769 | 142.2064 | 142.2064 | 131.9333 | 84.5175 | 142.2064 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 108.0769 | 10% | 1 | 12 | 0 | 0 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 13.5096 | 142.2064 | 142.2064 | 142.2064 | 142.2064 | 0 | 0 | 0 | 0 | 10.2731 | FALSE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 13.5096 | 8 | 10.1322 | 0.75 | TRUE | TRUE | 105313 | 13.5096 | 142.2064 | 13.5096 | 142.2064 | 113.7651 | 108.0769 | 142.2064 | 142.2064 | 126.7967 | 55.673 | 142.2064 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 108.0769 | 10% | 1 | 12 | 0 | 0 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 13.5096 | 142.2064 | 142.2064 | 142.2064 | 142.2064 | 0 | 0 | 0 | 0 | 15.4097 | FALSE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 13.5096 | 8 | 13.5096 | 1 | TRUE | TRUE | 105313 | 13.5096 | 142.2064 | 13.5096 | 142.2064 | 113.7651 | 108.0769 | 142.2064 | 142.2064 | 121.6602 | 27.0018 | 142.2064 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 108.0769 | 10% | 1 | 12 | 0 | 0 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 13.5096 | 142.2064 | 142.2064 | 142.2064 | 142.2064 | 0 | 0 | 0 | 0 | 20.5462 | FALSE

## Battery_Only
CandidateKey | GridID | SubstationID | CandidateLineID | BaseDCMW | ServiceTarget | ServedLoadMW | OutageDurationHours | PVCapacityMW | PVCapacityRatioToDC | PVOutageCreditEnabled | PVCanRechargeBatteryDuringOutage | HistoricalOutageWindowsEvaluated | BatteryPowerMW | BatteryInstalledMWh | UnmarginedBatteryPowerMW | UnmarginedBatteryInstalledMWh | BatteryUsableSOCWindowMWh | BatteryDeliverableFromStartMWh | P99EnergyOptimalBatteryInstalledMWhByHistoricalStart | P95EnergyOptimalBatteryInstalledMWhByHistoricalStart | P50EnergyOptimalBatteryInstalledMWhByHistoricalStart | MinimumEnergyOptimalBatteryInstalledMWhByHistoricalStart | WorstEnergyOptimalHistoricalStartMWh | CriticalHistoricalStartUTC | CriticalHistoricalStartLocal | CriticalWindowPVAvailableMWh | CriticalWindowPVUsedDirectMWh | CriticalWindowPVChargedToBatteryACMWh | CriticalWindowPVCurtailedMWh | CriticalWindowBatteryDeliveredMWh | CriticalWindowMinimumSOCFraction | ConstraintGenerationIterations | FinalCriticalWindowCount | FinalHistoricalViolationCount | FinalMinimumSOCMarginMWh | FinalMaximumPowerDeficitMW | BatteryStartSOCFraction | BatteryMinSOCFraction | BatteryMaxSOCFraction | BatteryChargeEfficiency | BatteryDischargeEfficiency | EnergyTermination | PowerTermination | BatteryOnlyPowerMW | BatteryOnlyInstalledMWh | BatteryOnlyP99InstalledMWh | BatteryOnlyP95InstalledMWh | BatteryOnlyP50InstalledMWh | RobustBatteryEnergySavingsFromPVMWh | RobustBatteryPowerSavingsFromPVMW | P99BatteryEnergySavingsFromPVMWh | P95BatteryEnergySavingsFromPVMWh | P50BatteryEnergySavingsFromPVMWh | ParetoEfficient
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 6.7548 | 1 | 0 | 0 | FALSE | TRUE | 105397 | 6.7548 | 8.8879 | 6.7548 | 8.8879 | 7.1103 | 6.7548 | 8.8879 | 8.8879 | 8.8879 | 8.8879 | 8.8879 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 6.7548 | 10% | 1 | 12 | 0 | 0 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 6.7548 | 8.8879 | 8.8879 | 8.8879 | 8.8879 | 0 | 0 | 0 | 0 | 0 | TRUE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 6.7548 | 2 | 0 | 0 | FALSE | TRUE | 105385 | 6.7548 | 17.7758 | 6.7548 | 17.7758 | 14.2206 | 13.5096 | 17.7758 | 17.7758 | 17.7758 | 17.7758 | 17.7758 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 13.5096 | 10% | 1 | 12 | 0 | 0 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 6.7548 | 17.7758 | 17.7758 | 17.7758 | 17.7758 | 0 | 0 | 0 | 0 | 0 | TRUE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 6.7548 | 4 | 0 | 0 | FALSE | TRUE | 105361 | 6.7548 | 35.5516 | 6.7548 | 35.5516 | 28.4413 | 27.0192 | 35.5516 | 35.5516 | 35.5516 | 35.5516 | 35.5516 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 27.0192 | 10% | 1 | 12 | 0 | 0 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 6.7548 | 35.5516 | 35.5516 | 35.5516 | 35.5516 | 0 | 0 | 0 | 0 | 0 | TRUE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 6.7548 | 8 | 0 | 0 | FALSE | TRUE | 105313 | 6.7548 | 71.1032 | 6.7548 | 71.1032 | 56.8826 | 54.0384 | 71.1032 | 71.1032 | 71.1032 | 71.1032 | 71.1032 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 54.0384 | 10% | 1 | 12 | 0 | 0 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 6.7548 | 71.1032 | 71.1032 | 71.1032 | 71.1032 | 0 | 0 | 0 | 0 | 0 | TRUE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 10.1322 | 1 | 0 | 0 | FALSE | TRUE | 105397 | 10.1322 | 13.3319 | 10.1322 | 13.3319 | 10.6655 | 10.1322 | 13.3319 | 13.3319 | 13.3319 | 13.3319 | 13.3319 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 10.1322 | 10% | 1 | 12 | 0 | 1.5543e-15 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 10.1322 | 13.3319 | 13.3319 | 13.3319 | 13.3319 | 0 | 0 | 0 | 0 | 0 | TRUE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 10.1322 | 2 | 0 | 0 | FALSE | TRUE | 105385 | 10.1322 | 26.6637 | 10.1322 | 26.6637 | 21.331 | 20.2644 | 26.6637 | 26.6637 | 26.6637 | 26.6637 | 26.6637 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 20.2644 | 10% | 1 | 12 | 0 | 3.1086e-15 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 10.1322 | 26.6637 | 26.6637 | 26.6637 | 26.6637 | 0 | 0 | 0 | 0 | 0 | TRUE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 10.1322 | 4 | 0 | 0 | FALSE | TRUE | 105361 | 10.1322 | 53.3274 | 10.1322 | 53.3274 | 42.6619 | 40.5288 | 53.3274 | 53.3274 | 53.3274 | 53.3274 | 53.3274 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 40.5288 | 10% | 1 | 12 | 0 | -1.6875e-14 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 10.1322 | 53.3274 | 53.3274 | 53.3274 | 53.3274 | 0 | 0 | 0 | 0 | 0 | TRUE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 10.1322 | 8 | 0 | 0 | FALSE | TRUE | 105313 | 10.1322 | 106.6548 | 10.1322 | 106.6548 | 85.3238 | 81.0576 | 106.6548 | 106.6548 | 106.6548 | 106.6548 | 106.6548 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 81.0576 | 10% | 1 | 12 | 0 | 4.6185e-14 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 10.1322 | 106.6548 | 106.6548 | 106.6548 | 106.6548 | 0 | 0 | 0 | 0 | 0 | TRUE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 12.1586 | 1 | 0 | 0 | FALSE | TRUE | 105397 | 12.1586 | 15.9982 | 12.1586 | 15.9982 | 12.7986 | 12.1586 | 15.9982 | 15.9982 | 15.9982 | 15.9982 | 15.9982 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 12.1586 | 10% | 1 | 12 | 0 | 4.4409e-16 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 12.1586 | 15.9982 | 15.9982 | 15.9982 | 15.9982 | 0 | 0 | 0 | 0 | 0 | TRUE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 12.1586 | 2 | 0 | 0 | FALSE | TRUE | 105385 | 12.1586 | 31.9964 | 12.1586 | 31.9964 | 25.5972 | 24.3173 | 31.9964 | 31.9964 | 31.9964 | 31.9964 | 31.9964 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 24.3173 | 10% | 1 | 12 | 0 | 2.2204e-15 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 12.1586 | 31.9964 | 31.9964 | 31.9964 | 31.9964 | 0 | 0 | 0 | 0 | 0 | TRUE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 12.1586 | 4 | 0 | 0 | FALSE | TRUE | 105361 | 12.1586 | 63.9929 | 12.1586 | 63.9929 | 51.1943 | 48.6346 | 63.9929 | 63.9929 | 63.9929 | 63.9929 | 63.9929 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 48.6346 | 10% | 1 | 12 | 0 | 1.4211e-14 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 12.1586 | 63.9929 | 63.9929 | 63.9929 | 63.9929 | 0 | 0 | 0 | 0 | 0 | TRUE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 12.1586 | 8 | 0 | 0 | FALSE | TRUE | 105313 | 12.1586 | 127.9858 | 12.1586 | 127.9858 | 102.3886 | 97.2692 | 127.9858 | 127.9858 | 127.9858 | 127.9858 | 127.9858 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 97.2692 | 10% | 1 | 12 | 0 | 3.0198e-14 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 12.1586 | 127.9858 | 127.9858 | 127.9858 | 127.9858 | 0 | 0 | 0 | 0 | 0 | TRUE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 13.5096 | 1 | 0 | 0 | FALSE | TRUE | 105397 | 13.5096 | 17.7758 | 13.5096 | 17.7758 | 14.2206 | 13.5096 | 17.7758 | 17.7758 | 17.7758 | 17.7758 | 17.7758 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 13.5096 | 10% | 1 | 12 | 0 | 0 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 13.5096 | 17.7758 | 17.7758 | 17.7758 | 17.7758 | 0 | 0 | 0 | 0 | 0 | TRUE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 13.5096 | 2 | 0 | 0 | FALSE | TRUE | 105385 | 13.5096 | 35.5516 | 13.5096 | 35.5516 | 28.4413 | 27.0192 | 35.5516 | 35.5516 | 35.5516 | 35.5516 | 35.5516 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 27.0192 | 10% | 1 | 12 | 0 | 0 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 13.5096 | 35.5516 | 35.5516 | 35.5516 | 35.5516 | 0 | 0 | 0 | 0 | 0 | TRUE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 13.5096 | 4 | 0 | 0 | FALSE | TRUE | 105361 | 13.5096 | 71.1032 | 13.5096 | 71.1032 | 56.8826 | 54.0384 | 71.1032 | 71.1032 | 71.1032 | 71.1032 | 71.1032 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 54.0384 | 10% | 1 | 12 | 0 | 0 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 13.5096 | 71.1032 | 71.1032 | 71.1032 | 71.1032 | 0 | 0 | 0 | 0 | 0 | TRUE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 13.5096 | 8 | 0 | 0 | FALSE | TRUE | 105313 | 13.5096 | 142.2064 | 13.5096 | 142.2064 | 113.7651 | 108.0769 | 142.2064 | 142.2064 | 142.2064 | 142.2064 | 142.2064 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 108.0769 | 10% | 1 | 12 | 0 | 0 | 0 | 90% | 10% | 100% | 0.95 | 0.95 | optimal | optimal | 13.5096 | 142.2064 | 142.2064 | 142.2064 | 142.2064 | 0 | 0 | 0 | 0 | 0 | TRUE

## PV_Battery_Tradeoff
CandidateKey | GridID | BaseDCMW | ServiceTarget | OutageDurationHours | PVCapacityMW | PVCapacityRatioToDC | BatteryPowerMW | BatteryInstalledMWh | RobustBatteryEnergySavingsFromPVMWh | RobustBatteryPowerSavingsFromPVMW | P95BatteryEnergySavingsFromPVMWh | P50BatteryEnergySavingsFromPVMWh | ParetoEfficient
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 0.5 | 1 | 0 | 0 | 6.7548 | 8.8879 | 0 | 0 | 0 | 0 | TRUE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 0.5 | 1 | 3.3774 | 0.25 | 6.7548 | 8.8879 | 0 | 0 | 0 | 0.088688 | FALSE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 0.5 | 1 | 6.7548 | 0.5 | 6.7548 | 8.8879 | 0 | 0 | 0 | 0.17738 | FALSE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 0.5 | 1 | 10.1322 | 0.75 | 6.7548 | 8.8879 | 0 | 0 | 0 | 0.26606 | FALSE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 0.5 | 1 | 13.5096 | 1 | 6.7548 | 8.8879 | 0 | 0 | 0 | 0.35475 | FALSE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 0.5 | 2 | 0 | 0 | 6.7548 | 17.7758 | 0 | 0 | 0 | 0 | TRUE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 0.5 | 2 | 3.3774 | 0.25 | 6.7548 | 17.7758 | 0 | 0 | 0 | 0.30075 | FALSE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 0.5 | 2 | 6.7548 | 0.5 | 6.7548 | 17.7758 | 0 | 0 | 0 | 0.6015 | FALSE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 0.5 | 2 | 10.1322 | 0.75 | 6.7548 | 17.7758 | 0 | 0 | 0 | 0.90225 | FALSE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 0.5 | 2 | 13.5096 | 1 | 6.7548 | 17.7758 | 0 | 0 | 0 | 1.203 | FALSE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 0.5 | 4 | 0 | 0 | 6.7548 | 35.5516 | 0 | 0 | 0 | 0 | TRUE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 0.5 | 4 | 3.3774 | 0.25 | 6.7548 | 35.5516 | 0 | 0 | 0 | 1.2425 | FALSE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 0.5 | 4 | 6.7548 | 0.5 | 6.7548 | 35.5516 | 0 | 0 | 0 | 2.4849 | FALSE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 0.5 | 4 | 10.1322 | 0.75 | 6.7548 | 35.5516 | 0 | 0 | 0 | 3.7274 | FALSE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 0.5 | 4 | 13.5096 | 1 | 6.7548 | 35.5516 | 0 | 0 | 0 | 4.9698 | FALSE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 0.5 | 8 | 0 | 0 | 6.7548 | 71.1032 | 0 | 0 | 0 | 0 | TRUE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 0.5 | 8 | 3.3774 | 0.25 | 6.7548 | 71.1032 | 0 | 0 | 0 | 5.1366 | FALSE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 0.5 | 8 | 6.7548 | 0.5 | 6.7548 | 71.1032 | 0 | 0 | 0 | 10.2731 | FALSE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 0.5 | 8 | 10.1322 | 0.75 | 6.7548 | 71.1032 | 0 | 0 | 0 | 15.4002 | FALSE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 0.5 | 8 | 13.5096 | 1 | 6.7548 | 71.1032 | 0 | 0 | 0 | 20.1635 | FALSE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 0.75 | 1 | 0 | 0 | 10.1322 | 13.3319 | 0 | 0 | 0 | 0 | TRUE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 0.75 | 1 | 3.3774 | 0.25 | 10.1322 | 13.3319 | 0 | 0 | 0 | 0.088688 | FALSE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 0.75 | 1 | 6.7548 | 0.5 | 10.1322 | 13.3319 | 0 | 0 | 0 | 0.17738 | FALSE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 0.75 | 1 | 10.1322 | 0.75 | 10.1322 | 13.3319 | 0 | 0 | 0 | 0.26606 | FALSE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 0.75 | 1 | 13.5096 | 1 | 10.1322 | 13.3319 | 0 | 0 | 0 | 0.35475 | FALSE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 0.75 | 2 | 0 | 0 | 10.1322 | 26.6637 | 0 | 0 | 0 | 0 | TRUE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 0.75 | 2 | 3.3774 | 0.25 | 10.1322 | 26.6637 | 0 | 0 | 0 | 0.30075 | FALSE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 0.75 | 2 | 6.7548 | 0.5 | 10.1322 | 26.6637 | 0 | 0 | 0 | 0.6015 | FALSE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 0.75 | 2 | 10.1322 | 0.75 | 10.1322 | 26.6637 | 0 | 0 | 0 | 0.90225 | FALSE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 0.75 | 2 | 13.5096 | 1 | 10.1322 | 26.6637 | 0 | 0 | 0 | 1.203 | FALSE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 0.75 | 4 | 0 | 0 | 10.1322 | 53.3274 | 0 | 0 | 0 | 0 | TRUE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 0.75 | 4 | 3.3774 | 0.25 | 10.1322 | 53.3274 | 0 | 0 | 0 | 1.2425 | FALSE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 0.75 | 4 | 6.7548 | 0.5 | 10.1322 | 53.3274 | 0 | 0 | 0 | 2.4849 | FALSE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 0.75 | 4 | 10.1322 | 0.75 | 10.1322 | 53.3274 | 0 | 0 | 0 | 3.7274 | FALSE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 0.75 | 4 | 13.5096 | 1 | 10.1322 | 53.3274 | 0 | 0 | 0 | 4.9698 | FALSE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 0.75 | 8 | 0 | 0 | 10.1322 | 106.6548 | 0 | 0 | 0 | 0 | TRUE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 0.75 | 8 | 3.3774 | 0.25 | 10.1322 | 106.6548 | 0 | 0 | 0 | 5.1366 | FALSE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 0.75 | 8 | 6.7548 | 0.5 | 10.1322 | 106.6548 | 0 | 0 | 0 | 10.2731 | FALSE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 0.75 | 8 | 10.1322 | 0.75 | 10.1322 | 106.6548 | 0 | 0 | 0 | 15.4097 | FALSE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 0.75 | 8 | 13.5096 | 1 | 10.1322 | 106.6548 | 0 | 0 | 0 | 20.5462 | FALSE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 0.9 | 1 | 0 | 0 | 12.1586 | 15.9982 | 0 | 0 | 0 | 0 | TRUE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 0.9 | 1 | 3.3774 | 0.25 | 12.1586 | 15.9982 | 0 | 0 | 0 | 0.088688 | FALSE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 0.9 | 1 | 6.7548 | 0.5 | 12.1586 | 15.9982 | 0 | 0 | 0 | 0.17738 | FALSE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 0.9 | 1 | 10.1322 | 0.75 | 12.1586 | 15.9982 | 0 | 0 | 0 | 0.26606 | FALSE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 0.9 | 1 | 13.5096 | 1 | 12.1586 | 15.9982 | 0 | 0 | 0 | 0.35475 | FALSE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 0.9 | 2 | 0 | 0 | 12.1586 | 31.9964 | 0 | 0 | 0 | 0 | TRUE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 0.9 | 2 | 3.3774 | 0.25 | 12.1586 | 31.9964 | 0 | 0 | 0 | 0.30075 | FALSE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 0.9 | 2 | 6.7548 | 0.5 | 12.1586 | 31.9964 | 0 | 0 | 0 | 0.6015 | FALSE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 0.9 | 2 | 10.1322 | 0.75 | 12.1586 | 31.9964 | 0 | 0 | 0 | 0.90225 | FALSE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 0.9 | 2 | 13.5096 | 1 | 12.1586 | 31.9964 | 0 | 0 | 0 | 1.203 | FALSE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 0.9 | 4 | 0 | 0 | 12.1586 | 63.9929 | 0 | 0 | 0 | 0 | TRUE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 0.9 | 4 | 3.3774 | 0.25 | 12.1586 | 63.9929 | 0 | 0 | 0 | 1.2425 | FALSE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 0.9 | 4 | 6.7548 | 0.5 | 12.1586 | 63.9929 | 0 | 0 | 0 | 2.4849 | FALSE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 0.9 | 4 | 10.1322 | 0.75 | 12.1586 | 63.9929 | 0 | 0 | 0 | 3.7274 | FALSE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 0.9 | 4 | 13.5096 | 1 | 12.1586 | 63.9929 | 0 | 0 | 0 | 4.9698 | FALSE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 0.9 | 8 | 0 | 0 | 12.1586 | 127.9858 | 0 | 0 | 0 | 0 | TRUE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 0.9 | 8 | 3.3774 | 0.25 | 12.1586 | 127.9858 | 0 | 0 | 0 | 5.1366 | FALSE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 0.9 | 8 | 6.7548 | 0.5 | 12.1586 | 127.9858 | 0 | 0 | 0 | 10.2731 | FALSE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 0.9 | 8 | 10.1322 | 0.75 | 12.1586 | 127.9858 | 0 | 0 | 0 | 15.4097 | FALSE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 0.9 | 8 | 13.5096 | 1 | 12.1586 | 127.9858 | 0 | 0 | 0 | 20.5462 | FALSE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 1 | 1 | 0 | 0 | 13.5096 | 17.7758 | 0 | 0 | 0 | 0 | TRUE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 1 | 1 | 3.3774 | 0.25 | 13.5096 | 17.7758 | 0 | 0 | 0 | 0.088688 | FALSE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 1 | 1 | 6.7548 | 0.5 | 13.5096 | 17.7758 | 0 | 0 | 0 | 0.17738 | FALSE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 1 | 1 | 10.1322 | 0.75 | 13.5096 | 17.7758 | 0 | 0 | 0 | 0.26606 | FALSE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 1 | 1 | 13.5096 | 1 | 13.5096 | 17.7758 | 0 | 0 | 0 | 0.35475 | FALSE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 1 | 2 | 0 | 0 | 13.5096 | 35.5516 | 0 | 0 | 0 | 0 | TRUE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 1 | 2 | 3.3774 | 0.25 | 13.5096 | 35.5516 | 0 | 0 | 0 | 0.30075 | FALSE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 1 | 2 | 6.7548 | 0.5 | 13.5096 | 35.5516 | 0 | 0 | 0 | 0.6015 | FALSE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 1 | 2 | 10.1322 | 0.75 | 13.5096 | 35.5516 | 0 | 0 | 0 | 0.90225 | FALSE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 1 | 2 | 13.5096 | 1 | 13.5096 | 35.5516 | 0 | 0 | 0 | 1.203 | FALSE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 1 | 4 | 0 | 0 | 13.5096 | 71.1032 | 0 | 0 | 0 | 0 | TRUE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 1 | 4 | 3.3774 | 0.25 | 13.5096 | 71.1032 | 0 | 0 | 0 | 1.2425 | FALSE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 1 | 4 | 6.7548 | 0.5 | 13.5096 | 71.1032 | 0 | 0 | 0 | 2.4849 | FALSE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 1 | 4 | 10.1322 | 0.75 | 13.5096 | 71.1032 | 0 | 0 | 0 | 3.7274 | FALSE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 1 | 4 | 13.5096 | 1 | 13.5096 | 71.1032 | 0 | 0 | 0 | 4.9698 | FALSE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 1 | 8 | 0 | 0 | 13.5096 | 142.2064 | 0 | 0 | 0 | 0 | TRUE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 1 | 8 | 3.3774 | 0.25 | 13.5096 | 142.2064 | 0 | 0 | 0 | 5.1366 | FALSE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 1 | 8 | 6.7548 | 0.5 | 13.5096 | 142.2064 | 0 | 0 | 0 | 10.2731 | FALSE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 1 | 8 | 10.1322 | 0.75 | 13.5096 | 142.2064 | 0 | 0 | 0 | 15.4097 | FALSE
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 1 | 8 | 13.5096 | 1 | 13.5096 | 142.2064 | 0 | 0 | 0 | 20.5462 | FALSE

## Critical_Window_Dispatch
CandidateKey | GridID | SubstationID | CandidateLineID | BaseDCMW | ServiceTarget | OutageDurationHours | PVCapacityMW | BatteryPowerMW | BatteryInstalledMWh | TimestampUTC | TimestampLocal | PVAvailabilityPU | PVAvailableMW | PVUsedDirectMW | PVExcessAvailableMW | BatteryChargeFromPVMW | PVCurtailedMW | BatteryDischargeMW | BatterySOCStartMWh | BatterySOCEndMWh | BatterySOCStartFraction | BatterySOCEndFraction | BatteryMinimumAllowedSOCMWh | ServedLoadMW | GridImportMW | UnservedLoadMW
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 1 | 0 | 6.7548 | 8.8879 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 7.9991 | 7.4066 | 90% | 83.33% | 0.88879 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 1 | 0 | 6.7548 | 8.8879 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 7.4066 | 6.8141 | 83.33% | 76.67% | 0.88879 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 1 | 0 | 6.7548 | 8.8879 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 6.8141 | 6.2215 | 76.67% | 70% | 0.88879 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 1 | 0 | 6.7548 | 8.8879 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 6.2215 | 5.629 | 70% | 63.33% | 0.88879 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 1 | 0 | 6.7548 | 8.8879 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 5.629 | 5.0365 | 63.33% | 56.67% | 0.88879 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 1 | 0 | 6.7548 | 8.8879 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 5.0365 | 4.444 | 56.67% | 50% | 0.88879 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 1 | 0 | 6.7548 | 8.8879 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 4.444 | 3.8514 | 50% | 43.33% | 0.88879 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 1 | 0 | 6.7548 | 8.8879 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 3.8514 | 3.2589 | 43.33% | 36.67% | 0.88879 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 1 | 0 | 6.7548 | 8.8879 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 3.2589 | 2.6664 | 36.67% | 30% | 0.88879 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 1 | 0 | 6.7548 | 8.8879 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 2.6664 | 2.0738 | 30% | 23.33% | 0.88879 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 1 | 0 | 6.7548 | 8.8879 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 2.0738 | 1.4813 | 23.33% | 16.67% | 0.88879 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 1 | 0 | 6.7548 | 8.8879 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 1.4813 | 0.88879 | 16.67% | 10% | 0.88879 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 1 | 3.3774 | 6.7548 | 8.8879 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 7.9991 | 7.4066 | 90% | 83.33% | 0.88879 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 1 | 3.3774 | 6.7548 | 8.8879 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 7.4066 | 6.8141 | 83.33% | 76.67% | 0.88879 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 1 | 3.3774 | 6.7548 | 8.8879 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 6.8141 | 6.2215 | 76.67% | 70% | 0.88879 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 1 | 3.3774 | 6.7548 | 8.8879 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 6.2215 | 5.629 | 70% | 63.33% | 0.88879 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 1 | 3.3774 | 6.7548 | 8.8879 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 5.629 | 5.0365 | 63.33% | 56.67% | 0.88879 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 1 | 3.3774 | 6.7548 | 8.8879 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 5.0365 | 4.444 | 56.67% | 50% | 0.88879 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 1 | 3.3774 | 6.7548 | 8.8879 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 4.444 | 3.8514 | 50% | 43.33% | 0.88879 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 1 | 3.3774 | 6.7548 | 8.8879 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 3.8514 | 3.2589 | 43.33% | 36.67% | 0.88879 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 1 | 3.3774 | 6.7548 | 8.8879 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 3.2589 | 2.6664 | 36.67% | 30% | 0.88879 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 1 | 3.3774 | 6.7548 | 8.8879 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 2.6664 | 2.0738 | 30% | 23.33% | 0.88879 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 1 | 3.3774 | 6.7548 | 8.8879 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 2.0738 | 1.4813 | 23.33% | 16.67% | 0.88879 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 1 | 3.3774 | 6.7548 | 8.8879 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 1.4813 | 0.88879 | 16.67% | 10% | 0.88879 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 1 | 6.7548 | 6.7548 | 8.8879 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 7.9991 | 7.4066 | 90% | 83.33% | 0.88879 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 1 | 6.7548 | 6.7548 | 8.8879 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 7.4066 | 6.8141 | 83.33% | 76.67% | 0.88879 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 1 | 6.7548 | 6.7548 | 8.8879 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 6.8141 | 6.2215 | 76.67% | 70% | 0.88879 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 1 | 6.7548 | 6.7548 | 8.8879 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 6.2215 | 5.629 | 70% | 63.33% | 0.88879 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 1 | 6.7548 | 6.7548 | 8.8879 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 5.629 | 5.0365 | 63.33% | 56.67% | 0.88879 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 1 | 6.7548 | 6.7548 | 8.8879 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 5.0365 | 4.444 | 56.67% | 50% | 0.88879 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 1 | 6.7548 | 6.7548 | 8.8879 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 4.444 | 3.8514 | 50% | 43.33% | 0.88879 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 1 | 6.7548 | 6.7548 | 8.8879 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 3.8514 | 3.2589 | 43.33% | 36.67% | 0.88879 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 1 | 6.7548 | 6.7548 | 8.8879 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 3.2589 | 2.6664 | 36.67% | 30% | 0.88879 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 1 | 6.7548 | 6.7548 | 8.8879 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 2.6664 | 2.0738 | 30% | 23.33% | 0.88879 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 1 | 6.7548 | 6.7548 | 8.8879 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 2.0738 | 1.4813 | 23.33% | 16.67% | 0.88879 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 1 | 6.7548 | 6.7548 | 8.8879 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 1.4813 | 0.88879 | 16.67% | 10% | 0.88879 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 1 | 10.1322 | 6.7548 | 8.8879 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 7.9991 | 7.4066 | 90% | 83.33% | 0.88879 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 1 | 10.1322 | 6.7548 | 8.8879 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 7.4066 | 6.8141 | 83.33% | 76.67% | 0.88879 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 1 | 10.1322 | 6.7548 | 8.8879 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 6.8141 | 6.2215 | 76.67% | 70% | 0.88879 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 1 | 10.1322 | 6.7548 | 8.8879 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 6.2215 | 5.629 | 70% | 63.33% | 0.88879 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 1 | 10.1322 | 6.7548 | 8.8879 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 5.629 | 5.0365 | 63.33% | 56.67% | 0.88879 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 1 | 10.1322 | 6.7548 | 8.8879 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 5.0365 | 4.444 | 56.67% | 50% | 0.88879 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 1 | 10.1322 | 6.7548 | 8.8879 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 4.444 | 3.8514 | 50% | 43.33% | 0.88879 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 1 | 10.1322 | 6.7548 | 8.8879 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 3.8514 | 3.2589 | 43.33% | 36.67% | 0.88879 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 1 | 10.1322 | 6.7548 | 8.8879 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 3.2589 | 2.6664 | 36.67% | 30% | 0.88879 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 1 | 10.1322 | 6.7548 | 8.8879 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 2.6664 | 2.0738 | 30% | 23.33% | 0.88879 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 1 | 10.1322 | 6.7548 | 8.8879 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 2.0738 | 1.4813 | 23.33% | 16.67% | 0.88879 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 1 | 10.1322 | 6.7548 | 8.8879 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 1.4813 | 0.88879 | 16.67% | 10% | 0.88879 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 1 | 13.5096 | 6.7548 | 8.8879 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 7.9991 | 7.4066 | 90% | 83.33% | 0.88879 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 1 | 13.5096 | 6.7548 | 8.8879 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 7.4066 | 6.8141 | 83.33% | 76.67% | 0.88879 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 1 | 13.5096 | 6.7548 | 8.8879 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 6.8141 | 6.2215 | 76.67% | 70% | 0.88879 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 1 | 13.5096 | 6.7548 | 8.8879 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 6.2215 | 5.629 | 70% | 63.33% | 0.88879 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 1 | 13.5096 | 6.7548 | 8.8879 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 5.629 | 5.0365 | 63.33% | 56.67% | 0.88879 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 1 | 13.5096 | 6.7548 | 8.8879 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 5.0365 | 4.444 | 56.67% | 50% | 0.88879 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 1 | 13.5096 | 6.7548 | 8.8879 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 4.444 | 3.8514 | 50% | 43.33% | 0.88879 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 1 | 13.5096 | 6.7548 | 8.8879 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 3.8514 | 3.2589 | 43.33% | 36.67% | 0.88879 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 1 | 13.5096 | 6.7548 | 8.8879 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 3.2589 | 2.6664 | 36.67% | 30% | 0.88879 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 1 | 13.5096 | 6.7548 | 8.8879 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 2.6664 | 2.0738 | 30% | 23.33% | 0.88879 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 1 | 13.5096 | 6.7548 | 8.8879 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 2.0738 | 1.4813 | 23.33% | 16.67% | 0.88879 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 1 | 13.5096 | 6.7548 | 8.8879 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 1.4813 | 0.88879 | 16.67% | 10% | 0.88879 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 0 | 6.7548 | 17.7758 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 15.9982 | 15.4057 | 90% | 86.67% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 0 | 6.7548 | 17.7758 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 15.4057 | 14.8132 | 86.67% | 83.33% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 0 | 6.7548 | 17.7758 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 14.8132 | 14.2206 | 83.33% | 80% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 0 | 6.7548 | 17.7758 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 14.2206 | 13.6281 | 80% | 76.67% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 0 | 6.7548 | 17.7758 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 13.6281 | 13.0356 | 76.67% | 73.33% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 0 | 6.7548 | 17.7758 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 13.0356 | 12.4431 | 73.33% | 70% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 0 | 6.7548 | 17.7758 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 12.4431 | 11.8505 | 70% | 66.67% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 0 | 6.7548 | 17.7758 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 11.8505 | 11.258 | 66.67% | 63.33% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 0 | 6.7548 | 17.7758 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 11.258 | 10.6655 | 63.33% | 60% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 0 | 6.7548 | 17.7758 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 10.6655 | 10.073 | 60% | 56.67% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 0 | 6.7548 | 17.7758 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 10.073 | 9.4804 | 56.67% | 53.33% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 0 | 6.7548 | 17.7758 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 9.4804 | 8.8879 | 53.33% | 50% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 0 | 6.7548 | 17.7758 | 2024-01-01 01:00 | 2023-12-31 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 8.8879 | 8.2954 | 50% | 46.67% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 0 | 6.7548 | 17.7758 | 2024-01-01 01:05 | 2023-12-31 20:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 8.2954 | 7.7028 | 46.67% | 43.33% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 0 | 6.7548 | 17.7758 | 2024-01-01 01:10 | 2023-12-31 20:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 7.7028 | 7.1103 | 43.33% | 40% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 0 | 6.7548 | 17.7758 | 2024-01-01 01:15 | 2023-12-31 20:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 7.1103 | 6.5178 | 40% | 36.67% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 0 | 6.7548 | 17.7758 | 2024-01-01 01:20 | 2023-12-31 20:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 6.5178 | 5.9253 | 36.67% | 33.33% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 0 | 6.7548 | 17.7758 | 2024-01-01 01:25 | 2023-12-31 20:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 5.9253 | 5.3327 | 33.33% | 30% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 0 | 6.7548 | 17.7758 | 2024-01-01 01:30 | 2023-12-31 20:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 5.3327 | 4.7402 | 30% | 26.67% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 0 | 6.7548 | 17.7758 | 2024-01-01 01:35 | 2023-12-31 20:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 4.7402 | 4.1477 | 26.67% | 23.33% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 0 | 6.7548 | 17.7758 | 2024-01-01 01:40 | 2023-12-31 20:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 4.1477 | 3.5552 | 23.33% | 20% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 0 | 6.7548 | 17.7758 | 2024-01-01 01:45 | 2023-12-31 20:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 3.5552 | 2.9626 | 20% | 16.67% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 0 | 6.7548 | 17.7758 | 2024-01-01 01:50 | 2023-12-31 20:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 2.9626 | 2.3701 | 16.67% | 13.33% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 0 | 6.7548 | 17.7758 | 2024-01-01 01:55 | 2023-12-31 20:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 2.3701 | 1.7776 | 13.33% | 10% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 3.3774 | 6.7548 | 17.7758 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 15.9982 | 15.4057 | 90% | 86.67% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 3.3774 | 6.7548 | 17.7758 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 15.4057 | 14.8132 | 86.67% | 83.33% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 3.3774 | 6.7548 | 17.7758 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 14.8132 | 14.2206 | 83.33% | 80% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 3.3774 | 6.7548 | 17.7758 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 14.2206 | 13.6281 | 80% | 76.67% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 3.3774 | 6.7548 | 17.7758 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 13.6281 | 13.0356 | 76.67% | 73.33% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 3.3774 | 6.7548 | 17.7758 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 13.0356 | 12.4431 | 73.33% | 70% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 3.3774 | 6.7548 | 17.7758 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 12.4431 | 11.8505 | 70% | 66.67% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 3.3774 | 6.7548 | 17.7758 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 11.8505 | 11.258 | 66.67% | 63.33% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 3.3774 | 6.7548 | 17.7758 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 11.258 | 10.6655 | 63.33% | 60% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 3.3774 | 6.7548 | 17.7758 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 10.6655 | 10.073 | 60% | 56.67% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 3.3774 | 6.7548 | 17.7758 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 10.073 | 9.4804 | 56.67% | 53.33% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 3.3774 | 6.7548 | 17.7758 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 9.4804 | 8.8879 | 53.33% | 50% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 3.3774 | 6.7548 | 17.7758 | 2024-01-01 01:00 | 2023-12-31 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 8.8879 | 8.2954 | 50% | 46.67% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 3.3774 | 6.7548 | 17.7758 | 2024-01-01 01:05 | 2023-12-31 20:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 8.2954 | 7.7028 | 46.67% | 43.33% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 3.3774 | 6.7548 | 17.7758 | 2024-01-01 01:10 | 2023-12-31 20:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 7.7028 | 7.1103 | 43.33% | 40% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 3.3774 | 6.7548 | 17.7758 | 2024-01-01 01:15 | 2023-12-31 20:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 7.1103 | 6.5178 | 40% | 36.67% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 3.3774 | 6.7548 | 17.7758 | 2024-01-01 01:20 | 2023-12-31 20:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 6.5178 | 5.9253 | 36.67% | 33.33% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 3.3774 | 6.7548 | 17.7758 | 2024-01-01 01:25 | 2023-12-31 20:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 5.9253 | 5.3327 | 33.33% | 30% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 3.3774 | 6.7548 | 17.7758 | 2024-01-01 01:30 | 2023-12-31 20:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 5.3327 | 4.7402 | 30% | 26.67% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 3.3774 | 6.7548 | 17.7758 | 2024-01-01 01:35 | 2023-12-31 20:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 4.7402 | 4.1477 | 26.67% | 23.33% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 3.3774 | 6.7548 | 17.7758 | 2024-01-01 01:40 | 2023-12-31 20:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 4.1477 | 3.5552 | 23.33% | 20% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 3.3774 | 6.7548 | 17.7758 | 2024-01-01 01:45 | 2023-12-31 20:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 3.5552 | 2.9626 | 20% | 16.67% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 3.3774 | 6.7548 | 17.7758 | 2024-01-01 01:50 | 2023-12-31 20:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 2.9626 | 2.3701 | 16.67% | 13.33% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 3.3774 | 6.7548 | 17.7758 | 2024-01-01 01:55 | 2023-12-31 20:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 2.3701 | 1.7776 | 13.33% | 10% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 6.7548 | 6.7548 | 17.7758 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 15.9982 | 15.4057 | 90% | 86.67% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 6.7548 | 6.7548 | 17.7758 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 15.4057 | 14.8132 | 86.67% | 83.33% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 6.7548 | 6.7548 | 17.7758 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 14.8132 | 14.2206 | 83.33% | 80% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 6.7548 | 6.7548 | 17.7758 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 14.2206 | 13.6281 | 80% | 76.67% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 6.7548 | 6.7548 | 17.7758 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 13.6281 | 13.0356 | 76.67% | 73.33% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 6.7548 | 6.7548 | 17.7758 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 13.0356 | 12.4431 | 73.33% | 70% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 6.7548 | 6.7548 | 17.7758 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 12.4431 | 11.8505 | 70% | 66.67% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 6.7548 | 6.7548 | 17.7758 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 11.8505 | 11.258 | 66.67% | 63.33% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 6.7548 | 6.7548 | 17.7758 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 11.258 | 10.6655 | 63.33% | 60% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 6.7548 | 6.7548 | 17.7758 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 10.6655 | 10.073 | 60% | 56.67% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 6.7548 | 6.7548 | 17.7758 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 10.073 | 9.4804 | 56.67% | 53.33% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 6.7548 | 6.7548 | 17.7758 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 9.4804 | 8.8879 | 53.33% | 50% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 6.7548 | 6.7548 | 17.7758 | 2024-01-01 01:00 | 2023-12-31 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 8.8879 | 8.2954 | 50% | 46.67% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 6.7548 | 6.7548 | 17.7758 | 2024-01-01 01:05 | 2023-12-31 20:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 8.2954 | 7.7028 | 46.67% | 43.33% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 6.7548 | 6.7548 | 17.7758 | 2024-01-01 01:10 | 2023-12-31 20:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 7.7028 | 7.1103 | 43.33% | 40% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 6.7548 | 6.7548 | 17.7758 | 2024-01-01 01:15 | 2023-12-31 20:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 7.1103 | 6.5178 | 40% | 36.67% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 6.7548 | 6.7548 | 17.7758 | 2024-01-01 01:20 | 2023-12-31 20:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 6.5178 | 5.9253 | 36.67% | 33.33% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 6.7548 | 6.7548 | 17.7758 | 2024-01-01 01:25 | 2023-12-31 20:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 5.9253 | 5.3327 | 33.33% | 30% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 6.7548 | 6.7548 | 17.7758 | 2024-01-01 01:30 | 2023-12-31 20:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 5.3327 | 4.7402 | 30% | 26.67% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 6.7548 | 6.7548 | 17.7758 | 2024-01-01 01:35 | 2023-12-31 20:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 4.7402 | 4.1477 | 26.67% | 23.33% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 6.7548 | 6.7548 | 17.7758 | 2024-01-01 01:40 | 2023-12-31 20:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 4.1477 | 3.5552 | 23.33% | 20% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 6.7548 | 6.7548 | 17.7758 | 2024-01-01 01:45 | 2023-12-31 20:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 3.5552 | 2.9626 | 20% | 16.67% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 6.7548 | 6.7548 | 17.7758 | 2024-01-01 01:50 | 2023-12-31 20:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 2.9626 | 2.3701 | 16.67% | 13.33% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 6.7548 | 6.7548 | 17.7758 | 2024-01-01 01:55 | 2023-12-31 20:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 2.3701 | 1.7776 | 13.33% | 10% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 10.1322 | 6.7548 | 17.7758 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 15.9982 | 15.4057 | 90% | 86.67% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 10.1322 | 6.7548 | 17.7758 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 15.4057 | 14.8132 | 86.67% | 83.33% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 10.1322 | 6.7548 | 17.7758 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 14.8132 | 14.2206 | 83.33% | 80% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 10.1322 | 6.7548 | 17.7758 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 14.2206 | 13.6281 | 80% | 76.67% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 10.1322 | 6.7548 | 17.7758 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 13.6281 | 13.0356 | 76.67% | 73.33% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 10.1322 | 6.7548 | 17.7758 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 13.0356 | 12.4431 | 73.33% | 70% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 10.1322 | 6.7548 | 17.7758 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 12.4431 | 11.8505 | 70% | 66.67% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 10.1322 | 6.7548 | 17.7758 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 11.8505 | 11.258 | 66.67% | 63.33% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 10.1322 | 6.7548 | 17.7758 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 11.258 | 10.6655 | 63.33% | 60% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 10.1322 | 6.7548 | 17.7758 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 10.6655 | 10.073 | 60% | 56.67% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 10.1322 | 6.7548 | 17.7758 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 10.073 | 9.4804 | 56.67% | 53.33% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 10.1322 | 6.7548 | 17.7758 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 9.4804 | 8.8879 | 53.33% | 50% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 10.1322 | 6.7548 | 17.7758 | 2024-01-01 01:00 | 2023-12-31 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 8.8879 | 8.2954 | 50% | 46.67% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 10.1322 | 6.7548 | 17.7758 | 2024-01-01 01:05 | 2023-12-31 20:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 8.2954 | 7.7028 | 46.67% | 43.33% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 10.1322 | 6.7548 | 17.7758 | 2024-01-01 01:10 | 2023-12-31 20:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 7.7028 | 7.1103 | 43.33% | 40% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 10.1322 | 6.7548 | 17.7758 | 2024-01-01 01:15 | 2023-12-31 20:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 7.1103 | 6.5178 | 40% | 36.67% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 10.1322 | 6.7548 | 17.7758 | 2024-01-01 01:20 | 2023-12-31 20:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 6.5178 | 5.9253 | 36.67% | 33.33% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 10.1322 | 6.7548 | 17.7758 | 2024-01-01 01:25 | 2023-12-31 20:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 5.9253 | 5.3327 | 33.33% | 30% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 10.1322 | 6.7548 | 17.7758 | 2024-01-01 01:30 | 2023-12-31 20:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 5.3327 | 4.7402 | 30% | 26.67% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 10.1322 | 6.7548 | 17.7758 | 2024-01-01 01:35 | 2023-12-31 20:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 4.7402 | 4.1477 | 26.67% | 23.33% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 10.1322 | 6.7548 | 17.7758 | 2024-01-01 01:40 | 2023-12-31 20:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 4.1477 | 3.5552 | 23.33% | 20% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 10.1322 | 6.7548 | 17.7758 | 2024-01-01 01:45 | 2023-12-31 20:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 3.5552 | 2.9626 | 20% | 16.67% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 10.1322 | 6.7548 | 17.7758 | 2024-01-01 01:50 | 2023-12-31 20:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 2.9626 | 2.3701 | 16.67% | 13.33% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 10.1322 | 6.7548 | 17.7758 | 2024-01-01 01:55 | 2023-12-31 20:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 2.3701 | 1.7776 | 13.33% | 10% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 13.5096 | 6.7548 | 17.7758 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 15.9982 | 15.4057 | 90% | 86.67% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 13.5096 | 6.7548 | 17.7758 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 15.4057 | 14.8132 | 86.67% | 83.33% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 13.5096 | 6.7548 | 17.7758 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 14.8132 | 14.2206 | 83.33% | 80% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 13.5096 | 6.7548 | 17.7758 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 14.2206 | 13.6281 | 80% | 76.67% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 13.5096 | 6.7548 | 17.7758 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 13.6281 | 13.0356 | 76.67% | 73.33% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 13.5096 | 6.7548 | 17.7758 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 13.0356 | 12.4431 | 73.33% | 70% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 13.5096 | 6.7548 | 17.7758 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 12.4431 | 11.8505 | 70% | 66.67% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 13.5096 | 6.7548 | 17.7758 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 11.8505 | 11.258 | 66.67% | 63.33% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 13.5096 | 6.7548 | 17.7758 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 11.258 | 10.6655 | 63.33% | 60% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 13.5096 | 6.7548 | 17.7758 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 10.6655 | 10.073 | 60% | 56.67% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 13.5096 | 6.7548 | 17.7758 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 10.073 | 9.4804 | 56.67% | 53.33% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 13.5096 | 6.7548 | 17.7758 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 9.4804 | 8.8879 | 53.33% | 50% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 13.5096 | 6.7548 | 17.7758 | 2024-01-01 01:00 | 2023-12-31 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 8.8879 | 8.2954 | 50% | 46.67% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 13.5096 | 6.7548 | 17.7758 | 2024-01-01 01:05 | 2023-12-31 20:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 8.2954 | 7.7028 | 46.67% | 43.33% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 13.5096 | 6.7548 | 17.7758 | 2024-01-01 01:10 | 2023-12-31 20:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 7.7028 | 7.1103 | 43.33% | 40% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 13.5096 | 6.7548 | 17.7758 | 2024-01-01 01:15 | 2023-12-31 20:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 7.1103 | 6.5178 | 40% | 36.67% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 13.5096 | 6.7548 | 17.7758 | 2024-01-01 01:20 | 2023-12-31 20:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 6.5178 | 5.9253 | 36.67% | 33.33% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 13.5096 | 6.7548 | 17.7758 | 2024-01-01 01:25 | 2023-12-31 20:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 5.9253 | 5.3327 | 33.33% | 30% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 13.5096 | 6.7548 | 17.7758 | 2024-01-01 01:30 | 2023-12-31 20:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 5.3327 | 4.7402 | 30% | 26.67% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 13.5096 | 6.7548 | 17.7758 | 2024-01-01 01:35 | 2023-12-31 20:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 4.7402 | 4.1477 | 26.67% | 23.33% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 13.5096 | 6.7548 | 17.7758 | 2024-01-01 01:40 | 2023-12-31 20:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 4.1477 | 3.5552 | 23.33% | 20% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 13.5096 | 6.7548 | 17.7758 | 2024-01-01 01:45 | 2023-12-31 20:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 3.5552 | 2.9626 | 20% | 16.67% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 13.5096 | 6.7548 | 17.7758 | 2024-01-01 01:50 | 2023-12-31 20:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 2.9626 | 2.3701 | 16.67% | 13.33% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 2 | 13.5096 | 6.7548 | 17.7758 | 2024-01-01 01:55 | 2023-12-31 20:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 2.3701 | 1.7776 | 13.33% | 10% | 1.7776 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 0 | 6.7548 | 35.5516 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 31.9964 | 31.4039 | 90% | 88.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 0 | 6.7548 | 35.5516 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 31.4039 | 30.8114 | 88.33% | 86.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 0 | 6.7548 | 35.5516 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 30.8114 | 30.2189 | 86.67% | 85% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 0 | 6.7548 | 35.5516 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 30.2189 | 29.6263 | 85% | 83.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 0 | 6.7548 | 35.5516 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 29.6263 | 29.0338 | 83.33% | 81.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 0 | 6.7548 | 35.5516 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 29.0338 | 28.4413 | 81.67% | 80% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 0 | 6.7548 | 35.5516 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 28.4413 | 27.8488 | 80% | 78.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 0 | 6.7548 | 35.5516 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 27.8488 | 27.2562 | 78.33% | 76.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 0 | 6.7548 | 35.5516 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 27.2562 | 26.6637 | 76.67% | 75% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 0 | 6.7548 | 35.5516 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 26.6637 | 26.0712 | 75% | 73.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 0 | 6.7548 | 35.5516 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 26.0712 | 25.4786 | 73.33% | 71.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 0 | 6.7548 | 35.5516 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 25.4786 | 24.8861 | 71.67% | 70% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 0 | 6.7548 | 35.5516 | 2024-01-01 01:00 | 2023-12-31 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 24.8861 | 24.2936 | 70% | 68.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 0 | 6.7548 | 35.5516 | 2024-01-01 01:05 | 2023-12-31 20:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 24.2936 | 23.7011 | 68.33% | 66.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 0 | 6.7548 | 35.5516 | 2024-01-01 01:10 | 2023-12-31 20:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 23.7011 | 23.1085 | 66.67% | 65% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 0 | 6.7548 | 35.5516 | 2024-01-01 01:15 | 2023-12-31 20:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 23.1085 | 22.516 | 65% | 63.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 0 | 6.7548 | 35.5516 | 2024-01-01 01:20 | 2023-12-31 20:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 22.516 | 21.9235 | 63.33% | 61.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 0 | 6.7548 | 35.5516 | 2024-01-01 01:25 | 2023-12-31 20:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 21.9235 | 21.331 | 61.67% | 60% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 0 | 6.7548 | 35.5516 | 2024-01-01 01:30 | 2023-12-31 20:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 21.331 | 20.7384 | 60% | 58.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 0 | 6.7548 | 35.5516 | 2024-01-01 01:35 | 2023-12-31 20:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 20.7384 | 20.1459 | 58.33% | 56.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 0 | 6.7548 | 35.5516 | 2024-01-01 01:40 | 2023-12-31 20:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 20.1459 | 19.5534 | 56.67% | 55% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 0 | 6.7548 | 35.5516 | 2024-01-01 01:45 | 2023-12-31 20:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 19.5534 | 18.9609 | 55% | 53.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 0 | 6.7548 | 35.5516 | 2024-01-01 01:50 | 2023-12-31 20:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 18.9609 | 18.3683 | 53.33% | 51.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 0 | 6.7548 | 35.5516 | 2024-01-01 01:55 | 2023-12-31 20:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 18.3683 | 17.7758 | 51.67% | 50% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 0 | 6.7548 | 35.5516 | 2024-01-01 02:00 | 2023-12-31 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 17.7758 | 17.1833 | 50% | 48.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 0 | 6.7548 | 35.5516 | 2024-01-01 02:05 | 2023-12-31 21:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 17.1833 | 16.5907 | 48.33% | 46.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 0 | 6.7548 | 35.5516 | 2024-01-01 02:10 | 2023-12-31 21:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 16.5907 | 15.9982 | 46.67% | 45% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 0 | 6.7548 | 35.5516 | 2024-01-01 02:15 | 2023-12-31 21:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 15.9982 | 15.4057 | 45% | 43.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 0 | 6.7548 | 35.5516 | 2024-01-01 02:20 | 2023-12-31 21:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 15.4057 | 14.8132 | 43.33% | 41.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 0 | 6.7548 | 35.5516 | 2024-01-01 02:25 | 2023-12-31 21:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 14.8132 | 14.2206 | 41.67% | 40% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 0 | 6.7548 | 35.5516 | 2024-01-01 02:30 | 2023-12-31 21:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 14.2206 | 13.6281 | 40% | 38.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 0 | 6.7548 | 35.5516 | 2024-01-01 02:35 | 2023-12-31 21:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 13.6281 | 13.0356 | 38.33% | 36.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 0 | 6.7548 | 35.5516 | 2024-01-01 02:40 | 2023-12-31 21:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 13.0356 | 12.4431 | 36.67% | 35% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 0 | 6.7548 | 35.5516 | 2024-01-01 02:45 | 2023-12-31 21:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 12.4431 | 11.8505 | 35% | 33.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 0 | 6.7548 | 35.5516 | 2024-01-01 02:50 | 2023-12-31 21:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 11.8505 | 11.258 | 33.33% | 31.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 0 | 6.7548 | 35.5516 | 2024-01-01 02:55 | 2023-12-31 21:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 11.258 | 10.6655 | 31.67% | 30% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 0 | 6.7548 | 35.5516 | 2024-01-01 03:00 | 2023-12-31 22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 10.6655 | 10.073 | 30% | 28.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 0 | 6.7548 | 35.5516 | 2024-01-01 03:05 | 2023-12-31 22:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 10.073 | 9.4804 | 28.33% | 26.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 0 | 6.7548 | 35.5516 | 2024-01-01 03:10 | 2023-12-31 22:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 9.4804 | 8.8879 | 26.67% | 25% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 0 | 6.7548 | 35.5516 | 2024-01-01 03:15 | 2023-12-31 22:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 8.8879 | 8.2954 | 25% | 23.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 0 | 6.7548 | 35.5516 | 2024-01-01 03:20 | 2023-12-31 22:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 8.2954 | 7.7028 | 23.33% | 21.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 0 | 6.7548 | 35.5516 | 2024-01-01 03:25 | 2023-12-31 22:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 7.7028 | 7.1103 | 21.67% | 20% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 0 | 6.7548 | 35.5516 | 2024-01-01 03:30 | 2023-12-31 22:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 7.1103 | 6.5178 | 20% | 18.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 0 | 6.7548 | 35.5516 | 2024-01-01 03:35 | 2023-12-31 22:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 6.5178 | 5.9253 | 18.33% | 16.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 0 | 6.7548 | 35.5516 | 2024-01-01 03:40 | 2023-12-31 22:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 5.9253 | 5.3327 | 16.67% | 15% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 0 | 6.7548 | 35.5516 | 2024-01-01 03:45 | 2023-12-31 22:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 5.3327 | 4.7402 | 15% | 13.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 0 | 6.7548 | 35.5516 | 2024-01-01 03:50 | 2023-12-31 22:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 4.7402 | 4.1477 | 13.33% | 11.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 0 | 6.7548 | 35.5516 | 2024-01-01 03:55 | 2023-12-31 22:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 4.1477 | 3.5552 | 11.67% | 10% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 3.3774 | 6.7548 | 35.5516 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 31.9964 | 31.4039 | 90% | 88.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 3.3774 | 6.7548 | 35.5516 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 31.4039 | 30.8114 | 88.33% | 86.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 3.3774 | 6.7548 | 35.5516 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 30.8114 | 30.2189 | 86.67% | 85% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 3.3774 | 6.7548 | 35.5516 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 30.2189 | 29.6263 | 85% | 83.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 3.3774 | 6.7548 | 35.5516 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 29.6263 | 29.0338 | 83.33% | 81.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 3.3774 | 6.7548 | 35.5516 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 29.0338 | 28.4413 | 81.67% | 80% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 3.3774 | 6.7548 | 35.5516 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 28.4413 | 27.8488 | 80% | 78.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 3.3774 | 6.7548 | 35.5516 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 27.8488 | 27.2562 | 78.33% | 76.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 3.3774 | 6.7548 | 35.5516 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 27.2562 | 26.6637 | 76.67% | 75% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 3.3774 | 6.7548 | 35.5516 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 26.6637 | 26.0712 | 75% | 73.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 3.3774 | 6.7548 | 35.5516 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 26.0712 | 25.4786 | 73.33% | 71.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 3.3774 | 6.7548 | 35.5516 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 25.4786 | 24.8861 | 71.67% | 70% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 3.3774 | 6.7548 | 35.5516 | 2024-01-01 01:00 | 2023-12-31 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 24.8861 | 24.2936 | 70% | 68.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 3.3774 | 6.7548 | 35.5516 | 2024-01-01 01:05 | 2023-12-31 20:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 24.2936 | 23.7011 | 68.33% | 66.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 3.3774 | 6.7548 | 35.5516 | 2024-01-01 01:10 | 2023-12-31 20:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 23.7011 | 23.1085 | 66.67% | 65% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 3.3774 | 6.7548 | 35.5516 | 2024-01-01 01:15 | 2023-12-31 20:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 23.1085 | 22.516 | 65% | 63.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 3.3774 | 6.7548 | 35.5516 | 2024-01-01 01:20 | 2023-12-31 20:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 22.516 | 21.9235 | 63.33% | 61.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 3.3774 | 6.7548 | 35.5516 | 2024-01-01 01:25 | 2023-12-31 20:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 21.9235 | 21.331 | 61.67% | 60% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 3.3774 | 6.7548 | 35.5516 | 2024-01-01 01:30 | 2023-12-31 20:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 21.331 | 20.7384 | 60% | 58.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 3.3774 | 6.7548 | 35.5516 | 2024-01-01 01:35 | 2023-12-31 20:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 20.7384 | 20.1459 | 58.33% | 56.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 3.3774 | 6.7548 | 35.5516 | 2024-01-01 01:40 | 2023-12-31 20:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 20.1459 | 19.5534 | 56.67% | 55% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 3.3774 | 6.7548 | 35.5516 | 2024-01-01 01:45 | 2023-12-31 20:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 19.5534 | 18.9609 | 55% | 53.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 3.3774 | 6.7548 | 35.5516 | 2024-01-01 01:50 | 2023-12-31 20:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 18.9609 | 18.3683 | 53.33% | 51.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 3.3774 | 6.7548 | 35.5516 | 2024-01-01 01:55 | 2023-12-31 20:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 18.3683 | 17.7758 | 51.67% | 50% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 3.3774 | 6.7548 | 35.5516 | 2024-01-01 02:00 | 2023-12-31 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 17.7758 | 17.1833 | 50% | 48.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 3.3774 | 6.7548 | 35.5516 | 2024-01-01 02:05 | 2023-12-31 21:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 17.1833 | 16.5907 | 48.33% | 46.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 3.3774 | 6.7548 | 35.5516 | 2024-01-01 02:10 | 2023-12-31 21:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 16.5907 | 15.9982 | 46.67% | 45% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 3.3774 | 6.7548 | 35.5516 | 2024-01-01 02:15 | 2023-12-31 21:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 15.9982 | 15.4057 | 45% | 43.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 3.3774 | 6.7548 | 35.5516 | 2024-01-01 02:20 | 2023-12-31 21:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 15.4057 | 14.8132 | 43.33% | 41.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 3.3774 | 6.7548 | 35.5516 | 2024-01-01 02:25 | 2023-12-31 21:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 14.8132 | 14.2206 | 41.67% | 40% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 3.3774 | 6.7548 | 35.5516 | 2024-01-01 02:30 | 2023-12-31 21:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 14.2206 | 13.6281 | 40% | 38.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 3.3774 | 6.7548 | 35.5516 | 2024-01-01 02:35 | 2023-12-31 21:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 13.6281 | 13.0356 | 38.33% | 36.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 3.3774 | 6.7548 | 35.5516 | 2024-01-01 02:40 | 2023-12-31 21:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 13.0356 | 12.4431 | 36.67% | 35% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 3.3774 | 6.7548 | 35.5516 | 2024-01-01 02:45 | 2023-12-31 21:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 12.4431 | 11.8505 | 35% | 33.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 3.3774 | 6.7548 | 35.5516 | 2024-01-01 02:50 | 2023-12-31 21:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 11.8505 | 11.258 | 33.33% | 31.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 3.3774 | 6.7548 | 35.5516 | 2024-01-01 02:55 | 2023-12-31 21:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 11.258 | 10.6655 | 31.67% | 30% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 3.3774 | 6.7548 | 35.5516 | 2024-01-01 03:00 | 2023-12-31 22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 10.6655 | 10.073 | 30% | 28.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 3.3774 | 6.7548 | 35.5516 | 2024-01-01 03:05 | 2023-12-31 22:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 10.073 | 9.4804 | 28.33% | 26.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 3.3774 | 6.7548 | 35.5516 | 2024-01-01 03:10 | 2023-12-31 22:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 9.4804 | 8.8879 | 26.67% | 25% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 3.3774 | 6.7548 | 35.5516 | 2024-01-01 03:15 | 2023-12-31 22:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 8.8879 | 8.2954 | 25% | 23.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 3.3774 | 6.7548 | 35.5516 | 2024-01-01 03:20 | 2023-12-31 22:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 8.2954 | 7.7028 | 23.33% | 21.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 3.3774 | 6.7548 | 35.5516 | 2024-01-01 03:25 | 2023-12-31 22:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 7.7028 | 7.1103 | 21.67% | 20% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 3.3774 | 6.7548 | 35.5516 | 2024-01-01 03:30 | 2023-12-31 22:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 7.1103 | 6.5178 | 20% | 18.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 3.3774 | 6.7548 | 35.5516 | 2024-01-01 03:35 | 2023-12-31 22:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 6.5178 | 5.9253 | 18.33% | 16.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 3.3774 | 6.7548 | 35.5516 | 2024-01-01 03:40 | 2023-12-31 22:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 5.9253 | 5.3327 | 16.67% | 15% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 3.3774 | 6.7548 | 35.5516 | 2024-01-01 03:45 | 2023-12-31 22:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 5.3327 | 4.7402 | 15% | 13.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 3.3774 | 6.7548 | 35.5516 | 2024-01-01 03:50 | 2023-12-31 22:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 4.7402 | 4.1477 | 13.33% | 11.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 3.3774 | 6.7548 | 35.5516 | 2024-01-01 03:55 | 2023-12-31 22:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 4.1477 | 3.5552 | 11.67% | 10% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 6.7548 | 6.7548 | 35.5516 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 31.9964 | 31.4039 | 90% | 88.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 6.7548 | 6.7548 | 35.5516 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 31.4039 | 30.8114 | 88.33% | 86.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 6.7548 | 6.7548 | 35.5516 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 30.8114 | 30.2189 | 86.67% | 85% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 6.7548 | 6.7548 | 35.5516 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 30.2189 | 29.6263 | 85% | 83.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 6.7548 | 6.7548 | 35.5516 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 29.6263 | 29.0338 | 83.33% | 81.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 6.7548 | 6.7548 | 35.5516 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 29.0338 | 28.4413 | 81.67% | 80% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 6.7548 | 6.7548 | 35.5516 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 28.4413 | 27.8488 | 80% | 78.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 6.7548 | 6.7548 | 35.5516 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 27.8488 | 27.2562 | 78.33% | 76.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 6.7548 | 6.7548 | 35.5516 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 27.2562 | 26.6637 | 76.67% | 75% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 6.7548 | 6.7548 | 35.5516 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 26.6637 | 26.0712 | 75% | 73.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 6.7548 | 6.7548 | 35.5516 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 26.0712 | 25.4786 | 73.33% | 71.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 6.7548 | 6.7548 | 35.5516 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 25.4786 | 24.8861 | 71.67% | 70% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 6.7548 | 6.7548 | 35.5516 | 2024-01-01 01:00 | 2023-12-31 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 24.8861 | 24.2936 | 70% | 68.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 6.7548 | 6.7548 | 35.5516 | 2024-01-01 01:05 | 2023-12-31 20:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 24.2936 | 23.7011 | 68.33% | 66.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 6.7548 | 6.7548 | 35.5516 | 2024-01-01 01:10 | 2023-12-31 20:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 23.7011 | 23.1085 | 66.67% | 65% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 6.7548 | 6.7548 | 35.5516 | 2024-01-01 01:15 | 2023-12-31 20:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 23.1085 | 22.516 | 65% | 63.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 6.7548 | 6.7548 | 35.5516 | 2024-01-01 01:20 | 2023-12-31 20:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 22.516 | 21.9235 | 63.33% | 61.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 6.7548 | 6.7548 | 35.5516 | 2024-01-01 01:25 | 2023-12-31 20:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 21.9235 | 21.331 | 61.67% | 60% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 6.7548 | 6.7548 | 35.5516 | 2024-01-01 01:30 | 2023-12-31 20:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 21.331 | 20.7384 | 60% | 58.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 6.7548 | 6.7548 | 35.5516 | 2024-01-01 01:35 | 2023-12-31 20:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 20.7384 | 20.1459 | 58.33% | 56.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 6.7548 | 6.7548 | 35.5516 | 2024-01-01 01:40 | 2023-12-31 20:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 20.1459 | 19.5534 | 56.67% | 55% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 6.7548 | 6.7548 | 35.5516 | 2024-01-01 01:45 | 2023-12-31 20:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 19.5534 | 18.9609 | 55% | 53.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 6.7548 | 6.7548 | 35.5516 | 2024-01-01 01:50 | 2023-12-31 20:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 18.9609 | 18.3683 | 53.33% | 51.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 6.7548 | 6.7548 | 35.5516 | 2024-01-01 01:55 | 2023-12-31 20:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 18.3683 | 17.7758 | 51.67% | 50% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 6.7548 | 6.7548 | 35.5516 | 2024-01-01 02:00 | 2023-12-31 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 17.7758 | 17.1833 | 50% | 48.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 6.7548 | 6.7548 | 35.5516 | 2024-01-01 02:05 | 2023-12-31 21:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 17.1833 | 16.5907 | 48.33% | 46.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 6.7548 | 6.7548 | 35.5516 | 2024-01-01 02:10 | 2023-12-31 21:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 16.5907 | 15.9982 | 46.67% | 45% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 6.7548 | 6.7548 | 35.5516 | 2024-01-01 02:15 | 2023-12-31 21:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 15.9982 | 15.4057 | 45% | 43.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 6.7548 | 6.7548 | 35.5516 | 2024-01-01 02:20 | 2023-12-31 21:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 15.4057 | 14.8132 | 43.33% | 41.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 6.7548 | 6.7548 | 35.5516 | 2024-01-01 02:25 | 2023-12-31 21:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 14.8132 | 14.2206 | 41.67% | 40% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 6.7548 | 6.7548 | 35.5516 | 2024-01-01 02:30 | 2023-12-31 21:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 14.2206 | 13.6281 | 40% | 38.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 6.7548 | 6.7548 | 35.5516 | 2024-01-01 02:35 | 2023-12-31 21:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 13.6281 | 13.0356 | 38.33% | 36.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 6.7548 | 6.7548 | 35.5516 | 2024-01-01 02:40 | 2023-12-31 21:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 13.0356 | 12.4431 | 36.67% | 35% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 6.7548 | 6.7548 | 35.5516 | 2024-01-01 02:45 | 2023-12-31 21:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 12.4431 | 11.8505 | 35% | 33.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 6.7548 | 6.7548 | 35.5516 | 2024-01-01 02:50 | 2023-12-31 21:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 11.8505 | 11.258 | 33.33% | 31.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 6.7548 | 6.7548 | 35.5516 | 2024-01-01 02:55 | 2023-12-31 21:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 11.258 | 10.6655 | 31.67% | 30% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 6.7548 | 6.7548 | 35.5516 | 2024-01-01 03:00 | 2023-12-31 22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 10.6655 | 10.073 | 30% | 28.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 6.7548 | 6.7548 | 35.5516 | 2024-01-01 03:05 | 2023-12-31 22:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 10.073 | 9.4804 | 28.33% | 26.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 6.7548 | 6.7548 | 35.5516 | 2024-01-01 03:10 | 2023-12-31 22:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 9.4804 | 8.8879 | 26.67% | 25% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 6.7548 | 6.7548 | 35.5516 | 2024-01-01 03:15 | 2023-12-31 22:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 8.8879 | 8.2954 | 25% | 23.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 6.7548 | 6.7548 | 35.5516 | 2024-01-01 03:20 | 2023-12-31 22:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 8.2954 | 7.7028 | 23.33% | 21.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 6.7548 | 6.7548 | 35.5516 | 2024-01-01 03:25 | 2023-12-31 22:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 7.7028 | 7.1103 | 21.67% | 20% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 6.7548 | 6.7548 | 35.5516 | 2024-01-01 03:30 | 2023-12-31 22:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 7.1103 | 6.5178 | 20% | 18.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 6.7548 | 6.7548 | 35.5516 | 2024-01-01 03:35 | 2023-12-31 22:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 6.5178 | 5.9253 | 18.33% | 16.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 6.7548 | 6.7548 | 35.5516 | 2024-01-01 03:40 | 2023-12-31 22:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 5.9253 | 5.3327 | 16.67% | 15% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 6.7548 | 6.7548 | 35.5516 | 2024-01-01 03:45 | 2023-12-31 22:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 5.3327 | 4.7402 | 15% | 13.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 6.7548 | 6.7548 | 35.5516 | 2024-01-01 03:50 | 2023-12-31 22:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 4.7402 | 4.1477 | 13.33% | 11.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 6.7548 | 6.7548 | 35.5516 | 2024-01-01 03:55 | 2023-12-31 22:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 4.1477 | 3.5552 | 11.67% | 10% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 10.1322 | 6.7548 | 35.5516 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 31.9964 | 31.4039 | 90% | 88.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 10.1322 | 6.7548 | 35.5516 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 31.4039 | 30.8114 | 88.33% | 86.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 10.1322 | 6.7548 | 35.5516 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 30.8114 | 30.2189 | 86.67% | 85% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 10.1322 | 6.7548 | 35.5516 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 30.2189 | 29.6263 | 85% | 83.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 10.1322 | 6.7548 | 35.5516 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 29.6263 | 29.0338 | 83.33% | 81.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 10.1322 | 6.7548 | 35.5516 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 29.0338 | 28.4413 | 81.67% | 80% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 10.1322 | 6.7548 | 35.5516 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 28.4413 | 27.8488 | 80% | 78.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 10.1322 | 6.7548 | 35.5516 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 27.8488 | 27.2562 | 78.33% | 76.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 10.1322 | 6.7548 | 35.5516 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 27.2562 | 26.6637 | 76.67% | 75% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 10.1322 | 6.7548 | 35.5516 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 26.6637 | 26.0712 | 75% | 73.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 10.1322 | 6.7548 | 35.5516 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 26.0712 | 25.4786 | 73.33% | 71.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 10.1322 | 6.7548 | 35.5516 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 25.4786 | 24.8861 | 71.67% | 70% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 10.1322 | 6.7548 | 35.5516 | 2024-01-01 01:00 | 2023-12-31 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 24.8861 | 24.2936 | 70% | 68.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 10.1322 | 6.7548 | 35.5516 | 2024-01-01 01:05 | 2023-12-31 20:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 24.2936 | 23.7011 | 68.33% | 66.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 10.1322 | 6.7548 | 35.5516 | 2024-01-01 01:10 | 2023-12-31 20:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 23.7011 | 23.1085 | 66.67% | 65% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 10.1322 | 6.7548 | 35.5516 | 2024-01-01 01:15 | 2023-12-31 20:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 23.1085 | 22.516 | 65% | 63.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 10.1322 | 6.7548 | 35.5516 | 2024-01-01 01:20 | 2023-12-31 20:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 22.516 | 21.9235 | 63.33% | 61.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 10.1322 | 6.7548 | 35.5516 | 2024-01-01 01:25 | 2023-12-31 20:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 21.9235 | 21.331 | 61.67% | 60% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 10.1322 | 6.7548 | 35.5516 | 2024-01-01 01:30 | 2023-12-31 20:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 21.331 | 20.7384 | 60% | 58.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 10.1322 | 6.7548 | 35.5516 | 2024-01-01 01:35 | 2023-12-31 20:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 20.7384 | 20.1459 | 58.33% | 56.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 10.1322 | 6.7548 | 35.5516 | 2024-01-01 01:40 | 2023-12-31 20:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 20.1459 | 19.5534 | 56.67% | 55% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 10.1322 | 6.7548 | 35.5516 | 2024-01-01 01:45 | 2023-12-31 20:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 19.5534 | 18.9609 | 55% | 53.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 10.1322 | 6.7548 | 35.5516 | 2024-01-01 01:50 | 2023-12-31 20:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 18.9609 | 18.3683 | 53.33% | 51.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 10.1322 | 6.7548 | 35.5516 | 2024-01-01 01:55 | 2023-12-31 20:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 18.3683 | 17.7758 | 51.67% | 50% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 10.1322 | 6.7548 | 35.5516 | 2024-01-01 02:00 | 2023-12-31 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 17.7758 | 17.1833 | 50% | 48.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 10.1322 | 6.7548 | 35.5516 | 2024-01-01 02:05 | 2023-12-31 21:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 17.1833 | 16.5907 | 48.33% | 46.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 10.1322 | 6.7548 | 35.5516 | 2024-01-01 02:10 | 2023-12-31 21:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 16.5907 | 15.9982 | 46.67% | 45% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 10.1322 | 6.7548 | 35.5516 | 2024-01-01 02:15 | 2023-12-31 21:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 15.9982 | 15.4057 | 45% | 43.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 10.1322 | 6.7548 | 35.5516 | 2024-01-01 02:20 | 2023-12-31 21:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 15.4057 | 14.8132 | 43.33% | 41.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 10.1322 | 6.7548 | 35.5516 | 2024-01-01 02:25 | 2023-12-31 21:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 14.8132 | 14.2206 | 41.67% | 40% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 10.1322 | 6.7548 | 35.5516 | 2024-01-01 02:30 | 2023-12-31 21:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 14.2206 | 13.6281 | 40% | 38.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 10.1322 | 6.7548 | 35.5516 | 2024-01-01 02:35 | 2023-12-31 21:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 13.6281 | 13.0356 | 38.33% | 36.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 10.1322 | 6.7548 | 35.5516 | 2024-01-01 02:40 | 2023-12-31 21:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 13.0356 | 12.4431 | 36.67% | 35% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 10.1322 | 6.7548 | 35.5516 | 2024-01-01 02:45 | 2023-12-31 21:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 12.4431 | 11.8505 | 35% | 33.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 10.1322 | 6.7548 | 35.5516 | 2024-01-01 02:50 | 2023-12-31 21:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 11.8505 | 11.258 | 33.33% | 31.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 10.1322 | 6.7548 | 35.5516 | 2024-01-01 02:55 | 2023-12-31 21:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 11.258 | 10.6655 | 31.67% | 30% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 10.1322 | 6.7548 | 35.5516 | 2024-01-01 03:00 | 2023-12-31 22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 10.6655 | 10.073 | 30% | 28.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 10.1322 | 6.7548 | 35.5516 | 2024-01-01 03:05 | 2023-12-31 22:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 10.073 | 9.4804 | 28.33% | 26.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 10.1322 | 6.7548 | 35.5516 | 2024-01-01 03:10 | 2023-12-31 22:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 9.4804 | 8.8879 | 26.67% | 25% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 10.1322 | 6.7548 | 35.5516 | 2024-01-01 03:15 | 2023-12-31 22:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 8.8879 | 8.2954 | 25% | 23.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 10.1322 | 6.7548 | 35.5516 | 2024-01-01 03:20 | 2023-12-31 22:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 8.2954 | 7.7028 | 23.33% | 21.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 10.1322 | 6.7548 | 35.5516 | 2024-01-01 03:25 | 2023-12-31 22:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 7.7028 | 7.1103 | 21.67% | 20% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 10.1322 | 6.7548 | 35.5516 | 2024-01-01 03:30 | 2023-12-31 22:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 7.1103 | 6.5178 | 20% | 18.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 10.1322 | 6.7548 | 35.5516 | 2024-01-01 03:35 | 2023-12-31 22:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 6.5178 | 5.9253 | 18.33% | 16.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 10.1322 | 6.7548 | 35.5516 | 2024-01-01 03:40 | 2023-12-31 22:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 5.9253 | 5.3327 | 16.67% | 15% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 10.1322 | 6.7548 | 35.5516 | 2024-01-01 03:45 | 2023-12-31 22:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 5.3327 | 4.7402 | 15% | 13.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 10.1322 | 6.7548 | 35.5516 | 2024-01-01 03:50 | 2023-12-31 22:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 4.7402 | 4.1477 | 13.33% | 11.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 10.1322 | 6.7548 | 35.5516 | 2024-01-01 03:55 | 2023-12-31 22:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 4.1477 | 3.5552 | 11.67% | 10% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 13.5096 | 6.7548 | 35.5516 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 31.9964 | 31.4039 | 90% | 88.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 13.5096 | 6.7548 | 35.5516 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 31.4039 | 30.8114 | 88.33% | 86.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 13.5096 | 6.7548 | 35.5516 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 30.8114 | 30.2189 | 86.67% | 85% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 13.5096 | 6.7548 | 35.5516 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 30.2189 | 29.6263 | 85% | 83.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 13.5096 | 6.7548 | 35.5516 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 29.6263 | 29.0338 | 83.33% | 81.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 13.5096 | 6.7548 | 35.5516 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 29.0338 | 28.4413 | 81.67% | 80% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 13.5096 | 6.7548 | 35.5516 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 28.4413 | 27.8488 | 80% | 78.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 13.5096 | 6.7548 | 35.5516 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 27.8488 | 27.2562 | 78.33% | 76.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 13.5096 | 6.7548 | 35.5516 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 27.2562 | 26.6637 | 76.67% | 75% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 13.5096 | 6.7548 | 35.5516 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 26.6637 | 26.0712 | 75% | 73.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 13.5096 | 6.7548 | 35.5516 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 26.0712 | 25.4786 | 73.33% | 71.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 13.5096 | 6.7548 | 35.5516 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 25.4786 | 24.8861 | 71.67% | 70% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 13.5096 | 6.7548 | 35.5516 | 2024-01-01 01:00 | 2023-12-31 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 24.8861 | 24.2936 | 70% | 68.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 13.5096 | 6.7548 | 35.5516 | 2024-01-01 01:05 | 2023-12-31 20:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 24.2936 | 23.7011 | 68.33% | 66.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 13.5096 | 6.7548 | 35.5516 | 2024-01-01 01:10 | 2023-12-31 20:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 23.7011 | 23.1085 | 66.67% | 65% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 13.5096 | 6.7548 | 35.5516 | 2024-01-01 01:15 | 2023-12-31 20:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 23.1085 | 22.516 | 65% | 63.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 13.5096 | 6.7548 | 35.5516 | 2024-01-01 01:20 | 2023-12-31 20:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 22.516 | 21.9235 | 63.33% | 61.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 13.5096 | 6.7548 | 35.5516 | 2024-01-01 01:25 | 2023-12-31 20:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 21.9235 | 21.331 | 61.67% | 60% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 13.5096 | 6.7548 | 35.5516 | 2024-01-01 01:30 | 2023-12-31 20:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 21.331 | 20.7384 | 60% | 58.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 13.5096 | 6.7548 | 35.5516 | 2024-01-01 01:35 | 2023-12-31 20:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 20.7384 | 20.1459 | 58.33% | 56.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 13.5096 | 6.7548 | 35.5516 | 2024-01-01 01:40 | 2023-12-31 20:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 20.1459 | 19.5534 | 56.67% | 55% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 13.5096 | 6.7548 | 35.5516 | 2024-01-01 01:45 | 2023-12-31 20:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 19.5534 | 18.9609 | 55% | 53.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 13.5096 | 6.7548 | 35.5516 | 2024-01-01 01:50 | 2023-12-31 20:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 18.9609 | 18.3683 | 53.33% | 51.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 13.5096 | 6.7548 | 35.5516 | 2024-01-01 01:55 | 2023-12-31 20:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 18.3683 | 17.7758 | 51.67% | 50% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 13.5096 | 6.7548 | 35.5516 | 2024-01-01 02:00 | 2023-12-31 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 17.7758 | 17.1833 | 50% | 48.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 13.5096 | 6.7548 | 35.5516 | 2024-01-01 02:05 | 2023-12-31 21:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 17.1833 | 16.5907 | 48.33% | 46.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 13.5096 | 6.7548 | 35.5516 | 2024-01-01 02:10 | 2023-12-31 21:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 16.5907 | 15.9982 | 46.67% | 45% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 13.5096 | 6.7548 | 35.5516 | 2024-01-01 02:15 | 2023-12-31 21:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 15.9982 | 15.4057 | 45% | 43.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 13.5096 | 6.7548 | 35.5516 | 2024-01-01 02:20 | 2023-12-31 21:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 15.4057 | 14.8132 | 43.33% | 41.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 13.5096 | 6.7548 | 35.5516 | 2024-01-01 02:25 | 2023-12-31 21:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 14.8132 | 14.2206 | 41.67% | 40% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 13.5096 | 6.7548 | 35.5516 | 2024-01-01 02:30 | 2023-12-31 21:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 14.2206 | 13.6281 | 40% | 38.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 13.5096 | 6.7548 | 35.5516 | 2024-01-01 02:35 | 2023-12-31 21:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 13.6281 | 13.0356 | 38.33% | 36.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 13.5096 | 6.7548 | 35.5516 | 2024-01-01 02:40 | 2023-12-31 21:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 13.0356 | 12.4431 | 36.67% | 35% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 13.5096 | 6.7548 | 35.5516 | 2024-01-01 02:45 | 2023-12-31 21:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 12.4431 | 11.8505 | 35% | 33.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 13.5096 | 6.7548 | 35.5516 | 2024-01-01 02:50 | 2023-12-31 21:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 11.8505 | 11.258 | 33.33% | 31.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 13.5096 | 6.7548 | 35.5516 | 2024-01-01 02:55 | 2023-12-31 21:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 11.258 | 10.6655 | 31.67% | 30% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 13.5096 | 6.7548 | 35.5516 | 2024-01-01 03:00 | 2023-12-31 22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 10.6655 | 10.073 | 30% | 28.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 13.5096 | 6.7548 | 35.5516 | 2024-01-01 03:05 | 2023-12-31 22:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 10.073 | 9.4804 | 28.33% | 26.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 13.5096 | 6.7548 | 35.5516 | 2024-01-01 03:10 | 2023-12-31 22:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 9.4804 | 8.8879 | 26.67% | 25% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 13.5096 | 6.7548 | 35.5516 | 2024-01-01 03:15 | 2023-12-31 22:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 8.8879 | 8.2954 | 25% | 23.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 13.5096 | 6.7548 | 35.5516 | 2024-01-01 03:20 | 2023-12-31 22:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 8.2954 | 7.7028 | 23.33% | 21.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 13.5096 | 6.7548 | 35.5516 | 2024-01-01 03:25 | 2023-12-31 22:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 7.7028 | 7.1103 | 21.67% | 20% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 13.5096 | 6.7548 | 35.5516 | 2024-01-01 03:30 | 2023-12-31 22:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 7.1103 | 6.5178 | 20% | 18.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 13.5096 | 6.7548 | 35.5516 | 2024-01-01 03:35 | 2023-12-31 22:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 6.5178 | 5.9253 | 18.33% | 16.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 13.5096 | 6.7548 | 35.5516 | 2024-01-01 03:40 | 2023-12-31 22:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 5.9253 | 5.3327 | 16.67% | 15% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 13.5096 | 6.7548 | 35.5516 | 2024-01-01 03:45 | 2023-12-31 22:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 5.3327 | 4.7402 | 15% | 13.33% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 13.5096 | 6.7548 | 35.5516 | 2024-01-01 03:50 | 2023-12-31 22:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 4.7402 | 4.1477 | 13.33% | 11.67% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 4 | 13.5096 | 6.7548 | 35.5516 | 2024-01-01 03:55 | 2023-12-31 22:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 4.1477 | 3.5552 | 11.67% | 10% | 3.5552 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 63.9929 | 63.4004 | 90% | 89.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 63.4004 | 62.8078 | 89.17% | 88.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 62.8078 | 62.2153 | 88.33% | 87.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 62.2153 | 61.6228 | 87.5% | 86.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 61.6228 | 61.0302 | 86.67% | 85.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 61.0302 | 60.4377 | 85.83% | 85% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 60.4377 | 59.8452 | 85% | 84.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 59.8452 | 59.2527 | 84.17% | 83.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 59.2527 | 58.6601 | 83.33% | 82.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 58.6601 | 58.0676 | 82.5% | 81.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 58.0676 | 57.4751 | 81.67% | 80.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 57.4751 | 56.8826 | 80.83% | 80% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 01:00 | 2023-12-31 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 56.8826 | 56.29 | 80% | 79.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 01:05 | 2023-12-31 20:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 56.29 | 55.6975 | 79.17% | 78.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 01:10 | 2023-12-31 20:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 55.6975 | 55.105 | 78.33% | 77.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 01:15 | 2023-12-31 20:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 55.105 | 54.5125 | 77.5% | 76.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 01:20 | 2023-12-31 20:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 54.5125 | 53.9199 | 76.67% | 75.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 01:25 | 2023-12-31 20:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 53.9199 | 53.3274 | 75.83% | 75% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 01:30 | 2023-12-31 20:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 53.3274 | 52.7349 | 75% | 74.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 01:35 | 2023-12-31 20:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 52.7349 | 52.1423 | 74.17% | 73.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 01:40 | 2023-12-31 20:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 52.1423 | 51.5498 | 73.33% | 72.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 01:45 | 2023-12-31 20:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 51.5498 | 50.9573 | 72.5% | 71.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 01:50 | 2023-12-31 20:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 50.9573 | 50.3648 | 71.67% | 70.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 01:55 | 2023-12-31 20:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 50.3648 | 49.7722 | 70.83% | 70% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 02:00 | 2023-12-31 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 49.7722 | 49.1797 | 70% | 69.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 02:05 | 2023-12-31 21:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 49.1797 | 48.5872 | 69.17% | 68.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 02:10 | 2023-12-31 21:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 48.5872 | 47.9947 | 68.33% | 67.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 02:15 | 2023-12-31 21:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 47.9947 | 47.4021 | 67.5% | 66.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 02:20 | 2023-12-31 21:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 47.4021 | 46.8096 | 66.67% | 65.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 02:25 | 2023-12-31 21:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 46.8096 | 46.2171 | 65.83% | 65% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 02:30 | 2023-12-31 21:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 46.2171 | 45.6246 | 65% | 64.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 02:35 | 2023-12-31 21:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 45.6246 | 45.032 | 64.17% | 63.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 02:40 | 2023-12-31 21:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 45.032 | 44.4395 | 63.33% | 62.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 02:45 | 2023-12-31 21:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 44.4395 | 43.847 | 62.5% | 61.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 02:50 | 2023-12-31 21:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 43.847 | 43.2544 | 61.67% | 60.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 02:55 | 2023-12-31 21:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 43.2544 | 42.6619 | 60.83% | 60% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 03:00 | 2023-12-31 22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 42.6619 | 42.0694 | 60% | 59.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 03:05 | 2023-12-31 22:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 42.0694 | 41.4769 | 59.17% | 58.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 03:10 | 2023-12-31 22:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 41.4769 | 40.8843 | 58.33% | 57.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 03:15 | 2023-12-31 22:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 40.8843 | 40.2918 | 57.5% | 56.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 03:20 | 2023-12-31 22:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 40.2918 | 39.6993 | 56.67% | 55.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 03:25 | 2023-12-31 22:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 39.6993 | 39.1068 | 55.83% | 55% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 03:30 | 2023-12-31 22:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 39.1068 | 38.5142 | 55% | 54.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 03:35 | 2023-12-31 22:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 38.5142 | 37.9217 | 54.17% | 53.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 03:40 | 2023-12-31 22:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 37.9217 | 37.3292 | 53.33% | 52.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 03:45 | 2023-12-31 22:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 37.3292 | 36.7367 | 52.5% | 51.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 03:50 | 2023-12-31 22:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 36.7367 | 36.1441 | 51.67% | 50.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 03:55 | 2023-12-31 22:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 36.1441 | 35.5516 | 50.83% | 50% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 04:00 | 2023-12-31 23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 35.5516 | 34.9591 | 50% | 49.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 04:05 | 2023-12-31 23:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 34.9591 | 34.3665 | 49.17% | 48.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 04:10 | 2023-12-31 23:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 34.3665 | 33.774 | 48.33% | 47.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 04:15 | 2023-12-31 23:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 33.774 | 33.1815 | 47.5% | 46.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 04:20 | 2023-12-31 23:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 33.1815 | 32.589 | 46.67% | 45.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 04:25 | 2023-12-31 23:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 32.589 | 31.9964 | 45.83% | 45% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 04:30 | 2023-12-31 23:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 31.9964 | 31.4039 | 45% | 44.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 04:35 | 2023-12-31 23:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 31.4039 | 30.8114 | 44.17% | 43.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 04:40 | 2023-12-31 23:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 30.8114 | 30.2189 | 43.33% | 42.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 04:45 | 2023-12-31 23:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 30.2189 | 29.6263 | 42.5% | 41.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 04:50 | 2023-12-31 23:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 29.6263 | 29.0338 | 41.67% | 40.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 04:55 | 2023-12-31 23:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 29.0338 | 28.4413 | 40.83% | 40% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 05:00 | 2024-01-01 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 28.4413 | 27.8488 | 40% | 39.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 05:05 | 2024-01-01 00:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 27.8488 | 27.2562 | 39.17% | 38.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 05:10 | 2024-01-01 00:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 27.2562 | 26.6637 | 38.33% | 37.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 05:15 | 2024-01-01 00:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 26.6637 | 26.0712 | 37.5% | 36.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 05:20 | 2024-01-01 00:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 26.0712 | 25.4786 | 36.67% | 35.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 05:25 | 2024-01-01 00:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 25.4786 | 24.8861 | 35.83% | 35% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 05:30 | 2024-01-01 00:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 24.8861 | 24.2936 | 35% | 34.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 05:35 | 2024-01-01 00:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 24.2936 | 23.7011 | 34.17% | 33.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 05:40 | 2024-01-01 00:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 23.7011 | 23.1085 | 33.33% | 32.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 05:45 | 2024-01-01 00:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 23.1085 | 22.516 | 32.5% | 31.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 05:50 | 2024-01-01 00:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 22.516 | 21.9235 | 31.67% | 30.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 05:55 | 2024-01-01 00:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 21.9235 | 21.331 | 30.83% | 30% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 06:00 | 2024-01-01 01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 21.331 | 20.7384 | 30% | 29.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 06:05 | 2024-01-01 01:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 20.7384 | 20.1459 | 29.17% | 28.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 06:10 | 2024-01-01 01:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 20.1459 | 19.5534 | 28.33% | 27.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 06:15 | 2024-01-01 01:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 19.5534 | 18.9609 | 27.5% | 26.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 06:20 | 2024-01-01 01:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 18.9609 | 18.3683 | 26.67% | 25.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 06:25 | 2024-01-01 01:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 18.3683 | 17.7758 | 25.83% | 25% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 06:30 | 2024-01-01 01:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 17.7758 | 17.1833 | 25% | 24.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 06:35 | 2024-01-01 01:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 17.1833 | 16.5907 | 24.17% | 23.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 06:40 | 2024-01-01 01:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 16.5907 | 15.9982 | 23.33% | 22.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 06:45 | 2024-01-01 01:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 15.9982 | 15.4057 | 22.5% | 21.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 06:50 | 2024-01-01 01:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 15.4057 | 14.8132 | 21.67% | 20.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 06:55 | 2024-01-01 01:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 14.8132 | 14.2206 | 20.83% | 20% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 07:00 | 2024-01-01 02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 14.2206 | 13.6281 | 20% | 19.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 07:05 | 2024-01-01 02:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 13.6281 | 13.0356 | 19.17% | 18.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 07:10 | 2024-01-01 02:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 13.0356 | 12.4431 | 18.33% | 17.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 07:15 | 2024-01-01 02:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 12.4431 | 11.8505 | 17.5% | 16.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 07:20 | 2024-01-01 02:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 11.8505 | 11.258 | 16.67% | 15.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 07:25 | 2024-01-01 02:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 11.258 | 10.6655 | 15.83% | 15% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 07:30 | 2024-01-01 02:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 10.6655 | 10.073 | 15% | 14.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 07:35 | 2024-01-01 02:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 10.073 | 9.4804 | 14.17% | 13.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 07:40 | 2024-01-01 02:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 9.4804 | 8.8879 | 13.33% | 12.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 07:45 | 2024-01-01 02:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 8.8879 | 8.2954 | 12.5% | 11.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 07:50 | 2024-01-01 02:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 8.2954 | 7.7028 | 11.67% | 10.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 0 | 6.7548 | 71.1032 | 2024-01-01 07:55 | 2024-01-01 02:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 7.7028 | 7.1103 | 10.83% | 10% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 63.9929 | 63.4004 | 90% | 89.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 63.4004 | 62.8078 | 89.17% | 88.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 62.8078 | 62.2153 | 88.33% | 87.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 62.2153 | 61.6228 | 87.5% | 86.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 61.6228 | 61.0302 | 86.67% | 85.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 61.0302 | 60.4377 | 85.83% | 85% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 60.4377 | 59.8452 | 85% | 84.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 59.8452 | 59.2527 | 84.17% | 83.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 59.2527 | 58.6601 | 83.33% | 82.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 58.6601 | 58.0676 | 82.5% | 81.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 58.0676 | 57.4751 | 81.67% | 80.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 57.4751 | 56.8826 | 80.83% | 80% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 01:00 | 2023-12-31 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 56.8826 | 56.29 | 80% | 79.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 01:05 | 2023-12-31 20:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 56.29 | 55.6975 | 79.17% | 78.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 01:10 | 2023-12-31 20:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 55.6975 | 55.105 | 78.33% | 77.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 01:15 | 2023-12-31 20:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 55.105 | 54.5125 | 77.5% | 76.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 01:20 | 2023-12-31 20:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 54.5125 | 53.9199 | 76.67% | 75.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 01:25 | 2023-12-31 20:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 53.9199 | 53.3274 | 75.83% | 75% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 01:30 | 2023-12-31 20:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 53.3274 | 52.7349 | 75% | 74.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 01:35 | 2023-12-31 20:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 52.7349 | 52.1423 | 74.17% | 73.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 01:40 | 2023-12-31 20:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 52.1423 | 51.5498 | 73.33% | 72.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 01:45 | 2023-12-31 20:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 51.5498 | 50.9573 | 72.5% | 71.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 01:50 | 2023-12-31 20:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 50.9573 | 50.3648 | 71.67% | 70.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 01:55 | 2023-12-31 20:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 50.3648 | 49.7722 | 70.83% | 70% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 02:00 | 2023-12-31 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 49.7722 | 49.1797 | 70% | 69.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 02:05 | 2023-12-31 21:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 49.1797 | 48.5872 | 69.17% | 68.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 02:10 | 2023-12-31 21:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 48.5872 | 47.9947 | 68.33% | 67.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 02:15 | 2023-12-31 21:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 47.9947 | 47.4021 | 67.5% | 66.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 02:20 | 2023-12-31 21:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 47.4021 | 46.8096 | 66.67% | 65.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 02:25 | 2023-12-31 21:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 46.8096 | 46.2171 | 65.83% | 65% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 02:30 | 2023-12-31 21:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 46.2171 | 45.6246 | 65% | 64.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 02:35 | 2023-12-31 21:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 45.6246 | 45.032 | 64.17% | 63.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 02:40 | 2023-12-31 21:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 45.032 | 44.4395 | 63.33% | 62.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 02:45 | 2023-12-31 21:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 44.4395 | 43.847 | 62.5% | 61.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 02:50 | 2023-12-31 21:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 43.847 | 43.2544 | 61.67% | 60.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 02:55 | 2023-12-31 21:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 43.2544 | 42.6619 | 60.83% | 60% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 03:00 | 2023-12-31 22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 42.6619 | 42.0694 | 60% | 59.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 03:05 | 2023-12-31 22:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 42.0694 | 41.4769 | 59.17% | 58.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 03:10 | 2023-12-31 22:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 41.4769 | 40.8843 | 58.33% | 57.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 03:15 | 2023-12-31 22:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 40.8843 | 40.2918 | 57.5% | 56.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 03:20 | 2023-12-31 22:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 40.2918 | 39.6993 | 56.67% | 55.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 03:25 | 2023-12-31 22:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 39.6993 | 39.1068 | 55.83% | 55% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 03:30 | 2023-12-31 22:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 39.1068 | 38.5142 | 55% | 54.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 03:35 | 2023-12-31 22:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 38.5142 | 37.9217 | 54.17% | 53.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 03:40 | 2023-12-31 22:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 37.9217 | 37.3292 | 53.33% | 52.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 03:45 | 2023-12-31 22:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 37.3292 | 36.7367 | 52.5% | 51.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 03:50 | 2023-12-31 22:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 36.7367 | 36.1441 | 51.67% | 50.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 03:55 | 2023-12-31 22:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 36.1441 | 35.5516 | 50.83% | 50% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 04:00 | 2023-12-31 23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 35.5516 | 34.9591 | 50% | 49.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 04:05 | 2023-12-31 23:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 34.9591 | 34.3665 | 49.17% | 48.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 04:10 | 2023-12-31 23:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 34.3665 | 33.774 | 48.33% | 47.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 04:15 | 2023-12-31 23:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 33.774 | 33.1815 | 47.5% | 46.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 04:20 | 2023-12-31 23:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 33.1815 | 32.589 | 46.67% | 45.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 04:25 | 2023-12-31 23:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 32.589 | 31.9964 | 45.83% | 45% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 04:30 | 2023-12-31 23:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 31.9964 | 31.4039 | 45% | 44.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 04:35 | 2023-12-31 23:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 31.4039 | 30.8114 | 44.17% | 43.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 04:40 | 2023-12-31 23:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 30.8114 | 30.2189 | 43.33% | 42.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 04:45 | 2023-12-31 23:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 30.2189 | 29.6263 | 42.5% | 41.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 04:50 | 2023-12-31 23:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 29.6263 | 29.0338 | 41.67% | 40.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 04:55 | 2023-12-31 23:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 29.0338 | 28.4413 | 40.83% | 40% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 05:00 | 2024-01-01 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 28.4413 | 27.8488 | 40% | 39.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 05:05 | 2024-01-01 00:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 27.8488 | 27.2562 | 39.17% | 38.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 05:10 | 2024-01-01 00:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 27.2562 | 26.6637 | 38.33% | 37.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 05:15 | 2024-01-01 00:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 26.6637 | 26.0712 | 37.5% | 36.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 05:20 | 2024-01-01 00:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 26.0712 | 25.4786 | 36.67% | 35.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 05:25 | 2024-01-01 00:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 25.4786 | 24.8861 | 35.83% | 35% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 05:30 | 2024-01-01 00:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 24.8861 | 24.2936 | 35% | 34.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 05:35 | 2024-01-01 00:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 24.2936 | 23.7011 | 34.17% | 33.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 05:40 | 2024-01-01 00:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 23.7011 | 23.1085 | 33.33% | 32.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 05:45 | 2024-01-01 00:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 23.1085 | 22.516 | 32.5% | 31.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 05:50 | 2024-01-01 00:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 22.516 | 21.9235 | 31.67% | 30.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 05:55 | 2024-01-01 00:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 21.9235 | 21.331 | 30.83% | 30% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 06:00 | 2024-01-01 01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 21.331 | 20.7384 | 30% | 29.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 06:05 | 2024-01-01 01:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 20.7384 | 20.1459 | 29.17% | 28.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 06:10 | 2024-01-01 01:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 20.1459 | 19.5534 | 28.33% | 27.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 06:15 | 2024-01-01 01:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 19.5534 | 18.9609 | 27.5% | 26.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 06:20 | 2024-01-01 01:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 18.9609 | 18.3683 | 26.67% | 25.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 06:25 | 2024-01-01 01:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 18.3683 | 17.7758 | 25.83% | 25% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 06:30 | 2024-01-01 01:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 17.7758 | 17.1833 | 25% | 24.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 06:35 | 2024-01-01 01:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 17.1833 | 16.5907 | 24.17% | 23.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 06:40 | 2024-01-01 01:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 16.5907 | 15.9982 | 23.33% | 22.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 06:45 | 2024-01-01 01:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 15.9982 | 15.4057 | 22.5% | 21.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 06:50 | 2024-01-01 01:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 15.4057 | 14.8132 | 21.67% | 20.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 06:55 | 2024-01-01 01:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 14.8132 | 14.2206 | 20.83% | 20% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 07:00 | 2024-01-01 02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 14.2206 | 13.6281 | 20% | 19.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 07:05 | 2024-01-01 02:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 13.6281 | 13.0356 | 19.17% | 18.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 07:10 | 2024-01-01 02:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 13.0356 | 12.4431 | 18.33% | 17.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 07:15 | 2024-01-01 02:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 12.4431 | 11.8505 | 17.5% | 16.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 07:20 | 2024-01-01 02:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 11.8505 | 11.258 | 16.67% | 15.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 07:25 | 2024-01-01 02:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 11.258 | 10.6655 | 15.83% | 15% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 07:30 | 2024-01-01 02:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 10.6655 | 10.073 | 15% | 14.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 07:35 | 2024-01-01 02:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 10.073 | 9.4804 | 14.17% | 13.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 07:40 | 2024-01-01 02:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 9.4804 | 8.8879 | 13.33% | 12.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 07:45 | 2024-01-01 02:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 8.8879 | 8.2954 | 12.5% | 11.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 07:50 | 2024-01-01 02:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 8.2954 | 7.7028 | 11.67% | 10.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 3.3774 | 6.7548 | 71.1032 | 2024-01-01 07:55 | 2024-01-01 02:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 7.7028 | 7.1103 | 10.83% | 10% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 63.9929 | 63.4004 | 90% | 89.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 63.4004 | 62.8078 | 89.17% | 88.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 62.8078 | 62.2153 | 88.33% | 87.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 62.2153 | 61.6228 | 87.5% | 86.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 61.6228 | 61.0302 | 86.67% | 85.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 61.0302 | 60.4377 | 85.83% | 85% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 60.4377 | 59.8452 | 85% | 84.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 59.8452 | 59.2527 | 84.17% | 83.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 59.2527 | 58.6601 | 83.33% | 82.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 58.6601 | 58.0676 | 82.5% | 81.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 58.0676 | 57.4751 | 81.67% | 80.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 57.4751 | 56.8826 | 80.83% | 80% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 01:00 | 2023-12-31 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 56.8826 | 56.29 | 80% | 79.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 01:05 | 2023-12-31 20:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 56.29 | 55.6975 | 79.17% | 78.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 01:10 | 2023-12-31 20:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 55.6975 | 55.105 | 78.33% | 77.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 01:15 | 2023-12-31 20:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 55.105 | 54.5125 | 77.5% | 76.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 01:20 | 2023-12-31 20:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 54.5125 | 53.9199 | 76.67% | 75.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 01:25 | 2023-12-31 20:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 53.9199 | 53.3274 | 75.83% | 75% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 01:30 | 2023-12-31 20:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 53.3274 | 52.7349 | 75% | 74.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 01:35 | 2023-12-31 20:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 52.7349 | 52.1423 | 74.17% | 73.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 01:40 | 2023-12-31 20:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 52.1423 | 51.5498 | 73.33% | 72.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 01:45 | 2023-12-31 20:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 51.5498 | 50.9573 | 72.5% | 71.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 01:50 | 2023-12-31 20:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 50.9573 | 50.3648 | 71.67% | 70.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 01:55 | 2023-12-31 20:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 50.3648 | 49.7722 | 70.83% | 70% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 02:00 | 2023-12-31 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 49.7722 | 49.1797 | 70% | 69.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 02:05 | 2023-12-31 21:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 49.1797 | 48.5872 | 69.17% | 68.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 02:10 | 2023-12-31 21:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 48.5872 | 47.9947 | 68.33% | 67.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 02:15 | 2023-12-31 21:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 47.9947 | 47.4021 | 67.5% | 66.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 02:20 | 2023-12-31 21:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 47.4021 | 46.8096 | 66.67% | 65.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 02:25 | 2023-12-31 21:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 46.8096 | 46.2171 | 65.83% | 65% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 02:30 | 2023-12-31 21:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 46.2171 | 45.6246 | 65% | 64.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 02:35 | 2023-12-31 21:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 45.6246 | 45.032 | 64.17% | 63.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 02:40 | 2023-12-31 21:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 45.032 | 44.4395 | 63.33% | 62.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 02:45 | 2023-12-31 21:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 44.4395 | 43.847 | 62.5% | 61.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 02:50 | 2023-12-31 21:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 43.847 | 43.2544 | 61.67% | 60.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 02:55 | 2023-12-31 21:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 43.2544 | 42.6619 | 60.83% | 60% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 03:00 | 2023-12-31 22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 42.6619 | 42.0694 | 60% | 59.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 03:05 | 2023-12-31 22:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 42.0694 | 41.4769 | 59.17% | 58.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 03:10 | 2023-12-31 22:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 41.4769 | 40.8843 | 58.33% | 57.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 03:15 | 2023-12-31 22:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 40.8843 | 40.2918 | 57.5% | 56.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 03:20 | 2023-12-31 22:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 40.2918 | 39.6993 | 56.67% | 55.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 03:25 | 2023-12-31 22:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 39.6993 | 39.1068 | 55.83% | 55% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 03:30 | 2023-12-31 22:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 39.1068 | 38.5142 | 55% | 54.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 03:35 | 2023-12-31 22:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 38.5142 | 37.9217 | 54.17% | 53.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 03:40 | 2023-12-31 22:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 37.9217 | 37.3292 | 53.33% | 52.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 03:45 | 2023-12-31 22:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 37.3292 | 36.7367 | 52.5% | 51.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 03:50 | 2023-12-31 22:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 36.7367 | 36.1441 | 51.67% | 50.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 03:55 | 2023-12-31 22:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 36.1441 | 35.5516 | 50.83% | 50% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 04:00 | 2023-12-31 23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 35.5516 | 34.9591 | 50% | 49.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 04:05 | 2023-12-31 23:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 34.9591 | 34.3665 | 49.17% | 48.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 04:10 | 2023-12-31 23:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 34.3665 | 33.774 | 48.33% | 47.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 04:15 | 2023-12-31 23:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 33.774 | 33.1815 | 47.5% | 46.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 04:20 | 2023-12-31 23:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 33.1815 | 32.589 | 46.67% | 45.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 04:25 | 2023-12-31 23:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 32.589 | 31.9964 | 45.83% | 45% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 04:30 | 2023-12-31 23:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 31.9964 | 31.4039 | 45% | 44.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 04:35 | 2023-12-31 23:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 31.4039 | 30.8114 | 44.17% | 43.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 04:40 | 2023-12-31 23:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 30.8114 | 30.2189 | 43.33% | 42.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 04:45 | 2023-12-31 23:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 30.2189 | 29.6263 | 42.5% | 41.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 04:50 | 2023-12-31 23:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 29.6263 | 29.0338 | 41.67% | 40.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 04:55 | 2023-12-31 23:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 29.0338 | 28.4413 | 40.83% | 40% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 05:00 | 2024-01-01 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 28.4413 | 27.8488 | 40% | 39.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 05:05 | 2024-01-01 00:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 27.8488 | 27.2562 | 39.17% | 38.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 05:10 | 2024-01-01 00:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 27.2562 | 26.6637 | 38.33% | 37.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 05:15 | 2024-01-01 00:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 26.6637 | 26.0712 | 37.5% | 36.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 05:20 | 2024-01-01 00:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 26.0712 | 25.4786 | 36.67% | 35.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 05:25 | 2024-01-01 00:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 25.4786 | 24.8861 | 35.83% | 35% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 05:30 | 2024-01-01 00:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 24.8861 | 24.2936 | 35% | 34.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 05:35 | 2024-01-01 00:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 24.2936 | 23.7011 | 34.17% | 33.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 05:40 | 2024-01-01 00:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 23.7011 | 23.1085 | 33.33% | 32.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 05:45 | 2024-01-01 00:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 23.1085 | 22.516 | 32.5% | 31.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 05:50 | 2024-01-01 00:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 22.516 | 21.9235 | 31.67% | 30.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 05:55 | 2024-01-01 00:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 21.9235 | 21.331 | 30.83% | 30% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 06:00 | 2024-01-01 01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 21.331 | 20.7384 | 30% | 29.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 06:05 | 2024-01-01 01:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 20.7384 | 20.1459 | 29.17% | 28.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 06:10 | 2024-01-01 01:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 20.1459 | 19.5534 | 28.33% | 27.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 06:15 | 2024-01-01 01:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 19.5534 | 18.9609 | 27.5% | 26.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 06:20 | 2024-01-01 01:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 18.9609 | 18.3683 | 26.67% | 25.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 06:25 | 2024-01-01 01:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 18.3683 | 17.7758 | 25.83% | 25% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 06:30 | 2024-01-01 01:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 17.7758 | 17.1833 | 25% | 24.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 06:35 | 2024-01-01 01:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 17.1833 | 16.5907 | 24.17% | 23.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 06:40 | 2024-01-01 01:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 16.5907 | 15.9982 | 23.33% | 22.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 06:45 | 2024-01-01 01:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 15.9982 | 15.4057 | 22.5% | 21.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 06:50 | 2024-01-01 01:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 15.4057 | 14.8132 | 21.67% | 20.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 06:55 | 2024-01-01 01:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 14.8132 | 14.2206 | 20.83% | 20% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 07:00 | 2024-01-01 02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 14.2206 | 13.6281 | 20% | 19.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 07:05 | 2024-01-01 02:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 13.6281 | 13.0356 | 19.17% | 18.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 07:10 | 2024-01-01 02:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 13.0356 | 12.4431 | 18.33% | 17.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 07:15 | 2024-01-01 02:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 12.4431 | 11.8505 | 17.5% | 16.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 07:20 | 2024-01-01 02:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 11.8505 | 11.258 | 16.67% | 15.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 07:25 | 2024-01-01 02:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 11.258 | 10.6655 | 15.83% | 15% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 07:30 | 2024-01-01 02:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 10.6655 | 10.073 | 15% | 14.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 07:35 | 2024-01-01 02:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 10.073 | 9.4804 | 14.17% | 13.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 07:40 | 2024-01-01 02:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 9.4804 | 8.8879 | 13.33% | 12.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 07:45 | 2024-01-01 02:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 8.8879 | 8.2954 | 12.5% | 11.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 07:50 | 2024-01-01 02:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 8.2954 | 7.7028 | 11.67% | 10.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 6.7548 | 6.7548 | 71.1032 | 2024-01-01 07:55 | 2024-01-01 02:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 7.7028 | 7.1103 | 10.83% | 10% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 63.9929 | 63.4004 | 90% | 89.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 63.4004 | 62.8078 | 89.17% | 88.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 62.8078 | 62.2153 | 88.33% | 87.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 62.2153 | 61.6228 | 87.5% | 86.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 61.6228 | 61.0302 | 86.67% | 85.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 61.0302 | 60.4377 | 85.83% | 85% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 60.4377 | 59.8452 | 85% | 84.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 59.8452 | 59.2527 | 84.17% | 83.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 59.2527 | 58.6601 | 83.33% | 82.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 58.6601 | 58.0676 | 82.5% | 81.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 58.0676 | 57.4751 | 81.67% | 80.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 57.4751 | 56.8826 | 80.83% | 80% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 01:00 | 2023-12-31 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 56.8826 | 56.29 | 80% | 79.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 01:05 | 2023-12-31 20:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 56.29 | 55.6975 | 79.17% | 78.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 01:10 | 2023-12-31 20:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 55.6975 | 55.105 | 78.33% | 77.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 01:15 | 2023-12-31 20:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 55.105 | 54.5125 | 77.5% | 76.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 01:20 | 2023-12-31 20:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 54.5125 | 53.9199 | 76.67% | 75.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 01:25 | 2023-12-31 20:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 53.9199 | 53.3274 | 75.83% | 75% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 01:30 | 2023-12-31 20:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 53.3274 | 52.7349 | 75% | 74.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 01:35 | 2023-12-31 20:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 52.7349 | 52.1423 | 74.17% | 73.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 01:40 | 2023-12-31 20:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 52.1423 | 51.5498 | 73.33% | 72.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 01:45 | 2023-12-31 20:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 51.5498 | 50.9573 | 72.5% | 71.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 01:50 | 2023-12-31 20:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 50.9573 | 50.3648 | 71.67% | 70.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 01:55 | 2023-12-31 20:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 50.3648 | 49.7722 | 70.83% | 70% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 02:00 | 2023-12-31 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 49.7722 | 49.1797 | 70% | 69.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 02:05 | 2023-12-31 21:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 49.1797 | 48.5872 | 69.17% | 68.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 02:10 | 2023-12-31 21:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 48.5872 | 47.9947 | 68.33% | 67.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 02:15 | 2023-12-31 21:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 47.9947 | 47.4021 | 67.5% | 66.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 02:20 | 2023-12-31 21:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 47.4021 | 46.8096 | 66.67% | 65.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 02:25 | 2023-12-31 21:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 46.8096 | 46.2171 | 65.83% | 65% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 02:30 | 2023-12-31 21:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 46.2171 | 45.6246 | 65% | 64.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 02:35 | 2023-12-31 21:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 45.6246 | 45.032 | 64.17% | 63.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 02:40 | 2023-12-31 21:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 45.032 | 44.4395 | 63.33% | 62.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 02:45 | 2023-12-31 21:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 44.4395 | 43.847 | 62.5% | 61.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 02:50 | 2023-12-31 21:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 43.847 | 43.2544 | 61.67% | 60.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 02:55 | 2023-12-31 21:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 43.2544 | 42.6619 | 60.83% | 60% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 03:00 | 2023-12-31 22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 42.6619 | 42.0694 | 60% | 59.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 03:05 | 2023-12-31 22:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 42.0694 | 41.4769 | 59.17% | 58.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 03:10 | 2023-12-31 22:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 41.4769 | 40.8843 | 58.33% | 57.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 03:15 | 2023-12-31 22:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 40.8843 | 40.2918 | 57.5% | 56.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 03:20 | 2023-12-31 22:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 40.2918 | 39.6993 | 56.67% | 55.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 03:25 | 2023-12-31 22:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 39.6993 | 39.1068 | 55.83% | 55% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 03:30 | 2023-12-31 22:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 39.1068 | 38.5142 | 55% | 54.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 03:35 | 2023-12-31 22:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 38.5142 | 37.9217 | 54.17% | 53.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 03:40 | 2023-12-31 22:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 37.9217 | 37.3292 | 53.33% | 52.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 03:45 | 2023-12-31 22:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 37.3292 | 36.7367 | 52.5% | 51.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 03:50 | 2023-12-31 22:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 36.7367 | 36.1441 | 51.67% | 50.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 03:55 | 2023-12-31 22:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 36.1441 | 35.5516 | 50.83% | 50% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 04:00 | 2023-12-31 23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 35.5516 | 34.9591 | 50% | 49.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 04:05 | 2023-12-31 23:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 34.9591 | 34.3665 | 49.17% | 48.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 04:10 | 2023-12-31 23:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 34.3665 | 33.774 | 48.33% | 47.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 04:15 | 2023-12-31 23:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 33.774 | 33.1815 | 47.5% | 46.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 04:20 | 2023-12-31 23:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 33.1815 | 32.589 | 46.67% | 45.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 04:25 | 2023-12-31 23:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 32.589 | 31.9964 | 45.83% | 45% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 04:30 | 2023-12-31 23:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 31.9964 | 31.4039 | 45% | 44.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 04:35 | 2023-12-31 23:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 31.4039 | 30.8114 | 44.17% | 43.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 04:40 | 2023-12-31 23:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 30.8114 | 30.2189 | 43.33% | 42.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 04:45 | 2023-12-31 23:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 30.2189 | 29.6263 | 42.5% | 41.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 04:50 | 2023-12-31 23:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 29.6263 | 29.0338 | 41.67% | 40.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 04:55 | 2023-12-31 23:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 29.0338 | 28.4413 | 40.83% | 40% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 05:00 | 2024-01-01 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 28.4413 | 27.8488 | 40% | 39.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 05:05 | 2024-01-01 00:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 27.8488 | 27.2562 | 39.17% | 38.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 05:10 | 2024-01-01 00:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 27.2562 | 26.6637 | 38.33% | 37.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 05:15 | 2024-01-01 00:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 26.6637 | 26.0712 | 37.5% | 36.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 05:20 | 2024-01-01 00:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 26.0712 | 25.4786 | 36.67% | 35.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 05:25 | 2024-01-01 00:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 25.4786 | 24.8861 | 35.83% | 35% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 05:30 | 2024-01-01 00:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 24.8861 | 24.2936 | 35% | 34.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 05:35 | 2024-01-01 00:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 24.2936 | 23.7011 | 34.17% | 33.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 05:40 | 2024-01-01 00:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 23.7011 | 23.1085 | 33.33% | 32.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 05:45 | 2024-01-01 00:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 23.1085 | 22.516 | 32.5% | 31.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 05:50 | 2024-01-01 00:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 22.516 | 21.9235 | 31.67% | 30.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 05:55 | 2024-01-01 00:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 21.9235 | 21.331 | 30.83% | 30% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 06:00 | 2024-01-01 01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 21.331 | 20.7384 | 30% | 29.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 06:05 | 2024-01-01 01:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 20.7384 | 20.1459 | 29.17% | 28.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 06:10 | 2024-01-01 01:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 20.1459 | 19.5534 | 28.33% | 27.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 06:15 | 2024-01-01 01:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 19.5534 | 18.9609 | 27.5% | 26.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 06:20 | 2024-01-01 01:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 18.9609 | 18.3683 | 26.67% | 25.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 06:25 | 2024-01-01 01:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 18.3683 | 17.7758 | 25.83% | 25% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 06:30 | 2024-01-01 01:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 17.7758 | 17.1833 | 25% | 24.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 06:35 | 2024-01-01 01:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 17.1833 | 16.5907 | 24.17% | 23.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 06:40 | 2024-01-01 01:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 16.5907 | 15.9982 | 23.33% | 22.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 06:45 | 2024-01-01 01:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 15.9982 | 15.4057 | 22.5% | 21.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 06:50 | 2024-01-01 01:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 15.4057 | 14.8132 | 21.67% | 20.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 06:55 | 2024-01-01 01:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 14.8132 | 14.2206 | 20.83% | 20% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 07:00 | 2024-01-01 02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 14.2206 | 13.6281 | 20% | 19.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 07:05 | 2024-01-01 02:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 13.6281 | 13.0356 | 19.17% | 18.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 07:10 | 2024-01-01 02:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 13.0356 | 12.4431 | 18.33% | 17.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 07:15 | 2024-01-01 02:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 12.4431 | 11.8505 | 17.5% | 16.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 07:20 | 2024-01-01 02:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 11.8505 | 11.258 | 16.67% | 15.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 07:25 | 2024-01-01 02:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 11.258 | 10.6655 | 15.83% | 15% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 07:30 | 2024-01-01 02:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 10.6655 | 10.073 | 15% | 14.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 07:35 | 2024-01-01 02:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 10.073 | 9.4804 | 14.17% | 13.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 07:40 | 2024-01-01 02:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 9.4804 | 8.8879 | 13.33% | 12.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 07:45 | 2024-01-01 02:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 8.8879 | 8.2954 | 12.5% | 11.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 07:50 | 2024-01-01 02:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 8.2954 | 7.7028 | 11.67% | 10.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 10.1322 | 6.7548 | 71.1032 | 2024-01-01 07:55 | 2024-01-01 02:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 7.7028 | 7.1103 | 10.83% | 10% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 63.9929 | 63.4004 | 90% | 89.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 63.4004 | 62.8078 | 89.17% | 88.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 62.8078 | 62.2153 | 88.33% | 87.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 62.2153 | 61.6228 | 87.5% | 86.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 61.6228 | 61.0302 | 86.67% | 85.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 61.0302 | 60.4377 | 85.83% | 85% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 60.4377 | 59.8452 | 85% | 84.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 59.8452 | 59.2527 | 84.17% | 83.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 59.2527 | 58.6601 | 83.33% | 82.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 58.6601 | 58.0676 | 82.5% | 81.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 58.0676 | 57.4751 | 81.67% | 80.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 57.4751 | 56.8826 | 80.83% | 80% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 01:00 | 2023-12-31 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 56.8826 | 56.29 | 80% | 79.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 01:05 | 2023-12-31 20:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 56.29 | 55.6975 | 79.17% | 78.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 01:10 | 2023-12-31 20:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 55.6975 | 55.105 | 78.33% | 77.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 01:15 | 2023-12-31 20:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 55.105 | 54.5125 | 77.5% | 76.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 01:20 | 2023-12-31 20:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 54.5125 | 53.9199 | 76.67% | 75.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 01:25 | 2023-12-31 20:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 53.9199 | 53.3274 | 75.83% | 75% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 01:30 | 2023-12-31 20:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 53.3274 | 52.7349 | 75% | 74.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 01:35 | 2023-12-31 20:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 52.7349 | 52.1423 | 74.17% | 73.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 01:40 | 2023-12-31 20:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 52.1423 | 51.5498 | 73.33% | 72.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 01:45 | 2023-12-31 20:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 51.5498 | 50.9573 | 72.5% | 71.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 01:50 | 2023-12-31 20:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 50.9573 | 50.3648 | 71.67% | 70.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 01:55 | 2023-12-31 20:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 50.3648 | 49.7722 | 70.83% | 70% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 02:00 | 2023-12-31 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 49.7722 | 49.1797 | 70% | 69.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 02:05 | 2023-12-31 21:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 49.1797 | 48.5872 | 69.17% | 68.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 02:10 | 2023-12-31 21:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 48.5872 | 47.9947 | 68.33% | 67.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 02:15 | 2023-12-31 21:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 47.9947 | 47.4021 | 67.5% | 66.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 02:20 | 2023-12-31 21:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 47.4021 | 46.8096 | 66.67% | 65.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 02:25 | 2023-12-31 21:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 46.8096 | 46.2171 | 65.83% | 65% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 02:30 | 2023-12-31 21:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 46.2171 | 45.6246 | 65% | 64.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 02:35 | 2023-12-31 21:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 45.6246 | 45.032 | 64.17% | 63.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 02:40 | 2023-12-31 21:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 45.032 | 44.4395 | 63.33% | 62.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 02:45 | 2023-12-31 21:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 44.4395 | 43.847 | 62.5% | 61.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 02:50 | 2023-12-31 21:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 43.847 | 43.2544 | 61.67% | 60.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 02:55 | 2023-12-31 21:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 43.2544 | 42.6619 | 60.83% | 60% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 03:00 | 2023-12-31 22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 42.6619 | 42.0694 | 60% | 59.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 03:05 | 2023-12-31 22:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 42.0694 | 41.4769 | 59.17% | 58.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 03:10 | 2023-12-31 22:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 41.4769 | 40.8843 | 58.33% | 57.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 03:15 | 2023-12-31 22:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 40.8843 | 40.2918 | 57.5% | 56.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 03:20 | 2023-12-31 22:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 40.2918 | 39.6993 | 56.67% | 55.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 03:25 | 2023-12-31 22:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 39.6993 | 39.1068 | 55.83% | 55% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 03:30 | 2023-12-31 22:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 39.1068 | 38.5142 | 55% | 54.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 03:35 | 2023-12-31 22:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 38.5142 | 37.9217 | 54.17% | 53.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 03:40 | 2023-12-31 22:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 37.9217 | 37.3292 | 53.33% | 52.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 03:45 | 2023-12-31 22:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 37.3292 | 36.7367 | 52.5% | 51.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 03:50 | 2023-12-31 22:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 36.7367 | 36.1441 | 51.67% | 50.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 03:55 | 2023-12-31 22:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 36.1441 | 35.5516 | 50.83% | 50% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 04:00 | 2023-12-31 23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 35.5516 | 34.9591 | 50% | 49.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 04:05 | 2023-12-31 23:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 34.9591 | 34.3665 | 49.17% | 48.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 04:10 | 2023-12-31 23:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 34.3665 | 33.774 | 48.33% | 47.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 04:15 | 2023-12-31 23:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 33.774 | 33.1815 | 47.5% | 46.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 04:20 | 2023-12-31 23:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 33.1815 | 32.589 | 46.67% | 45.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 04:25 | 2023-12-31 23:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 32.589 | 31.9964 | 45.83% | 45% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 04:30 | 2023-12-31 23:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 31.9964 | 31.4039 | 45% | 44.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 04:35 | 2023-12-31 23:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 31.4039 | 30.8114 | 44.17% | 43.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 04:40 | 2023-12-31 23:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 30.8114 | 30.2189 | 43.33% | 42.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 04:45 | 2023-12-31 23:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 30.2189 | 29.6263 | 42.5% | 41.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 04:50 | 2023-12-31 23:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 29.6263 | 29.0338 | 41.67% | 40.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 04:55 | 2023-12-31 23:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 29.0338 | 28.4413 | 40.83% | 40% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 05:00 | 2024-01-01 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 28.4413 | 27.8488 | 40% | 39.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 05:05 | 2024-01-01 00:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 27.8488 | 27.2562 | 39.17% | 38.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 05:10 | 2024-01-01 00:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 27.2562 | 26.6637 | 38.33% | 37.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 05:15 | 2024-01-01 00:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 26.6637 | 26.0712 | 37.5% | 36.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 05:20 | 2024-01-01 00:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 26.0712 | 25.4786 | 36.67% | 35.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 05:25 | 2024-01-01 00:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 25.4786 | 24.8861 | 35.83% | 35% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 05:30 | 2024-01-01 00:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 24.8861 | 24.2936 | 35% | 34.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 05:35 | 2024-01-01 00:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 24.2936 | 23.7011 | 34.17% | 33.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 05:40 | 2024-01-01 00:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 23.7011 | 23.1085 | 33.33% | 32.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 05:45 | 2024-01-01 00:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 23.1085 | 22.516 | 32.5% | 31.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 05:50 | 2024-01-01 00:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 22.516 | 21.9235 | 31.67% | 30.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 05:55 | 2024-01-01 00:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 21.9235 | 21.331 | 30.83% | 30% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 06:00 | 2024-01-01 01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 21.331 | 20.7384 | 30% | 29.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 06:05 | 2024-01-01 01:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 20.7384 | 20.1459 | 29.17% | 28.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 06:10 | 2024-01-01 01:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 20.1459 | 19.5534 | 28.33% | 27.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 06:15 | 2024-01-01 01:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 19.5534 | 18.9609 | 27.5% | 26.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 06:20 | 2024-01-01 01:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 18.9609 | 18.3683 | 26.67% | 25.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 06:25 | 2024-01-01 01:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 18.3683 | 17.7758 | 25.83% | 25% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 06:30 | 2024-01-01 01:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 17.7758 | 17.1833 | 25% | 24.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 06:35 | 2024-01-01 01:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 17.1833 | 16.5907 | 24.17% | 23.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 06:40 | 2024-01-01 01:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 16.5907 | 15.9982 | 23.33% | 22.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 06:45 | 2024-01-01 01:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 15.9982 | 15.4057 | 22.5% | 21.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 06:50 | 2024-01-01 01:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 15.4057 | 14.8132 | 21.67% | 20.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 06:55 | 2024-01-01 01:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 14.8132 | 14.2206 | 20.83% | 20% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 07:00 | 2024-01-01 02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 14.2206 | 13.6281 | 20% | 19.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 07:05 | 2024-01-01 02:05 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 13.6281 | 13.0356 | 19.17% | 18.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 07:10 | 2024-01-01 02:10 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 13.0356 | 12.4431 | 18.33% | 17.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 07:15 | 2024-01-01 02:15 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 12.4431 | 11.8505 | 17.5% | 16.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 07:20 | 2024-01-01 02:20 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 11.8505 | 11.258 | 16.67% | 15.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 07:25 | 2024-01-01 02:25 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 11.258 | 10.6655 | 15.83% | 15% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 07:30 | 2024-01-01 02:30 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 10.6655 | 10.073 | 15% | 14.17% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 07:35 | 2024-01-01 02:35 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 10.073 | 9.4804 | 14.17% | 13.33% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 07:40 | 2024-01-01 02:40 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 9.4804 | 8.8879 | 13.33% | 12.5% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 07:45 | 2024-01-01 02:45 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 8.8879 | 8.2954 | 12.5% | 11.67% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 07:50 | 2024-01-01 02:50 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 8.2954 | 7.7028 | 11.67% | 10.83% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.5 | 8 | 13.5096 | 6.7548 | 71.1032 | 2024-01-01 07:55 | 2024-01-01 02:55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7548 | 7.7028 | 7.1103 | 10.83% | 10% | 7.1103 | 6.7548 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 1 | 0 | 10.1322 | 13.3319 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 11.9987 | 11.1099 | 90% | 83.33% | 1.3332 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 1 | 0 | 10.1322 | 13.3319 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 11.1099 | 10.2211 | 83.33% | 76.67% | 1.3332 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 1 | 0 | 10.1322 | 13.3319 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 10.2211 | 9.3323 | 76.67% | 70% | 1.3332 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 1 | 0 | 10.1322 | 13.3319 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 9.3323 | 8.4435 | 70% | 63.33% | 1.3332 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 1 | 0 | 10.1322 | 13.3319 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 8.4435 | 7.5547 | 63.33% | 56.67% | 1.3332 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 1 | 0 | 10.1322 | 13.3319 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 7.5547 | 6.6659 | 56.67% | 50% | 1.3332 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 1 | 0 | 10.1322 | 13.3319 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 6.6659 | 5.7771 | 50% | 43.33% | 1.3332 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 1 | 0 | 10.1322 | 13.3319 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 5.7771 | 4.8883 | 43.33% | 36.67% | 1.3332 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 1 | 0 | 10.1322 | 13.3319 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 4.8883 | 3.9996 | 36.67% | 30% | 1.3332 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 1 | 0 | 10.1322 | 13.3319 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 3.9996 | 3.1108 | 30% | 23.33% | 1.3332 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 1 | 0 | 10.1322 | 13.3319 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 3.1108 | 2.222 | 23.33% | 16.67% | 1.3332 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 1 | 0 | 10.1322 | 13.3319 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 2.222 | 1.3332 | 16.67% | 10% | 1.3332 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 1 | 3.3774 | 10.1322 | 13.3319 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 11.9987 | 11.1099 | 90% | 83.33% | 1.3332 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 1 | 3.3774 | 10.1322 | 13.3319 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 11.1099 | 10.2211 | 83.33% | 76.67% | 1.3332 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 1 | 3.3774 | 10.1322 | 13.3319 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 10.2211 | 9.3323 | 76.67% | 70% | 1.3332 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 1 | 3.3774 | 10.1322 | 13.3319 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 9.3323 | 8.4435 | 70% | 63.33% | 1.3332 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 1 | 3.3774 | 10.1322 | 13.3319 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 8.4435 | 7.5547 | 63.33% | 56.67% | 1.3332 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 1 | 3.3774 | 10.1322 | 13.3319 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 7.5547 | 6.6659 | 56.67% | 50% | 1.3332 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 1 | 3.3774 | 10.1322 | 13.3319 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 6.6659 | 5.7771 | 50% | 43.33% | 1.3332 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 1 | 3.3774 | 10.1322 | 13.3319 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 5.7771 | 4.8883 | 43.33% | 36.67% | 1.3332 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 1 | 3.3774 | 10.1322 | 13.3319 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 4.8883 | 3.9996 | 36.67% | 30% | 1.3332 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 1 | 3.3774 | 10.1322 | 13.3319 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 3.9996 | 3.1108 | 30% | 23.33% | 1.3332 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 1 | 3.3774 | 10.1322 | 13.3319 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 3.1108 | 2.222 | 23.33% | 16.67% | 1.3332 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 1 | 3.3774 | 10.1322 | 13.3319 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 2.222 | 1.3332 | 16.67% | 10% | 1.3332 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 1 | 6.7548 | 10.1322 | 13.3319 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 11.9987 | 11.1099 | 90% | 83.33% | 1.3332 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 1 | 6.7548 | 10.1322 | 13.3319 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 11.1099 | 10.2211 | 83.33% | 76.67% | 1.3332 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 1 | 6.7548 | 10.1322 | 13.3319 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 10.2211 | 9.3323 | 76.67% | 70% | 1.3332 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 1 | 6.7548 | 10.1322 | 13.3319 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 9.3323 | 8.4435 | 70% | 63.33% | 1.3332 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 1 | 6.7548 | 10.1322 | 13.3319 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 8.4435 | 7.5547 | 63.33% | 56.67% | 1.3332 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 1 | 6.7548 | 10.1322 | 13.3319 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 7.5547 | 6.6659 | 56.67% | 50% | 1.3332 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 1 | 6.7548 | 10.1322 | 13.3319 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 6.6659 | 5.7771 | 50% | 43.33% | 1.3332 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 1 | 6.7548 | 10.1322 | 13.3319 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 5.7771 | 4.8883 | 43.33% | 36.67% | 1.3332 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 1 | 6.7548 | 10.1322 | 13.3319 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 4.8883 | 3.9996 | 36.67% | 30% | 1.3332 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 1 | 6.7548 | 10.1322 | 13.3319 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 3.9996 | 3.1108 | 30% | 23.33% | 1.3332 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 1 | 6.7548 | 10.1322 | 13.3319 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 3.1108 | 2.222 | 23.33% | 16.67% | 1.3332 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 1 | 6.7548 | 10.1322 | 13.3319 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 2.222 | 1.3332 | 16.67% | 10% | 1.3332 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 1 | 10.1322 | 10.1322 | 13.3319 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 11.9987 | 11.1099 | 90% | 83.33% | 1.3332 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 1 | 10.1322 | 10.1322 | 13.3319 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 11.1099 | 10.2211 | 83.33% | 76.67% | 1.3332 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 1 | 10.1322 | 10.1322 | 13.3319 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 10.2211 | 9.3323 | 76.67% | 70% | 1.3332 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 1 | 10.1322 | 10.1322 | 13.3319 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 9.3323 | 8.4435 | 70% | 63.33% | 1.3332 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 1 | 10.1322 | 10.1322 | 13.3319 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 8.4435 | 7.5547 | 63.33% | 56.67% | 1.3332 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 1 | 10.1322 | 10.1322 | 13.3319 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 7.5547 | 6.6659 | 56.67% | 50% | 1.3332 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 1 | 10.1322 | 10.1322 | 13.3319 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 6.6659 | 5.7771 | 50% | 43.33% | 1.3332 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 1 | 10.1322 | 10.1322 | 13.3319 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 5.7771 | 4.8883 | 43.33% | 36.67% | 1.3332 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 1 | 10.1322 | 10.1322 | 13.3319 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 4.8883 | 3.9996 | 36.67% | 30% | 1.3332 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 1 | 10.1322 | 10.1322 | 13.3319 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 3.9996 | 3.1108 | 30% | 23.33% | 1.3332 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 1 | 10.1322 | 10.1322 | 13.3319 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 3.1108 | 2.222 | 23.33% | 16.67% | 1.3332 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 1 | 10.1322 | 10.1322 | 13.3319 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 2.222 | 1.3332 | 16.67% | 10% | 1.3332 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 1 | 13.5096 | 10.1322 | 13.3319 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 11.9987 | 11.1099 | 90% | 83.33% | 1.3332 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 1 | 13.5096 | 10.1322 | 13.3319 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 11.1099 | 10.2211 | 83.33% | 76.67% | 1.3332 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 1 | 13.5096 | 10.1322 | 13.3319 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 10.2211 | 9.3323 | 76.67% | 70% | 1.3332 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 1 | 13.5096 | 10.1322 | 13.3319 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 9.3323 | 8.4435 | 70% | 63.33% | 1.3332 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 1 | 13.5096 | 10.1322 | 13.3319 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 8.4435 | 7.5547 | 63.33% | 56.67% | 1.3332 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 1 | 13.5096 | 10.1322 | 13.3319 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 7.5547 | 6.6659 | 56.67% | 50% | 1.3332 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 1 | 13.5096 | 10.1322 | 13.3319 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 6.6659 | 5.7771 | 50% | 43.33% | 1.3332 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 1 | 13.5096 | 10.1322 | 13.3319 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 5.7771 | 4.8883 | 43.33% | 36.67% | 1.3332 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 1 | 13.5096 | 10.1322 | 13.3319 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 4.8883 | 3.9996 | 36.67% | 30% | 1.3332 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 1 | 13.5096 | 10.1322 | 13.3319 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 3.9996 | 3.1108 | 30% | 23.33% | 1.3332 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 1 | 13.5096 | 10.1322 | 13.3319 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 3.1108 | 2.222 | 23.33% | 16.67% | 1.3332 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 1 | 13.5096 | 10.1322 | 13.3319 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 2.222 | 1.3332 | 16.67% | 10% | 1.3332 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 0 | 10.1322 | 26.6637 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 23.9973 | 23.1085 | 90% | 86.67% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 0 | 10.1322 | 26.6637 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 23.1085 | 22.2198 | 86.67% | 83.33% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 0 | 10.1322 | 26.6637 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 22.2198 | 21.331 | 83.33% | 80% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 0 | 10.1322 | 26.6637 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 21.331 | 20.4422 | 80% | 76.67% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 0 | 10.1322 | 26.6637 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 20.4422 | 19.5534 | 76.67% | 73.33% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 0 | 10.1322 | 26.6637 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 19.5534 | 18.6646 | 73.33% | 70% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 0 | 10.1322 | 26.6637 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 18.6646 | 17.7758 | 70% | 66.67% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 0 | 10.1322 | 26.6637 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 17.7758 | 16.887 | 66.67% | 63.33% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 0 | 10.1322 | 26.6637 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 16.887 | 15.9982 | 63.33% | 60% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 0 | 10.1322 | 26.6637 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 15.9982 | 15.1094 | 60% | 56.67% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 0 | 10.1322 | 26.6637 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 15.1094 | 14.2206 | 56.67% | 53.33% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 0 | 10.1322 | 26.6637 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 14.2206 | 13.3319 | 53.33% | 50% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 0 | 10.1322 | 26.6637 | 2024-01-01 01:00 | 2023-12-31 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 13.3319 | 12.4431 | 50% | 46.67% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 0 | 10.1322 | 26.6637 | 2024-01-01 01:05 | 2023-12-31 20:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 12.4431 | 11.5543 | 46.67% | 43.33% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 0 | 10.1322 | 26.6637 | 2024-01-01 01:10 | 2023-12-31 20:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 11.5543 | 10.6655 | 43.33% | 40% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 0 | 10.1322 | 26.6637 | 2024-01-01 01:15 | 2023-12-31 20:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 10.6655 | 9.7767 | 40% | 36.67% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 0 | 10.1322 | 26.6637 | 2024-01-01 01:20 | 2023-12-31 20:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 9.7767 | 8.8879 | 36.67% | 33.33% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 0 | 10.1322 | 26.6637 | 2024-01-01 01:25 | 2023-12-31 20:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 8.8879 | 7.9991 | 33.33% | 30% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 0 | 10.1322 | 26.6637 | 2024-01-01 01:30 | 2023-12-31 20:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 7.9991 | 7.1103 | 30% | 26.67% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 0 | 10.1322 | 26.6637 | 2024-01-01 01:35 | 2023-12-31 20:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 7.1103 | 6.2215 | 26.67% | 23.33% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 0 | 10.1322 | 26.6637 | 2024-01-01 01:40 | 2023-12-31 20:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 6.2215 | 5.3327 | 23.33% | 20% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 0 | 10.1322 | 26.6637 | 2024-01-01 01:45 | 2023-12-31 20:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 5.3327 | 4.444 | 20% | 16.67% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 0 | 10.1322 | 26.6637 | 2024-01-01 01:50 | 2023-12-31 20:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 4.444 | 3.5552 | 16.67% | 13.33% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 0 | 10.1322 | 26.6637 | 2024-01-01 01:55 | 2023-12-31 20:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 3.5552 | 2.6664 | 13.33% | 10% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 3.3774 | 10.1322 | 26.6637 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 23.9973 | 23.1085 | 90% | 86.67% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 3.3774 | 10.1322 | 26.6637 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 23.1085 | 22.2198 | 86.67% | 83.33% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 3.3774 | 10.1322 | 26.6637 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 22.2198 | 21.331 | 83.33% | 80% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 3.3774 | 10.1322 | 26.6637 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 21.331 | 20.4422 | 80% | 76.67% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 3.3774 | 10.1322 | 26.6637 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 20.4422 | 19.5534 | 76.67% | 73.33% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 3.3774 | 10.1322 | 26.6637 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 19.5534 | 18.6646 | 73.33% | 70% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 3.3774 | 10.1322 | 26.6637 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 18.6646 | 17.7758 | 70% | 66.67% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 3.3774 | 10.1322 | 26.6637 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 17.7758 | 16.887 | 66.67% | 63.33% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 3.3774 | 10.1322 | 26.6637 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 16.887 | 15.9982 | 63.33% | 60% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 3.3774 | 10.1322 | 26.6637 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 15.9982 | 15.1094 | 60% | 56.67% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 3.3774 | 10.1322 | 26.6637 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 15.1094 | 14.2206 | 56.67% | 53.33% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 3.3774 | 10.1322 | 26.6637 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 14.2206 | 13.3319 | 53.33% | 50% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 3.3774 | 10.1322 | 26.6637 | 2024-01-01 01:00 | 2023-12-31 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 13.3319 | 12.4431 | 50% | 46.67% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 3.3774 | 10.1322 | 26.6637 | 2024-01-01 01:05 | 2023-12-31 20:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 12.4431 | 11.5543 | 46.67% | 43.33% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 3.3774 | 10.1322 | 26.6637 | 2024-01-01 01:10 | 2023-12-31 20:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 11.5543 | 10.6655 | 43.33% | 40% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 3.3774 | 10.1322 | 26.6637 | 2024-01-01 01:15 | 2023-12-31 20:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 10.6655 | 9.7767 | 40% | 36.67% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 3.3774 | 10.1322 | 26.6637 | 2024-01-01 01:20 | 2023-12-31 20:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 9.7767 | 8.8879 | 36.67% | 33.33% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 3.3774 | 10.1322 | 26.6637 | 2024-01-01 01:25 | 2023-12-31 20:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 8.8879 | 7.9991 | 33.33% | 30% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 3.3774 | 10.1322 | 26.6637 | 2024-01-01 01:30 | 2023-12-31 20:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 7.9991 | 7.1103 | 30% | 26.67% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 3.3774 | 10.1322 | 26.6637 | 2024-01-01 01:35 | 2023-12-31 20:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 7.1103 | 6.2215 | 26.67% | 23.33% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 3.3774 | 10.1322 | 26.6637 | 2024-01-01 01:40 | 2023-12-31 20:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 6.2215 | 5.3327 | 23.33% | 20% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 3.3774 | 10.1322 | 26.6637 | 2024-01-01 01:45 | 2023-12-31 20:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 5.3327 | 4.444 | 20% | 16.67% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 3.3774 | 10.1322 | 26.6637 | 2024-01-01 01:50 | 2023-12-31 20:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 4.444 | 3.5552 | 16.67% | 13.33% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 3.3774 | 10.1322 | 26.6637 | 2024-01-01 01:55 | 2023-12-31 20:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 3.5552 | 2.6664 | 13.33% | 10% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 6.7548 | 10.1322 | 26.6637 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 23.9973 | 23.1085 | 90% | 86.67% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 6.7548 | 10.1322 | 26.6637 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 23.1085 | 22.2198 | 86.67% | 83.33% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 6.7548 | 10.1322 | 26.6637 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 22.2198 | 21.331 | 83.33% | 80% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 6.7548 | 10.1322 | 26.6637 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 21.331 | 20.4422 | 80% | 76.67% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 6.7548 | 10.1322 | 26.6637 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 20.4422 | 19.5534 | 76.67% | 73.33% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 6.7548 | 10.1322 | 26.6637 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 19.5534 | 18.6646 | 73.33% | 70% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 6.7548 | 10.1322 | 26.6637 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 18.6646 | 17.7758 | 70% | 66.67% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 6.7548 | 10.1322 | 26.6637 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 17.7758 | 16.887 | 66.67% | 63.33% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 6.7548 | 10.1322 | 26.6637 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 16.887 | 15.9982 | 63.33% | 60% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 6.7548 | 10.1322 | 26.6637 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 15.9982 | 15.1094 | 60% | 56.67% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 6.7548 | 10.1322 | 26.6637 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 15.1094 | 14.2206 | 56.67% | 53.33% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 6.7548 | 10.1322 | 26.6637 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 14.2206 | 13.3319 | 53.33% | 50% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 6.7548 | 10.1322 | 26.6637 | 2024-01-01 01:00 | 2023-12-31 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 13.3319 | 12.4431 | 50% | 46.67% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 6.7548 | 10.1322 | 26.6637 | 2024-01-01 01:05 | 2023-12-31 20:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 12.4431 | 11.5543 | 46.67% | 43.33% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 6.7548 | 10.1322 | 26.6637 | 2024-01-01 01:10 | 2023-12-31 20:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 11.5543 | 10.6655 | 43.33% | 40% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 6.7548 | 10.1322 | 26.6637 | 2024-01-01 01:15 | 2023-12-31 20:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 10.6655 | 9.7767 | 40% | 36.67% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 6.7548 | 10.1322 | 26.6637 | 2024-01-01 01:20 | 2023-12-31 20:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 9.7767 | 8.8879 | 36.67% | 33.33% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 6.7548 | 10.1322 | 26.6637 | 2024-01-01 01:25 | 2023-12-31 20:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 8.8879 | 7.9991 | 33.33% | 30% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 6.7548 | 10.1322 | 26.6637 | 2024-01-01 01:30 | 2023-12-31 20:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 7.9991 | 7.1103 | 30% | 26.67% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 6.7548 | 10.1322 | 26.6637 | 2024-01-01 01:35 | 2023-12-31 20:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 7.1103 | 6.2215 | 26.67% | 23.33% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 6.7548 | 10.1322 | 26.6637 | 2024-01-01 01:40 | 2023-12-31 20:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 6.2215 | 5.3327 | 23.33% | 20% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 6.7548 | 10.1322 | 26.6637 | 2024-01-01 01:45 | 2023-12-31 20:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 5.3327 | 4.444 | 20% | 16.67% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 6.7548 | 10.1322 | 26.6637 | 2024-01-01 01:50 | 2023-12-31 20:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 4.444 | 3.5552 | 16.67% | 13.33% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 6.7548 | 10.1322 | 26.6637 | 2024-01-01 01:55 | 2023-12-31 20:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 3.5552 | 2.6664 | 13.33% | 10% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 10.1322 | 10.1322 | 26.6637 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 23.9973 | 23.1085 | 90% | 86.67% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 10.1322 | 10.1322 | 26.6637 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 23.1085 | 22.2198 | 86.67% | 83.33% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 10.1322 | 10.1322 | 26.6637 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 22.2198 | 21.331 | 83.33% | 80% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 10.1322 | 10.1322 | 26.6637 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 21.331 | 20.4422 | 80% | 76.67% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 10.1322 | 10.1322 | 26.6637 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 20.4422 | 19.5534 | 76.67% | 73.33% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 10.1322 | 10.1322 | 26.6637 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 19.5534 | 18.6646 | 73.33% | 70% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 10.1322 | 10.1322 | 26.6637 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 18.6646 | 17.7758 | 70% | 66.67% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 10.1322 | 10.1322 | 26.6637 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 17.7758 | 16.887 | 66.67% | 63.33% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 10.1322 | 10.1322 | 26.6637 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 16.887 | 15.9982 | 63.33% | 60% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 10.1322 | 10.1322 | 26.6637 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 15.9982 | 15.1094 | 60% | 56.67% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 10.1322 | 10.1322 | 26.6637 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 15.1094 | 14.2206 | 56.67% | 53.33% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 10.1322 | 10.1322 | 26.6637 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 14.2206 | 13.3319 | 53.33% | 50% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 10.1322 | 10.1322 | 26.6637 | 2024-01-01 01:00 | 2023-12-31 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 13.3319 | 12.4431 | 50% | 46.67% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 10.1322 | 10.1322 | 26.6637 | 2024-01-01 01:05 | 2023-12-31 20:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 12.4431 | 11.5543 | 46.67% | 43.33% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 10.1322 | 10.1322 | 26.6637 | 2024-01-01 01:10 | 2023-12-31 20:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 11.5543 | 10.6655 | 43.33% | 40% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 10.1322 | 10.1322 | 26.6637 | 2024-01-01 01:15 | 2023-12-31 20:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 10.6655 | 9.7767 | 40% | 36.67% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 10.1322 | 10.1322 | 26.6637 | 2024-01-01 01:20 | 2023-12-31 20:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 9.7767 | 8.8879 | 36.67% | 33.33% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 10.1322 | 10.1322 | 26.6637 | 2024-01-01 01:25 | 2023-12-31 20:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 8.8879 | 7.9991 | 33.33% | 30% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 10.1322 | 10.1322 | 26.6637 | 2024-01-01 01:30 | 2023-12-31 20:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 7.9991 | 7.1103 | 30% | 26.67% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 10.1322 | 10.1322 | 26.6637 | 2024-01-01 01:35 | 2023-12-31 20:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 7.1103 | 6.2215 | 26.67% | 23.33% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 10.1322 | 10.1322 | 26.6637 | 2024-01-01 01:40 | 2023-12-31 20:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 6.2215 | 5.3327 | 23.33% | 20% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 10.1322 | 10.1322 | 26.6637 | 2024-01-01 01:45 | 2023-12-31 20:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 5.3327 | 4.444 | 20% | 16.67% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 10.1322 | 10.1322 | 26.6637 | 2024-01-01 01:50 | 2023-12-31 20:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 4.444 | 3.5552 | 16.67% | 13.33% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 10.1322 | 10.1322 | 26.6637 | 2024-01-01 01:55 | 2023-12-31 20:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 3.5552 | 2.6664 | 13.33% | 10% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 13.5096 | 10.1322 | 26.6637 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 23.9973 | 23.1085 | 90% | 86.67% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 13.5096 | 10.1322 | 26.6637 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 23.1085 | 22.2198 | 86.67% | 83.33% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 13.5096 | 10.1322 | 26.6637 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 22.2198 | 21.331 | 83.33% | 80% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 13.5096 | 10.1322 | 26.6637 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 21.331 | 20.4422 | 80% | 76.67% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 13.5096 | 10.1322 | 26.6637 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 20.4422 | 19.5534 | 76.67% | 73.33% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 13.5096 | 10.1322 | 26.6637 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 19.5534 | 18.6646 | 73.33% | 70% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 13.5096 | 10.1322 | 26.6637 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 18.6646 | 17.7758 | 70% | 66.67% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 13.5096 | 10.1322 | 26.6637 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 17.7758 | 16.887 | 66.67% | 63.33% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 13.5096 | 10.1322 | 26.6637 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 16.887 | 15.9982 | 63.33% | 60% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 13.5096 | 10.1322 | 26.6637 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 15.9982 | 15.1094 | 60% | 56.67% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 13.5096 | 10.1322 | 26.6637 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 15.1094 | 14.2206 | 56.67% | 53.33% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 13.5096 | 10.1322 | 26.6637 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 14.2206 | 13.3319 | 53.33% | 50% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 13.5096 | 10.1322 | 26.6637 | 2024-01-01 01:00 | 2023-12-31 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 13.3319 | 12.4431 | 50% | 46.67% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 13.5096 | 10.1322 | 26.6637 | 2024-01-01 01:05 | 2023-12-31 20:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 12.4431 | 11.5543 | 46.67% | 43.33% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 13.5096 | 10.1322 | 26.6637 | 2024-01-01 01:10 | 2023-12-31 20:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 11.5543 | 10.6655 | 43.33% | 40% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 13.5096 | 10.1322 | 26.6637 | 2024-01-01 01:15 | 2023-12-31 20:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 10.6655 | 9.7767 | 40% | 36.67% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 13.5096 | 10.1322 | 26.6637 | 2024-01-01 01:20 | 2023-12-31 20:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 9.7767 | 8.8879 | 36.67% | 33.33% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 13.5096 | 10.1322 | 26.6637 | 2024-01-01 01:25 | 2023-12-31 20:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 8.8879 | 7.9991 | 33.33% | 30% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 13.5096 | 10.1322 | 26.6637 | 2024-01-01 01:30 | 2023-12-31 20:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 7.9991 | 7.1103 | 30% | 26.67% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 13.5096 | 10.1322 | 26.6637 | 2024-01-01 01:35 | 2023-12-31 20:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 7.1103 | 6.2215 | 26.67% | 23.33% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 13.5096 | 10.1322 | 26.6637 | 2024-01-01 01:40 | 2023-12-31 20:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 6.2215 | 5.3327 | 23.33% | 20% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 13.5096 | 10.1322 | 26.6637 | 2024-01-01 01:45 | 2023-12-31 20:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 5.3327 | 4.444 | 20% | 16.67% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 13.5096 | 10.1322 | 26.6637 | 2024-01-01 01:50 | 2023-12-31 20:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 4.444 | 3.5552 | 16.67% | 13.33% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 2 | 13.5096 | 10.1322 | 26.6637 | 2024-01-01 01:55 | 2023-12-31 20:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 3.5552 | 2.6664 | 13.33% | 10% | 2.6664 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 0 | 10.1322 | 53.3274 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 47.9947 | 47.1059 | 90% | 88.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 0 | 10.1322 | 53.3274 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 47.1059 | 46.2171 | 88.33% | 86.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 0 | 10.1322 | 53.3274 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 46.2171 | 45.3283 | 86.67% | 85% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 0 | 10.1322 | 53.3274 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 45.3283 | 44.4395 | 85% | 83.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 0 | 10.1322 | 53.3274 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 44.4395 | 43.5507 | 83.33% | 81.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 0 | 10.1322 | 53.3274 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 43.5507 | 42.6619 | 81.67% | 80% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 0 | 10.1322 | 53.3274 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 42.6619 | 41.7731 | 80% | 78.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 0 | 10.1322 | 53.3274 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 41.7731 | 40.8843 | 78.33% | 76.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 0 | 10.1322 | 53.3274 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 40.8843 | 39.9956 | 76.67% | 75% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 0 | 10.1322 | 53.3274 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 39.9956 | 39.1068 | 75% | 73.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 0 | 10.1322 | 53.3274 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 39.1068 | 38.218 | 73.33% | 71.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 0 | 10.1322 | 53.3274 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 38.218 | 37.3292 | 71.67% | 70% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 0 | 10.1322 | 53.3274 | 2024-01-01 01:00 | 2023-12-31 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 37.3292 | 36.4404 | 70% | 68.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 0 | 10.1322 | 53.3274 | 2024-01-01 01:05 | 2023-12-31 20:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 36.4404 | 35.5516 | 68.33% | 66.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 0 | 10.1322 | 53.3274 | 2024-01-01 01:10 | 2023-12-31 20:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 35.5516 | 34.6628 | 66.67% | 65% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 0 | 10.1322 | 53.3274 | 2024-01-01 01:15 | 2023-12-31 20:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 34.6628 | 33.774 | 65% | 63.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 0 | 10.1322 | 53.3274 | 2024-01-01 01:20 | 2023-12-31 20:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 33.774 | 32.8852 | 63.33% | 61.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 0 | 10.1322 | 53.3274 | 2024-01-01 01:25 | 2023-12-31 20:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 32.8852 | 31.9964 | 61.67% | 60% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 0 | 10.1322 | 53.3274 | 2024-01-01 01:30 | 2023-12-31 20:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 31.9964 | 31.1077 | 60% | 58.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 0 | 10.1322 | 53.3274 | 2024-01-01 01:35 | 2023-12-31 20:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 31.1077 | 30.2189 | 58.33% | 56.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 0 | 10.1322 | 53.3274 | 2024-01-01 01:40 | 2023-12-31 20:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 30.2189 | 29.3301 | 56.67% | 55% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 0 | 10.1322 | 53.3274 | 2024-01-01 01:45 | 2023-12-31 20:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 29.3301 | 28.4413 | 55% | 53.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 0 | 10.1322 | 53.3274 | 2024-01-01 01:50 | 2023-12-31 20:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 28.4413 | 27.5525 | 53.33% | 51.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 0 | 10.1322 | 53.3274 | 2024-01-01 01:55 | 2023-12-31 20:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 27.5525 | 26.6637 | 51.67% | 50% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 0 | 10.1322 | 53.3274 | 2024-01-01 02:00 | 2023-12-31 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 26.6637 | 25.7749 | 50% | 48.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 0 | 10.1322 | 53.3274 | 2024-01-01 02:05 | 2023-12-31 21:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 25.7749 | 24.8861 | 48.33% | 46.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 0 | 10.1322 | 53.3274 | 2024-01-01 02:10 | 2023-12-31 21:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 24.8861 | 23.9973 | 46.67% | 45% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 0 | 10.1322 | 53.3274 | 2024-01-01 02:15 | 2023-12-31 21:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 23.9973 | 23.1085 | 45% | 43.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 0 | 10.1322 | 53.3274 | 2024-01-01 02:20 | 2023-12-31 21:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 23.1085 | 22.2198 | 43.33% | 41.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 0 | 10.1322 | 53.3274 | 2024-01-01 02:25 | 2023-12-31 21:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 22.2198 | 21.331 | 41.67% | 40% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 0 | 10.1322 | 53.3274 | 2024-01-01 02:30 | 2023-12-31 21:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 21.331 | 20.4422 | 40% | 38.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 0 | 10.1322 | 53.3274 | 2024-01-01 02:35 | 2023-12-31 21:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 20.4422 | 19.5534 | 38.33% | 36.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 0 | 10.1322 | 53.3274 | 2024-01-01 02:40 | 2023-12-31 21:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 19.5534 | 18.6646 | 36.67% | 35% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 0 | 10.1322 | 53.3274 | 2024-01-01 02:45 | 2023-12-31 21:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 18.6646 | 17.7758 | 35% | 33.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 0 | 10.1322 | 53.3274 | 2024-01-01 02:50 | 2023-12-31 21:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 17.7758 | 16.887 | 33.33% | 31.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 0 | 10.1322 | 53.3274 | 2024-01-01 02:55 | 2023-12-31 21:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 16.887 | 15.9982 | 31.67% | 30% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 0 | 10.1322 | 53.3274 | 2024-01-01 03:00 | 2023-12-31 22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 15.9982 | 15.1094 | 30% | 28.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 0 | 10.1322 | 53.3274 | 2024-01-01 03:05 | 2023-12-31 22:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 15.1094 | 14.2206 | 28.33% | 26.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 0 | 10.1322 | 53.3274 | 2024-01-01 03:10 | 2023-12-31 22:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 14.2206 | 13.3319 | 26.67% | 25% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 0 | 10.1322 | 53.3274 | 2024-01-01 03:15 | 2023-12-31 22:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 13.3319 | 12.4431 | 25% | 23.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 0 | 10.1322 | 53.3274 | 2024-01-01 03:20 | 2023-12-31 22:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 12.4431 | 11.5543 | 23.33% | 21.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 0 | 10.1322 | 53.3274 | 2024-01-01 03:25 | 2023-12-31 22:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 11.5543 | 10.6655 | 21.67% | 20% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 0 | 10.1322 | 53.3274 | 2024-01-01 03:30 | 2023-12-31 22:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 10.6655 | 9.7767 | 20% | 18.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 0 | 10.1322 | 53.3274 | 2024-01-01 03:35 | 2023-12-31 22:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 9.7767 | 8.8879 | 18.33% | 16.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 0 | 10.1322 | 53.3274 | 2024-01-01 03:40 | 2023-12-31 22:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 8.8879 | 7.9991 | 16.67% | 15% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 0 | 10.1322 | 53.3274 | 2024-01-01 03:45 | 2023-12-31 22:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 7.9991 | 7.1103 | 15% | 13.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 0 | 10.1322 | 53.3274 | 2024-01-01 03:50 | 2023-12-31 22:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 7.1103 | 6.2215 | 13.33% | 11.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 0 | 10.1322 | 53.3274 | 2024-01-01 03:55 | 2023-12-31 22:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 6.2215 | 5.3327 | 11.67% | 10% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 3.3774 | 10.1322 | 53.3274 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 47.9947 | 47.1059 | 90% | 88.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 3.3774 | 10.1322 | 53.3274 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 47.1059 | 46.2171 | 88.33% | 86.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 3.3774 | 10.1322 | 53.3274 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 46.2171 | 45.3283 | 86.67% | 85% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 3.3774 | 10.1322 | 53.3274 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 45.3283 | 44.4395 | 85% | 83.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 3.3774 | 10.1322 | 53.3274 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 44.4395 | 43.5507 | 83.33% | 81.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 3.3774 | 10.1322 | 53.3274 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 43.5507 | 42.6619 | 81.67% | 80% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 3.3774 | 10.1322 | 53.3274 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 42.6619 | 41.7731 | 80% | 78.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 3.3774 | 10.1322 | 53.3274 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 41.7731 | 40.8843 | 78.33% | 76.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 3.3774 | 10.1322 | 53.3274 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 40.8843 | 39.9956 | 76.67% | 75% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 3.3774 | 10.1322 | 53.3274 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 39.9956 | 39.1068 | 75% | 73.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 3.3774 | 10.1322 | 53.3274 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 39.1068 | 38.218 | 73.33% | 71.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 3.3774 | 10.1322 | 53.3274 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 38.218 | 37.3292 | 71.67% | 70% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 3.3774 | 10.1322 | 53.3274 | 2024-01-01 01:00 | 2023-12-31 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 37.3292 | 36.4404 | 70% | 68.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 3.3774 | 10.1322 | 53.3274 | 2024-01-01 01:05 | 2023-12-31 20:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 36.4404 | 35.5516 | 68.33% | 66.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 3.3774 | 10.1322 | 53.3274 | 2024-01-01 01:10 | 2023-12-31 20:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 35.5516 | 34.6628 | 66.67% | 65% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 3.3774 | 10.1322 | 53.3274 | 2024-01-01 01:15 | 2023-12-31 20:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 34.6628 | 33.774 | 65% | 63.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 3.3774 | 10.1322 | 53.3274 | 2024-01-01 01:20 | 2023-12-31 20:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 33.774 | 32.8852 | 63.33% | 61.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 3.3774 | 10.1322 | 53.3274 | 2024-01-01 01:25 | 2023-12-31 20:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 32.8852 | 31.9964 | 61.67% | 60% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 3.3774 | 10.1322 | 53.3274 | 2024-01-01 01:30 | 2023-12-31 20:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 31.9964 | 31.1077 | 60% | 58.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 3.3774 | 10.1322 | 53.3274 | 2024-01-01 01:35 | 2023-12-31 20:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 31.1077 | 30.2189 | 58.33% | 56.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 3.3774 | 10.1322 | 53.3274 | 2024-01-01 01:40 | 2023-12-31 20:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 30.2189 | 29.3301 | 56.67% | 55% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 3.3774 | 10.1322 | 53.3274 | 2024-01-01 01:45 | 2023-12-31 20:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 29.3301 | 28.4413 | 55% | 53.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 3.3774 | 10.1322 | 53.3274 | 2024-01-01 01:50 | 2023-12-31 20:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 28.4413 | 27.5525 | 53.33% | 51.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 3.3774 | 10.1322 | 53.3274 | 2024-01-01 01:55 | 2023-12-31 20:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 27.5525 | 26.6637 | 51.67% | 50% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 3.3774 | 10.1322 | 53.3274 | 2024-01-01 02:00 | 2023-12-31 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 26.6637 | 25.7749 | 50% | 48.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 3.3774 | 10.1322 | 53.3274 | 2024-01-01 02:05 | 2023-12-31 21:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 25.7749 | 24.8861 | 48.33% | 46.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 3.3774 | 10.1322 | 53.3274 | 2024-01-01 02:10 | 2023-12-31 21:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 24.8861 | 23.9973 | 46.67% | 45% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 3.3774 | 10.1322 | 53.3274 | 2024-01-01 02:15 | 2023-12-31 21:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 23.9973 | 23.1085 | 45% | 43.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 3.3774 | 10.1322 | 53.3274 | 2024-01-01 02:20 | 2023-12-31 21:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 23.1085 | 22.2198 | 43.33% | 41.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 3.3774 | 10.1322 | 53.3274 | 2024-01-01 02:25 | 2023-12-31 21:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 22.2198 | 21.331 | 41.67% | 40% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 3.3774 | 10.1322 | 53.3274 | 2024-01-01 02:30 | 2023-12-31 21:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 21.331 | 20.4422 | 40% | 38.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 3.3774 | 10.1322 | 53.3274 | 2024-01-01 02:35 | 2023-12-31 21:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 20.4422 | 19.5534 | 38.33% | 36.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 3.3774 | 10.1322 | 53.3274 | 2024-01-01 02:40 | 2023-12-31 21:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 19.5534 | 18.6646 | 36.67% | 35% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 3.3774 | 10.1322 | 53.3274 | 2024-01-01 02:45 | 2023-12-31 21:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 18.6646 | 17.7758 | 35% | 33.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 3.3774 | 10.1322 | 53.3274 | 2024-01-01 02:50 | 2023-12-31 21:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 17.7758 | 16.887 | 33.33% | 31.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 3.3774 | 10.1322 | 53.3274 | 2024-01-01 02:55 | 2023-12-31 21:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 16.887 | 15.9982 | 31.67% | 30% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 3.3774 | 10.1322 | 53.3274 | 2024-01-01 03:00 | 2023-12-31 22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 15.9982 | 15.1094 | 30% | 28.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 3.3774 | 10.1322 | 53.3274 | 2024-01-01 03:05 | 2023-12-31 22:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 15.1094 | 14.2206 | 28.33% | 26.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 3.3774 | 10.1322 | 53.3274 | 2024-01-01 03:10 | 2023-12-31 22:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 14.2206 | 13.3319 | 26.67% | 25% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 3.3774 | 10.1322 | 53.3274 | 2024-01-01 03:15 | 2023-12-31 22:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 13.3319 | 12.4431 | 25% | 23.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 3.3774 | 10.1322 | 53.3274 | 2024-01-01 03:20 | 2023-12-31 22:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 12.4431 | 11.5543 | 23.33% | 21.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 3.3774 | 10.1322 | 53.3274 | 2024-01-01 03:25 | 2023-12-31 22:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 11.5543 | 10.6655 | 21.67% | 20% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 3.3774 | 10.1322 | 53.3274 | 2024-01-01 03:30 | 2023-12-31 22:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 10.6655 | 9.7767 | 20% | 18.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 3.3774 | 10.1322 | 53.3274 | 2024-01-01 03:35 | 2023-12-31 22:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 9.7767 | 8.8879 | 18.33% | 16.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 3.3774 | 10.1322 | 53.3274 | 2024-01-01 03:40 | 2023-12-31 22:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 8.8879 | 7.9991 | 16.67% | 15% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 3.3774 | 10.1322 | 53.3274 | 2024-01-01 03:45 | 2023-12-31 22:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 7.9991 | 7.1103 | 15% | 13.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 3.3774 | 10.1322 | 53.3274 | 2024-01-01 03:50 | 2023-12-31 22:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 7.1103 | 6.2215 | 13.33% | 11.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 3.3774 | 10.1322 | 53.3274 | 2024-01-01 03:55 | 2023-12-31 22:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 6.2215 | 5.3327 | 11.67% | 10% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 6.7548 | 10.1322 | 53.3274 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 47.9947 | 47.1059 | 90% | 88.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 6.7548 | 10.1322 | 53.3274 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 47.1059 | 46.2171 | 88.33% | 86.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 6.7548 | 10.1322 | 53.3274 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 46.2171 | 45.3283 | 86.67% | 85% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 6.7548 | 10.1322 | 53.3274 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 45.3283 | 44.4395 | 85% | 83.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 6.7548 | 10.1322 | 53.3274 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 44.4395 | 43.5507 | 83.33% | 81.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 6.7548 | 10.1322 | 53.3274 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 43.5507 | 42.6619 | 81.67% | 80% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 6.7548 | 10.1322 | 53.3274 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 42.6619 | 41.7731 | 80% | 78.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 6.7548 | 10.1322 | 53.3274 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 41.7731 | 40.8843 | 78.33% | 76.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 6.7548 | 10.1322 | 53.3274 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 40.8843 | 39.9956 | 76.67% | 75% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 6.7548 | 10.1322 | 53.3274 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 39.9956 | 39.1068 | 75% | 73.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 6.7548 | 10.1322 | 53.3274 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 39.1068 | 38.218 | 73.33% | 71.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 6.7548 | 10.1322 | 53.3274 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 38.218 | 37.3292 | 71.67% | 70% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 6.7548 | 10.1322 | 53.3274 | 2024-01-01 01:00 | 2023-12-31 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 37.3292 | 36.4404 | 70% | 68.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 6.7548 | 10.1322 | 53.3274 | 2024-01-01 01:05 | 2023-12-31 20:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 36.4404 | 35.5516 | 68.33% | 66.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 6.7548 | 10.1322 | 53.3274 | 2024-01-01 01:10 | 2023-12-31 20:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 35.5516 | 34.6628 | 66.67% | 65% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 6.7548 | 10.1322 | 53.3274 | 2024-01-01 01:15 | 2023-12-31 20:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 34.6628 | 33.774 | 65% | 63.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 6.7548 | 10.1322 | 53.3274 | 2024-01-01 01:20 | 2023-12-31 20:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 33.774 | 32.8852 | 63.33% | 61.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 6.7548 | 10.1322 | 53.3274 | 2024-01-01 01:25 | 2023-12-31 20:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 32.8852 | 31.9964 | 61.67% | 60% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 6.7548 | 10.1322 | 53.3274 | 2024-01-01 01:30 | 2023-12-31 20:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 31.9964 | 31.1077 | 60% | 58.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 6.7548 | 10.1322 | 53.3274 | 2024-01-01 01:35 | 2023-12-31 20:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 31.1077 | 30.2189 | 58.33% | 56.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 6.7548 | 10.1322 | 53.3274 | 2024-01-01 01:40 | 2023-12-31 20:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 30.2189 | 29.3301 | 56.67% | 55% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 6.7548 | 10.1322 | 53.3274 | 2024-01-01 01:45 | 2023-12-31 20:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 29.3301 | 28.4413 | 55% | 53.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 6.7548 | 10.1322 | 53.3274 | 2024-01-01 01:50 | 2023-12-31 20:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 28.4413 | 27.5525 | 53.33% | 51.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 6.7548 | 10.1322 | 53.3274 | 2024-01-01 01:55 | 2023-12-31 20:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 27.5525 | 26.6637 | 51.67% | 50% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 6.7548 | 10.1322 | 53.3274 | 2024-01-01 02:00 | 2023-12-31 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 26.6637 | 25.7749 | 50% | 48.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 6.7548 | 10.1322 | 53.3274 | 2024-01-01 02:05 | 2023-12-31 21:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 25.7749 | 24.8861 | 48.33% | 46.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 6.7548 | 10.1322 | 53.3274 | 2024-01-01 02:10 | 2023-12-31 21:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 24.8861 | 23.9973 | 46.67% | 45% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 6.7548 | 10.1322 | 53.3274 | 2024-01-01 02:15 | 2023-12-31 21:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 23.9973 | 23.1085 | 45% | 43.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 6.7548 | 10.1322 | 53.3274 | 2024-01-01 02:20 | 2023-12-31 21:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 23.1085 | 22.2198 | 43.33% | 41.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 6.7548 | 10.1322 | 53.3274 | 2024-01-01 02:25 | 2023-12-31 21:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 22.2198 | 21.331 | 41.67% | 40% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 6.7548 | 10.1322 | 53.3274 | 2024-01-01 02:30 | 2023-12-31 21:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 21.331 | 20.4422 | 40% | 38.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 6.7548 | 10.1322 | 53.3274 | 2024-01-01 02:35 | 2023-12-31 21:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 20.4422 | 19.5534 | 38.33% | 36.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 6.7548 | 10.1322 | 53.3274 | 2024-01-01 02:40 | 2023-12-31 21:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 19.5534 | 18.6646 | 36.67% | 35% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 6.7548 | 10.1322 | 53.3274 | 2024-01-01 02:45 | 2023-12-31 21:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 18.6646 | 17.7758 | 35% | 33.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 6.7548 | 10.1322 | 53.3274 | 2024-01-01 02:50 | 2023-12-31 21:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 17.7758 | 16.887 | 33.33% | 31.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 6.7548 | 10.1322 | 53.3274 | 2024-01-01 02:55 | 2023-12-31 21:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 16.887 | 15.9982 | 31.67% | 30% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 6.7548 | 10.1322 | 53.3274 | 2024-01-01 03:00 | 2023-12-31 22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 15.9982 | 15.1094 | 30% | 28.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 6.7548 | 10.1322 | 53.3274 | 2024-01-01 03:05 | 2023-12-31 22:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 15.1094 | 14.2206 | 28.33% | 26.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 6.7548 | 10.1322 | 53.3274 | 2024-01-01 03:10 | 2023-12-31 22:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 14.2206 | 13.3319 | 26.67% | 25% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 6.7548 | 10.1322 | 53.3274 | 2024-01-01 03:15 | 2023-12-31 22:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 13.3319 | 12.4431 | 25% | 23.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 6.7548 | 10.1322 | 53.3274 | 2024-01-01 03:20 | 2023-12-31 22:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 12.4431 | 11.5543 | 23.33% | 21.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 6.7548 | 10.1322 | 53.3274 | 2024-01-01 03:25 | 2023-12-31 22:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 11.5543 | 10.6655 | 21.67% | 20% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 6.7548 | 10.1322 | 53.3274 | 2024-01-01 03:30 | 2023-12-31 22:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 10.6655 | 9.7767 | 20% | 18.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 6.7548 | 10.1322 | 53.3274 | 2024-01-01 03:35 | 2023-12-31 22:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 9.7767 | 8.8879 | 18.33% | 16.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 6.7548 | 10.1322 | 53.3274 | 2024-01-01 03:40 | 2023-12-31 22:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 8.8879 | 7.9991 | 16.67% | 15% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 6.7548 | 10.1322 | 53.3274 | 2024-01-01 03:45 | 2023-12-31 22:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 7.9991 | 7.1103 | 15% | 13.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 6.7548 | 10.1322 | 53.3274 | 2024-01-01 03:50 | 2023-12-31 22:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 7.1103 | 6.2215 | 13.33% | 11.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 6.7548 | 10.1322 | 53.3274 | 2024-01-01 03:55 | 2023-12-31 22:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 6.2215 | 5.3327 | 11.67% | 10% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 10.1322 | 10.1322 | 53.3274 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 47.9947 | 47.1059 | 90% | 88.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 10.1322 | 10.1322 | 53.3274 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 47.1059 | 46.2171 | 88.33% | 86.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 10.1322 | 10.1322 | 53.3274 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 46.2171 | 45.3283 | 86.67% | 85% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 10.1322 | 10.1322 | 53.3274 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 45.3283 | 44.4395 | 85% | 83.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 10.1322 | 10.1322 | 53.3274 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 44.4395 | 43.5507 | 83.33% | 81.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 10.1322 | 10.1322 | 53.3274 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 43.5507 | 42.6619 | 81.67% | 80% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 10.1322 | 10.1322 | 53.3274 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 42.6619 | 41.7731 | 80% | 78.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 10.1322 | 10.1322 | 53.3274 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 41.7731 | 40.8843 | 78.33% | 76.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 10.1322 | 10.1322 | 53.3274 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 40.8843 | 39.9956 | 76.67% | 75% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 10.1322 | 10.1322 | 53.3274 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 39.9956 | 39.1068 | 75% | 73.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 10.1322 | 10.1322 | 53.3274 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 39.1068 | 38.218 | 73.33% | 71.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 10.1322 | 10.1322 | 53.3274 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 38.218 | 37.3292 | 71.67% | 70% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 10.1322 | 10.1322 | 53.3274 | 2024-01-01 01:00 | 2023-12-31 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 37.3292 | 36.4404 | 70% | 68.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 10.1322 | 10.1322 | 53.3274 | 2024-01-01 01:05 | 2023-12-31 20:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 36.4404 | 35.5516 | 68.33% | 66.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 10.1322 | 10.1322 | 53.3274 | 2024-01-01 01:10 | 2023-12-31 20:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 35.5516 | 34.6628 | 66.67% | 65% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 10.1322 | 10.1322 | 53.3274 | 2024-01-01 01:15 | 2023-12-31 20:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 34.6628 | 33.774 | 65% | 63.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 10.1322 | 10.1322 | 53.3274 | 2024-01-01 01:20 | 2023-12-31 20:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 33.774 | 32.8852 | 63.33% | 61.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 10.1322 | 10.1322 | 53.3274 | 2024-01-01 01:25 | 2023-12-31 20:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 32.8852 | 31.9964 | 61.67% | 60% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 10.1322 | 10.1322 | 53.3274 | 2024-01-01 01:30 | 2023-12-31 20:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 31.9964 | 31.1077 | 60% | 58.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 10.1322 | 10.1322 | 53.3274 | 2024-01-01 01:35 | 2023-12-31 20:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 31.1077 | 30.2189 | 58.33% | 56.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 10.1322 | 10.1322 | 53.3274 | 2024-01-01 01:40 | 2023-12-31 20:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 30.2189 | 29.3301 | 56.67% | 55% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 10.1322 | 10.1322 | 53.3274 | 2024-01-01 01:45 | 2023-12-31 20:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 29.3301 | 28.4413 | 55% | 53.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 10.1322 | 10.1322 | 53.3274 | 2024-01-01 01:50 | 2023-12-31 20:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 28.4413 | 27.5525 | 53.33% | 51.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 10.1322 | 10.1322 | 53.3274 | 2024-01-01 01:55 | 2023-12-31 20:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 27.5525 | 26.6637 | 51.67% | 50% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 10.1322 | 10.1322 | 53.3274 | 2024-01-01 02:00 | 2023-12-31 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 26.6637 | 25.7749 | 50% | 48.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 10.1322 | 10.1322 | 53.3274 | 2024-01-01 02:05 | 2023-12-31 21:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 25.7749 | 24.8861 | 48.33% | 46.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 10.1322 | 10.1322 | 53.3274 | 2024-01-01 02:10 | 2023-12-31 21:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 24.8861 | 23.9973 | 46.67% | 45% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 10.1322 | 10.1322 | 53.3274 | 2024-01-01 02:15 | 2023-12-31 21:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 23.9973 | 23.1085 | 45% | 43.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 10.1322 | 10.1322 | 53.3274 | 2024-01-01 02:20 | 2023-12-31 21:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 23.1085 | 22.2198 | 43.33% | 41.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 10.1322 | 10.1322 | 53.3274 | 2024-01-01 02:25 | 2023-12-31 21:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 22.2198 | 21.331 | 41.67% | 40% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 10.1322 | 10.1322 | 53.3274 | 2024-01-01 02:30 | 2023-12-31 21:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 21.331 | 20.4422 | 40% | 38.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 10.1322 | 10.1322 | 53.3274 | 2024-01-01 02:35 | 2023-12-31 21:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 20.4422 | 19.5534 | 38.33% | 36.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 10.1322 | 10.1322 | 53.3274 | 2024-01-01 02:40 | 2023-12-31 21:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 19.5534 | 18.6646 | 36.67% | 35% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 10.1322 | 10.1322 | 53.3274 | 2024-01-01 02:45 | 2023-12-31 21:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 18.6646 | 17.7758 | 35% | 33.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 10.1322 | 10.1322 | 53.3274 | 2024-01-01 02:50 | 2023-12-31 21:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 17.7758 | 16.887 | 33.33% | 31.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 10.1322 | 10.1322 | 53.3274 | 2024-01-01 02:55 | 2023-12-31 21:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 16.887 | 15.9982 | 31.67% | 30% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 10.1322 | 10.1322 | 53.3274 | 2024-01-01 03:00 | 2023-12-31 22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 15.9982 | 15.1094 | 30% | 28.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 10.1322 | 10.1322 | 53.3274 | 2024-01-01 03:05 | 2023-12-31 22:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 15.1094 | 14.2206 | 28.33% | 26.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 10.1322 | 10.1322 | 53.3274 | 2024-01-01 03:10 | 2023-12-31 22:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 14.2206 | 13.3319 | 26.67% | 25% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 10.1322 | 10.1322 | 53.3274 | 2024-01-01 03:15 | 2023-12-31 22:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 13.3319 | 12.4431 | 25% | 23.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 10.1322 | 10.1322 | 53.3274 | 2024-01-01 03:20 | 2023-12-31 22:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 12.4431 | 11.5543 | 23.33% | 21.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 10.1322 | 10.1322 | 53.3274 | 2024-01-01 03:25 | 2023-12-31 22:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 11.5543 | 10.6655 | 21.67% | 20% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 10.1322 | 10.1322 | 53.3274 | 2024-01-01 03:30 | 2023-12-31 22:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 10.6655 | 9.7767 | 20% | 18.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 10.1322 | 10.1322 | 53.3274 | 2024-01-01 03:35 | 2023-12-31 22:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 9.7767 | 8.8879 | 18.33% | 16.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 10.1322 | 10.1322 | 53.3274 | 2024-01-01 03:40 | 2023-12-31 22:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 8.8879 | 7.9991 | 16.67% | 15% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 10.1322 | 10.1322 | 53.3274 | 2024-01-01 03:45 | 2023-12-31 22:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 7.9991 | 7.1103 | 15% | 13.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 10.1322 | 10.1322 | 53.3274 | 2024-01-01 03:50 | 2023-12-31 22:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 7.1103 | 6.2215 | 13.33% | 11.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 10.1322 | 10.1322 | 53.3274 | 2024-01-01 03:55 | 2023-12-31 22:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 6.2215 | 5.3327 | 11.67% | 10% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 13.5096 | 10.1322 | 53.3274 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 47.9947 | 47.1059 | 90% | 88.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 13.5096 | 10.1322 | 53.3274 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 47.1059 | 46.2171 | 88.33% | 86.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 13.5096 | 10.1322 | 53.3274 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 46.2171 | 45.3283 | 86.67% | 85% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 13.5096 | 10.1322 | 53.3274 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 45.3283 | 44.4395 | 85% | 83.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 13.5096 | 10.1322 | 53.3274 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 44.4395 | 43.5507 | 83.33% | 81.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 13.5096 | 10.1322 | 53.3274 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 43.5507 | 42.6619 | 81.67% | 80% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 13.5096 | 10.1322 | 53.3274 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 42.6619 | 41.7731 | 80% | 78.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 13.5096 | 10.1322 | 53.3274 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 41.7731 | 40.8843 | 78.33% | 76.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 13.5096 | 10.1322 | 53.3274 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 40.8843 | 39.9956 | 76.67% | 75% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 13.5096 | 10.1322 | 53.3274 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 39.9956 | 39.1068 | 75% | 73.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 13.5096 | 10.1322 | 53.3274 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 39.1068 | 38.218 | 73.33% | 71.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 13.5096 | 10.1322 | 53.3274 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 38.218 | 37.3292 | 71.67% | 70% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 13.5096 | 10.1322 | 53.3274 | 2024-01-01 01:00 | 2023-12-31 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 37.3292 | 36.4404 | 70% | 68.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 13.5096 | 10.1322 | 53.3274 | 2024-01-01 01:05 | 2023-12-31 20:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 36.4404 | 35.5516 | 68.33% | 66.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 13.5096 | 10.1322 | 53.3274 | 2024-01-01 01:10 | 2023-12-31 20:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 35.5516 | 34.6628 | 66.67% | 65% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 13.5096 | 10.1322 | 53.3274 | 2024-01-01 01:15 | 2023-12-31 20:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 34.6628 | 33.774 | 65% | 63.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 13.5096 | 10.1322 | 53.3274 | 2024-01-01 01:20 | 2023-12-31 20:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 33.774 | 32.8852 | 63.33% | 61.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 13.5096 | 10.1322 | 53.3274 | 2024-01-01 01:25 | 2023-12-31 20:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 32.8852 | 31.9964 | 61.67% | 60% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 13.5096 | 10.1322 | 53.3274 | 2024-01-01 01:30 | 2023-12-31 20:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 31.9964 | 31.1077 | 60% | 58.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 13.5096 | 10.1322 | 53.3274 | 2024-01-01 01:35 | 2023-12-31 20:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 31.1077 | 30.2189 | 58.33% | 56.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 13.5096 | 10.1322 | 53.3274 | 2024-01-01 01:40 | 2023-12-31 20:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 30.2189 | 29.3301 | 56.67% | 55% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 13.5096 | 10.1322 | 53.3274 | 2024-01-01 01:45 | 2023-12-31 20:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 29.3301 | 28.4413 | 55% | 53.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 13.5096 | 10.1322 | 53.3274 | 2024-01-01 01:50 | 2023-12-31 20:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 28.4413 | 27.5525 | 53.33% | 51.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 13.5096 | 10.1322 | 53.3274 | 2024-01-01 01:55 | 2023-12-31 20:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 27.5525 | 26.6637 | 51.67% | 50% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 13.5096 | 10.1322 | 53.3274 | 2024-01-01 02:00 | 2023-12-31 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 26.6637 | 25.7749 | 50% | 48.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 13.5096 | 10.1322 | 53.3274 | 2024-01-01 02:05 | 2023-12-31 21:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 25.7749 | 24.8861 | 48.33% | 46.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 13.5096 | 10.1322 | 53.3274 | 2024-01-01 02:10 | 2023-12-31 21:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 24.8861 | 23.9973 | 46.67% | 45% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 13.5096 | 10.1322 | 53.3274 | 2024-01-01 02:15 | 2023-12-31 21:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 23.9973 | 23.1085 | 45% | 43.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 13.5096 | 10.1322 | 53.3274 | 2024-01-01 02:20 | 2023-12-31 21:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 23.1085 | 22.2198 | 43.33% | 41.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 13.5096 | 10.1322 | 53.3274 | 2024-01-01 02:25 | 2023-12-31 21:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 22.2198 | 21.331 | 41.67% | 40% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 13.5096 | 10.1322 | 53.3274 | 2024-01-01 02:30 | 2023-12-31 21:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 21.331 | 20.4422 | 40% | 38.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 13.5096 | 10.1322 | 53.3274 | 2024-01-01 02:35 | 2023-12-31 21:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 20.4422 | 19.5534 | 38.33% | 36.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 13.5096 | 10.1322 | 53.3274 | 2024-01-01 02:40 | 2023-12-31 21:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 19.5534 | 18.6646 | 36.67% | 35% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 13.5096 | 10.1322 | 53.3274 | 2024-01-01 02:45 | 2023-12-31 21:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 18.6646 | 17.7758 | 35% | 33.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 13.5096 | 10.1322 | 53.3274 | 2024-01-01 02:50 | 2023-12-31 21:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 17.7758 | 16.887 | 33.33% | 31.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 13.5096 | 10.1322 | 53.3274 | 2024-01-01 02:55 | 2023-12-31 21:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 16.887 | 15.9982 | 31.67% | 30% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 13.5096 | 10.1322 | 53.3274 | 2024-01-01 03:00 | 2023-12-31 22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 15.9982 | 15.1094 | 30% | 28.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 13.5096 | 10.1322 | 53.3274 | 2024-01-01 03:05 | 2023-12-31 22:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 15.1094 | 14.2206 | 28.33% | 26.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 13.5096 | 10.1322 | 53.3274 | 2024-01-01 03:10 | 2023-12-31 22:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 14.2206 | 13.3319 | 26.67% | 25% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 13.5096 | 10.1322 | 53.3274 | 2024-01-01 03:15 | 2023-12-31 22:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 13.3319 | 12.4431 | 25% | 23.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 13.5096 | 10.1322 | 53.3274 | 2024-01-01 03:20 | 2023-12-31 22:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 12.4431 | 11.5543 | 23.33% | 21.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 13.5096 | 10.1322 | 53.3274 | 2024-01-01 03:25 | 2023-12-31 22:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 11.5543 | 10.6655 | 21.67% | 20% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 13.5096 | 10.1322 | 53.3274 | 2024-01-01 03:30 | 2023-12-31 22:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 10.6655 | 9.7767 | 20% | 18.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 13.5096 | 10.1322 | 53.3274 | 2024-01-01 03:35 | 2023-12-31 22:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 9.7767 | 8.8879 | 18.33% | 16.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 13.5096 | 10.1322 | 53.3274 | 2024-01-01 03:40 | 2023-12-31 22:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 8.8879 | 7.9991 | 16.67% | 15% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 13.5096 | 10.1322 | 53.3274 | 2024-01-01 03:45 | 2023-12-31 22:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 7.9991 | 7.1103 | 15% | 13.33% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 13.5096 | 10.1322 | 53.3274 | 2024-01-01 03:50 | 2023-12-31 22:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 7.1103 | 6.2215 | 13.33% | 11.67% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 4 | 13.5096 | 10.1322 | 53.3274 | 2024-01-01 03:55 | 2023-12-31 22:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 6.2215 | 5.3327 | 11.67% | 10% | 5.3327 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 95.9893 | 95.1005 | 90% | 89.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 95.1005 | 94.2117 | 89.17% | 88.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 94.2117 | 93.323 | 88.33% | 87.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 93.323 | 92.4342 | 87.5% | 86.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 92.4342 | 91.5454 | 86.67% | 85.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 91.5454 | 90.6566 | 85.83% | 85% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 90.6566 | 89.7678 | 85% | 84.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 89.7678 | 88.879 | 84.17% | 83.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 88.879 | 87.9902 | 83.33% | 82.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 87.9902 | 87.1014 | 82.5% | 81.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 87.1014 | 86.2126 | 81.67% | 80.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 86.2126 | 85.3238 | 80.83% | 80% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 01:00 | 2023-12-31 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 85.3238 | 84.4351 | 80% | 79.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 01:05 | 2023-12-31 20:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 84.4351 | 83.5463 | 79.17% | 78.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 01:10 | 2023-12-31 20:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 83.5463 | 82.6575 | 78.33% | 77.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 01:15 | 2023-12-31 20:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 82.6575 | 81.7687 | 77.5% | 76.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 01:20 | 2023-12-31 20:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 81.7687 | 80.8799 | 76.67% | 75.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 01:25 | 2023-12-31 20:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 80.8799 | 79.9911 | 75.83% | 75% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 01:30 | 2023-12-31 20:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 79.9911 | 79.1023 | 75% | 74.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 01:35 | 2023-12-31 20:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 79.1023 | 78.2135 | 74.17% | 73.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 01:40 | 2023-12-31 20:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 78.2135 | 77.3247 | 73.33% | 72.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 01:45 | 2023-12-31 20:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 77.3247 | 76.4359 | 72.5% | 71.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 01:50 | 2023-12-31 20:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 76.4359 | 75.5472 | 71.67% | 70.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 01:55 | 2023-12-31 20:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 75.5472 | 74.6584 | 70.83% | 70% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 02:00 | 2023-12-31 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 74.6584 | 73.7696 | 70% | 69.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 02:05 | 2023-12-31 21:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 73.7696 | 72.8808 | 69.17% | 68.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 02:10 | 2023-12-31 21:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 72.8808 | 71.992 | 68.33% | 67.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 02:15 | 2023-12-31 21:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 71.992 | 71.1032 | 67.5% | 66.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 02:20 | 2023-12-31 21:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 71.1032 | 70.2144 | 66.67% | 65.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 02:25 | 2023-12-31 21:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 70.2144 | 69.3256 | 65.83% | 65% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 02:30 | 2023-12-31 21:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 69.3256 | 68.4368 | 65% | 64.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 02:35 | 2023-12-31 21:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 68.4368 | 67.548 | 64.17% | 63.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 02:40 | 2023-12-31 21:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 67.548 | 66.6593 | 63.33% | 62.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 02:45 | 2023-12-31 21:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 66.6593 | 65.7705 | 62.5% | 61.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 02:50 | 2023-12-31 21:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 65.7705 | 64.8817 | 61.67% | 60.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 02:55 | 2023-12-31 21:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 64.8817 | 63.9929 | 60.83% | 60% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 03:00 | 2023-12-31 22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 63.9929 | 63.1041 | 60% | 59.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 03:05 | 2023-12-31 22:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 63.1041 | 62.2153 | 59.17% | 58.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 03:10 | 2023-12-31 22:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 62.2153 | 61.3265 | 58.33% | 57.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 03:15 | 2023-12-31 22:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 61.3265 | 60.4377 | 57.5% | 56.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 03:20 | 2023-12-31 22:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 60.4377 | 59.5489 | 56.67% | 55.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 03:25 | 2023-12-31 22:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 59.5489 | 58.6601 | 55.83% | 55% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 03:30 | 2023-12-31 22:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 58.6601 | 57.7714 | 55% | 54.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 03:35 | 2023-12-31 22:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 57.7714 | 56.8826 | 54.17% | 53.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 03:40 | 2023-12-31 22:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 56.8826 | 55.9938 | 53.33% | 52.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 03:45 | 2023-12-31 22:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 55.9938 | 55.105 | 52.5% | 51.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 03:50 | 2023-12-31 22:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 55.105 | 54.2162 | 51.67% | 50.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 03:55 | 2023-12-31 22:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 54.2162 | 53.3274 | 50.83% | 50% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 04:00 | 2023-12-31 23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 53.3274 | 52.4386 | 50% | 49.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 04:05 | 2023-12-31 23:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 52.4386 | 51.5498 | 49.17% | 48.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 04:10 | 2023-12-31 23:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 51.5498 | 50.661 | 48.33% | 47.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 04:15 | 2023-12-31 23:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 50.661 | 49.7722 | 47.5% | 46.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 04:20 | 2023-12-31 23:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 49.7722 | 48.8835 | 46.67% | 45.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 04:25 | 2023-12-31 23:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 48.8835 | 47.9947 | 45.83% | 45% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 04:30 | 2023-12-31 23:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 47.9947 | 47.1059 | 45% | 44.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 04:35 | 2023-12-31 23:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 47.1059 | 46.2171 | 44.17% | 43.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 04:40 | 2023-12-31 23:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 46.2171 | 45.3283 | 43.33% | 42.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 04:45 | 2023-12-31 23:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 45.3283 | 44.4395 | 42.5% | 41.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 04:50 | 2023-12-31 23:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 44.4395 | 43.5507 | 41.67% | 40.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 04:55 | 2023-12-31 23:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 43.5507 | 42.6619 | 40.83% | 40% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 05:00 | 2024-01-01 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 42.6619 | 41.7731 | 40% | 39.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 05:05 | 2024-01-01 00:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 41.7731 | 40.8843 | 39.17% | 38.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 05:10 | 2024-01-01 00:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 40.8843 | 39.9956 | 38.33% | 37.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 05:15 | 2024-01-01 00:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 39.9956 | 39.1068 | 37.5% | 36.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 05:20 | 2024-01-01 00:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 39.1068 | 38.218 | 36.67% | 35.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 05:25 | 2024-01-01 00:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 38.218 | 37.3292 | 35.83% | 35% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 05:30 | 2024-01-01 00:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 37.3292 | 36.4404 | 35% | 34.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 05:35 | 2024-01-01 00:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 36.4404 | 35.5516 | 34.17% | 33.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 05:40 | 2024-01-01 00:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 35.5516 | 34.6628 | 33.33% | 32.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 05:45 | 2024-01-01 00:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 34.6628 | 33.774 | 32.5% | 31.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 05:50 | 2024-01-01 00:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 33.774 | 32.8852 | 31.67% | 30.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 05:55 | 2024-01-01 00:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 32.8852 | 31.9964 | 30.83% | 30% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 06:00 | 2024-01-01 01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 31.9964 | 31.1077 | 30% | 29.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 06:05 | 2024-01-01 01:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 31.1077 | 30.2189 | 29.17% | 28.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 06:10 | 2024-01-01 01:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 30.2189 | 29.3301 | 28.33% | 27.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 06:15 | 2024-01-01 01:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 29.3301 | 28.4413 | 27.5% | 26.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 06:20 | 2024-01-01 01:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 28.4413 | 27.5525 | 26.67% | 25.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 06:25 | 2024-01-01 01:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 27.5525 | 26.6637 | 25.83% | 25% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 06:30 | 2024-01-01 01:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 26.6637 | 25.7749 | 25% | 24.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 06:35 | 2024-01-01 01:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 25.7749 | 24.8861 | 24.17% | 23.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 06:40 | 2024-01-01 01:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 24.8861 | 23.9973 | 23.33% | 22.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 06:45 | 2024-01-01 01:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 23.9973 | 23.1085 | 22.5% | 21.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 06:50 | 2024-01-01 01:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 23.1085 | 22.2198 | 21.67% | 20.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 06:55 | 2024-01-01 01:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 22.2198 | 21.331 | 20.83% | 20% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 07:00 | 2024-01-01 02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 21.331 | 20.4422 | 20% | 19.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 07:05 | 2024-01-01 02:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 20.4422 | 19.5534 | 19.17% | 18.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 07:10 | 2024-01-01 02:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 19.5534 | 18.6646 | 18.33% | 17.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 07:15 | 2024-01-01 02:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 18.6646 | 17.7758 | 17.5% | 16.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 07:20 | 2024-01-01 02:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 17.7758 | 16.887 | 16.67% | 15.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 07:25 | 2024-01-01 02:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 16.887 | 15.9982 | 15.83% | 15% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 07:30 | 2024-01-01 02:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 15.9982 | 15.1094 | 15% | 14.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 07:35 | 2024-01-01 02:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 15.1094 | 14.2206 | 14.17% | 13.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 07:40 | 2024-01-01 02:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 14.2206 | 13.3319 | 13.33% | 12.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 07:45 | 2024-01-01 02:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 13.3319 | 12.4431 | 12.5% | 11.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 07:50 | 2024-01-01 02:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 12.4431 | 11.5543 | 11.67% | 10.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 0 | 10.1322 | 106.6548 | 2024-01-01 07:55 | 2024-01-01 02:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 11.5543 | 10.6655 | 10.83% | 10% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 95.9893 | 95.1005 | 90% | 89.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 95.1005 | 94.2117 | 89.17% | 88.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 94.2117 | 93.323 | 88.33% | 87.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 93.323 | 92.4342 | 87.5% | 86.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 92.4342 | 91.5454 | 86.67% | 85.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 91.5454 | 90.6566 | 85.83% | 85% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 90.6566 | 89.7678 | 85% | 84.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 89.7678 | 88.879 | 84.17% | 83.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 88.879 | 87.9902 | 83.33% | 82.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 87.9902 | 87.1014 | 82.5% | 81.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 87.1014 | 86.2126 | 81.67% | 80.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 86.2126 | 85.3238 | 80.83% | 80% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 01:00 | 2023-12-31 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 85.3238 | 84.4351 | 80% | 79.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 01:05 | 2023-12-31 20:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 84.4351 | 83.5463 | 79.17% | 78.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 01:10 | 2023-12-31 20:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 83.5463 | 82.6575 | 78.33% | 77.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 01:15 | 2023-12-31 20:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 82.6575 | 81.7687 | 77.5% | 76.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 01:20 | 2023-12-31 20:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 81.7687 | 80.8799 | 76.67% | 75.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 01:25 | 2023-12-31 20:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 80.8799 | 79.9911 | 75.83% | 75% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 01:30 | 2023-12-31 20:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 79.9911 | 79.1023 | 75% | 74.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 01:35 | 2023-12-31 20:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 79.1023 | 78.2135 | 74.17% | 73.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 01:40 | 2023-12-31 20:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 78.2135 | 77.3247 | 73.33% | 72.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 01:45 | 2023-12-31 20:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 77.3247 | 76.4359 | 72.5% | 71.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 01:50 | 2023-12-31 20:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 76.4359 | 75.5472 | 71.67% | 70.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 01:55 | 2023-12-31 20:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 75.5472 | 74.6584 | 70.83% | 70% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 02:00 | 2023-12-31 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 74.6584 | 73.7696 | 70% | 69.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 02:05 | 2023-12-31 21:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 73.7696 | 72.8808 | 69.17% | 68.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 02:10 | 2023-12-31 21:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 72.8808 | 71.992 | 68.33% | 67.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 02:15 | 2023-12-31 21:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 71.992 | 71.1032 | 67.5% | 66.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 02:20 | 2023-12-31 21:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 71.1032 | 70.2144 | 66.67% | 65.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 02:25 | 2023-12-31 21:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 70.2144 | 69.3256 | 65.83% | 65% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 02:30 | 2023-12-31 21:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 69.3256 | 68.4368 | 65% | 64.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 02:35 | 2023-12-31 21:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 68.4368 | 67.548 | 64.17% | 63.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 02:40 | 2023-12-31 21:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 67.548 | 66.6593 | 63.33% | 62.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 02:45 | 2023-12-31 21:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 66.6593 | 65.7705 | 62.5% | 61.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 02:50 | 2023-12-31 21:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 65.7705 | 64.8817 | 61.67% | 60.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 02:55 | 2023-12-31 21:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 64.8817 | 63.9929 | 60.83% | 60% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 03:00 | 2023-12-31 22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 63.9929 | 63.1041 | 60% | 59.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 03:05 | 2023-12-31 22:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 63.1041 | 62.2153 | 59.17% | 58.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 03:10 | 2023-12-31 22:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 62.2153 | 61.3265 | 58.33% | 57.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 03:15 | 2023-12-31 22:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 61.3265 | 60.4377 | 57.5% | 56.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 03:20 | 2023-12-31 22:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 60.4377 | 59.5489 | 56.67% | 55.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 03:25 | 2023-12-31 22:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 59.5489 | 58.6601 | 55.83% | 55% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 03:30 | 2023-12-31 22:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 58.6601 | 57.7714 | 55% | 54.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 03:35 | 2023-12-31 22:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 57.7714 | 56.8826 | 54.17% | 53.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 03:40 | 2023-12-31 22:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 56.8826 | 55.9938 | 53.33% | 52.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 03:45 | 2023-12-31 22:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 55.9938 | 55.105 | 52.5% | 51.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 03:50 | 2023-12-31 22:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 55.105 | 54.2162 | 51.67% | 50.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 03:55 | 2023-12-31 22:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 54.2162 | 53.3274 | 50.83% | 50% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 04:00 | 2023-12-31 23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 53.3274 | 52.4386 | 50% | 49.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 04:05 | 2023-12-31 23:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 52.4386 | 51.5498 | 49.17% | 48.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 04:10 | 2023-12-31 23:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 51.5498 | 50.661 | 48.33% | 47.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 04:15 | 2023-12-31 23:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 50.661 | 49.7722 | 47.5% | 46.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 04:20 | 2023-12-31 23:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 49.7722 | 48.8835 | 46.67% | 45.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 04:25 | 2023-12-31 23:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 48.8835 | 47.9947 | 45.83% | 45% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 04:30 | 2023-12-31 23:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 47.9947 | 47.1059 | 45% | 44.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 04:35 | 2023-12-31 23:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 47.1059 | 46.2171 | 44.17% | 43.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 04:40 | 2023-12-31 23:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 46.2171 | 45.3283 | 43.33% | 42.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 04:45 | 2023-12-31 23:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 45.3283 | 44.4395 | 42.5% | 41.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 04:50 | 2023-12-31 23:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 44.4395 | 43.5507 | 41.67% | 40.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 04:55 | 2023-12-31 23:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 43.5507 | 42.6619 | 40.83% | 40% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 05:00 | 2024-01-01 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 42.6619 | 41.7731 | 40% | 39.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 05:05 | 2024-01-01 00:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 41.7731 | 40.8843 | 39.17% | 38.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 05:10 | 2024-01-01 00:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 40.8843 | 39.9956 | 38.33% | 37.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 05:15 | 2024-01-01 00:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 39.9956 | 39.1068 | 37.5% | 36.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 05:20 | 2024-01-01 00:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 39.1068 | 38.218 | 36.67% | 35.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 05:25 | 2024-01-01 00:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 38.218 | 37.3292 | 35.83% | 35% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 05:30 | 2024-01-01 00:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 37.3292 | 36.4404 | 35% | 34.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 05:35 | 2024-01-01 00:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 36.4404 | 35.5516 | 34.17% | 33.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 05:40 | 2024-01-01 00:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 35.5516 | 34.6628 | 33.33% | 32.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 05:45 | 2024-01-01 00:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 34.6628 | 33.774 | 32.5% | 31.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 05:50 | 2024-01-01 00:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 33.774 | 32.8852 | 31.67% | 30.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 05:55 | 2024-01-01 00:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 32.8852 | 31.9964 | 30.83% | 30% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 06:00 | 2024-01-01 01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 31.9964 | 31.1077 | 30% | 29.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 06:05 | 2024-01-01 01:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 31.1077 | 30.2189 | 29.17% | 28.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 06:10 | 2024-01-01 01:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 30.2189 | 29.3301 | 28.33% | 27.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 06:15 | 2024-01-01 01:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 29.3301 | 28.4413 | 27.5% | 26.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 06:20 | 2024-01-01 01:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 28.4413 | 27.5525 | 26.67% | 25.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 06:25 | 2024-01-01 01:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 27.5525 | 26.6637 | 25.83% | 25% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 06:30 | 2024-01-01 01:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 26.6637 | 25.7749 | 25% | 24.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 06:35 | 2024-01-01 01:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 25.7749 | 24.8861 | 24.17% | 23.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 06:40 | 2024-01-01 01:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 24.8861 | 23.9973 | 23.33% | 22.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 06:45 | 2024-01-01 01:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 23.9973 | 23.1085 | 22.5% | 21.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 06:50 | 2024-01-01 01:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 23.1085 | 22.2198 | 21.67% | 20.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 06:55 | 2024-01-01 01:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 22.2198 | 21.331 | 20.83% | 20% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 07:00 | 2024-01-01 02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 21.331 | 20.4422 | 20% | 19.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 07:05 | 2024-01-01 02:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 20.4422 | 19.5534 | 19.17% | 18.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 07:10 | 2024-01-01 02:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 19.5534 | 18.6646 | 18.33% | 17.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 07:15 | 2024-01-01 02:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 18.6646 | 17.7758 | 17.5% | 16.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 07:20 | 2024-01-01 02:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 17.7758 | 16.887 | 16.67% | 15.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 07:25 | 2024-01-01 02:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 16.887 | 15.9982 | 15.83% | 15% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 07:30 | 2024-01-01 02:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 15.9982 | 15.1094 | 15% | 14.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 07:35 | 2024-01-01 02:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 15.1094 | 14.2206 | 14.17% | 13.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 07:40 | 2024-01-01 02:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 14.2206 | 13.3319 | 13.33% | 12.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 07:45 | 2024-01-01 02:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 13.3319 | 12.4431 | 12.5% | 11.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 07:50 | 2024-01-01 02:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 12.4431 | 11.5543 | 11.67% | 10.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 3.3774 | 10.1322 | 106.6548 | 2024-01-01 07:55 | 2024-01-01 02:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 11.5543 | 10.6655 | 10.83% | 10% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 95.9893 | 95.1005 | 90% | 89.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 95.1005 | 94.2117 | 89.17% | 88.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 94.2117 | 93.323 | 88.33% | 87.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 93.323 | 92.4342 | 87.5% | 86.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 92.4342 | 91.5454 | 86.67% | 85.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 91.5454 | 90.6566 | 85.83% | 85% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 90.6566 | 89.7678 | 85% | 84.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 89.7678 | 88.879 | 84.17% | 83.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 88.879 | 87.9902 | 83.33% | 82.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 87.9902 | 87.1014 | 82.5% | 81.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 87.1014 | 86.2126 | 81.67% | 80.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 86.2126 | 85.3238 | 80.83% | 80% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 01:00 | 2023-12-31 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 85.3238 | 84.4351 | 80% | 79.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 01:05 | 2023-12-31 20:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 84.4351 | 83.5463 | 79.17% | 78.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 01:10 | 2023-12-31 20:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 83.5463 | 82.6575 | 78.33% | 77.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 01:15 | 2023-12-31 20:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 82.6575 | 81.7687 | 77.5% | 76.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 01:20 | 2023-12-31 20:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 81.7687 | 80.8799 | 76.67% | 75.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 01:25 | 2023-12-31 20:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 80.8799 | 79.9911 | 75.83% | 75% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 01:30 | 2023-12-31 20:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 79.9911 | 79.1023 | 75% | 74.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 01:35 | 2023-12-31 20:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 79.1023 | 78.2135 | 74.17% | 73.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 01:40 | 2023-12-31 20:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 78.2135 | 77.3247 | 73.33% | 72.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 01:45 | 2023-12-31 20:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 77.3247 | 76.4359 | 72.5% | 71.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 01:50 | 2023-12-31 20:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 76.4359 | 75.5472 | 71.67% | 70.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 01:55 | 2023-12-31 20:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 75.5472 | 74.6584 | 70.83% | 70% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 02:00 | 2023-12-31 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 74.6584 | 73.7696 | 70% | 69.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 02:05 | 2023-12-31 21:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 73.7696 | 72.8808 | 69.17% | 68.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 02:10 | 2023-12-31 21:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 72.8808 | 71.992 | 68.33% | 67.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 02:15 | 2023-12-31 21:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 71.992 | 71.1032 | 67.5% | 66.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 02:20 | 2023-12-31 21:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 71.1032 | 70.2144 | 66.67% | 65.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 02:25 | 2023-12-31 21:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 70.2144 | 69.3256 | 65.83% | 65% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 02:30 | 2023-12-31 21:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 69.3256 | 68.4368 | 65% | 64.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 02:35 | 2023-12-31 21:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 68.4368 | 67.548 | 64.17% | 63.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 02:40 | 2023-12-31 21:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 67.548 | 66.6593 | 63.33% | 62.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 02:45 | 2023-12-31 21:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 66.6593 | 65.7705 | 62.5% | 61.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 02:50 | 2023-12-31 21:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 65.7705 | 64.8817 | 61.67% | 60.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 02:55 | 2023-12-31 21:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 64.8817 | 63.9929 | 60.83% | 60% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 03:00 | 2023-12-31 22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 63.9929 | 63.1041 | 60% | 59.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 03:05 | 2023-12-31 22:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 63.1041 | 62.2153 | 59.17% | 58.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 03:10 | 2023-12-31 22:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 62.2153 | 61.3265 | 58.33% | 57.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 03:15 | 2023-12-31 22:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 61.3265 | 60.4377 | 57.5% | 56.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 03:20 | 2023-12-31 22:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 60.4377 | 59.5489 | 56.67% | 55.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 03:25 | 2023-12-31 22:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 59.5489 | 58.6601 | 55.83% | 55% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 03:30 | 2023-12-31 22:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 58.6601 | 57.7714 | 55% | 54.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 03:35 | 2023-12-31 22:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 57.7714 | 56.8826 | 54.17% | 53.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 03:40 | 2023-12-31 22:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 56.8826 | 55.9938 | 53.33% | 52.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 03:45 | 2023-12-31 22:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 55.9938 | 55.105 | 52.5% | 51.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 03:50 | 2023-12-31 22:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 55.105 | 54.2162 | 51.67% | 50.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 03:55 | 2023-12-31 22:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 54.2162 | 53.3274 | 50.83% | 50% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 04:00 | 2023-12-31 23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 53.3274 | 52.4386 | 50% | 49.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 04:05 | 2023-12-31 23:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 52.4386 | 51.5498 | 49.17% | 48.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 04:10 | 2023-12-31 23:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 51.5498 | 50.661 | 48.33% | 47.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 04:15 | 2023-12-31 23:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 50.661 | 49.7722 | 47.5% | 46.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 04:20 | 2023-12-31 23:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 49.7722 | 48.8835 | 46.67% | 45.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 04:25 | 2023-12-31 23:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 48.8835 | 47.9947 | 45.83% | 45% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 04:30 | 2023-12-31 23:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 47.9947 | 47.1059 | 45% | 44.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 04:35 | 2023-12-31 23:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 47.1059 | 46.2171 | 44.17% | 43.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 04:40 | 2023-12-31 23:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 46.2171 | 45.3283 | 43.33% | 42.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 04:45 | 2023-12-31 23:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 45.3283 | 44.4395 | 42.5% | 41.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 04:50 | 2023-12-31 23:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 44.4395 | 43.5507 | 41.67% | 40.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 04:55 | 2023-12-31 23:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 43.5507 | 42.6619 | 40.83% | 40% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 05:00 | 2024-01-01 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 42.6619 | 41.7731 | 40% | 39.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 05:05 | 2024-01-01 00:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 41.7731 | 40.8843 | 39.17% | 38.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 05:10 | 2024-01-01 00:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 40.8843 | 39.9956 | 38.33% | 37.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 05:15 | 2024-01-01 00:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 39.9956 | 39.1068 | 37.5% | 36.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 05:20 | 2024-01-01 00:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 39.1068 | 38.218 | 36.67% | 35.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 05:25 | 2024-01-01 00:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 38.218 | 37.3292 | 35.83% | 35% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 05:30 | 2024-01-01 00:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 37.3292 | 36.4404 | 35% | 34.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 05:35 | 2024-01-01 00:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 36.4404 | 35.5516 | 34.17% | 33.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 05:40 | 2024-01-01 00:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 35.5516 | 34.6628 | 33.33% | 32.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 05:45 | 2024-01-01 00:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 34.6628 | 33.774 | 32.5% | 31.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 05:50 | 2024-01-01 00:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 33.774 | 32.8852 | 31.67% | 30.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 05:55 | 2024-01-01 00:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 32.8852 | 31.9964 | 30.83% | 30% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 06:00 | 2024-01-01 01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 31.9964 | 31.1077 | 30% | 29.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 06:05 | 2024-01-01 01:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 31.1077 | 30.2189 | 29.17% | 28.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 06:10 | 2024-01-01 01:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 30.2189 | 29.3301 | 28.33% | 27.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 06:15 | 2024-01-01 01:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 29.3301 | 28.4413 | 27.5% | 26.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 06:20 | 2024-01-01 01:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 28.4413 | 27.5525 | 26.67% | 25.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 06:25 | 2024-01-01 01:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 27.5525 | 26.6637 | 25.83% | 25% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 06:30 | 2024-01-01 01:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 26.6637 | 25.7749 | 25% | 24.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 06:35 | 2024-01-01 01:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 25.7749 | 24.8861 | 24.17% | 23.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 06:40 | 2024-01-01 01:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 24.8861 | 23.9973 | 23.33% | 22.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 06:45 | 2024-01-01 01:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 23.9973 | 23.1085 | 22.5% | 21.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 06:50 | 2024-01-01 01:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 23.1085 | 22.2198 | 21.67% | 20.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 06:55 | 2024-01-01 01:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 22.2198 | 21.331 | 20.83% | 20% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 07:00 | 2024-01-01 02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 21.331 | 20.4422 | 20% | 19.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 07:05 | 2024-01-01 02:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 20.4422 | 19.5534 | 19.17% | 18.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 07:10 | 2024-01-01 02:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 19.5534 | 18.6646 | 18.33% | 17.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 07:15 | 2024-01-01 02:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 18.6646 | 17.7758 | 17.5% | 16.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 07:20 | 2024-01-01 02:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 17.7758 | 16.887 | 16.67% | 15.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 07:25 | 2024-01-01 02:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 16.887 | 15.9982 | 15.83% | 15% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 07:30 | 2024-01-01 02:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 15.9982 | 15.1094 | 15% | 14.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 07:35 | 2024-01-01 02:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 15.1094 | 14.2206 | 14.17% | 13.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 07:40 | 2024-01-01 02:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 14.2206 | 13.3319 | 13.33% | 12.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 07:45 | 2024-01-01 02:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 13.3319 | 12.4431 | 12.5% | 11.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 07:50 | 2024-01-01 02:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 12.4431 | 11.5543 | 11.67% | 10.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 6.7548 | 10.1322 | 106.6548 | 2024-01-01 07:55 | 2024-01-01 02:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 11.5543 | 10.6655 | 10.83% | 10% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 95.9893 | 95.1005 | 90% | 89.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 95.1005 | 94.2117 | 89.17% | 88.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 94.2117 | 93.323 | 88.33% | 87.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 93.323 | 92.4342 | 87.5% | 86.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 92.4342 | 91.5454 | 86.67% | 85.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 91.5454 | 90.6566 | 85.83% | 85% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 90.6566 | 89.7678 | 85% | 84.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 89.7678 | 88.879 | 84.17% | 83.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 88.879 | 87.9902 | 83.33% | 82.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 87.9902 | 87.1014 | 82.5% | 81.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 87.1014 | 86.2126 | 81.67% | 80.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 86.2126 | 85.3238 | 80.83% | 80% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 01:00 | 2023-12-31 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 85.3238 | 84.4351 | 80% | 79.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 01:05 | 2023-12-31 20:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 84.4351 | 83.5463 | 79.17% | 78.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 01:10 | 2023-12-31 20:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 83.5463 | 82.6575 | 78.33% | 77.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 01:15 | 2023-12-31 20:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 82.6575 | 81.7687 | 77.5% | 76.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 01:20 | 2023-12-31 20:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 81.7687 | 80.8799 | 76.67% | 75.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 01:25 | 2023-12-31 20:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 80.8799 | 79.9911 | 75.83% | 75% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 01:30 | 2023-12-31 20:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 79.9911 | 79.1023 | 75% | 74.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 01:35 | 2023-12-31 20:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 79.1023 | 78.2135 | 74.17% | 73.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 01:40 | 2023-12-31 20:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 78.2135 | 77.3247 | 73.33% | 72.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 01:45 | 2023-12-31 20:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 77.3247 | 76.4359 | 72.5% | 71.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 01:50 | 2023-12-31 20:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 76.4359 | 75.5472 | 71.67% | 70.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 01:55 | 2023-12-31 20:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 75.5472 | 74.6584 | 70.83% | 70% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 02:00 | 2023-12-31 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 74.6584 | 73.7696 | 70% | 69.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 02:05 | 2023-12-31 21:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 73.7696 | 72.8808 | 69.17% | 68.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 02:10 | 2023-12-31 21:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 72.8808 | 71.992 | 68.33% | 67.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 02:15 | 2023-12-31 21:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 71.992 | 71.1032 | 67.5% | 66.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 02:20 | 2023-12-31 21:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 71.1032 | 70.2144 | 66.67% | 65.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 02:25 | 2023-12-31 21:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 70.2144 | 69.3256 | 65.83% | 65% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 02:30 | 2023-12-31 21:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 69.3256 | 68.4368 | 65% | 64.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 02:35 | 2023-12-31 21:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 68.4368 | 67.548 | 64.17% | 63.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 02:40 | 2023-12-31 21:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 67.548 | 66.6593 | 63.33% | 62.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 02:45 | 2023-12-31 21:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 66.6593 | 65.7705 | 62.5% | 61.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 02:50 | 2023-12-31 21:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 65.7705 | 64.8817 | 61.67% | 60.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 02:55 | 2023-12-31 21:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 64.8817 | 63.9929 | 60.83% | 60% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 03:00 | 2023-12-31 22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 63.9929 | 63.1041 | 60% | 59.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 03:05 | 2023-12-31 22:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 63.1041 | 62.2153 | 59.17% | 58.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 03:10 | 2023-12-31 22:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 62.2153 | 61.3265 | 58.33% | 57.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 03:15 | 2023-12-31 22:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 61.3265 | 60.4377 | 57.5% | 56.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 03:20 | 2023-12-31 22:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 60.4377 | 59.5489 | 56.67% | 55.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 03:25 | 2023-12-31 22:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 59.5489 | 58.6601 | 55.83% | 55% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 03:30 | 2023-12-31 22:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 58.6601 | 57.7714 | 55% | 54.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 03:35 | 2023-12-31 22:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 57.7714 | 56.8826 | 54.17% | 53.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 03:40 | 2023-12-31 22:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 56.8826 | 55.9938 | 53.33% | 52.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 03:45 | 2023-12-31 22:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 55.9938 | 55.105 | 52.5% | 51.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 03:50 | 2023-12-31 22:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 55.105 | 54.2162 | 51.67% | 50.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 03:55 | 2023-12-31 22:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 54.2162 | 53.3274 | 50.83% | 50% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 04:00 | 2023-12-31 23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 53.3274 | 52.4386 | 50% | 49.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 04:05 | 2023-12-31 23:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 52.4386 | 51.5498 | 49.17% | 48.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 04:10 | 2023-12-31 23:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 51.5498 | 50.661 | 48.33% | 47.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 04:15 | 2023-12-31 23:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 50.661 | 49.7722 | 47.5% | 46.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 04:20 | 2023-12-31 23:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 49.7722 | 48.8835 | 46.67% | 45.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 04:25 | 2023-12-31 23:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 48.8835 | 47.9947 | 45.83% | 45% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 04:30 | 2023-12-31 23:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 47.9947 | 47.1059 | 45% | 44.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 04:35 | 2023-12-31 23:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 47.1059 | 46.2171 | 44.17% | 43.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 04:40 | 2023-12-31 23:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 46.2171 | 45.3283 | 43.33% | 42.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 04:45 | 2023-12-31 23:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 45.3283 | 44.4395 | 42.5% | 41.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 04:50 | 2023-12-31 23:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 44.4395 | 43.5507 | 41.67% | 40.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 04:55 | 2023-12-31 23:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 43.5507 | 42.6619 | 40.83% | 40% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 05:00 | 2024-01-01 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 42.6619 | 41.7731 | 40% | 39.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 05:05 | 2024-01-01 00:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 41.7731 | 40.8843 | 39.17% | 38.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 05:10 | 2024-01-01 00:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 40.8843 | 39.9956 | 38.33% | 37.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 05:15 | 2024-01-01 00:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 39.9956 | 39.1068 | 37.5% | 36.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 05:20 | 2024-01-01 00:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 39.1068 | 38.218 | 36.67% | 35.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 05:25 | 2024-01-01 00:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 38.218 | 37.3292 | 35.83% | 35% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 05:30 | 2024-01-01 00:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 37.3292 | 36.4404 | 35% | 34.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 05:35 | 2024-01-01 00:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 36.4404 | 35.5516 | 34.17% | 33.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 05:40 | 2024-01-01 00:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 35.5516 | 34.6628 | 33.33% | 32.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 05:45 | 2024-01-01 00:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 34.6628 | 33.774 | 32.5% | 31.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 05:50 | 2024-01-01 00:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 33.774 | 32.8852 | 31.67% | 30.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 05:55 | 2024-01-01 00:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 32.8852 | 31.9964 | 30.83% | 30% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 06:00 | 2024-01-01 01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 31.9964 | 31.1077 | 30% | 29.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 06:05 | 2024-01-01 01:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 31.1077 | 30.2189 | 29.17% | 28.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 06:10 | 2024-01-01 01:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 30.2189 | 29.3301 | 28.33% | 27.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 06:15 | 2024-01-01 01:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 29.3301 | 28.4413 | 27.5% | 26.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 06:20 | 2024-01-01 01:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 28.4413 | 27.5525 | 26.67% | 25.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 06:25 | 2024-01-01 01:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 27.5525 | 26.6637 | 25.83% | 25% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 06:30 | 2024-01-01 01:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 26.6637 | 25.7749 | 25% | 24.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 06:35 | 2024-01-01 01:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 25.7749 | 24.8861 | 24.17% | 23.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 06:40 | 2024-01-01 01:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 24.8861 | 23.9973 | 23.33% | 22.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 06:45 | 2024-01-01 01:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 23.9973 | 23.1085 | 22.5% | 21.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 06:50 | 2024-01-01 01:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 23.1085 | 22.2198 | 21.67% | 20.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 06:55 | 2024-01-01 01:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 22.2198 | 21.331 | 20.83% | 20% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 07:00 | 2024-01-01 02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 21.331 | 20.4422 | 20% | 19.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 07:05 | 2024-01-01 02:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 20.4422 | 19.5534 | 19.17% | 18.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 07:10 | 2024-01-01 02:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 19.5534 | 18.6646 | 18.33% | 17.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 07:15 | 2024-01-01 02:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 18.6646 | 17.7758 | 17.5% | 16.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 07:20 | 2024-01-01 02:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 17.7758 | 16.887 | 16.67% | 15.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 07:25 | 2024-01-01 02:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 16.887 | 15.9982 | 15.83% | 15% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 07:30 | 2024-01-01 02:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 15.9982 | 15.1094 | 15% | 14.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 07:35 | 2024-01-01 02:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 15.1094 | 14.2206 | 14.17% | 13.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 07:40 | 2024-01-01 02:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 14.2206 | 13.3319 | 13.33% | 12.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 07:45 | 2024-01-01 02:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 13.3319 | 12.4431 | 12.5% | 11.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 07:50 | 2024-01-01 02:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 12.4431 | 11.5543 | 11.67% | 10.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 10.1322 | 10.1322 | 106.6548 | 2024-01-01 07:55 | 2024-01-01 02:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 11.5543 | 10.6655 | 10.83% | 10% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 95.9893 | 95.1005 | 90% | 89.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 95.1005 | 94.2117 | 89.17% | 88.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 94.2117 | 93.323 | 88.33% | 87.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 93.323 | 92.4342 | 87.5% | 86.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 92.4342 | 91.5454 | 86.67% | 85.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 91.5454 | 90.6566 | 85.83% | 85% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 90.6566 | 89.7678 | 85% | 84.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 89.7678 | 88.879 | 84.17% | 83.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 88.879 | 87.9902 | 83.33% | 82.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 87.9902 | 87.1014 | 82.5% | 81.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 87.1014 | 86.2126 | 81.67% | 80.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 86.2126 | 85.3238 | 80.83% | 80% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 01:00 | 2023-12-31 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 85.3238 | 84.4351 | 80% | 79.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 01:05 | 2023-12-31 20:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 84.4351 | 83.5463 | 79.17% | 78.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 01:10 | 2023-12-31 20:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 83.5463 | 82.6575 | 78.33% | 77.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 01:15 | 2023-12-31 20:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 82.6575 | 81.7687 | 77.5% | 76.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 01:20 | 2023-12-31 20:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 81.7687 | 80.8799 | 76.67% | 75.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 01:25 | 2023-12-31 20:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 80.8799 | 79.9911 | 75.83% | 75% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 01:30 | 2023-12-31 20:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 79.9911 | 79.1023 | 75% | 74.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 01:35 | 2023-12-31 20:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 79.1023 | 78.2135 | 74.17% | 73.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 01:40 | 2023-12-31 20:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 78.2135 | 77.3247 | 73.33% | 72.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 01:45 | 2023-12-31 20:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 77.3247 | 76.4359 | 72.5% | 71.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 01:50 | 2023-12-31 20:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 76.4359 | 75.5472 | 71.67% | 70.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 01:55 | 2023-12-31 20:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 75.5472 | 74.6584 | 70.83% | 70% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 02:00 | 2023-12-31 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 74.6584 | 73.7696 | 70% | 69.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 02:05 | 2023-12-31 21:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 73.7696 | 72.8808 | 69.17% | 68.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 02:10 | 2023-12-31 21:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 72.8808 | 71.992 | 68.33% | 67.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 02:15 | 2023-12-31 21:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 71.992 | 71.1032 | 67.5% | 66.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 02:20 | 2023-12-31 21:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 71.1032 | 70.2144 | 66.67% | 65.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 02:25 | 2023-12-31 21:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 70.2144 | 69.3256 | 65.83% | 65% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 02:30 | 2023-12-31 21:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 69.3256 | 68.4368 | 65% | 64.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 02:35 | 2023-12-31 21:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 68.4368 | 67.548 | 64.17% | 63.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 02:40 | 2023-12-31 21:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 67.548 | 66.6593 | 63.33% | 62.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 02:45 | 2023-12-31 21:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 66.6593 | 65.7705 | 62.5% | 61.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 02:50 | 2023-12-31 21:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 65.7705 | 64.8817 | 61.67% | 60.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 02:55 | 2023-12-31 21:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 64.8817 | 63.9929 | 60.83% | 60% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 03:00 | 2023-12-31 22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 63.9929 | 63.1041 | 60% | 59.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 03:05 | 2023-12-31 22:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 63.1041 | 62.2153 | 59.17% | 58.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 03:10 | 2023-12-31 22:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 62.2153 | 61.3265 | 58.33% | 57.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 03:15 | 2023-12-31 22:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 61.3265 | 60.4377 | 57.5% | 56.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 03:20 | 2023-12-31 22:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 60.4377 | 59.5489 | 56.67% | 55.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 03:25 | 2023-12-31 22:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 59.5489 | 58.6601 | 55.83% | 55% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 03:30 | 2023-12-31 22:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 58.6601 | 57.7714 | 55% | 54.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 03:35 | 2023-12-31 22:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 57.7714 | 56.8826 | 54.17% | 53.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 03:40 | 2023-12-31 22:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 56.8826 | 55.9938 | 53.33% | 52.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 03:45 | 2023-12-31 22:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 55.9938 | 55.105 | 52.5% | 51.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 03:50 | 2023-12-31 22:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 55.105 | 54.2162 | 51.67% | 50.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 03:55 | 2023-12-31 22:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 54.2162 | 53.3274 | 50.83% | 50% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 04:00 | 2023-12-31 23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 53.3274 | 52.4386 | 50% | 49.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 04:05 | 2023-12-31 23:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 52.4386 | 51.5498 | 49.17% | 48.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 04:10 | 2023-12-31 23:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 51.5498 | 50.661 | 48.33% | 47.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 04:15 | 2023-12-31 23:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 50.661 | 49.7722 | 47.5% | 46.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 04:20 | 2023-12-31 23:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 49.7722 | 48.8835 | 46.67% | 45.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 04:25 | 2023-12-31 23:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 48.8835 | 47.9947 | 45.83% | 45% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 04:30 | 2023-12-31 23:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 47.9947 | 47.1059 | 45% | 44.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 04:35 | 2023-12-31 23:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 47.1059 | 46.2171 | 44.17% | 43.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 04:40 | 2023-12-31 23:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 46.2171 | 45.3283 | 43.33% | 42.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 04:45 | 2023-12-31 23:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 45.3283 | 44.4395 | 42.5% | 41.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 04:50 | 2023-12-31 23:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 44.4395 | 43.5507 | 41.67% | 40.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 04:55 | 2023-12-31 23:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 43.5507 | 42.6619 | 40.83% | 40% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 05:00 | 2024-01-01 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 42.6619 | 41.7731 | 40% | 39.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 05:05 | 2024-01-01 00:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 41.7731 | 40.8843 | 39.17% | 38.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 05:10 | 2024-01-01 00:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 40.8843 | 39.9956 | 38.33% | 37.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 05:15 | 2024-01-01 00:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 39.9956 | 39.1068 | 37.5% | 36.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 05:20 | 2024-01-01 00:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 39.1068 | 38.218 | 36.67% | 35.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 05:25 | 2024-01-01 00:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 38.218 | 37.3292 | 35.83% | 35% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 05:30 | 2024-01-01 00:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 37.3292 | 36.4404 | 35% | 34.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 05:35 | 2024-01-01 00:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 36.4404 | 35.5516 | 34.17% | 33.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 05:40 | 2024-01-01 00:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 35.5516 | 34.6628 | 33.33% | 32.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 05:45 | 2024-01-01 00:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 34.6628 | 33.774 | 32.5% | 31.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 05:50 | 2024-01-01 00:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 33.774 | 32.8852 | 31.67% | 30.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 05:55 | 2024-01-01 00:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 32.8852 | 31.9964 | 30.83% | 30% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 06:00 | 2024-01-01 01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 31.9964 | 31.1077 | 30% | 29.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 06:05 | 2024-01-01 01:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 31.1077 | 30.2189 | 29.17% | 28.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 06:10 | 2024-01-01 01:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 30.2189 | 29.3301 | 28.33% | 27.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 06:15 | 2024-01-01 01:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 29.3301 | 28.4413 | 27.5% | 26.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 06:20 | 2024-01-01 01:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 28.4413 | 27.5525 | 26.67% | 25.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 06:25 | 2024-01-01 01:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 27.5525 | 26.6637 | 25.83% | 25% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 06:30 | 2024-01-01 01:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 26.6637 | 25.7749 | 25% | 24.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 06:35 | 2024-01-01 01:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 25.7749 | 24.8861 | 24.17% | 23.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 06:40 | 2024-01-01 01:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 24.8861 | 23.9973 | 23.33% | 22.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 06:45 | 2024-01-01 01:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 23.9973 | 23.1085 | 22.5% | 21.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 06:50 | 2024-01-01 01:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 23.1085 | 22.2198 | 21.67% | 20.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 06:55 | 2024-01-01 01:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 22.2198 | 21.331 | 20.83% | 20% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 07:00 | 2024-01-01 02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 21.331 | 20.4422 | 20% | 19.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 07:05 | 2024-01-01 02:05 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 20.4422 | 19.5534 | 19.17% | 18.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 07:10 | 2024-01-01 02:10 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 19.5534 | 18.6646 | 18.33% | 17.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 07:15 | 2024-01-01 02:15 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 18.6646 | 17.7758 | 17.5% | 16.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 07:20 | 2024-01-01 02:20 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 17.7758 | 16.887 | 16.67% | 15.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 07:25 | 2024-01-01 02:25 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 16.887 | 15.9982 | 15.83% | 15% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 07:30 | 2024-01-01 02:30 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 15.9982 | 15.1094 | 15% | 14.17% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 07:35 | 2024-01-01 02:35 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 15.1094 | 14.2206 | 14.17% | 13.33% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 07:40 | 2024-01-01 02:40 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 14.2206 | 13.3319 | 13.33% | 12.5% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 07:45 | 2024-01-01 02:45 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 13.3319 | 12.4431 | 12.5% | 11.67% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 07:50 | 2024-01-01 02:50 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 12.4431 | 11.5543 | 11.67% | 10.83% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.75 | 8 | 13.5096 | 10.1322 | 106.6548 | 2024-01-01 07:55 | 2024-01-01 02:55 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1322 | 11.5543 | 10.6655 | 10.83% | 10% | 10.6655 | 10.1322 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 1 | 0 | 12.1586 | 15.9982 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 14.3984 | 13.3319 | 90% | 83.33% | 1.5998 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 1 | 0 | 12.1586 | 15.9982 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 13.3319 | 12.2653 | 83.33% | 76.67% | 1.5998 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 1 | 0 | 12.1586 | 15.9982 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 12.2653 | 11.1988 | 76.67% | 70% | 1.5998 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 1 | 0 | 12.1586 | 15.9982 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 11.1988 | 10.1322 | 70% | 63.33% | 1.5998 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 1 | 0 | 12.1586 | 15.9982 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 10.1322 | 9.0657 | 63.33% | 56.67% | 1.5998 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 1 | 0 | 12.1586 | 15.9982 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 9.0657 | 7.9991 | 56.67% | 50% | 1.5998 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 1 | 0 | 12.1586 | 15.9982 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 7.9991 | 6.9326 | 50% | 43.33% | 1.5998 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 1 | 0 | 12.1586 | 15.9982 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 6.9326 | 5.866 | 43.33% | 36.67% | 1.5998 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 1 | 0 | 12.1586 | 15.9982 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 5.866 | 4.7995 | 36.67% | 30% | 1.5998 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 1 | 0 | 12.1586 | 15.9982 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 4.7995 | 3.7329 | 30% | 23.33% | 1.5998 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 1 | 0 | 12.1586 | 15.9982 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 3.7329 | 2.6664 | 23.33% | 16.67% | 1.5998 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 1 | 0 | 12.1586 | 15.9982 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 2.6664 | 1.5998 | 16.67% | 10% | 1.5998 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 1 | 3.3774 | 12.1586 | 15.9982 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 14.3984 | 13.3319 | 90% | 83.33% | 1.5998 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 1 | 3.3774 | 12.1586 | 15.9982 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 13.3319 | 12.2653 | 83.33% | 76.67% | 1.5998 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 1 | 3.3774 | 12.1586 | 15.9982 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 12.2653 | 11.1988 | 76.67% | 70% | 1.5998 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 1 | 3.3774 | 12.1586 | 15.9982 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 11.1988 | 10.1322 | 70% | 63.33% | 1.5998 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 1 | 3.3774 | 12.1586 | 15.9982 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 10.1322 | 9.0657 | 63.33% | 56.67% | 1.5998 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 1 | 3.3774 | 12.1586 | 15.9982 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 9.0657 | 7.9991 | 56.67% | 50% | 1.5998 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 1 | 3.3774 | 12.1586 | 15.9982 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 7.9991 | 6.9326 | 50% | 43.33% | 1.5998 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 1 | 3.3774 | 12.1586 | 15.9982 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 6.9326 | 5.866 | 43.33% | 36.67% | 1.5998 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 1 | 3.3774 | 12.1586 | 15.9982 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 5.866 | 4.7995 | 36.67% | 30% | 1.5998 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 1 | 3.3774 | 12.1586 | 15.9982 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 4.7995 | 3.7329 | 30% | 23.33% | 1.5998 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 1 | 3.3774 | 12.1586 | 15.9982 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 3.7329 | 2.6664 | 23.33% | 16.67% | 1.5998 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 1 | 3.3774 | 12.1586 | 15.9982 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 2.6664 | 1.5998 | 16.67% | 10% | 1.5998 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 1 | 6.7548 | 12.1586 | 15.9982 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 14.3984 | 13.3319 | 90% | 83.33% | 1.5998 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 1 | 6.7548 | 12.1586 | 15.9982 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 13.3319 | 12.2653 | 83.33% | 76.67% | 1.5998 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 1 | 6.7548 | 12.1586 | 15.9982 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 12.2653 | 11.1988 | 76.67% | 70% | 1.5998 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 1 | 6.7548 | 12.1586 | 15.9982 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 11.1988 | 10.1322 | 70% | 63.33% | 1.5998 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 1 | 6.7548 | 12.1586 | 15.9982 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 10.1322 | 9.0657 | 63.33% | 56.67% | 1.5998 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 1 | 6.7548 | 12.1586 | 15.9982 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 9.0657 | 7.9991 | 56.67% | 50% | 1.5998 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 1 | 6.7548 | 12.1586 | 15.9982 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 7.9991 | 6.9326 | 50% | 43.33% | 1.5998 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 1 | 6.7548 | 12.1586 | 15.9982 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 6.9326 | 5.866 | 43.33% | 36.67% | 1.5998 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 1 | 6.7548 | 12.1586 | 15.9982 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 5.866 | 4.7995 | 36.67% | 30% | 1.5998 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 1 | 6.7548 | 12.1586 | 15.9982 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 4.7995 | 3.7329 | 30% | 23.33% | 1.5998 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 1 | 6.7548 | 12.1586 | 15.9982 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 3.7329 | 2.6664 | 23.33% | 16.67% | 1.5998 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 1 | 6.7548 | 12.1586 | 15.9982 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 2.6664 | 1.5998 | 16.67% | 10% | 1.5998 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 1 | 10.1322 | 12.1586 | 15.9982 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 14.3984 | 13.3319 | 90% | 83.33% | 1.5998 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 1 | 10.1322 | 12.1586 | 15.9982 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 13.3319 | 12.2653 | 83.33% | 76.67% | 1.5998 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 1 | 10.1322 | 12.1586 | 15.9982 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 12.2653 | 11.1988 | 76.67% | 70% | 1.5998 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 1 | 10.1322 | 12.1586 | 15.9982 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 11.1988 | 10.1322 | 70% | 63.33% | 1.5998 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 1 | 10.1322 | 12.1586 | 15.9982 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 10.1322 | 9.0657 | 63.33% | 56.67% | 1.5998 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 1 | 10.1322 | 12.1586 | 15.9982 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 9.0657 | 7.9991 | 56.67% | 50% | 1.5998 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 1 | 10.1322 | 12.1586 | 15.9982 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 7.9991 | 6.9326 | 50% | 43.33% | 1.5998 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 1 | 10.1322 | 12.1586 | 15.9982 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 6.9326 | 5.866 | 43.33% | 36.67% | 1.5998 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 1 | 10.1322 | 12.1586 | 15.9982 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 5.866 | 4.7995 | 36.67% | 30% | 1.5998 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 1 | 10.1322 | 12.1586 | 15.9982 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 4.7995 | 3.7329 | 30% | 23.33% | 1.5998 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 1 | 10.1322 | 12.1586 | 15.9982 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 3.7329 | 2.6664 | 23.33% | 16.67% | 1.5998 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 1 | 10.1322 | 12.1586 | 15.9982 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 2.6664 | 1.5998 | 16.67% | 10% | 1.5998 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 1 | 13.5096 | 12.1586 | 15.9982 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 14.3984 | 13.3319 | 90% | 83.33% | 1.5998 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 1 | 13.5096 | 12.1586 | 15.9982 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 13.3319 | 12.2653 | 83.33% | 76.67% | 1.5998 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 1 | 13.5096 | 12.1586 | 15.9982 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 12.2653 | 11.1988 | 76.67% | 70% | 1.5998 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 1 | 13.5096 | 12.1586 | 15.9982 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 11.1988 | 10.1322 | 70% | 63.33% | 1.5998 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 1 | 13.5096 | 12.1586 | 15.9982 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 10.1322 | 9.0657 | 63.33% | 56.67% | 1.5998 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 1 | 13.5096 | 12.1586 | 15.9982 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 9.0657 | 7.9991 | 56.67% | 50% | 1.5998 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 1 | 13.5096 | 12.1586 | 15.9982 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 7.9991 | 6.9326 | 50% | 43.33% | 1.5998 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 1 | 13.5096 | 12.1586 | 15.9982 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 6.9326 | 5.866 | 43.33% | 36.67% | 1.5998 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 1 | 13.5096 | 12.1586 | 15.9982 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 5.866 | 4.7995 | 36.67% | 30% | 1.5998 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 1 | 13.5096 | 12.1586 | 15.9982 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 4.7995 | 3.7329 | 30% | 23.33% | 1.5998 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 1 | 13.5096 | 12.1586 | 15.9982 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 3.7329 | 2.6664 | 23.33% | 16.67% | 1.5998 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 1 | 13.5096 | 12.1586 | 15.9982 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 2.6664 | 1.5998 | 16.67% | 10% | 1.5998 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 0 | 12.1586 | 31.9964 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 28.7968 | 27.7302 | 90% | 86.67% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 0 | 12.1586 | 31.9964 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 27.7302 | 26.6637 | 86.67% | 83.33% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 0 | 12.1586 | 31.9964 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 26.6637 | 25.5972 | 83.33% | 80% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 0 | 12.1586 | 31.9964 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 25.5972 | 24.5306 | 80% | 76.67% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 0 | 12.1586 | 31.9964 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 24.5306 | 23.4641 | 76.67% | 73.33% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 0 | 12.1586 | 31.9964 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 23.4641 | 22.3975 | 73.33% | 70% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 0 | 12.1586 | 31.9964 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 22.3975 | 21.331 | 70% | 66.67% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 0 | 12.1586 | 31.9964 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 21.331 | 20.2644 | 66.67% | 63.33% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 0 | 12.1586 | 31.9964 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 20.2644 | 19.1979 | 63.33% | 60% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 0 | 12.1586 | 31.9964 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 19.1979 | 18.1313 | 60% | 56.67% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 0 | 12.1586 | 31.9964 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 18.1313 | 17.0648 | 56.67% | 53.33% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 0 | 12.1586 | 31.9964 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 17.0648 | 15.9982 | 53.33% | 50% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 0 | 12.1586 | 31.9964 | 2024-01-01 01:00 | 2023-12-31 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 15.9982 | 14.9317 | 50% | 46.67% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 0 | 12.1586 | 31.9964 | 2024-01-01 01:05 | 2023-12-31 20:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 14.9317 | 13.8651 | 46.67% | 43.33% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 0 | 12.1586 | 31.9964 | 2024-01-01 01:10 | 2023-12-31 20:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 13.8651 | 12.7986 | 43.33% | 40% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 0 | 12.1586 | 31.9964 | 2024-01-01 01:15 | 2023-12-31 20:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 12.7986 | 11.732 | 40% | 36.67% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 0 | 12.1586 | 31.9964 | 2024-01-01 01:20 | 2023-12-31 20:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 11.732 | 10.6655 | 36.67% | 33.33% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 0 | 12.1586 | 31.9964 | 2024-01-01 01:25 | 2023-12-31 20:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 10.6655 | 9.5989 | 33.33% | 30% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 0 | 12.1586 | 31.9964 | 2024-01-01 01:30 | 2023-12-31 20:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 9.5989 | 8.5324 | 30% | 26.67% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 0 | 12.1586 | 31.9964 | 2024-01-01 01:35 | 2023-12-31 20:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 8.5324 | 7.4658 | 26.67% | 23.33% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 0 | 12.1586 | 31.9964 | 2024-01-01 01:40 | 2023-12-31 20:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 7.4658 | 6.3993 | 23.33% | 20% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 0 | 12.1586 | 31.9964 | 2024-01-01 01:45 | 2023-12-31 20:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 6.3993 | 5.3327 | 20% | 16.67% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 0 | 12.1586 | 31.9964 | 2024-01-01 01:50 | 2023-12-31 20:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 5.3327 | 4.2662 | 16.67% | 13.33% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 0 | 12.1586 | 31.9964 | 2024-01-01 01:55 | 2023-12-31 20:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 4.2662 | 3.1996 | 13.33% | 10% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 3.3774 | 12.1586 | 31.9964 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 28.7968 | 27.7302 | 90% | 86.67% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 3.3774 | 12.1586 | 31.9964 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 27.7302 | 26.6637 | 86.67% | 83.33% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 3.3774 | 12.1586 | 31.9964 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 26.6637 | 25.5972 | 83.33% | 80% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 3.3774 | 12.1586 | 31.9964 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 25.5972 | 24.5306 | 80% | 76.67% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 3.3774 | 12.1586 | 31.9964 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 24.5306 | 23.4641 | 76.67% | 73.33% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 3.3774 | 12.1586 | 31.9964 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 23.4641 | 22.3975 | 73.33% | 70% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 3.3774 | 12.1586 | 31.9964 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 22.3975 | 21.331 | 70% | 66.67% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 3.3774 | 12.1586 | 31.9964 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 21.331 | 20.2644 | 66.67% | 63.33% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 3.3774 | 12.1586 | 31.9964 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 20.2644 | 19.1979 | 63.33% | 60% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 3.3774 | 12.1586 | 31.9964 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 19.1979 | 18.1313 | 60% | 56.67% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 3.3774 | 12.1586 | 31.9964 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 18.1313 | 17.0648 | 56.67% | 53.33% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 3.3774 | 12.1586 | 31.9964 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 17.0648 | 15.9982 | 53.33% | 50% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 3.3774 | 12.1586 | 31.9964 | 2024-01-01 01:00 | 2023-12-31 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 15.9982 | 14.9317 | 50% | 46.67% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 3.3774 | 12.1586 | 31.9964 | 2024-01-01 01:05 | 2023-12-31 20:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 14.9317 | 13.8651 | 46.67% | 43.33% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 3.3774 | 12.1586 | 31.9964 | 2024-01-01 01:10 | 2023-12-31 20:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 13.8651 | 12.7986 | 43.33% | 40% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 3.3774 | 12.1586 | 31.9964 | 2024-01-01 01:15 | 2023-12-31 20:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 12.7986 | 11.732 | 40% | 36.67% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 3.3774 | 12.1586 | 31.9964 | 2024-01-01 01:20 | 2023-12-31 20:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 11.732 | 10.6655 | 36.67% | 33.33% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 3.3774 | 12.1586 | 31.9964 | 2024-01-01 01:25 | 2023-12-31 20:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 10.6655 | 9.5989 | 33.33% | 30% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 3.3774 | 12.1586 | 31.9964 | 2024-01-01 01:30 | 2023-12-31 20:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 9.5989 | 8.5324 | 30% | 26.67% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 3.3774 | 12.1586 | 31.9964 | 2024-01-01 01:35 | 2023-12-31 20:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 8.5324 | 7.4658 | 26.67% | 23.33% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 3.3774 | 12.1586 | 31.9964 | 2024-01-01 01:40 | 2023-12-31 20:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 7.4658 | 6.3993 | 23.33% | 20% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 3.3774 | 12.1586 | 31.9964 | 2024-01-01 01:45 | 2023-12-31 20:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 6.3993 | 5.3327 | 20% | 16.67% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 3.3774 | 12.1586 | 31.9964 | 2024-01-01 01:50 | 2023-12-31 20:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 5.3327 | 4.2662 | 16.67% | 13.33% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 3.3774 | 12.1586 | 31.9964 | 2024-01-01 01:55 | 2023-12-31 20:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 4.2662 | 3.1996 | 13.33% | 10% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 6.7548 | 12.1586 | 31.9964 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 28.7968 | 27.7302 | 90% | 86.67% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 6.7548 | 12.1586 | 31.9964 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 27.7302 | 26.6637 | 86.67% | 83.33% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 6.7548 | 12.1586 | 31.9964 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 26.6637 | 25.5972 | 83.33% | 80% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 6.7548 | 12.1586 | 31.9964 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 25.5972 | 24.5306 | 80% | 76.67% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 6.7548 | 12.1586 | 31.9964 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 24.5306 | 23.4641 | 76.67% | 73.33% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 6.7548 | 12.1586 | 31.9964 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 23.4641 | 22.3975 | 73.33% | 70% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 6.7548 | 12.1586 | 31.9964 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 22.3975 | 21.331 | 70% | 66.67% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 6.7548 | 12.1586 | 31.9964 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 21.331 | 20.2644 | 66.67% | 63.33% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 6.7548 | 12.1586 | 31.9964 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 20.2644 | 19.1979 | 63.33% | 60% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 6.7548 | 12.1586 | 31.9964 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 19.1979 | 18.1313 | 60% | 56.67% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 6.7548 | 12.1586 | 31.9964 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 18.1313 | 17.0648 | 56.67% | 53.33% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 6.7548 | 12.1586 | 31.9964 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 17.0648 | 15.9982 | 53.33% | 50% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 6.7548 | 12.1586 | 31.9964 | 2024-01-01 01:00 | 2023-12-31 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 15.9982 | 14.9317 | 50% | 46.67% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 6.7548 | 12.1586 | 31.9964 | 2024-01-01 01:05 | 2023-12-31 20:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 14.9317 | 13.8651 | 46.67% | 43.33% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 6.7548 | 12.1586 | 31.9964 | 2024-01-01 01:10 | 2023-12-31 20:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 13.8651 | 12.7986 | 43.33% | 40% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 6.7548 | 12.1586 | 31.9964 | 2024-01-01 01:15 | 2023-12-31 20:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 12.7986 | 11.732 | 40% | 36.67% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 6.7548 | 12.1586 | 31.9964 | 2024-01-01 01:20 | 2023-12-31 20:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 11.732 | 10.6655 | 36.67% | 33.33% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 6.7548 | 12.1586 | 31.9964 | 2024-01-01 01:25 | 2023-12-31 20:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 10.6655 | 9.5989 | 33.33% | 30% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 6.7548 | 12.1586 | 31.9964 | 2024-01-01 01:30 | 2023-12-31 20:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 9.5989 | 8.5324 | 30% | 26.67% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 6.7548 | 12.1586 | 31.9964 | 2024-01-01 01:35 | 2023-12-31 20:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 8.5324 | 7.4658 | 26.67% | 23.33% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 6.7548 | 12.1586 | 31.9964 | 2024-01-01 01:40 | 2023-12-31 20:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 7.4658 | 6.3993 | 23.33% | 20% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 6.7548 | 12.1586 | 31.9964 | 2024-01-01 01:45 | 2023-12-31 20:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 6.3993 | 5.3327 | 20% | 16.67% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 6.7548 | 12.1586 | 31.9964 | 2024-01-01 01:50 | 2023-12-31 20:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 5.3327 | 4.2662 | 16.67% | 13.33% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 6.7548 | 12.1586 | 31.9964 | 2024-01-01 01:55 | 2023-12-31 20:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 4.2662 | 3.1996 | 13.33% | 10% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 10.1322 | 12.1586 | 31.9964 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 28.7968 | 27.7302 | 90% | 86.67% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 10.1322 | 12.1586 | 31.9964 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 27.7302 | 26.6637 | 86.67% | 83.33% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 10.1322 | 12.1586 | 31.9964 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 26.6637 | 25.5972 | 83.33% | 80% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 10.1322 | 12.1586 | 31.9964 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 25.5972 | 24.5306 | 80% | 76.67% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 10.1322 | 12.1586 | 31.9964 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 24.5306 | 23.4641 | 76.67% | 73.33% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 10.1322 | 12.1586 | 31.9964 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 23.4641 | 22.3975 | 73.33% | 70% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 10.1322 | 12.1586 | 31.9964 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 22.3975 | 21.331 | 70% | 66.67% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 10.1322 | 12.1586 | 31.9964 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 21.331 | 20.2644 | 66.67% | 63.33% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 10.1322 | 12.1586 | 31.9964 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 20.2644 | 19.1979 | 63.33% | 60% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 10.1322 | 12.1586 | 31.9964 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 19.1979 | 18.1313 | 60% | 56.67% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 10.1322 | 12.1586 | 31.9964 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 18.1313 | 17.0648 | 56.67% | 53.33% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 10.1322 | 12.1586 | 31.9964 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 17.0648 | 15.9982 | 53.33% | 50% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 10.1322 | 12.1586 | 31.9964 | 2024-01-01 01:00 | 2023-12-31 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 15.9982 | 14.9317 | 50% | 46.67% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 10.1322 | 12.1586 | 31.9964 | 2024-01-01 01:05 | 2023-12-31 20:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 14.9317 | 13.8651 | 46.67% | 43.33% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 10.1322 | 12.1586 | 31.9964 | 2024-01-01 01:10 | 2023-12-31 20:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 13.8651 | 12.7986 | 43.33% | 40% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 10.1322 | 12.1586 | 31.9964 | 2024-01-01 01:15 | 2023-12-31 20:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 12.7986 | 11.732 | 40% | 36.67% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 10.1322 | 12.1586 | 31.9964 | 2024-01-01 01:20 | 2023-12-31 20:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 11.732 | 10.6655 | 36.67% | 33.33% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 10.1322 | 12.1586 | 31.9964 | 2024-01-01 01:25 | 2023-12-31 20:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 10.6655 | 9.5989 | 33.33% | 30% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 10.1322 | 12.1586 | 31.9964 | 2024-01-01 01:30 | 2023-12-31 20:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 9.5989 | 8.5324 | 30% | 26.67% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 10.1322 | 12.1586 | 31.9964 | 2024-01-01 01:35 | 2023-12-31 20:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 8.5324 | 7.4658 | 26.67% | 23.33% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 10.1322 | 12.1586 | 31.9964 | 2024-01-01 01:40 | 2023-12-31 20:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 7.4658 | 6.3993 | 23.33% | 20% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 10.1322 | 12.1586 | 31.9964 | 2024-01-01 01:45 | 2023-12-31 20:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 6.3993 | 5.3327 | 20% | 16.67% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 10.1322 | 12.1586 | 31.9964 | 2024-01-01 01:50 | 2023-12-31 20:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 5.3327 | 4.2662 | 16.67% | 13.33% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 10.1322 | 12.1586 | 31.9964 | 2024-01-01 01:55 | 2023-12-31 20:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 4.2662 | 3.1996 | 13.33% | 10% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 13.5096 | 12.1586 | 31.9964 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 28.7968 | 27.7302 | 90% | 86.67% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 13.5096 | 12.1586 | 31.9964 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 27.7302 | 26.6637 | 86.67% | 83.33% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 13.5096 | 12.1586 | 31.9964 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 26.6637 | 25.5972 | 83.33% | 80% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 13.5096 | 12.1586 | 31.9964 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 25.5972 | 24.5306 | 80% | 76.67% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 13.5096 | 12.1586 | 31.9964 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 24.5306 | 23.4641 | 76.67% | 73.33% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 13.5096 | 12.1586 | 31.9964 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 23.4641 | 22.3975 | 73.33% | 70% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 13.5096 | 12.1586 | 31.9964 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 22.3975 | 21.331 | 70% | 66.67% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 13.5096 | 12.1586 | 31.9964 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 21.331 | 20.2644 | 66.67% | 63.33% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 13.5096 | 12.1586 | 31.9964 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 20.2644 | 19.1979 | 63.33% | 60% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 13.5096 | 12.1586 | 31.9964 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 19.1979 | 18.1313 | 60% | 56.67% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 13.5096 | 12.1586 | 31.9964 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 18.1313 | 17.0648 | 56.67% | 53.33% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 13.5096 | 12.1586 | 31.9964 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 17.0648 | 15.9982 | 53.33% | 50% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 13.5096 | 12.1586 | 31.9964 | 2024-01-01 01:00 | 2023-12-31 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 15.9982 | 14.9317 | 50% | 46.67% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 13.5096 | 12.1586 | 31.9964 | 2024-01-01 01:05 | 2023-12-31 20:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 14.9317 | 13.8651 | 46.67% | 43.33% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 13.5096 | 12.1586 | 31.9964 | 2024-01-01 01:10 | 2023-12-31 20:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 13.8651 | 12.7986 | 43.33% | 40% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 13.5096 | 12.1586 | 31.9964 | 2024-01-01 01:15 | 2023-12-31 20:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 12.7986 | 11.732 | 40% | 36.67% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 13.5096 | 12.1586 | 31.9964 | 2024-01-01 01:20 | 2023-12-31 20:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 11.732 | 10.6655 | 36.67% | 33.33% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 13.5096 | 12.1586 | 31.9964 | 2024-01-01 01:25 | 2023-12-31 20:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 10.6655 | 9.5989 | 33.33% | 30% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 13.5096 | 12.1586 | 31.9964 | 2024-01-01 01:30 | 2023-12-31 20:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 9.5989 | 8.5324 | 30% | 26.67% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 13.5096 | 12.1586 | 31.9964 | 2024-01-01 01:35 | 2023-12-31 20:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 8.5324 | 7.4658 | 26.67% | 23.33% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 13.5096 | 12.1586 | 31.9964 | 2024-01-01 01:40 | 2023-12-31 20:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 7.4658 | 6.3993 | 23.33% | 20% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 13.5096 | 12.1586 | 31.9964 | 2024-01-01 01:45 | 2023-12-31 20:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 6.3993 | 5.3327 | 20% | 16.67% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 13.5096 | 12.1586 | 31.9964 | 2024-01-01 01:50 | 2023-12-31 20:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 5.3327 | 4.2662 | 16.67% | 13.33% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 2 | 13.5096 | 12.1586 | 31.9964 | 2024-01-01 01:55 | 2023-12-31 20:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 4.2662 | 3.1996 | 13.33% | 10% | 3.1996 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 0 | 12.1586 | 63.9929 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 57.5936 | 56.527 | 90% | 88.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 0 | 12.1586 | 63.9929 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 56.527 | 55.4605 | 88.33% | 86.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 0 | 12.1586 | 63.9929 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 55.4605 | 54.3939 | 86.67% | 85% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 0 | 12.1586 | 63.9929 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 54.3939 | 53.3274 | 85% | 83.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 0 | 12.1586 | 63.9929 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 53.3274 | 52.2609 | 83.33% | 81.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 0 | 12.1586 | 63.9929 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 52.2609 | 51.1943 | 81.67% | 80% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 0 | 12.1586 | 63.9929 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 51.1943 | 50.1278 | 80% | 78.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 0 | 12.1586 | 63.9929 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 50.1278 | 49.0612 | 78.33% | 76.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 0 | 12.1586 | 63.9929 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 49.0612 | 47.9947 | 76.67% | 75% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 0 | 12.1586 | 63.9929 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 47.9947 | 46.9281 | 75% | 73.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 0 | 12.1586 | 63.9929 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 46.9281 | 45.8616 | 73.33% | 71.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 0 | 12.1586 | 63.9929 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 45.8616 | 44.795 | 71.67% | 70% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 0 | 12.1586 | 63.9929 | 2024-01-01 01:00 | 2023-12-31 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 44.795 | 43.7285 | 70% | 68.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 0 | 12.1586 | 63.9929 | 2024-01-01 01:05 | 2023-12-31 20:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 43.7285 | 42.6619 | 68.33% | 66.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 0 | 12.1586 | 63.9929 | 2024-01-01 01:10 | 2023-12-31 20:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 42.6619 | 41.5954 | 66.67% | 65% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 0 | 12.1586 | 63.9929 | 2024-01-01 01:15 | 2023-12-31 20:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 41.5954 | 40.5288 | 65% | 63.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 0 | 12.1586 | 63.9929 | 2024-01-01 01:20 | 2023-12-31 20:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 40.5288 | 39.4623 | 63.33% | 61.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 0 | 12.1586 | 63.9929 | 2024-01-01 01:25 | 2023-12-31 20:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 39.4623 | 38.3957 | 61.67% | 60% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 0 | 12.1586 | 63.9929 | 2024-01-01 01:30 | 2023-12-31 20:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 38.3957 | 37.3292 | 60% | 58.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 0 | 12.1586 | 63.9929 | 2024-01-01 01:35 | 2023-12-31 20:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 37.3292 | 36.2626 | 58.33% | 56.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 0 | 12.1586 | 63.9929 | 2024-01-01 01:40 | 2023-12-31 20:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 36.2626 | 35.1961 | 56.67% | 55% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 0 | 12.1586 | 63.9929 | 2024-01-01 01:45 | 2023-12-31 20:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 35.1961 | 34.1295 | 55% | 53.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 0 | 12.1586 | 63.9929 | 2024-01-01 01:50 | 2023-12-31 20:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 34.1295 | 33.063 | 53.33% | 51.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 0 | 12.1586 | 63.9929 | 2024-01-01 01:55 | 2023-12-31 20:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 33.063 | 31.9964 | 51.67% | 50% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 0 | 12.1586 | 63.9929 | 2024-01-01 02:00 | 2023-12-31 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 31.9964 | 30.9299 | 50% | 48.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 0 | 12.1586 | 63.9929 | 2024-01-01 02:05 | 2023-12-31 21:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 30.9299 | 29.8633 | 48.33% | 46.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 0 | 12.1586 | 63.9929 | 2024-01-01 02:10 | 2023-12-31 21:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 29.8633 | 28.7968 | 46.67% | 45% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 0 | 12.1586 | 63.9929 | 2024-01-01 02:15 | 2023-12-31 21:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 28.7968 | 27.7302 | 45% | 43.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 0 | 12.1586 | 63.9929 | 2024-01-01 02:20 | 2023-12-31 21:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 27.7302 | 26.6637 | 43.33% | 41.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 0 | 12.1586 | 63.9929 | 2024-01-01 02:25 | 2023-12-31 21:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 26.6637 | 25.5972 | 41.67% | 40% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 0 | 12.1586 | 63.9929 | 2024-01-01 02:30 | 2023-12-31 21:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 25.5972 | 24.5306 | 40% | 38.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 0 | 12.1586 | 63.9929 | 2024-01-01 02:35 | 2023-12-31 21:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 24.5306 | 23.4641 | 38.33% | 36.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 0 | 12.1586 | 63.9929 | 2024-01-01 02:40 | 2023-12-31 21:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 23.4641 | 22.3975 | 36.67% | 35% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 0 | 12.1586 | 63.9929 | 2024-01-01 02:45 | 2023-12-31 21:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 22.3975 | 21.331 | 35% | 33.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 0 | 12.1586 | 63.9929 | 2024-01-01 02:50 | 2023-12-31 21:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 21.331 | 20.2644 | 33.33% | 31.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 0 | 12.1586 | 63.9929 | 2024-01-01 02:55 | 2023-12-31 21:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 20.2644 | 19.1979 | 31.67% | 30% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 0 | 12.1586 | 63.9929 | 2024-01-01 03:00 | 2023-12-31 22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 19.1979 | 18.1313 | 30% | 28.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 0 | 12.1586 | 63.9929 | 2024-01-01 03:05 | 2023-12-31 22:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 18.1313 | 17.0648 | 28.33% | 26.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 0 | 12.1586 | 63.9929 | 2024-01-01 03:10 | 2023-12-31 22:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 17.0648 | 15.9982 | 26.67% | 25% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 0 | 12.1586 | 63.9929 | 2024-01-01 03:15 | 2023-12-31 22:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 15.9982 | 14.9317 | 25% | 23.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 0 | 12.1586 | 63.9929 | 2024-01-01 03:20 | 2023-12-31 22:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 14.9317 | 13.8651 | 23.33% | 21.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 0 | 12.1586 | 63.9929 | 2024-01-01 03:25 | 2023-12-31 22:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 13.8651 | 12.7986 | 21.67% | 20% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 0 | 12.1586 | 63.9929 | 2024-01-01 03:30 | 2023-12-31 22:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 12.7986 | 11.732 | 20% | 18.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 0 | 12.1586 | 63.9929 | 2024-01-01 03:35 | 2023-12-31 22:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 11.732 | 10.6655 | 18.33% | 16.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 0 | 12.1586 | 63.9929 | 2024-01-01 03:40 | 2023-12-31 22:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 10.6655 | 9.5989 | 16.67% | 15% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 0 | 12.1586 | 63.9929 | 2024-01-01 03:45 | 2023-12-31 22:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 9.5989 | 8.5324 | 15% | 13.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 0 | 12.1586 | 63.9929 | 2024-01-01 03:50 | 2023-12-31 22:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 8.5324 | 7.4658 | 13.33% | 11.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 0 | 12.1586 | 63.9929 | 2024-01-01 03:55 | 2023-12-31 22:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 7.4658 | 6.3993 | 11.67% | 10% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 3.3774 | 12.1586 | 63.9929 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 57.5936 | 56.527 | 90% | 88.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 3.3774 | 12.1586 | 63.9929 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 56.527 | 55.4605 | 88.33% | 86.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 3.3774 | 12.1586 | 63.9929 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 55.4605 | 54.3939 | 86.67% | 85% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 3.3774 | 12.1586 | 63.9929 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 54.3939 | 53.3274 | 85% | 83.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 3.3774 | 12.1586 | 63.9929 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 53.3274 | 52.2609 | 83.33% | 81.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 3.3774 | 12.1586 | 63.9929 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 52.2609 | 51.1943 | 81.67% | 80% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 3.3774 | 12.1586 | 63.9929 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 51.1943 | 50.1278 | 80% | 78.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 3.3774 | 12.1586 | 63.9929 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 50.1278 | 49.0612 | 78.33% | 76.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 3.3774 | 12.1586 | 63.9929 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 49.0612 | 47.9947 | 76.67% | 75% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 3.3774 | 12.1586 | 63.9929 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 47.9947 | 46.9281 | 75% | 73.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 3.3774 | 12.1586 | 63.9929 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 46.9281 | 45.8616 | 73.33% | 71.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 3.3774 | 12.1586 | 63.9929 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 45.8616 | 44.795 | 71.67% | 70% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 3.3774 | 12.1586 | 63.9929 | 2024-01-01 01:00 | 2023-12-31 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 44.795 | 43.7285 | 70% | 68.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 3.3774 | 12.1586 | 63.9929 | 2024-01-01 01:05 | 2023-12-31 20:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 43.7285 | 42.6619 | 68.33% | 66.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 3.3774 | 12.1586 | 63.9929 | 2024-01-01 01:10 | 2023-12-31 20:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 42.6619 | 41.5954 | 66.67% | 65% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 3.3774 | 12.1586 | 63.9929 | 2024-01-01 01:15 | 2023-12-31 20:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 41.5954 | 40.5288 | 65% | 63.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 3.3774 | 12.1586 | 63.9929 | 2024-01-01 01:20 | 2023-12-31 20:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 40.5288 | 39.4623 | 63.33% | 61.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 3.3774 | 12.1586 | 63.9929 | 2024-01-01 01:25 | 2023-12-31 20:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 39.4623 | 38.3957 | 61.67% | 60% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 3.3774 | 12.1586 | 63.9929 | 2024-01-01 01:30 | 2023-12-31 20:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 38.3957 | 37.3292 | 60% | 58.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 3.3774 | 12.1586 | 63.9929 | 2024-01-01 01:35 | 2023-12-31 20:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 37.3292 | 36.2626 | 58.33% | 56.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 3.3774 | 12.1586 | 63.9929 | 2024-01-01 01:40 | 2023-12-31 20:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 36.2626 | 35.1961 | 56.67% | 55% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 3.3774 | 12.1586 | 63.9929 | 2024-01-01 01:45 | 2023-12-31 20:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 35.1961 | 34.1295 | 55% | 53.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 3.3774 | 12.1586 | 63.9929 | 2024-01-01 01:50 | 2023-12-31 20:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 34.1295 | 33.063 | 53.33% | 51.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 3.3774 | 12.1586 | 63.9929 | 2024-01-01 01:55 | 2023-12-31 20:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 33.063 | 31.9964 | 51.67% | 50% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 3.3774 | 12.1586 | 63.9929 | 2024-01-01 02:00 | 2023-12-31 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 31.9964 | 30.9299 | 50% | 48.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 3.3774 | 12.1586 | 63.9929 | 2024-01-01 02:05 | 2023-12-31 21:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 30.9299 | 29.8633 | 48.33% | 46.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 3.3774 | 12.1586 | 63.9929 | 2024-01-01 02:10 | 2023-12-31 21:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 29.8633 | 28.7968 | 46.67% | 45% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 3.3774 | 12.1586 | 63.9929 | 2024-01-01 02:15 | 2023-12-31 21:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 28.7968 | 27.7302 | 45% | 43.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 3.3774 | 12.1586 | 63.9929 | 2024-01-01 02:20 | 2023-12-31 21:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 27.7302 | 26.6637 | 43.33% | 41.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 3.3774 | 12.1586 | 63.9929 | 2024-01-01 02:25 | 2023-12-31 21:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 26.6637 | 25.5972 | 41.67% | 40% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 3.3774 | 12.1586 | 63.9929 | 2024-01-01 02:30 | 2023-12-31 21:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 25.5972 | 24.5306 | 40% | 38.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 3.3774 | 12.1586 | 63.9929 | 2024-01-01 02:35 | 2023-12-31 21:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 24.5306 | 23.4641 | 38.33% | 36.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 3.3774 | 12.1586 | 63.9929 | 2024-01-01 02:40 | 2023-12-31 21:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 23.4641 | 22.3975 | 36.67% | 35% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 3.3774 | 12.1586 | 63.9929 | 2024-01-01 02:45 | 2023-12-31 21:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 22.3975 | 21.331 | 35% | 33.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 3.3774 | 12.1586 | 63.9929 | 2024-01-01 02:50 | 2023-12-31 21:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 21.331 | 20.2644 | 33.33% | 31.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 3.3774 | 12.1586 | 63.9929 | 2024-01-01 02:55 | 2023-12-31 21:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 20.2644 | 19.1979 | 31.67% | 30% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 3.3774 | 12.1586 | 63.9929 | 2024-01-01 03:00 | 2023-12-31 22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 19.1979 | 18.1313 | 30% | 28.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 3.3774 | 12.1586 | 63.9929 | 2024-01-01 03:05 | 2023-12-31 22:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 18.1313 | 17.0648 | 28.33% | 26.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 3.3774 | 12.1586 | 63.9929 | 2024-01-01 03:10 | 2023-12-31 22:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 17.0648 | 15.9982 | 26.67% | 25% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 3.3774 | 12.1586 | 63.9929 | 2024-01-01 03:15 | 2023-12-31 22:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 15.9982 | 14.9317 | 25% | 23.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 3.3774 | 12.1586 | 63.9929 | 2024-01-01 03:20 | 2023-12-31 22:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 14.9317 | 13.8651 | 23.33% | 21.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 3.3774 | 12.1586 | 63.9929 | 2024-01-01 03:25 | 2023-12-31 22:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 13.8651 | 12.7986 | 21.67% | 20% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 3.3774 | 12.1586 | 63.9929 | 2024-01-01 03:30 | 2023-12-31 22:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 12.7986 | 11.732 | 20% | 18.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 3.3774 | 12.1586 | 63.9929 | 2024-01-01 03:35 | 2023-12-31 22:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 11.732 | 10.6655 | 18.33% | 16.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 3.3774 | 12.1586 | 63.9929 | 2024-01-01 03:40 | 2023-12-31 22:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 10.6655 | 9.5989 | 16.67% | 15% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 3.3774 | 12.1586 | 63.9929 | 2024-01-01 03:45 | 2023-12-31 22:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 9.5989 | 8.5324 | 15% | 13.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 3.3774 | 12.1586 | 63.9929 | 2024-01-01 03:50 | 2023-12-31 22:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 8.5324 | 7.4658 | 13.33% | 11.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 3.3774 | 12.1586 | 63.9929 | 2024-01-01 03:55 | 2023-12-31 22:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 7.4658 | 6.3993 | 11.67% | 10% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 6.7548 | 12.1586 | 63.9929 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 57.5936 | 56.527 | 90% | 88.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 6.7548 | 12.1586 | 63.9929 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 56.527 | 55.4605 | 88.33% | 86.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 6.7548 | 12.1586 | 63.9929 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 55.4605 | 54.3939 | 86.67% | 85% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 6.7548 | 12.1586 | 63.9929 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 54.3939 | 53.3274 | 85% | 83.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 6.7548 | 12.1586 | 63.9929 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 53.3274 | 52.2609 | 83.33% | 81.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 6.7548 | 12.1586 | 63.9929 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 52.2609 | 51.1943 | 81.67% | 80% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 6.7548 | 12.1586 | 63.9929 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 51.1943 | 50.1278 | 80% | 78.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 6.7548 | 12.1586 | 63.9929 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 50.1278 | 49.0612 | 78.33% | 76.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 6.7548 | 12.1586 | 63.9929 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 49.0612 | 47.9947 | 76.67% | 75% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 6.7548 | 12.1586 | 63.9929 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 47.9947 | 46.9281 | 75% | 73.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 6.7548 | 12.1586 | 63.9929 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 46.9281 | 45.8616 | 73.33% | 71.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 6.7548 | 12.1586 | 63.9929 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 45.8616 | 44.795 | 71.67% | 70% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 6.7548 | 12.1586 | 63.9929 | 2024-01-01 01:00 | 2023-12-31 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 44.795 | 43.7285 | 70% | 68.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 6.7548 | 12.1586 | 63.9929 | 2024-01-01 01:05 | 2023-12-31 20:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 43.7285 | 42.6619 | 68.33% | 66.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 6.7548 | 12.1586 | 63.9929 | 2024-01-01 01:10 | 2023-12-31 20:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 42.6619 | 41.5954 | 66.67% | 65% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 6.7548 | 12.1586 | 63.9929 | 2024-01-01 01:15 | 2023-12-31 20:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 41.5954 | 40.5288 | 65% | 63.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 6.7548 | 12.1586 | 63.9929 | 2024-01-01 01:20 | 2023-12-31 20:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 40.5288 | 39.4623 | 63.33% | 61.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 6.7548 | 12.1586 | 63.9929 | 2024-01-01 01:25 | 2023-12-31 20:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 39.4623 | 38.3957 | 61.67% | 60% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 6.7548 | 12.1586 | 63.9929 | 2024-01-01 01:30 | 2023-12-31 20:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 38.3957 | 37.3292 | 60% | 58.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 6.7548 | 12.1586 | 63.9929 | 2024-01-01 01:35 | 2023-12-31 20:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 37.3292 | 36.2626 | 58.33% | 56.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 6.7548 | 12.1586 | 63.9929 | 2024-01-01 01:40 | 2023-12-31 20:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 36.2626 | 35.1961 | 56.67% | 55% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 6.7548 | 12.1586 | 63.9929 | 2024-01-01 01:45 | 2023-12-31 20:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 35.1961 | 34.1295 | 55% | 53.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 6.7548 | 12.1586 | 63.9929 | 2024-01-01 01:50 | 2023-12-31 20:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 34.1295 | 33.063 | 53.33% | 51.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 6.7548 | 12.1586 | 63.9929 | 2024-01-01 01:55 | 2023-12-31 20:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 33.063 | 31.9964 | 51.67% | 50% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 6.7548 | 12.1586 | 63.9929 | 2024-01-01 02:00 | 2023-12-31 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 31.9964 | 30.9299 | 50% | 48.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 6.7548 | 12.1586 | 63.9929 | 2024-01-01 02:05 | 2023-12-31 21:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 30.9299 | 29.8633 | 48.33% | 46.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 6.7548 | 12.1586 | 63.9929 | 2024-01-01 02:10 | 2023-12-31 21:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 29.8633 | 28.7968 | 46.67% | 45% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 6.7548 | 12.1586 | 63.9929 | 2024-01-01 02:15 | 2023-12-31 21:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 28.7968 | 27.7302 | 45% | 43.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 6.7548 | 12.1586 | 63.9929 | 2024-01-01 02:20 | 2023-12-31 21:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 27.7302 | 26.6637 | 43.33% | 41.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 6.7548 | 12.1586 | 63.9929 | 2024-01-01 02:25 | 2023-12-31 21:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 26.6637 | 25.5972 | 41.67% | 40% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 6.7548 | 12.1586 | 63.9929 | 2024-01-01 02:30 | 2023-12-31 21:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 25.5972 | 24.5306 | 40% | 38.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 6.7548 | 12.1586 | 63.9929 | 2024-01-01 02:35 | 2023-12-31 21:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 24.5306 | 23.4641 | 38.33% | 36.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 6.7548 | 12.1586 | 63.9929 | 2024-01-01 02:40 | 2023-12-31 21:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 23.4641 | 22.3975 | 36.67% | 35% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 6.7548 | 12.1586 | 63.9929 | 2024-01-01 02:45 | 2023-12-31 21:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 22.3975 | 21.331 | 35% | 33.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 6.7548 | 12.1586 | 63.9929 | 2024-01-01 02:50 | 2023-12-31 21:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 21.331 | 20.2644 | 33.33% | 31.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 6.7548 | 12.1586 | 63.9929 | 2024-01-01 02:55 | 2023-12-31 21:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 20.2644 | 19.1979 | 31.67% | 30% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 6.7548 | 12.1586 | 63.9929 | 2024-01-01 03:00 | 2023-12-31 22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 19.1979 | 18.1313 | 30% | 28.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 6.7548 | 12.1586 | 63.9929 | 2024-01-01 03:05 | 2023-12-31 22:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 18.1313 | 17.0648 | 28.33% | 26.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 6.7548 | 12.1586 | 63.9929 | 2024-01-01 03:10 | 2023-12-31 22:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 17.0648 | 15.9982 | 26.67% | 25% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 6.7548 | 12.1586 | 63.9929 | 2024-01-01 03:15 | 2023-12-31 22:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 15.9982 | 14.9317 | 25% | 23.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 6.7548 | 12.1586 | 63.9929 | 2024-01-01 03:20 | 2023-12-31 22:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 14.9317 | 13.8651 | 23.33% | 21.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 6.7548 | 12.1586 | 63.9929 | 2024-01-01 03:25 | 2023-12-31 22:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 13.8651 | 12.7986 | 21.67% | 20% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 6.7548 | 12.1586 | 63.9929 | 2024-01-01 03:30 | 2023-12-31 22:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 12.7986 | 11.732 | 20% | 18.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 6.7548 | 12.1586 | 63.9929 | 2024-01-01 03:35 | 2023-12-31 22:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 11.732 | 10.6655 | 18.33% | 16.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 6.7548 | 12.1586 | 63.9929 | 2024-01-01 03:40 | 2023-12-31 22:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 10.6655 | 9.5989 | 16.67% | 15% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 6.7548 | 12.1586 | 63.9929 | 2024-01-01 03:45 | 2023-12-31 22:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 9.5989 | 8.5324 | 15% | 13.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 6.7548 | 12.1586 | 63.9929 | 2024-01-01 03:50 | 2023-12-31 22:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 8.5324 | 7.4658 | 13.33% | 11.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 6.7548 | 12.1586 | 63.9929 | 2024-01-01 03:55 | 2023-12-31 22:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 7.4658 | 6.3993 | 11.67% | 10% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 10.1322 | 12.1586 | 63.9929 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 57.5936 | 56.527 | 90% | 88.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 10.1322 | 12.1586 | 63.9929 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 56.527 | 55.4605 | 88.33% | 86.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 10.1322 | 12.1586 | 63.9929 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 55.4605 | 54.3939 | 86.67% | 85% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 10.1322 | 12.1586 | 63.9929 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 54.3939 | 53.3274 | 85% | 83.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 10.1322 | 12.1586 | 63.9929 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 53.3274 | 52.2609 | 83.33% | 81.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 10.1322 | 12.1586 | 63.9929 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 52.2609 | 51.1943 | 81.67% | 80% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 10.1322 | 12.1586 | 63.9929 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 51.1943 | 50.1278 | 80% | 78.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 10.1322 | 12.1586 | 63.9929 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 50.1278 | 49.0612 | 78.33% | 76.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 10.1322 | 12.1586 | 63.9929 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 49.0612 | 47.9947 | 76.67% | 75% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 10.1322 | 12.1586 | 63.9929 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 47.9947 | 46.9281 | 75% | 73.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 10.1322 | 12.1586 | 63.9929 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 46.9281 | 45.8616 | 73.33% | 71.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 10.1322 | 12.1586 | 63.9929 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 45.8616 | 44.795 | 71.67% | 70% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 10.1322 | 12.1586 | 63.9929 | 2024-01-01 01:00 | 2023-12-31 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 44.795 | 43.7285 | 70% | 68.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 10.1322 | 12.1586 | 63.9929 | 2024-01-01 01:05 | 2023-12-31 20:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 43.7285 | 42.6619 | 68.33% | 66.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 10.1322 | 12.1586 | 63.9929 | 2024-01-01 01:10 | 2023-12-31 20:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 42.6619 | 41.5954 | 66.67% | 65% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 10.1322 | 12.1586 | 63.9929 | 2024-01-01 01:15 | 2023-12-31 20:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 41.5954 | 40.5288 | 65% | 63.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 10.1322 | 12.1586 | 63.9929 | 2024-01-01 01:20 | 2023-12-31 20:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 40.5288 | 39.4623 | 63.33% | 61.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 10.1322 | 12.1586 | 63.9929 | 2024-01-01 01:25 | 2023-12-31 20:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 39.4623 | 38.3957 | 61.67% | 60% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 10.1322 | 12.1586 | 63.9929 | 2024-01-01 01:30 | 2023-12-31 20:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 38.3957 | 37.3292 | 60% | 58.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 10.1322 | 12.1586 | 63.9929 | 2024-01-01 01:35 | 2023-12-31 20:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 37.3292 | 36.2626 | 58.33% | 56.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 10.1322 | 12.1586 | 63.9929 | 2024-01-01 01:40 | 2023-12-31 20:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 36.2626 | 35.1961 | 56.67% | 55% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 10.1322 | 12.1586 | 63.9929 | 2024-01-01 01:45 | 2023-12-31 20:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 35.1961 | 34.1295 | 55% | 53.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 10.1322 | 12.1586 | 63.9929 | 2024-01-01 01:50 | 2023-12-31 20:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 34.1295 | 33.063 | 53.33% | 51.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 10.1322 | 12.1586 | 63.9929 | 2024-01-01 01:55 | 2023-12-31 20:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 33.063 | 31.9964 | 51.67% | 50% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 10.1322 | 12.1586 | 63.9929 | 2024-01-01 02:00 | 2023-12-31 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 31.9964 | 30.9299 | 50% | 48.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 10.1322 | 12.1586 | 63.9929 | 2024-01-01 02:05 | 2023-12-31 21:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 30.9299 | 29.8633 | 48.33% | 46.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 10.1322 | 12.1586 | 63.9929 | 2024-01-01 02:10 | 2023-12-31 21:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 29.8633 | 28.7968 | 46.67% | 45% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 10.1322 | 12.1586 | 63.9929 | 2024-01-01 02:15 | 2023-12-31 21:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 28.7968 | 27.7302 | 45% | 43.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 10.1322 | 12.1586 | 63.9929 | 2024-01-01 02:20 | 2023-12-31 21:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 27.7302 | 26.6637 | 43.33% | 41.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 10.1322 | 12.1586 | 63.9929 | 2024-01-01 02:25 | 2023-12-31 21:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 26.6637 | 25.5972 | 41.67% | 40% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 10.1322 | 12.1586 | 63.9929 | 2024-01-01 02:30 | 2023-12-31 21:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 25.5972 | 24.5306 | 40% | 38.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 10.1322 | 12.1586 | 63.9929 | 2024-01-01 02:35 | 2023-12-31 21:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 24.5306 | 23.4641 | 38.33% | 36.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 10.1322 | 12.1586 | 63.9929 | 2024-01-01 02:40 | 2023-12-31 21:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 23.4641 | 22.3975 | 36.67% | 35% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 10.1322 | 12.1586 | 63.9929 | 2024-01-01 02:45 | 2023-12-31 21:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 22.3975 | 21.331 | 35% | 33.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 10.1322 | 12.1586 | 63.9929 | 2024-01-01 02:50 | 2023-12-31 21:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 21.331 | 20.2644 | 33.33% | 31.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 10.1322 | 12.1586 | 63.9929 | 2024-01-01 02:55 | 2023-12-31 21:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 20.2644 | 19.1979 | 31.67% | 30% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 10.1322 | 12.1586 | 63.9929 | 2024-01-01 03:00 | 2023-12-31 22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 19.1979 | 18.1313 | 30% | 28.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 10.1322 | 12.1586 | 63.9929 | 2024-01-01 03:05 | 2023-12-31 22:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 18.1313 | 17.0648 | 28.33% | 26.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 10.1322 | 12.1586 | 63.9929 | 2024-01-01 03:10 | 2023-12-31 22:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 17.0648 | 15.9982 | 26.67% | 25% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 10.1322 | 12.1586 | 63.9929 | 2024-01-01 03:15 | 2023-12-31 22:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 15.9982 | 14.9317 | 25% | 23.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 10.1322 | 12.1586 | 63.9929 | 2024-01-01 03:20 | 2023-12-31 22:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 14.9317 | 13.8651 | 23.33% | 21.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 10.1322 | 12.1586 | 63.9929 | 2024-01-01 03:25 | 2023-12-31 22:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 13.8651 | 12.7986 | 21.67% | 20% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 10.1322 | 12.1586 | 63.9929 | 2024-01-01 03:30 | 2023-12-31 22:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 12.7986 | 11.732 | 20% | 18.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 10.1322 | 12.1586 | 63.9929 | 2024-01-01 03:35 | 2023-12-31 22:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 11.732 | 10.6655 | 18.33% | 16.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 10.1322 | 12.1586 | 63.9929 | 2024-01-01 03:40 | 2023-12-31 22:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 10.6655 | 9.5989 | 16.67% | 15% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 10.1322 | 12.1586 | 63.9929 | 2024-01-01 03:45 | 2023-12-31 22:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 9.5989 | 8.5324 | 15% | 13.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 10.1322 | 12.1586 | 63.9929 | 2024-01-01 03:50 | 2023-12-31 22:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 8.5324 | 7.4658 | 13.33% | 11.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 10.1322 | 12.1586 | 63.9929 | 2024-01-01 03:55 | 2023-12-31 22:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 7.4658 | 6.3993 | 11.67% | 10% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 13.5096 | 12.1586 | 63.9929 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 57.5936 | 56.527 | 90% | 88.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 13.5096 | 12.1586 | 63.9929 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 56.527 | 55.4605 | 88.33% | 86.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 13.5096 | 12.1586 | 63.9929 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 55.4605 | 54.3939 | 86.67% | 85% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 13.5096 | 12.1586 | 63.9929 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 54.3939 | 53.3274 | 85% | 83.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 13.5096 | 12.1586 | 63.9929 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 53.3274 | 52.2609 | 83.33% | 81.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 13.5096 | 12.1586 | 63.9929 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 52.2609 | 51.1943 | 81.67% | 80% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 13.5096 | 12.1586 | 63.9929 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 51.1943 | 50.1278 | 80% | 78.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 13.5096 | 12.1586 | 63.9929 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 50.1278 | 49.0612 | 78.33% | 76.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 13.5096 | 12.1586 | 63.9929 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 49.0612 | 47.9947 | 76.67% | 75% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 13.5096 | 12.1586 | 63.9929 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 47.9947 | 46.9281 | 75% | 73.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 13.5096 | 12.1586 | 63.9929 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 46.9281 | 45.8616 | 73.33% | 71.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 13.5096 | 12.1586 | 63.9929 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 45.8616 | 44.795 | 71.67% | 70% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 13.5096 | 12.1586 | 63.9929 | 2024-01-01 01:00 | 2023-12-31 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 44.795 | 43.7285 | 70% | 68.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 13.5096 | 12.1586 | 63.9929 | 2024-01-01 01:05 | 2023-12-31 20:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 43.7285 | 42.6619 | 68.33% | 66.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 13.5096 | 12.1586 | 63.9929 | 2024-01-01 01:10 | 2023-12-31 20:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 42.6619 | 41.5954 | 66.67% | 65% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 13.5096 | 12.1586 | 63.9929 | 2024-01-01 01:15 | 2023-12-31 20:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 41.5954 | 40.5288 | 65% | 63.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 13.5096 | 12.1586 | 63.9929 | 2024-01-01 01:20 | 2023-12-31 20:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 40.5288 | 39.4623 | 63.33% | 61.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 13.5096 | 12.1586 | 63.9929 | 2024-01-01 01:25 | 2023-12-31 20:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 39.4623 | 38.3957 | 61.67% | 60% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 13.5096 | 12.1586 | 63.9929 | 2024-01-01 01:30 | 2023-12-31 20:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 38.3957 | 37.3292 | 60% | 58.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 13.5096 | 12.1586 | 63.9929 | 2024-01-01 01:35 | 2023-12-31 20:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 37.3292 | 36.2626 | 58.33% | 56.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 13.5096 | 12.1586 | 63.9929 | 2024-01-01 01:40 | 2023-12-31 20:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 36.2626 | 35.1961 | 56.67% | 55% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 13.5096 | 12.1586 | 63.9929 | 2024-01-01 01:45 | 2023-12-31 20:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 35.1961 | 34.1295 | 55% | 53.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 13.5096 | 12.1586 | 63.9929 | 2024-01-01 01:50 | 2023-12-31 20:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 34.1295 | 33.063 | 53.33% | 51.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 13.5096 | 12.1586 | 63.9929 | 2024-01-01 01:55 | 2023-12-31 20:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 33.063 | 31.9964 | 51.67% | 50% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 13.5096 | 12.1586 | 63.9929 | 2024-01-01 02:00 | 2023-12-31 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 31.9964 | 30.9299 | 50% | 48.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 13.5096 | 12.1586 | 63.9929 | 2024-01-01 02:05 | 2023-12-31 21:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 30.9299 | 29.8633 | 48.33% | 46.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 13.5096 | 12.1586 | 63.9929 | 2024-01-01 02:10 | 2023-12-31 21:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 29.8633 | 28.7968 | 46.67% | 45% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 13.5096 | 12.1586 | 63.9929 | 2024-01-01 02:15 | 2023-12-31 21:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 28.7968 | 27.7302 | 45% | 43.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 13.5096 | 12.1586 | 63.9929 | 2024-01-01 02:20 | 2023-12-31 21:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 27.7302 | 26.6637 | 43.33% | 41.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 13.5096 | 12.1586 | 63.9929 | 2024-01-01 02:25 | 2023-12-31 21:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 26.6637 | 25.5972 | 41.67% | 40% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 13.5096 | 12.1586 | 63.9929 | 2024-01-01 02:30 | 2023-12-31 21:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 25.5972 | 24.5306 | 40% | 38.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 13.5096 | 12.1586 | 63.9929 | 2024-01-01 02:35 | 2023-12-31 21:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 24.5306 | 23.4641 | 38.33% | 36.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 13.5096 | 12.1586 | 63.9929 | 2024-01-01 02:40 | 2023-12-31 21:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 23.4641 | 22.3975 | 36.67% | 35% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 13.5096 | 12.1586 | 63.9929 | 2024-01-01 02:45 | 2023-12-31 21:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 22.3975 | 21.331 | 35% | 33.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 13.5096 | 12.1586 | 63.9929 | 2024-01-01 02:50 | 2023-12-31 21:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 21.331 | 20.2644 | 33.33% | 31.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 13.5096 | 12.1586 | 63.9929 | 2024-01-01 02:55 | 2023-12-31 21:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 20.2644 | 19.1979 | 31.67% | 30% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 13.5096 | 12.1586 | 63.9929 | 2024-01-01 03:00 | 2023-12-31 22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 19.1979 | 18.1313 | 30% | 28.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 13.5096 | 12.1586 | 63.9929 | 2024-01-01 03:05 | 2023-12-31 22:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 18.1313 | 17.0648 | 28.33% | 26.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 13.5096 | 12.1586 | 63.9929 | 2024-01-01 03:10 | 2023-12-31 22:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 17.0648 | 15.9982 | 26.67% | 25% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 13.5096 | 12.1586 | 63.9929 | 2024-01-01 03:15 | 2023-12-31 22:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 15.9982 | 14.9317 | 25% | 23.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 13.5096 | 12.1586 | 63.9929 | 2024-01-01 03:20 | 2023-12-31 22:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 14.9317 | 13.8651 | 23.33% | 21.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 13.5096 | 12.1586 | 63.9929 | 2024-01-01 03:25 | 2023-12-31 22:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 13.8651 | 12.7986 | 21.67% | 20% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 13.5096 | 12.1586 | 63.9929 | 2024-01-01 03:30 | 2023-12-31 22:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 12.7986 | 11.732 | 20% | 18.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 13.5096 | 12.1586 | 63.9929 | 2024-01-01 03:35 | 2023-12-31 22:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 11.732 | 10.6655 | 18.33% | 16.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 13.5096 | 12.1586 | 63.9929 | 2024-01-01 03:40 | 2023-12-31 22:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 10.6655 | 9.5989 | 16.67% | 15% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 13.5096 | 12.1586 | 63.9929 | 2024-01-01 03:45 | 2023-12-31 22:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 9.5989 | 8.5324 | 15% | 13.33% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 13.5096 | 12.1586 | 63.9929 | 2024-01-01 03:50 | 2023-12-31 22:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 8.5324 | 7.4658 | 13.33% | 11.67% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 4 | 13.5096 | 12.1586 | 63.9929 | 2024-01-01 03:55 | 2023-12-31 22:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 7.4658 | 6.3993 | 11.67% | 10% | 6.3993 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 115.1872 | 114.1206 | 90% | 89.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 114.1206 | 113.0541 | 89.17% | 88.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 113.0541 | 111.9875 | 88.33% | 87.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 111.9875 | 110.921 | 87.5% | 86.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 110.921 | 109.8544 | 86.67% | 85.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 109.8544 | 108.7879 | 85.83% | 85% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 108.7879 | 107.7214 | 85% | 84.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 107.7214 | 106.6548 | 84.17% | 83.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 106.6548 | 105.5883 | 83.33% | 82.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 105.5883 | 104.5217 | 82.5% | 81.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 104.5217 | 103.4552 | 81.67% | 80.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 103.4552 | 102.3886 | 80.83% | 80% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 01:00 | 2023-12-31 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 102.3886 | 101.3221 | 80% | 79.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 01:05 | 2023-12-31 20:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 101.3221 | 100.2555 | 79.17% | 78.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 01:10 | 2023-12-31 20:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 100.2555 | 99.189 | 78.33% | 77.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 01:15 | 2023-12-31 20:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 99.189 | 98.1224 | 77.5% | 76.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 01:20 | 2023-12-31 20:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 98.1224 | 97.0559 | 76.67% | 75.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 01:25 | 2023-12-31 20:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 97.0559 | 95.9893 | 75.83% | 75% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 01:30 | 2023-12-31 20:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 95.9893 | 94.9228 | 75% | 74.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 01:35 | 2023-12-31 20:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 94.9228 | 93.8562 | 74.17% | 73.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 01:40 | 2023-12-31 20:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 93.8562 | 92.7897 | 73.33% | 72.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 01:45 | 2023-12-31 20:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 92.7897 | 91.7231 | 72.5% | 71.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 01:50 | 2023-12-31 20:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 91.7231 | 90.6566 | 71.67% | 70.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 01:55 | 2023-12-31 20:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 90.6566 | 89.59 | 70.83% | 70% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 02:00 | 2023-12-31 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 89.59 | 88.5235 | 70% | 69.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 02:05 | 2023-12-31 21:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 88.5235 | 87.4569 | 69.17% | 68.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 02:10 | 2023-12-31 21:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 87.4569 | 86.3904 | 68.33% | 67.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 02:15 | 2023-12-31 21:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 86.3904 | 85.3238 | 67.5% | 66.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 02:20 | 2023-12-31 21:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 85.3238 | 84.2573 | 66.67% | 65.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 02:25 | 2023-12-31 21:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 84.2573 | 83.1907 | 65.83% | 65% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 02:30 | 2023-12-31 21:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 83.1907 | 82.1242 | 65% | 64.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 02:35 | 2023-12-31 21:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 82.1242 | 81.0576 | 64.17% | 63.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 02:40 | 2023-12-31 21:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 81.0576 | 79.9911 | 63.33% | 62.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 02:45 | 2023-12-31 21:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 79.9911 | 78.9246 | 62.5% | 61.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 02:50 | 2023-12-31 21:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 78.9246 | 77.858 | 61.67% | 60.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 02:55 | 2023-12-31 21:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 77.858 | 76.7915 | 60.83% | 60% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 03:00 | 2023-12-31 22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 76.7915 | 75.7249 | 60% | 59.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 03:05 | 2023-12-31 22:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 75.7249 | 74.6584 | 59.17% | 58.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 03:10 | 2023-12-31 22:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 74.6584 | 73.5918 | 58.33% | 57.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 03:15 | 2023-12-31 22:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 73.5918 | 72.5253 | 57.5% | 56.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 03:20 | 2023-12-31 22:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 72.5253 | 71.4587 | 56.67% | 55.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 03:25 | 2023-12-31 22:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 71.4587 | 70.3922 | 55.83% | 55% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 03:30 | 2023-12-31 22:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 70.3922 | 69.3256 | 55% | 54.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 03:35 | 2023-12-31 22:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 69.3256 | 68.2591 | 54.17% | 53.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 03:40 | 2023-12-31 22:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 68.2591 | 67.1925 | 53.33% | 52.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 03:45 | 2023-12-31 22:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 67.1925 | 66.126 | 52.5% | 51.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 03:50 | 2023-12-31 22:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 66.126 | 65.0594 | 51.67% | 50.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 03:55 | 2023-12-31 22:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 65.0594 | 63.9929 | 50.83% | 50% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 04:00 | 2023-12-31 23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 63.9929 | 62.9263 | 50% | 49.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 04:05 | 2023-12-31 23:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 62.9263 | 61.8598 | 49.17% | 48.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 04:10 | 2023-12-31 23:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 61.8598 | 60.7932 | 48.33% | 47.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 04:15 | 2023-12-31 23:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 60.7932 | 59.7267 | 47.5% | 46.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 04:20 | 2023-12-31 23:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 59.7267 | 58.6601 | 46.67% | 45.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 04:25 | 2023-12-31 23:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 58.6601 | 57.5936 | 45.83% | 45% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 04:30 | 2023-12-31 23:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 57.5936 | 56.527 | 45% | 44.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 04:35 | 2023-12-31 23:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 56.527 | 55.4605 | 44.17% | 43.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 04:40 | 2023-12-31 23:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 55.4605 | 54.3939 | 43.33% | 42.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 04:45 | 2023-12-31 23:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 54.3939 | 53.3274 | 42.5% | 41.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 04:50 | 2023-12-31 23:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 53.3274 | 52.2609 | 41.67% | 40.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 04:55 | 2023-12-31 23:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 52.2609 | 51.1943 | 40.83% | 40% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 05:00 | 2024-01-01 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 51.1943 | 50.1278 | 40% | 39.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 05:05 | 2024-01-01 00:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 50.1278 | 49.0612 | 39.17% | 38.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 05:10 | 2024-01-01 00:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 49.0612 | 47.9947 | 38.33% | 37.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 05:15 | 2024-01-01 00:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 47.9947 | 46.9281 | 37.5% | 36.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 05:20 | 2024-01-01 00:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 46.9281 | 45.8616 | 36.67% | 35.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 05:25 | 2024-01-01 00:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 45.8616 | 44.795 | 35.83% | 35% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 05:30 | 2024-01-01 00:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 44.795 | 43.7285 | 35% | 34.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 05:35 | 2024-01-01 00:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 43.7285 | 42.6619 | 34.17% | 33.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 05:40 | 2024-01-01 00:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 42.6619 | 41.5954 | 33.33% | 32.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 05:45 | 2024-01-01 00:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 41.5954 | 40.5288 | 32.5% | 31.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 05:50 | 2024-01-01 00:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 40.5288 | 39.4623 | 31.67% | 30.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 05:55 | 2024-01-01 00:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 39.4623 | 38.3957 | 30.83% | 30% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 06:00 | 2024-01-01 01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 38.3957 | 37.3292 | 30% | 29.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 06:05 | 2024-01-01 01:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 37.3292 | 36.2626 | 29.17% | 28.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 06:10 | 2024-01-01 01:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 36.2626 | 35.1961 | 28.33% | 27.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 06:15 | 2024-01-01 01:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 35.1961 | 34.1295 | 27.5% | 26.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 06:20 | 2024-01-01 01:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 34.1295 | 33.063 | 26.67% | 25.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 06:25 | 2024-01-01 01:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 33.063 | 31.9964 | 25.83% | 25% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 06:30 | 2024-01-01 01:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 31.9964 | 30.9299 | 25% | 24.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 06:35 | 2024-01-01 01:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 30.9299 | 29.8633 | 24.17% | 23.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 06:40 | 2024-01-01 01:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 29.8633 | 28.7968 | 23.33% | 22.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 06:45 | 2024-01-01 01:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 28.7968 | 27.7302 | 22.5% | 21.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 06:50 | 2024-01-01 01:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 27.7302 | 26.6637 | 21.67% | 20.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 06:55 | 2024-01-01 01:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 26.6637 | 25.5972 | 20.83% | 20% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 07:00 | 2024-01-01 02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 25.5972 | 24.5306 | 20% | 19.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 07:05 | 2024-01-01 02:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 24.5306 | 23.4641 | 19.17% | 18.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 07:10 | 2024-01-01 02:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 23.4641 | 22.3975 | 18.33% | 17.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 07:15 | 2024-01-01 02:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 22.3975 | 21.331 | 17.5% | 16.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 07:20 | 2024-01-01 02:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 21.331 | 20.2644 | 16.67% | 15.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 07:25 | 2024-01-01 02:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 20.2644 | 19.1979 | 15.83% | 15% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 07:30 | 2024-01-01 02:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 19.1979 | 18.1313 | 15% | 14.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 07:35 | 2024-01-01 02:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 18.1313 | 17.0648 | 14.17% | 13.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 07:40 | 2024-01-01 02:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 17.0648 | 15.9982 | 13.33% | 12.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 07:45 | 2024-01-01 02:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 15.9982 | 14.9317 | 12.5% | 11.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 07:50 | 2024-01-01 02:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 14.9317 | 13.8651 | 11.67% | 10.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 0 | 12.1586 | 127.9858 | 2024-01-01 07:55 | 2024-01-01 02:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 13.8651 | 12.7986 | 10.83% | 10% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 115.1872 | 114.1206 | 90% | 89.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 114.1206 | 113.0541 | 89.17% | 88.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 113.0541 | 111.9875 | 88.33% | 87.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 111.9875 | 110.921 | 87.5% | 86.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 110.921 | 109.8544 | 86.67% | 85.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 109.8544 | 108.7879 | 85.83% | 85% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 108.7879 | 107.7214 | 85% | 84.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 107.7214 | 106.6548 | 84.17% | 83.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 106.6548 | 105.5883 | 83.33% | 82.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 105.5883 | 104.5217 | 82.5% | 81.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 104.5217 | 103.4552 | 81.67% | 80.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 103.4552 | 102.3886 | 80.83% | 80% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 01:00 | 2023-12-31 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 102.3886 | 101.3221 | 80% | 79.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 01:05 | 2023-12-31 20:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 101.3221 | 100.2555 | 79.17% | 78.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 01:10 | 2023-12-31 20:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 100.2555 | 99.189 | 78.33% | 77.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 01:15 | 2023-12-31 20:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 99.189 | 98.1224 | 77.5% | 76.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 01:20 | 2023-12-31 20:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 98.1224 | 97.0559 | 76.67% | 75.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 01:25 | 2023-12-31 20:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 97.0559 | 95.9893 | 75.83% | 75% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 01:30 | 2023-12-31 20:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 95.9893 | 94.9228 | 75% | 74.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 01:35 | 2023-12-31 20:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 94.9228 | 93.8562 | 74.17% | 73.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 01:40 | 2023-12-31 20:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 93.8562 | 92.7897 | 73.33% | 72.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 01:45 | 2023-12-31 20:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 92.7897 | 91.7231 | 72.5% | 71.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 01:50 | 2023-12-31 20:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 91.7231 | 90.6566 | 71.67% | 70.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 01:55 | 2023-12-31 20:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 90.6566 | 89.59 | 70.83% | 70% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 02:00 | 2023-12-31 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 89.59 | 88.5235 | 70% | 69.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 02:05 | 2023-12-31 21:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 88.5235 | 87.4569 | 69.17% | 68.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 02:10 | 2023-12-31 21:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 87.4569 | 86.3904 | 68.33% | 67.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 02:15 | 2023-12-31 21:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 86.3904 | 85.3238 | 67.5% | 66.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 02:20 | 2023-12-31 21:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 85.3238 | 84.2573 | 66.67% | 65.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 02:25 | 2023-12-31 21:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 84.2573 | 83.1907 | 65.83% | 65% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 02:30 | 2023-12-31 21:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 83.1907 | 82.1242 | 65% | 64.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 02:35 | 2023-12-31 21:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 82.1242 | 81.0576 | 64.17% | 63.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 02:40 | 2023-12-31 21:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 81.0576 | 79.9911 | 63.33% | 62.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 02:45 | 2023-12-31 21:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 79.9911 | 78.9246 | 62.5% | 61.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 02:50 | 2023-12-31 21:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 78.9246 | 77.858 | 61.67% | 60.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 02:55 | 2023-12-31 21:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 77.858 | 76.7915 | 60.83% | 60% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 03:00 | 2023-12-31 22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 76.7915 | 75.7249 | 60% | 59.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 03:05 | 2023-12-31 22:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 75.7249 | 74.6584 | 59.17% | 58.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 03:10 | 2023-12-31 22:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 74.6584 | 73.5918 | 58.33% | 57.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 03:15 | 2023-12-31 22:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 73.5918 | 72.5253 | 57.5% | 56.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 03:20 | 2023-12-31 22:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 72.5253 | 71.4587 | 56.67% | 55.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 03:25 | 2023-12-31 22:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 71.4587 | 70.3922 | 55.83% | 55% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 03:30 | 2023-12-31 22:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 70.3922 | 69.3256 | 55% | 54.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 03:35 | 2023-12-31 22:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 69.3256 | 68.2591 | 54.17% | 53.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 03:40 | 2023-12-31 22:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 68.2591 | 67.1925 | 53.33% | 52.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 03:45 | 2023-12-31 22:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 67.1925 | 66.126 | 52.5% | 51.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 03:50 | 2023-12-31 22:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 66.126 | 65.0594 | 51.67% | 50.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 03:55 | 2023-12-31 22:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 65.0594 | 63.9929 | 50.83% | 50% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 04:00 | 2023-12-31 23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 63.9929 | 62.9263 | 50% | 49.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 04:05 | 2023-12-31 23:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 62.9263 | 61.8598 | 49.17% | 48.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 04:10 | 2023-12-31 23:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 61.8598 | 60.7932 | 48.33% | 47.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 04:15 | 2023-12-31 23:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 60.7932 | 59.7267 | 47.5% | 46.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 04:20 | 2023-12-31 23:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 59.7267 | 58.6601 | 46.67% | 45.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 04:25 | 2023-12-31 23:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 58.6601 | 57.5936 | 45.83% | 45% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 04:30 | 2023-12-31 23:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 57.5936 | 56.527 | 45% | 44.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 04:35 | 2023-12-31 23:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 56.527 | 55.4605 | 44.17% | 43.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 04:40 | 2023-12-31 23:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 55.4605 | 54.3939 | 43.33% | 42.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 04:45 | 2023-12-31 23:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 54.3939 | 53.3274 | 42.5% | 41.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 04:50 | 2023-12-31 23:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 53.3274 | 52.2609 | 41.67% | 40.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 04:55 | 2023-12-31 23:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 52.2609 | 51.1943 | 40.83% | 40% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 05:00 | 2024-01-01 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 51.1943 | 50.1278 | 40% | 39.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 05:05 | 2024-01-01 00:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 50.1278 | 49.0612 | 39.17% | 38.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 05:10 | 2024-01-01 00:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 49.0612 | 47.9947 | 38.33% | 37.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 05:15 | 2024-01-01 00:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 47.9947 | 46.9281 | 37.5% | 36.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 05:20 | 2024-01-01 00:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 46.9281 | 45.8616 | 36.67% | 35.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 05:25 | 2024-01-01 00:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 45.8616 | 44.795 | 35.83% | 35% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 05:30 | 2024-01-01 00:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 44.795 | 43.7285 | 35% | 34.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 05:35 | 2024-01-01 00:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 43.7285 | 42.6619 | 34.17% | 33.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 05:40 | 2024-01-01 00:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 42.6619 | 41.5954 | 33.33% | 32.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 05:45 | 2024-01-01 00:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 41.5954 | 40.5288 | 32.5% | 31.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 05:50 | 2024-01-01 00:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 40.5288 | 39.4623 | 31.67% | 30.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 05:55 | 2024-01-01 00:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 39.4623 | 38.3957 | 30.83% | 30% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 06:00 | 2024-01-01 01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 38.3957 | 37.3292 | 30% | 29.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 06:05 | 2024-01-01 01:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 37.3292 | 36.2626 | 29.17% | 28.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 06:10 | 2024-01-01 01:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 36.2626 | 35.1961 | 28.33% | 27.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 06:15 | 2024-01-01 01:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 35.1961 | 34.1295 | 27.5% | 26.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 06:20 | 2024-01-01 01:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 34.1295 | 33.063 | 26.67% | 25.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 06:25 | 2024-01-01 01:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 33.063 | 31.9964 | 25.83% | 25% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 06:30 | 2024-01-01 01:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 31.9964 | 30.9299 | 25% | 24.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 06:35 | 2024-01-01 01:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 30.9299 | 29.8633 | 24.17% | 23.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 06:40 | 2024-01-01 01:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 29.8633 | 28.7968 | 23.33% | 22.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 06:45 | 2024-01-01 01:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 28.7968 | 27.7302 | 22.5% | 21.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 06:50 | 2024-01-01 01:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 27.7302 | 26.6637 | 21.67% | 20.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 06:55 | 2024-01-01 01:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 26.6637 | 25.5972 | 20.83% | 20% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 07:00 | 2024-01-01 02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 25.5972 | 24.5306 | 20% | 19.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 07:05 | 2024-01-01 02:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 24.5306 | 23.4641 | 19.17% | 18.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 07:10 | 2024-01-01 02:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 23.4641 | 22.3975 | 18.33% | 17.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 07:15 | 2024-01-01 02:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 22.3975 | 21.331 | 17.5% | 16.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 07:20 | 2024-01-01 02:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 21.331 | 20.2644 | 16.67% | 15.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 07:25 | 2024-01-01 02:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 20.2644 | 19.1979 | 15.83% | 15% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 07:30 | 2024-01-01 02:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 19.1979 | 18.1313 | 15% | 14.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 07:35 | 2024-01-01 02:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 18.1313 | 17.0648 | 14.17% | 13.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 07:40 | 2024-01-01 02:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 17.0648 | 15.9982 | 13.33% | 12.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 07:45 | 2024-01-01 02:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 15.9982 | 14.9317 | 12.5% | 11.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 07:50 | 2024-01-01 02:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 14.9317 | 13.8651 | 11.67% | 10.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 3.3774 | 12.1586 | 127.9858 | 2024-01-01 07:55 | 2024-01-01 02:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 13.8651 | 12.7986 | 10.83% | 10% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 115.1872 | 114.1206 | 90% | 89.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 114.1206 | 113.0541 | 89.17% | 88.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 113.0541 | 111.9875 | 88.33% | 87.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 111.9875 | 110.921 | 87.5% | 86.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 110.921 | 109.8544 | 86.67% | 85.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 109.8544 | 108.7879 | 85.83% | 85% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 108.7879 | 107.7214 | 85% | 84.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 107.7214 | 106.6548 | 84.17% | 83.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 106.6548 | 105.5883 | 83.33% | 82.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 105.5883 | 104.5217 | 82.5% | 81.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 104.5217 | 103.4552 | 81.67% | 80.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 103.4552 | 102.3886 | 80.83% | 80% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 01:00 | 2023-12-31 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 102.3886 | 101.3221 | 80% | 79.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 01:05 | 2023-12-31 20:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 101.3221 | 100.2555 | 79.17% | 78.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 01:10 | 2023-12-31 20:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 100.2555 | 99.189 | 78.33% | 77.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 01:15 | 2023-12-31 20:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 99.189 | 98.1224 | 77.5% | 76.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 01:20 | 2023-12-31 20:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 98.1224 | 97.0559 | 76.67% | 75.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 01:25 | 2023-12-31 20:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 97.0559 | 95.9893 | 75.83% | 75% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 01:30 | 2023-12-31 20:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 95.9893 | 94.9228 | 75% | 74.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 01:35 | 2023-12-31 20:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 94.9228 | 93.8562 | 74.17% | 73.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 01:40 | 2023-12-31 20:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 93.8562 | 92.7897 | 73.33% | 72.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 01:45 | 2023-12-31 20:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 92.7897 | 91.7231 | 72.5% | 71.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 01:50 | 2023-12-31 20:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 91.7231 | 90.6566 | 71.67% | 70.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 01:55 | 2023-12-31 20:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 90.6566 | 89.59 | 70.83% | 70% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 02:00 | 2023-12-31 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 89.59 | 88.5235 | 70% | 69.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 02:05 | 2023-12-31 21:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 88.5235 | 87.4569 | 69.17% | 68.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 02:10 | 2023-12-31 21:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 87.4569 | 86.3904 | 68.33% | 67.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 02:15 | 2023-12-31 21:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 86.3904 | 85.3238 | 67.5% | 66.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 02:20 | 2023-12-31 21:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 85.3238 | 84.2573 | 66.67% | 65.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 02:25 | 2023-12-31 21:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 84.2573 | 83.1907 | 65.83% | 65% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 02:30 | 2023-12-31 21:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 83.1907 | 82.1242 | 65% | 64.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 02:35 | 2023-12-31 21:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 82.1242 | 81.0576 | 64.17% | 63.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 02:40 | 2023-12-31 21:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 81.0576 | 79.9911 | 63.33% | 62.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 02:45 | 2023-12-31 21:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 79.9911 | 78.9246 | 62.5% | 61.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 02:50 | 2023-12-31 21:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 78.9246 | 77.858 | 61.67% | 60.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 02:55 | 2023-12-31 21:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 77.858 | 76.7915 | 60.83% | 60% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 03:00 | 2023-12-31 22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 76.7915 | 75.7249 | 60% | 59.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 03:05 | 2023-12-31 22:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 75.7249 | 74.6584 | 59.17% | 58.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 03:10 | 2023-12-31 22:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 74.6584 | 73.5918 | 58.33% | 57.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 03:15 | 2023-12-31 22:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 73.5918 | 72.5253 | 57.5% | 56.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 03:20 | 2023-12-31 22:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 72.5253 | 71.4587 | 56.67% | 55.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 03:25 | 2023-12-31 22:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 71.4587 | 70.3922 | 55.83% | 55% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 03:30 | 2023-12-31 22:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 70.3922 | 69.3256 | 55% | 54.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 03:35 | 2023-12-31 22:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 69.3256 | 68.2591 | 54.17% | 53.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 03:40 | 2023-12-31 22:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 68.2591 | 67.1925 | 53.33% | 52.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 03:45 | 2023-12-31 22:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 67.1925 | 66.126 | 52.5% | 51.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 03:50 | 2023-12-31 22:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 66.126 | 65.0594 | 51.67% | 50.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 03:55 | 2023-12-31 22:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 65.0594 | 63.9929 | 50.83% | 50% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 04:00 | 2023-12-31 23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 63.9929 | 62.9263 | 50% | 49.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 04:05 | 2023-12-31 23:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 62.9263 | 61.8598 | 49.17% | 48.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 04:10 | 2023-12-31 23:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 61.8598 | 60.7932 | 48.33% | 47.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 04:15 | 2023-12-31 23:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 60.7932 | 59.7267 | 47.5% | 46.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 04:20 | 2023-12-31 23:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 59.7267 | 58.6601 | 46.67% | 45.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 04:25 | 2023-12-31 23:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 58.6601 | 57.5936 | 45.83% | 45% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 04:30 | 2023-12-31 23:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 57.5936 | 56.527 | 45% | 44.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 04:35 | 2023-12-31 23:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 56.527 | 55.4605 | 44.17% | 43.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 04:40 | 2023-12-31 23:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 55.4605 | 54.3939 | 43.33% | 42.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 04:45 | 2023-12-31 23:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 54.3939 | 53.3274 | 42.5% | 41.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 04:50 | 2023-12-31 23:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 53.3274 | 52.2609 | 41.67% | 40.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 04:55 | 2023-12-31 23:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 52.2609 | 51.1943 | 40.83% | 40% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 05:00 | 2024-01-01 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 51.1943 | 50.1278 | 40% | 39.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 05:05 | 2024-01-01 00:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 50.1278 | 49.0612 | 39.17% | 38.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 05:10 | 2024-01-01 00:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 49.0612 | 47.9947 | 38.33% | 37.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 05:15 | 2024-01-01 00:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 47.9947 | 46.9281 | 37.5% | 36.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 05:20 | 2024-01-01 00:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 46.9281 | 45.8616 | 36.67% | 35.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 05:25 | 2024-01-01 00:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 45.8616 | 44.795 | 35.83% | 35% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 05:30 | 2024-01-01 00:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 44.795 | 43.7285 | 35% | 34.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 05:35 | 2024-01-01 00:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 43.7285 | 42.6619 | 34.17% | 33.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 05:40 | 2024-01-01 00:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 42.6619 | 41.5954 | 33.33% | 32.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 05:45 | 2024-01-01 00:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 41.5954 | 40.5288 | 32.5% | 31.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 05:50 | 2024-01-01 00:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 40.5288 | 39.4623 | 31.67% | 30.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 05:55 | 2024-01-01 00:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 39.4623 | 38.3957 | 30.83% | 30% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 06:00 | 2024-01-01 01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 38.3957 | 37.3292 | 30% | 29.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 06:05 | 2024-01-01 01:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 37.3292 | 36.2626 | 29.17% | 28.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 06:10 | 2024-01-01 01:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 36.2626 | 35.1961 | 28.33% | 27.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 06:15 | 2024-01-01 01:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 35.1961 | 34.1295 | 27.5% | 26.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 06:20 | 2024-01-01 01:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 34.1295 | 33.063 | 26.67% | 25.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 06:25 | 2024-01-01 01:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 33.063 | 31.9964 | 25.83% | 25% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 06:30 | 2024-01-01 01:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 31.9964 | 30.9299 | 25% | 24.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 06:35 | 2024-01-01 01:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 30.9299 | 29.8633 | 24.17% | 23.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 06:40 | 2024-01-01 01:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 29.8633 | 28.7968 | 23.33% | 22.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 06:45 | 2024-01-01 01:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 28.7968 | 27.7302 | 22.5% | 21.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 06:50 | 2024-01-01 01:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 27.7302 | 26.6637 | 21.67% | 20.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 06:55 | 2024-01-01 01:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 26.6637 | 25.5972 | 20.83% | 20% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 07:00 | 2024-01-01 02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 25.5972 | 24.5306 | 20% | 19.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 07:05 | 2024-01-01 02:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 24.5306 | 23.4641 | 19.17% | 18.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 07:10 | 2024-01-01 02:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 23.4641 | 22.3975 | 18.33% | 17.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 07:15 | 2024-01-01 02:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 22.3975 | 21.331 | 17.5% | 16.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 07:20 | 2024-01-01 02:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 21.331 | 20.2644 | 16.67% | 15.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 07:25 | 2024-01-01 02:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 20.2644 | 19.1979 | 15.83% | 15% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 07:30 | 2024-01-01 02:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 19.1979 | 18.1313 | 15% | 14.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 07:35 | 2024-01-01 02:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 18.1313 | 17.0648 | 14.17% | 13.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 07:40 | 2024-01-01 02:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 17.0648 | 15.9982 | 13.33% | 12.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 07:45 | 2024-01-01 02:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 15.9982 | 14.9317 | 12.5% | 11.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 07:50 | 2024-01-01 02:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 14.9317 | 13.8651 | 11.67% | 10.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 6.7548 | 12.1586 | 127.9858 | 2024-01-01 07:55 | 2024-01-01 02:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 13.8651 | 12.7986 | 10.83% | 10% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 115.1872 | 114.1206 | 90% | 89.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 114.1206 | 113.0541 | 89.17% | 88.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 113.0541 | 111.9875 | 88.33% | 87.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 111.9875 | 110.921 | 87.5% | 86.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 110.921 | 109.8544 | 86.67% | 85.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 109.8544 | 108.7879 | 85.83% | 85% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 108.7879 | 107.7214 | 85% | 84.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 107.7214 | 106.6548 | 84.17% | 83.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 106.6548 | 105.5883 | 83.33% | 82.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 105.5883 | 104.5217 | 82.5% | 81.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 104.5217 | 103.4552 | 81.67% | 80.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 103.4552 | 102.3886 | 80.83% | 80% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 01:00 | 2023-12-31 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 102.3886 | 101.3221 | 80% | 79.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 01:05 | 2023-12-31 20:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 101.3221 | 100.2555 | 79.17% | 78.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 01:10 | 2023-12-31 20:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 100.2555 | 99.189 | 78.33% | 77.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 01:15 | 2023-12-31 20:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 99.189 | 98.1224 | 77.5% | 76.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 01:20 | 2023-12-31 20:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 98.1224 | 97.0559 | 76.67% | 75.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 01:25 | 2023-12-31 20:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 97.0559 | 95.9893 | 75.83% | 75% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 01:30 | 2023-12-31 20:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 95.9893 | 94.9228 | 75% | 74.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 01:35 | 2023-12-31 20:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 94.9228 | 93.8562 | 74.17% | 73.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 01:40 | 2023-12-31 20:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 93.8562 | 92.7897 | 73.33% | 72.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 01:45 | 2023-12-31 20:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 92.7897 | 91.7231 | 72.5% | 71.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 01:50 | 2023-12-31 20:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 91.7231 | 90.6566 | 71.67% | 70.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 01:55 | 2023-12-31 20:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 90.6566 | 89.59 | 70.83% | 70% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 02:00 | 2023-12-31 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 89.59 | 88.5235 | 70% | 69.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 02:05 | 2023-12-31 21:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 88.5235 | 87.4569 | 69.17% | 68.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 02:10 | 2023-12-31 21:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 87.4569 | 86.3904 | 68.33% | 67.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 02:15 | 2023-12-31 21:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 86.3904 | 85.3238 | 67.5% | 66.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 02:20 | 2023-12-31 21:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 85.3238 | 84.2573 | 66.67% | 65.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 02:25 | 2023-12-31 21:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 84.2573 | 83.1907 | 65.83% | 65% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 02:30 | 2023-12-31 21:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 83.1907 | 82.1242 | 65% | 64.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 02:35 | 2023-12-31 21:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 82.1242 | 81.0576 | 64.17% | 63.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 02:40 | 2023-12-31 21:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 81.0576 | 79.9911 | 63.33% | 62.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 02:45 | 2023-12-31 21:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 79.9911 | 78.9246 | 62.5% | 61.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 02:50 | 2023-12-31 21:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 78.9246 | 77.858 | 61.67% | 60.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 02:55 | 2023-12-31 21:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 77.858 | 76.7915 | 60.83% | 60% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 03:00 | 2023-12-31 22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 76.7915 | 75.7249 | 60% | 59.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 03:05 | 2023-12-31 22:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 75.7249 | 74.6584 | 59.17% | 58.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 03:10 | 2023-12-31 22:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 74.6584 | 73.5918 | 58.33% | 57.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 03:15 | 2023-12-31 22:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 73.5918 | 72.5253 | 57.5% | 56.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 03:20 | 2023-12-31 22:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 72.5253 | 71.4587 | 56.67% | 55.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 03:25 | 2023-12-31 22:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 71.4587 | 70.3922 | 55.83% | 55% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 03:30 | 2023-12-31 22:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 70.3922 | 69.3256 | 55% | 54.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 03:35 | 2023-12-31 22:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 69.3256 | 68.2591 | 54.17% | 53.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 03:40 | 2023-12-31 22:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 68.2591 | 67.1925 | 53.33% | 52.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 03:45 | 2023-12-31 22:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 67.1925 | 66.126 | 52.5% | 51.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 03:50 | 2023-12-31 22:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 66.126 | 65.0594 | 51.67% | 50.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 03:55 | 2023-12-31 22:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 65.0594 | 63.9929 | 50.83% | 50% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 04:00 | 2023-12-31 23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 63.9929 | 62.9263 | 50% | 49.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 04:05 | 2023-12-31 23:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 62.9263 | 61.8598 | 49.17% | 48.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 04:10 | 2023-12-31 23:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 61.8598 | 60.7932 | 48.33% | 47.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 04:15 | 2023-12-31 23:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 60.7932 | 59.7267 | 47.5% | 46.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 04:20 | 2023-12-31 23:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 59.7267 | 58.6601 | 46.67% | 45.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 04:25 | 2023-12-31 23:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 58.6601 | 57.5936 | 45.83% | 45% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 04:30 | 2023-12-31 23:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 57.5936 | 56.527 | 45% | 44.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 04:35 | 2023-12-31 23:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 56.527 | 55.4605 | 44.17% | 43.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 04:40 | 2023-12-31 23:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 55.4605 | 54.3939 | 43.33% | 42.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 04:45 | 2023-12-31 23:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 54.3939 | 53.3274 | 42.5% | 41.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 04:50 | 2023-12-31 23:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 53.3274 | 52.2609 | 41.67% | 40.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 04:55 | 2023-12-31 23:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 52.2609 | 51.1943 | 40.83% | 40% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 05:00 | 2024-01-01 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 51.1943 | 50.1278 | 40% | 39.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 05:05 | 2024-01-01 00:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 50.1278 | 49.0612 | 39.17% | 38.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 05:10 | 2024-01-01 00:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 49.0612 | 47.9947 | 38.33% | 37.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 05:15 | 2024-01-01 00:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 47.9947 | 46.9281 | 37.5% | 36.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 05:20 | 2024-01-01 00:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 46.9281 | 45.8616 | 36.67% | 35.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 05:25 | 2024-01-01 00:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 45.8616 | 44.795 | 35.83% | 35% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 05:30 | 2024-01-01 00:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 44.795 | 43.7285 | 35% | 34.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 05:35 | 2024-01-01 00:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 43.7285 | 42.6619 | 34.17% | 33.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 05:40 | 2024-01-01 00:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 42.6619 | 41.5954 | 33.33% | 32.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 05:45 | 2024-01-01 00:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 41.5954 | 40.5288 | 32.5% | 31.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 05:50 | 2024-01-01 00:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 40.5288 | 39.4623 | 31.67% | 30.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 05:55 | 2024-01-01 00:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 39.4623 | 38.3957 | 30.83% | 30% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 06:00 | 2024-01-01 01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 38.3957 | 37.3292 | 30% | 29.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 06:05 | 2024-01-01 01:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 37.3292 | 36.2626 | 29.17% | 28.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 06:10 | 2024-01-01 01:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 36.2626 | 35.1961 | 28.33% | 27.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 06:15 | 2024-01-01 01:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 35.1961 | 34.1295 | 27.5% | 26.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 06:20 | 2024-01-01 01:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 34.1295 | 33.063 | 26.67% | 25.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 06:25 | 2024-01-01 01:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 33.063 | 31.9964 | 25.83% | 25% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 06:30 | 2024-01-01 01:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 31.9964 | 30.9299 | 25% | 24.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 06:35 | 2024-01-01 01:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 30.9299 | 29.8633 | 24.17% | 23.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 06:40 | 2024-01-01 01:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 29.8633 | 28.7968 | 23.33% | 22.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 06:45 | 2024-01-01 01:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 28.7968 | 27.7302 | 22.5% | 21.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 06:50 | 2024-01-01 01:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 27.7302 | 26.6637 | 21.67% | 20.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 06:55 | 2024-01-01 01:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 26.6637 | 25.5972 | 20.83% | 20% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 07:00 | 2024-01-01 02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 25.5972 | 24.5306 | 20% | 19.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 07:05 | 2024-01-01 02:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 24.5306 | 23.4641 | 19.17% | 18.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 07:10 | 2024-01-01 02:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 23.4641 | 22.3975 | 18.33% | 17.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 07:15 | 2024-01-01 02:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 22.3975 | 21.331 | 17.5% | 16.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 07:20 | 2024-01-01 02:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 21.331 | 20.2644 | 16.67% | 15.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 07:25 | 2024-01-01 02:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 20.2644 | 19.1979 | 15.83% | 15% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 07:30 | 2024-01-01 02:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 19.1979 | 18.1313 | 15% | 14.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 07:35 | 2024-01-01 02:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 18.1313 | 17.0648 | 14.17% | 13.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 07:40 | 2024-01-01 02:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 17.0648 | 15.9982 | 13.33% | 12.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 07:45 | 2024-01-01 02:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 15.9982 | 14.9317 | 12.5% | 11.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 07:50 | 2024-01-01 02:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 14.9317 | 13.8651 | 11.67% | 10.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 10.1322 | 12.1586 | 127.9858 | 2024-01-01 07:55 | 2024-01-01 02:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 13.8651 | 12.7986 | 10.83% | 10% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 115.1872 | 114.1206 | 90% | 89.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 114.1206 | 113.0541 | 89.17% | 88.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 113.0541 | 111.9875 | 88.33% | 87.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 111.9875 | 110.921 | 87.5% | 86.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 110.921 | 109.8544 | 86.67% | 85.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 109.8544 | 108.7879 | 85.83% | 85% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 108.7879 | 107.7214 | 85% | 84.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 107.7214 | 106.6548 | 84.17% | 83.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 106.6548 | 105.5883 | 83.33% | 82.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 105.5883 | 104.5217 | 82.5% | 81.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 104.5217 | 103.4552 | 81.67% | 80.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 103.4552 | 102.3886 | 80.83% | 80% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 01:00 | 2023-12-31 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 102.3886 | 101.3221 | 80% | 79.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 01:05 | 2023-12-31 20:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 101.3221 | 100.2555 | 79.17% | 78.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 01:10 | 2023-12-31 20:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 100.2555 | 99.189 | 78.33% | 77.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 01:15 | 2023-12-31 20:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 99.189 | 98.1224 | 77.5% | 76.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 01:20 | 2023-12-31 20:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 98.1224 | 97.0559 | 76.67% | 75.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 01:25 | 2023-12-31 20:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 97.0559 | 95.9893 | 75.83% | 75% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 01:30 | 2023-12-31 20:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 95.9893 | 94.9228 | 75% | 74.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 01:35 | 2023-12-31 20:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 94.9228 | 93.8562 | 74.17% | 73.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 01:40 | 2023-12-31 20:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 93.8562 | 92.7897 | 73.33% | 72.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 01:45 | 2023-12-31 20:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 92.7897 | 91.7231 | 72.5% | 71.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 01:50 | 2023-12-31 20:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 91.7231 | 90.6566 | 71.67% | 70.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 01:55 | 2023-12-31 20:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 90.6566 | 89.59 | 70.83% | 70% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 02:00 | 2023-12-31 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 89.59 | 88.5235 | 70% | 69.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 02:05 | 2023-12-31 21:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 88.5235 | 87.4569 | 69.17% | 68.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 02:10 | 2023-12-31 21:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 87.4569 | 86.3904 | 68.33% | 67.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 02:15 | 2023-12-31 21:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 86.3904 | 85.3238 | 67.5% | 66.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 02:20 | 2023-12-31 21:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 85.3238 | 84.2573 | 66.67% | 65.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 02:25 | 2023-12-31 21:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 84.2573 | 83.1907 | 65.83% | 65% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 02:30 | 2023-12-31 21:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 83.1907 | 82.1242 | 65% | 64.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 02:35 | 2023-12-31 21:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 82.1242 | 81.0576 | 64.17% | 63.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 02:40 | 2023-12-31 21:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 81.0576 | 79.9911 | 63.33% | 62.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 02:45 | 2023-12-31 21:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 79.9911 | 78.9246 | 62.5% | 61.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 02:50 | 2023-12-31 21:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 78.9246 | 77.858 | 61.67% | 60.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 02:55 | 2023-12-31 21:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 77.858 | 76.7915 | 60.83% | 60% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 03:00 | 2023-12-31 22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 76.7915 | 75.7249 | 60% | 59.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 03:05 | 2023-12-31 22:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 75.7249 | 74.6584 | 59.17% | 58.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 03:10 | 2023-12-31 22:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 74.6584 | 73.5918 | 58.33% | 57.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 03:15 | 2023-12-31 22:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 73.5918 | 72.5253 | 57.5% | 56.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 03:20 | 2023-12-31 22:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 72.5253 | 71.4587 | 56.67% | 55.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 03:25 | 2023-12-31 22:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 71.4587 | 70.3922 | 55.83% | 55% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 03:30 | 2023-12-31 22:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 70.3922 | 69.3256 | 55% | 54.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 03:35 | 2023-12-31 22:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 69.3256 | 68.2591 | 54.17% | 53.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 03:40 | 2023-12-31 22:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 68.2591 | 67.1925 | 53.33% | 52.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 03:45 | 2023-12-31 22:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 67.1925 | 66.126 | 52.5% | 51.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 03:50 | 2023-12-31 22:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 66.126 | 65.0594 | 51.67% | 50.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 03:55 | 2023-12-31 22:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 65.0594 | 63.9929 | 50.83% | 50% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 04:00 | 2023-12-31 23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 63.9929 | 62.9263 | 50% | 49.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 04:05 | 2023-12-31 23:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 62.9263 | 61.8598 | 49.17% | 48.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 04:10 | 2023-12-31 23:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 61.8598 | 60.7932 | 48.33% | 47.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 04:15 | 2023-12-31 23:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 60.7932 | 59.7267 | 47.5% | 46.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 04:20 | 2023-12-31 23:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 59.7267 | 58.6601 | 46.67% | 45.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 04:25 | 2023-12-31 23:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 58.6601 | 57.5936 | 45.83% | 45% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 04:30 | 2023-12-31 23:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 57.5936 | 56.527 | 45% | 44.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 04:35 | 2023-12-31 23:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 56.527 | 55.4605 | 44.17% | 43.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 04:40 | 2023-12-31 23:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 55.4605 | 54.3939 | 43.33% | 42.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 04:45 | 2023-12-31 23:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 54.3939 | 53.3274 | 42.5% | 41.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 04:50 | 2023-12-31 23:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 53.3274 | 52.2609 | 41.67% | 40.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 04:55 | 2023-12-31 23:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 52.2609 | 51.1943 | 40.83% | 40% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 05:00 | 2024-01-01 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 51.1943 | 50.1278 | 40% | 39.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 05:05 | 2024-01-01 00:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 50.1278 | 49.0612 | 39.17% | 38.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 05:10 | 2024-01-01 00:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 49.0612 | 47.9947 | 38.33% | 37.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 05:15 | 2024-01-01 00:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 47.9947 | 46.9281 | 37.5% | 36.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 05:20 | 2024-01-01 00:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 46.9281 | 45.8616 | 36.67% | 35.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 05:25 | 2024-01-01 00:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 45.8616 | 44.795 | 35.83% | 35% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 05:30 | 2024-01-01 00:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 44.795 | 43.7285 | 35% | 34.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 05:35 | 2024-01-01 00:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 43.7285 | 42.6619 | 34.17% | 33.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 05:40 | 2024-01-01 00:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 42.6619 | 41.5954 | 33.33% | 32.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 05:45 | 2024-01-01 00:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 41.5954 | 40.5288 | 32.5% | 31.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 05:50 | 2024-01-01 00:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 40.5288 | 39.4623 | 31.67% | 30.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 05:55 | 2024-01-01 00:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 39.4623 | 38.3957 | 30.83% | 30% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 06:00 | 2024-01-01 01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 38.3957 | 37.3292 | 30% | 29.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 06:05 | 2024-01-01 01:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 37.3292 | 36.2626 | 29.17% | 28.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 06:10 | 2024-01-01 01:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 36.2626 | 35.1961 | 28.33% | 27.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 06:15 | 2024-01-01 01:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 35.1961 | 34.1295 | 27.5% | 26.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 06:20 | 2024-01-01 01:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 34.1295 | 33.063 | 26.67% | 25.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 06:25 | 2024-01-01 01:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 33.063 | 31.9964 | 25.83% | 25% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 06:30 | 2024-01-01 01:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 31.9964 | 30.9299 | 25% | 24.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 06:35 | 2024-01-01 01:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 30.9299 | 29.8633 | 24.17% | 23.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 06:40 | 2024-01-01 01:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 29.8633 | 28.7968 | 23.33% | 22.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 06:45 | 2024-01-01 01:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 28.7968 | 27.7302 | 22.5% | 21.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 06:50 | 2024-01-01 01:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 27.7302 | 26.6637 | 21.67% | 20.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 06:55 | 2024-01-01 01:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 26.6637 | 25.5972 | 20.83% | 20% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 07:00 | 2024-01-01 02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 25.5972 | 24.5306 | 20% | 19.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 07:05 | 2024-01-01 02:05 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 24.5306 | 23.4641 | 19.17% | 18.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 07:10 | 2024-01-01 02:10 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 23.4641 | 22.3975 | 18.33% | 17.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 07:15 | 2024-01-01 02:15 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 22.3975 | 21.331 | 17.5% | 16.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 07:20 | 2024-01-01 02:20 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 21.331 | 20.2644 | 16.67% | 15.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 07:25 | 2024-01-01 02:25 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 20.2644 | 19.1979 | 15.83% | 15% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 07:30 | 2024-01-01 02:30 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 19.1979 | 18.1313 | 15% | 14.17% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 07:35 | 2024-01-01 02:35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 18.1313 | 17.0648 | 14.17% | 13.33% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 07:40 | 2024-01-01 02:40 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 17.0648 | 15.9982 | 13.33% | 12.5% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 07:45 | 2024-01-01 02:45 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 15.9982 | 14.9317 | 12.5% | 11.67% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 07:50 | 2024-01-01 02:50 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 14.9317 | 13.8651 | 11.67% | 10.83% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 0.9 | 8 | 13.5096 | 12.1586 | 127.9858 | 2024-01-01 07:55 | 2024-01-01 02:55 | 0 | 0 | 0 | 0 | 0 | 0 | 12.1586 | 13.8651 | 12.7986 | 10.83% | 10% | 12.7986 | 12.1586 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 1 | 0 | 13.5096 | 17.7758 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 15.9982 | 14.8132 | 90% | 83.33% | 1.7776 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 1 | 0 | 13.5096 | 17.7758 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 14.8132 | 13.6281 | 83.33% | 76.67% | 1.7776 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 1 | 0 | 13.5096 | 17.7758 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 13.6281 | 12.4431 | 76.67% | 70% | 1.7776 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 1 | 0 | 13.5096 | 17.7758 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 12.4431 | 11.258 | 70% | 63.33% | 1.7776 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 1 | 0 | 13.5096 | 17.7758 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 11.258 | 10.073 | 63.33% | 56.67% | 1.7776 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 1 | 0 | 13.5096 | 17.7758 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 10.073 | 8.8879 | 56.67% | 50% | 1.7776 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 1 | 0 | 13.5096 | 17.7758 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 8.8879 | 7.7028 | 50% | 43.33% | 1.7776 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 1 | 0 | 13.5096 | 17.7758 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 7.7028 | 6.5178 | 43.33% | 36.67% | 1.7776 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 1 | 0 | 13.5096 | 17.7758 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 6.5178 | 5.3327 | 36.67% | 30% | 1.7776 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 1 | 0 | 13.5096 | 17.7758 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 5.3327 | 4.1477 | 30% | 23.33% | 1.7776 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 1 | 0 | 13.5096 | 17.7758 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 4.1477 | 2.9626 | 23.33% | 16.67% | 1.7776 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 1 | 0 | 13.5096 | 17.7758 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 2.9626 | 1.7776 | 16.67% | 10% | 1.7776 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 1 | 3.3774 | 13.5096 | 17.7758 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 15.9982 | 14.8132 | 90% | 83.33% | 1.7776 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 1 | 3.3774 | 13.5096 | 17.7758 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 14.8132 | 13.6281 | 83.33% | 76.67% | 1.7776 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 1 | 3.3774 | 13.5096 | 17.7758 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 13.6281 | 12.4431 | 76.67% | 70% | 1.7776 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 1 | 3.3774 | 13.5096 | 17.7758 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 12.4431 | 11.258 | 70% | 63.33% | 1.7776 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 1 | 3.3774 | 13.5096 | 17.7758 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 11.258 | 10.073 | 63.33% | 56.67% | 1.7776 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 1 | 3.3774 | 13.5096 | 17.7758 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 10.073 | 8.8879 | 56.67% | 50% | 1.7776 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 1 | 3.3774 | 13.5096 | 17.7758 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 8.8879 | 7.7028 | 50% | 43.33% | 1.7776 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 1 | 3.3774 | 13.5096 | 17.7758 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 7.7028 | 6.5178 | 43.33% | 36.67% | 1.7776 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 1 | 3.3774 | 13.5096 | 17.7758 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 6.5178 | 5.3327 | 36.67% | 30% | 1.7776 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 1 | 3.3774 | 13.5096 | 17.7758 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 5.3327 | 4.1477 | 30% | 23.33% | 1.7776 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 1 | 3.3774 | 13.5096 | 17.7758 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 4.1477 | 2.9626 | 23.33% | 16.67% | 1.7776 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 1 | 3.3774 | 13.5096 | 17.7758 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 2.9626 | 1.7776 | 16.67% | 10% | 1.7776 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 1 | 6.7548 | 13.5096 | 17.7758 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 15.9982 | 14.8132 | 90% | 83.33% | 1.7776 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 1 | 6.7548 | 13.5096 | 17.7758 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 14.8132 | 13.6281 | 83.33% | 76.67% | 1.7776 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 1 | 6.7548 | 13.5096 | 17.7758 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 13.6281 | 12.4431 | 76.67% | 70% | 1.7776 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 1 | 6.7548 | 13.5096 | 17.7758 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 12.4431 | 11.258 | 70% | 63.33% | 1.7776 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 1 | 6.7548 | 13.5096 | 17.7758 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 11.258 | 10.073 | 63.33% | 56.67% | 1.7776 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 1 | 6.7548 | 13.5096 | 17.7758 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 10.073 | 8.8879 | 56.67% | 50% | 1.7776 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 1 | 6.7548 | 13.5096 | 17.7758 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 8.8879 | 7.7028 | 50% | 43.33% | 1.7776 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 1 | 6.7548 | 13.5096 | 17.7758 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 7.7028 | 6.5178 | 43.33% | 36.67% | 1.7776 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 1 | 6.7548 | 13.5096 | 17.7758 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 6.5178 | 5.3327 | 36.67% | 30% | 1.7776 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 1 | 6.7548 | 13.5096 | 17.7758 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 5.3327 | 4.1477 | 30% | 23.33% | 1.7776 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 1 | 6.7548 | 13.5096 | 17.7758 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 4.1477 | 2.9626 | 23.33% | 16.67% | 1.7776 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 1 | 6.7548 | 13.5096 | 17.7758 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 2.9626 | 1.7776 | 16.67% | 10% | 1.7776 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 1 | 10.1322 | 13.5096 | 17.7758 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 15.9982 | 14.8132 | 90% | 83.33% | 1.7776 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 1 | 10.1322 | 13.5096 | 17.7758 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 14.8132 | 13.6281 | 83.33% | 76.67% | 1.7776 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 1 | 10.1322 | 13.5096 | 17.7758 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 13.6281 | 12.4431 | 76.67% | 70% | 1.7776 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 1 | 10.1322 | 13.5096 | 17.7758 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 12.4431 | 11.258 | 70% | 63.33% | 1.7776 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 1 | 10.1322 | 13.5096 | 17.7758 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 11.258 | 10.073 | 63.33% | 56.67% | 1.7776 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 1 | 10.1322 | 13.5096 | 17.7758 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 10.073 | 8.8879 | 56.67% | 50% | 1.7776 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 1 | 10.1322 | 13.5096 | 17.7758 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 8.8879 | 7.7028 | 50% | 43.33% | 1.7776 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 1 | 10.1322 | 13.5096 | 17.7758 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 7.7028 | 6.5178 | 43.33% | 36.67% | 1.7776 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 1 | 10.1322 | 13.5096 | 17.7758 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 6.5178 | 5.3327 | 36.67% | 30% | 1.7776 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 1 | 10.1322 | 13.5096 | 17.7758 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 5.3327 | 4.1477 | 30% | 23.33% | 1.7776 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 1 | 10.1322 | 13.5096 | 17.7758 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 4.1477 | 2.9626 | 23.33% | 16.67% | 1.7776 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 1 | 10.1322 | 13.5096 | 17.7758 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 2.9626 | 1.7776 | 16.67% | 10% | 1.7776 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 1 | 13.5096 | 13.5096 | 17.7758 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 15.9982 | 14.8132 | 90% | 83.33% | 1.7776 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 1 | 13.5096 | 13.5096 | 17.7758 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 14.8132 | 13.6281 | 83.33% | 76.67% | 1.7776 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 1 | 13.5096 | 13.5096 | 17.7758 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 13.6281 | 12.4431 | 76.67% | 70% | 1.7776 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 1 | 13.5096 | 13.5096 | 17.7758 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 12.4431 | 11.258 | 70% | 63.33% | 1.7776 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 1 | 13.5096 | 13.5096 | 17.7758 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 11.258 | 10.073 | 63.33% | 56.67% | 1.7776 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 1 | 13.5096 | 13.5096 | 17.7758 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 10.073 | 8.8879 | 56.67% | 50% | 1.7776 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 1 | 13.5096 | 13.5096 | 17.7758 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 8.8879 | 7.7028 | 50% | 43.33% | 1.7776 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 1 | 13.5096 | 13.5096 | 17.7758 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 7.7028 | 6.5178 | 43.33% | 36.67% | 1.7776 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 1 | 13.5096 | 13.5096 | 17.7758 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 6.5178 | 5.3327 | 36.67% | 30% | 1.7776 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 1 | 13.5096 | 13.5096 | 17.7758 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 5.3327 | 4.1477 | 30% | 23.33% | 1.7776 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 1 | 13.5096 | 13.5096 | 17.7758 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 4.1477 | 2.9626 | 23.33% | 16.67% | 1.7776 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 1 | 13.5096 | 13.5096 | 17.7758 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 2.9626 | 1.7776 | 16.67% | 10% | 1.7776 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 0 | 13.5096 | 35.5516 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 31.9964 | 30.8114 | 90% | 86.67% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 0 | 13.5096 | 35.5516 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 30.8114 | 29.6263 | 86.67% | 83.33% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 0 | 13.5096 | 35.5516 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 29.6263 | 28.4413 | 83.33% | 80% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 0 | 13.5096 | 35.5516 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 28.4413 | 27.2562 | 80% | 76.67% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 0 | 13.5096 | 35.5516 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 27.2562 | 26.0712 | 76.67% | 73.33% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 0 | 13.5096 | 35.5516 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 26.0712 | 24.8861 | 73.33% | 70% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 0 | 13.5096 | 35.5516 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 24.8861 | 23.7011 | 70% | 66.67% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 0 | 13.5096 | 35.5516 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 23.7011 | 22.516 | 66.67% | 63.33% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 0 | 13.5096 | 35.5516 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 22.516 | 21.331 | 63.33% | 60% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 0 | 13.5096 | 35.5516 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 21.331 | 20.1459 | 60% | 56.67% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 0 | 13.5096 | 35.5516 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 20.1459 | 18.9609 | 56.67% | 53.33% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 0 | 13.5096 | 35.5516 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 18.9609 | 17.7758 | 53.33% | 50% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 0 | 13.5096 | 35.5516 | 2024-01-01 01:00 | 2023-12-31 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 17.7758 | 16.5907 | 50% | 46.67% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 0 | 13.5096 | 35.5516 | 2024-01-01 01:05 | 2023-12-31 20:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 16.5907 | 15.4057 | 46.67% | 43.33% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 0 | 13.5096 | 35.5516 | 2024-01-01 01:10 | 2023-12-31 20:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 15.4057 | 14.2206 | 43.33% | 40% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 0 | 13.5096 | 35.5516 | 2024-01-01 01:15 | 2023-12-31 20:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 14.2206 | 13.0356 | 40% | 36.67% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 0 | 13.5096 | 35.5516 | 2024-01-01 01:20 | 2023-12-31 20:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 13.0356 | 11.8505 | 36.67% | 33.33% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 0 | 13.5096 | 35.5516 | 2024-01-01 01:25 | 2023-12-31 20:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 11.8505 | 10.6655 | 33.33% | 30% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 0 | 13.5096 | 35.5516 | 2024-01-01 01:30 | 2023-12-31 20:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 10.6655 | 9.4804 | 30% | 26.67% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 0 | 13.5096 | 35.5516 | 2024-01-01 01:35 | 2023-12-31 20:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 9.4804 | 8.2954 | 26.67% | 23.33% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 0 | 13.5096 | 35.5516 | 2024-01-01 01:40 | 2023-12-31 20:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 8.2954 | 7.1103 | 23.33% | 20% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 0 | 13.5096 | 35.5516 | 2024-01-01 01:45 | 2023-12-31 20:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 7.1103 | 5.9253 | 20% | 16.67% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 0 | 13.5096 | 35.5516 | 2024-01-01 01:50 | 2023-12-31 20:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 5.9253 | 4.7402 | 16.67% | 13.33% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 0 | 13.5096 | 35.5516 | 2024-01-01 01:55 | 2023-12-31 20:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 4.7402 | 3.5552 | 13.33% | 10% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 3.3774 | 13.5096 | 35.5516 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 31.9964 | 30.8114 | 90% | 86.67% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 3.3774 | 13.5096 | 35.5516 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 30.8114 | 29.6263 | 86.67% | 83.33% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 3.3774 | 13.5096 | 35.5516 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 29.6263 | 28.4413 | 83.33% | 80% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 3.3774 | 13.5096 | 35.5516 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 28.4413 | 27.2562 | 80% | 76.67% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 3.3774 | 13.5096 | 35.5516 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 27.2562 | 26.0712 | 76.67% | 73.33% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 3.3774 | 13.5096 | 35.5516 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 26.0712 | 24.8861 | 73.33% | 70% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 3.3774 | 13.5096 | 35.5516 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 24.8861 | 23.7011 | 70% | 66.67% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 3.3774 | 13.5096 | 35.5516 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 23.7011 | 22.516 | 66.67% | 63.33% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 3.3774 | 13.5096 | 35.5516 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 22.516 | 21.331 | 63.33% | 60% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 3.3774 | 13.5096 | 35.5516 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 21.331 | 20.1459 | 60% | 56.67% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 3.3774 | 13.5096 | 35.5516 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 20.1459 | 18.9609 | 56.67% | 53.33% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 3.3774 | 13.5096 | 35.5516 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 18.9609 | 17.7758 | 53.33% | 50% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 3.3774 | 13.5096 | 35.5516 | 2024-01-01 01:00 | 2023-12-31 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 17.7758 | 16.5907 | 50% | 46.67% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 3.3774 | 13.5096 | 35.5516 | 2024-01-01 01:05 | 2023-12-31 20:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 16.5907 | 15.4057 | 46.67% | 43.33% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 3.3774 | 13.5096 | 35.5516 | 2024-01-01 01:10 | 2023-12-31 20:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 15.4057 | 14.2206 | 43.33% | 40% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 3.3774 | 13.5096 | 35.5516 | 2024-01-01 01:15 | 2023-12-31 20:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 14.2206 | 13.0356 | 40% | 36.67% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 3.3774 | 13.5096 | 35.5516 | 2024-01-01 01:20 | 2023-12-31 20:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 13.0356 | 11.8505 | 36.67% | 33.33% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 3.3774 | 13.5096 | 35.5516 | 2024-01-01 01:25 | 2023-12-31 20:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 11.8505 | 10.6655 | 33.33% | 30% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 3.3774 | 13.5096 | 35.5516 | 2024-01-01 01:30 | 2023-12-31 20:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 10.6655 | 9.4804 | 30% | 26.67% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 3.3774 | 13.5096 | 35.5516 | 2024-01-01 01:35 | 2023-12-31 20:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 9.4804 | 8.2954 | 26.67% | 23.33% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 3.3774 | 13.5096 | 35.5516 | 2024-01-01 01:40 | 2023-12-31 20:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 8.2954 | 7.1103 | 23.33% | 20% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 3.3774 | 13.5096 | 35.5516 | 2024-01-01 01:45 | 2023-12-31 20:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 7.1103 | 5.9253 | 20% | 16.67% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 3.3774 | 13.5096 | 35.5516 | 2024-01-01 01:50 | 2023-12-31 20:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 5.9253 | 4.7402 | 16.67% | 13.33% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 3.3774 | 13.5096 | 35.5516 | 2024-01-01 01:55 | 2023-12-31 20:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 4.7402 | 3.5552 | 13.33% | 10% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 6.7548 | 13.5096 | 35.5516 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 31.9964 | 30.8114 | 90% | 86.67% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 6.7548 | 13.5096 | 35.5516 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 30.8114 | 29.6263 | 86.67% | 83.33% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 6.7548 | 13.5096 | 35.5516 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 29.6263 | 28.4413 | 83.33% | 80% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 6.7548 | 13.5096 | 35.5516 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 28.4413 | 27.2562 | 80% | 76.67% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 6.7548 | 13.5096 | 35.5516 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 27.2562 | 26.0712 | 76.67% | 73.33% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 6.7548 | 13.5096 | 35.5516 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 26.0712 | 24.8861 | 73.33% | 70% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 6.7548 | 13.5096 | 35.5516 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 24.8861 | 23.7011 | 70% | 66.67% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 6.7548 | 13.5096 | 35.5516 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 23.7011 | 22.516 | 66.67% | 63.33% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 6.7548 | 13.5096 | 35.5516 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 22.516 | 21.331 | 63.33% | 60% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 6.7548 | 13.5096 | 35.5516 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 21.331 | 20.1459 | 60% | 56.67% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 6.7548 | 13.5096 | 35.5516 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 20.1459 | 18.9609 | 56.67% | 53.33% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 6.7548 | 13.5096 | 35.5516 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 18.9609 | 17.7758 | 53.33% | 50% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 6.7548 | 13.5096 | 35.5516 | 2024-01-01 01:00 | 2023-12-31 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 17.7758 | 16.5907 | 50% | 46.67% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 6.7548 | 13.5096 | 35.5516 | 2024-01-01 01:05 | 2023-12-31 20:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 16.5907 | 15.4057 | 46.67% | 43.33% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 6.7548 | 13.5096 | 35.5516 | 2024-01-01 01:10 | 2023-12-31 20:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 15.4057 | 14.2206 | 43.33% | 40% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 6.7548 | 13.5096 | 35.5516 | 2024-01-01 01:15 | 2023-12-31 20:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 14.2206 | 13.0356 | 40% | 36.67% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 6.7548 | 13.5096 | 35.5516 | 2024-01-01 01:20 | 2023-12-31 20:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 13.0356 | 11.8505 | 36.67% | 33.33% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 6.7548 | 13.5096 | 35.5516 | 2024-01-01 01:25 | 2023-12-31 20:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 11.8505 | 10.6655 | 33.33% | 30% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 6.7548 | 13.5096 | 35.5516 | 2024-01-01 01:30 | 2023-12-31 20:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 10.6655 | 9.4804 | 30% | 26.67% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 6.7548 | 13.5096 | 35.5516 | 2024-01-01 01:35 | 2023-12-31 20:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 9.4804 | 8.2954 | 26.67% | 23.33% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 6.7548 | 13.5096 | 35.5516 | 2024-01-01 01:40 | 2023-12-31 20:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 8.2954 | 7.1103 | 23.33% | 20% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 6.7548 | 13.5096 | 35.5516 | 2024-01-01 01:45 | 2023-12-31 20:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 7.1103 | 5.9253 | 20% | 16.67% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 6.7548 | 13.5096 | 35.5516 | 2024-01-01 01:50 | 2023-12-31 20:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 5.9253 | 4.7402 | 16.67% | 13.33% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 6.7548 | 13.5096 | 35.5516 | 2024-01-01 01:55 | 2023-12-31 20:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 4.7402 | 3.5552 | 13.33% | 10% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 10.1322 | 13.5096 | 35.5516 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 31.9964 | 30.8114 | 90% | 86.67% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 10.1322 | 13.5096 | 35.5516 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 30.8114 | 29.6263 | 86.67% | 83.33% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 10.1322 | 13.5096 | 35.5516 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 29.6263 | 28.4413 | 83.33% | 80% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 10.1322 | 13.5096 | 35.5516 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 28.4413 | 27.2562 | 80% | 76.67% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 10.1322 | 13.5096 | 35.5516 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 27.2562 | 26.0712 | 76.67% | 73.33% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 10.1322 | 13.5096 | 35.5516 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 26.0712 | 24.8861 | 73.33% | 70% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 10.1322 | 13.5096 | 35.5516 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 24.8861 | 23.7011 | 70% | 66.67% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 10.1322 | 13.5096 | 35.5516 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 23.7011 | 22.516 | 66.67% | 63.33% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 10.1322 | 13.5096 | 35.5516 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 22.516 | 21.331 | 63.33% | 60% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 10.1322 | 13.5096 | 35.5516 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 21.331 | 20.1459 | 60% | 56.67% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 10.1322 | 13.5096 | 35.5516 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 20.1459 | 18.9609 | 56.67% | 53.33% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 10.1322 | 13.5096 | 35.5516 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 18.9609 | 17.7758 | 53.33% | 50% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 10.1322 | 13.5096 | 35.5516 | 2024-01-01 01:00 | 2023-12-31 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 17.7758 | 16.5907 | 50% | 46.67% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 10.1322 | 13.5096 | 35.5516 | 2024-01-01 01:05 | 2023-12-31 20:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 16.5907 | 15.4057 | 46.67% | 43.33% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 10.1322 | 13.5096 | 35.5516 | 2024-01-01 01:10 | 2023-12-31 20:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 15.4057 | 14.2206 | 43.33% | 40% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 10.1322 | 13.5096 | 35.5516 | 2024-01-01 01:15 | 2023-12-31 20:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 14.2206 | 13.0356 | 40% | 36.67% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 10.1322 | 13.5096 | 35.5516 | 2024-01-01 01:20 | 2023-12-31 20:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 13.0356 | 11.8505 | 36.67% | 33.33% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 10.1322 | 13.5096 | 35.5516 | 2024-01-01 01:25 | 2023-12-31 20:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 11.8505 | 10.6655 | 33.33% | 30% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 10.1322 | 13.5096 | 35.5516 | 2024-01-01 01:30 | 2023-12-31 20:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 10.6655 | 9.4804 | 30% | 26.67% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 10.1322 | 13.5096 | 35.5516 | 2024-01-01 01:35 | 2023-12-31 20:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 9.4804 | 8.2954 | 26.67% | 23.33% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 10.1322 | 13.5096 | 35.5516 | 2024-01-01 01:40 | 2023-12-31 20:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 8.2954 | 7.1103 | 23.33% | 20% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 10.1322 | 13.5096 | 35.5516 | 2024-01-01 01:45 | 2023-12-31 20:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 7.1103 | 5.9253 | 20% | 16.67% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 10.1322 | 13.5096 | 35.5516 | 2024-01-01 01:50 | 2023-12-31 20:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 5.9253 | 4.7402 | 16.67% | 13.33% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 10.1322 | 13.5096 | 35.5516 | 2024-01-01 01:55 | 2023-12-31 20:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 4.7402 | 3.5552 | 13.33% | 10% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 13.5096 | 13.5096 | 35.5516 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 31.9964 | 30.8114 | 90% | 86.67% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 13.5096 | 13.5096 | 35.5516 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 30.8114 | 29.6263 | 86.67% | 83.33% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 13.5096 | 13.5096 | 35.5516 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 29.6263 | 28.4413 | 83.33% | 80% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 13.5096 | 13.5096 | 35.5516 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 28.4413 | 27.2562 | 80% | 76.67% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 13.5096 | 13.5096 | 35.5516 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 27.2562 | 26.0712 | 76.67% | 73.33% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 13.5096 | 13.5096 | 35.5516 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 26.0712 | 24.8861 | 73.33% | 70% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 13.5096 | 13.5096 | 35.5516 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 24.8861 | 23.7011 | 70% | 66.67% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 13.5096 | 13.5096 | 35.5516 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 23.7011 | 22.516 | 66.67% | 63.33% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 13.5096 | 13.5096 | 35.5516 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 22.516 | 21.331 | 63.33% | 60% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 13.5096 | 13.5096 | 35.5516 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 21.331 | 20.1459 | 60% | 56.67% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 13.5096 | 13.5096 | 35.5516 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 20.1459 | 18.9609 | 56.67% | 53.33% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 13.5096 | 13.5096 | 35.5516 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 18.9609 | 17.7758 | 53.33% | 50% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 13.5096 | 13.5096 | 35.5516 | 2024-01-01 01:00 | 2023-12-31 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 17.7758 | 16.5907 | 50% | 46.67% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 13.5096 | 13.5096 | 35.5516 | 2024-01-01 01:05 | 2023-12-31 20:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 16.5907 | 15.4057 | 46.67% | 43.33% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 13.5096 | 13.5096 | 35.5516 | 2024-01-01 01:10 | 2023-12-31 20:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 15.4057 | 14.2206 | 43.33% | 40% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 13.5096 | 13.5096 | 35.5516 | 2024-01-01 01:15 | 2023-12-31 20:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 14.2206 | 13.0356 | 40% | 36.67% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 13.5096 | 13.5096 | 35.5516 | 2024-01-01 01:20 | 2023-12-31 20:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 13.0356 | 11.8505 | 36.67% | 33.33% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 13.5096 | 13.5096 | 35.5516 | 2024-01-01 01:25 | 2023-12-31 20:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 11.8505 | 10.6655 | 33.33% | 30% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 13.5096 | 13.5096 | 35.5516 | 2024-01-01 01:30 | 2023-12-31 20:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 10.6655 | 9.4804 | 30% | 26.67% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 13.5096 | 13.5096 | 35.5516 | 2024-01-01 01:35 | 2023-12-31 20:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 9.4804 | 8.2954 | 26.67% | 23.33% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 13.5096 | 13.5096 | 35.5516 | 2024-01-01 01:40 | 2023-12-31 20:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 8.2954 | 7.1103 | 23.33% | 20% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 13.5096 | 13.5096 | 35.5516 | 2024-01-01 01:45 | 2023-12-31 20:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 7.1103 | 5.9253 | 20% | 16.67% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 13.5096 | 13.5096 | 35.5516 | 2024-01-01 01:50 | 2023-12-31 20:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 5.9253 | 4.7402 | 16.67% | 13.33% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 2 | 13.5096 | 13.5096 | 35.5516 | 2024-01-01 01:55 | 2023-12-31 20:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 4.7402 | 3.5552 | 13.33% | 10% | 3.5552 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 0 | 13.5096 | 71.1032 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 63.9929 | 62.8078 | 90% | 88.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 0 | 13.5096 | 71.1032 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 62.8078 | 61.6228 | 88.33% | 86.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 0 | 13.5096 | 71.1032 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 61.6228 | 60.4377 | 86.67% | 85% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 0 | 13.5096 | 71.1032 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 60.4377 | 59.2527 | 85% | 83.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 0 | 13.5096 | 71.1032 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 59.2527 | 58.0676 | 83.33% | 81.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 0 | 13.5096 | 71.1032 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 58.0676 | 56.8826 | 81.67% | 80% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 0 | 13.5096 | 71.1032 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 56.8826 | 55.6975 | 80% | 78.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 0 | 13.5096 | 71.1032 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 55.6975 | 54.5125 | 78.33% | 76.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 0 | 13.5096 | 71.1032 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 54.5125 | 53.3274 | 76.67% | 75% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 0 | 13.5096 | 71.1032 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 53.3274 | 52.1423 | 75% | 73.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 0 | 13.5096 | 71.1032 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 52.1423 | 50.9573 | 73.33% | 71.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 0 | 13.5096 | 71.1032 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 50.9573 | 49.7722 | 71.67% | 70% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 0 | 13.5096 | 71.1032 | 2024-01-01 01:00 | 2023-12-31 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 49.7722 | 48.5872 | 70% | 68.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 0 | 13.5096 | 71.1032 | 2024-01-01 01:05 | 2023-12-31 20:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 48.5872 | 47.4021 | 68.33% | 66.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 0 | 13.5096 | 71.1032 | 2024-01-01 01:10 | 2023-12-31 20:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 47.4021 | 46.2171 | 66.67% | 65% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 0 | 13.5096 | 71.1032 | 2024-01-01 01:15 | 2023-12-31 20:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 46.2171 | 45.032 | 65% | 63.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 0 | 13.5096 | 71.1032 | 2024-01-01 01:20 | 2023-12-31 20:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 45.032 | 43.847 | 63.33% | 61.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 0 | 13.5096 | 71.1032 | 2024-01-01 01:25 | 2023-12-31 20:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 43.847 | 42.6619 | 61.67% | 60% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 0 | 13.5096 | 71.1032 | 2024-01-01 01:30 | 2023-12-31 20:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 42.6619 | 41.4769 | 60% | 58.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 0 | 13.5096 | 71.1032 | 2024-01-01 01:35 | 2023-12-31 20:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 41.4769 | 40.2918 | 58.33% | 56.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 0 | 13.5096 | 71.1032 | 2024-01-01 01:40 | 2023-12-31 20:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 40.2918 | 39.1068 | 56.67% | 55% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 0 | 13.5096 | 71.1032 | 2024-01-01 01:45 | 2023-12-31 20:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 39.1068 | 37.9217 | 55% | 53.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 0 | 13.5096 | 71.1032 | 2024-01-01 01:50 | 2023-12-31 20:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 37.9217 | 36.7367 | 53.33% | 51.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 0 | 13.5096 | 71.1032 | 2024-01-01 01:55 | 2023-12-31 20:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 36.7367 | 35.5516 | 51.67% | 50% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 0 | 13.5096 | 71.1032 | 2024-01-01 02:00 | 2023-12-31 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 35.5516 | 34.3665 | 50% | 48.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 0 | 13.5096 | 71.1032 | 2024-01-01 02:05 | 2023-12-31 21:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 34.3665 | 33.1815 | 48.33% | 46.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 0 | 13.5096 | 71.1032 | 2024-01-01 02:10 | 2023-12-31 21:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 33.1815 | 31.9964 | 46.67% | 45% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 0 | 13.5096 | 71.1032 | 2024-01-01 02:15 | 2023-12-31 21:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 31.9964 | 30.8114 | 45% | 43.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 0 | 13.5096 | 71.1032 | 2024-01-01 02:20 | 2023-12-31 21:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 30.8114 | 29.6263 | 43.33% | 41.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 0 | 13.5096 | 71.1032 | 2024-01-01 02:25 | 2023-12-31 21:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 29.6263 | 28.4413 | 41.67% | 40% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 0 | 13.5096 | 71.1032 | 2024-01-01 02:30 | 2023-12-31 21:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 28.4413 | 27.2562 | 40% | 38.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 0 | 13.5096 | 71.1032 | 2024-01-01 02:35 | 2023-12-31 21:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 27.2562 | 26.0712 | 38.33% | 36.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 0 | 13.5096 | 71.1032 | 2024-01-01 02:40 | 2023-12-31 21:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 26.0712 | 24.8861 | 36.67% | 35% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 0 | 13.5096 | 71.1032 | 2024-01-01 02:45 | 2023-12-31 21:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 24.8861 | 23.7011 | 35% | 33.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 0 | 13.5096 | 71.1032 | 2024-01-01 02:50 | 2023-12-31 21:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 23.7011 | 22.516 | 33.33% | 31.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 0 | 13.5096 | 71.1032 | 2024-01-01 02:55 | 2023-12-31 21:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 22.516 | 21.331 | 31.67% | 30% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 0 | 13.5096 | 71.1032 | 2024-01-01 03:00 | 2023-12-31 22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 21.331 | 20.1459 | 30% | 28.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 0 | 13.5096 | 71.1032 | 2024-01-01 03:05 | 2023-12-31 22:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 20.1459 | 18.9609 | 28.33% | 26.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 0 | 13.5096 | 71.1032 | 2024-01-01 03:10 | 2023-12-31 22:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 18.9609 | 17.7758 | 26.67% | 25% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 0 | 13.5096 | 71.1032 | 2024-01-01 03:15 | 2023-12-31 22:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 17.7758 | 16.5907 | 25% | 23.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 0 | 13.5096 | 71.1032 | 2024-01-01 03:20 | 2023-12-31 22:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 16.5907 | 15.4057 | 23.33% | 21.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 0 | 13.5096 | 71.1032 | 2024-01-01 03:25 | 2023-12-31 22:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 15.4057 | 14.2206 | 21.67% | 20% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 0 | 13.5096 | 71.1032 | 2024-01-01 03:30 | 2023-12-31 22:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 14.2206 | 13.0356 | 20% | 18.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 0 | 13.5096 | 71.1032 | 2024-01-01 03:35 | 2023-12-31 22:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 13.0356 | 11.8505 | 18.33% | 16.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 0 | 13.5096 | 71.1032 | 2024-01-01 03:40 | 2023-12-31 22:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 11.8505 | 10.6655 | 16.67% | 15% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 0 | 13.5096 | 71.1032 | 2024-01-01 03:45 | 2023-12-31 22:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 10.6655 | 9.4804 | 15% | 13.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 0 | 13.5096 | 71.1032 | 2024-01-01 03:50 | 2023-12-31 22:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 9.4804 | 8.2954 | 13.33% | 11.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 0 | 13.5096 | 71.1032 | 2024-01-01 03:55 | 2023-12-31 22:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 8.2954 | 7.1103 | 11.67% | 10% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 3.3774 | 13.5096 | 71.1032 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 63.9929 | 62.8078 | 90% | 88.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 3.3774 | 13.5096 | 71.1032 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 62.8078 | 61.6228 | 88.33% | 86.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 3.3774 | 13.5096 | 71.1032 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 61.6228 | 60.4377 | 86.67% | 85% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 3.3774 | 13.5096 | 71.1032 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 60.4377 | 59.2527 | 85% | 83.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 3.3774 | 13.5096 | 71.1032 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 59.2527 | 58.0676 | 83.33% | 81.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 3.3774 | 13.5096 | 71.1032 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 58.0676 | 56.8826 | 81.67% | 80% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 3.3774 | 13.5096 | 71.1032 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 56.8826 | 55.6975 | 80% | 78.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 3.3774 | 13.5096 | 71.1032 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 55.6975 | 54.5125 | 78.33% | 76.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 3.3774 | 13.5096 | 71.1032 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 54.5125 | 53.3274 | 76.67% | 75% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 3.3774 | 13.5096 | 71.1032 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 53.3274 | 52.1423 | 75% | 73.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 3.3774 | 13.5096 | 71.1032 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 52.1423 | 50.9573 | 73.33% | 71.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 3.3774 | 13.5096 | 71.1032 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 50.9573 | 49.7722 | 71.67% | 70% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 3.3774 | 13.5096 | 71.1032 | 2024-01-01 01:00 | 2023-12-31 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 49.7722 | 48.5872 | 70% | 68.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 3.3774 | 13.5096 | 71.1032 | 2024-01-01 01:05 | 2023-12-31 20:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 48.5872 | 47.4021 | 68.33% | 66.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 3.3774 | 13.5096 | 71.1032 | 2024-01-01 01:10 | 2023-12-31 20:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 47.4021 | 46.2171 | 66.67% | 65% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 3.3774 | 13.5096 | 71.1032 | 2024-01-01 01:15 | 2023-12-31 20:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 46.2171 | 45.032 | 65% | 63.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 3.3774 | 13.5096 | 71.1032 | 2024-01-01 01:20 | 2023-12-31 20:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 45.032 | 43.847 | 63.33% | 61.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 3.3774 | 13.5096 | 71.1032 | 2024-01-01 01:25 | 2023-12-31 20:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 43.847 | 42.6619 | 61.67% | 60% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 3.3774 | 13.5096 | 71.1032 | 2024-01-01 01:30 | 2023-12-31 20:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 42.6619 | 41.4769 | 60% | 58.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 3.3774 | 13.5096 | 71.1032 | 2024-01-01 01:35 | 2023-12-31 20:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 41.4769 | 40.2918 | 58.33% | 56.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 3.3774 | 13.5096 | 71.1032 | 2024-01-01 01:40 | 2023-12-31 20:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 40.2918 | 39.1068 | 56.67% | 55% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 3.3774 | 13.5096 | 71.1032 | 2024-01-01 01:45 | 2023-12-31 20:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 39.1068 | 37.9217 | 55% | 53.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 3.3774 | 13.5096 | 71.1032 | 2024-01-01 01:50 | 2023-12-31 20:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 37.9217 | 36.7367 | 53.33% | 51.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 3.3774 | 13.5096 | 71.1032 | 2024-01-01 01:55 | 2023-12-31 20:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 36.7367 | 35.5516 | 51.67% | 50% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 3.3774 | 13.5096 | 71.1032 | 2024-01-01 02:00 | 2023-12-31 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 35.5516 | 34.3665 | 50% | 48.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 3.3774 | 13.5096 | 71.1032 | 2024-01-01 02:05 | 2023-12-31 21:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 34.3665 | 33.1815 | 48.33% | 46.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 3.3774 | 13.5096 | 71.1032 | 2024-01-01 02:10 | 2023-12-31 21:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 33.1815 | 31.9964 | 46.67% | 45% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 3.3774 | 13.5096 | 71.1032 | 2024-01-01 02:15 | 2023-12-31 21:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 31.9964 | 30.8114 | 45% | 43.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 3.3774 | 13.5096 | 71.1032 | 2024-01-01 02:20 | 2023-12-31 21:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 30.8114 | 29.6263 | 43.33% | 41.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 3.3774 | 13.5096 | 71.1032 | 2024-01-01 02:25 | 2023-12-31 21:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 29.6263 | 28.4413 | 41.67% | 40% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 3.3774 | 13.5096 | 71.1032 | 2024-01-01 02:30 | 2023-12-31 21:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 28.4413 | 27.2562 | 40% | 38.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 3.3774 | 13.5096 | 71.1032 | 2024-01-01 02:35 | 2023-12-31 21:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 27.2562 | 26.0712 | 38.33% | 36.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 3.3774 | 13.5096 | 71.1032 | 2024-01-01 02:40 | 2023-12-31 21:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 26.0712 | 24.8861 | 36.67% | 35% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 3.3774 | 13.5096 | 71.1032 | 2024-01-01 02:45 | 2023-12-31 21:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 24.8861 | 23.7011 | 35% | 33.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 3.3774 | 13.5096 | 71.1032 | 2024-01-01 02:50 | 2023-12-31 21:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 23.7011 | 22.516 | 33.33% | 31.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 3.3774 | 13.5096 | 71.1032 | 2024-01-01 02:55 | 2023-12-31 21:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 22.516 | 21.331 | 31.67% | 30% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 3.3774 | 13.5096 | 71.1032 | 2024-01-01 03:00 | 2023-12-31 22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 21.331 | 20.1459 | 30% | 28.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 3.3774 | 13.5096 | 71.1032 | 2024-01-01 03:05 | 2023-12-31 22:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 20.1459 | 18.9609 | 28.33% | 26.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 3.3774 | 13.5096 | 71.1032 | 2024-01-01 03:10 | 2023-12-31 22:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 18.9609 | 17.7758 | 26.67% | 25% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 3.3774 | 13.5096 | 71.1032 | 2024-01-01 03:15 | 2023-12-31 22:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 17.7758 | 16.5907 | 25% | 23.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 3.3774 | 13.5096 | 71.1032 | 2024-01-01 03:20 | 2023-12-31 22:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 16.5907 | 15.4057 | 23.33% | 21.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 3.3774 | 13.5096 | 71.1032 | 2024-01-01 03:25 | 2023-12-31 22:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 15.4057 | 14.2206 | 21.67% | 20% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 3.3774 | 13.5096 | 71.1032 | 2024-01-01 03:30 | 2023-12-31 22:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 14.2206 | 13.0356 | 20% | 18.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 3.3774 | 13.5096 | 71.1032 | 2024-01-01 03:35 | 2023-12-31 22:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 13.0356 | 11.8505 | 18.33% | 16.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 3.3774 | 13.5096 | 71.1032 | 2024-01-01 03:40 | 2023-12-31 22:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 11.8505 | 10.6655 | 16.67% | 15% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 3.3774 | 13.5096 | 71.1032 | 2024-01-01 03:45 | 2023-12-31 22:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 10.6655 | 9.4804 | 15% | 13.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 3.3774 | 13.5096 | 71.1032 | 2024-01-01 03:50 | 2023-12-31 22:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 9.4804 | 8.2954 | 13.33% | 11.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 3.3774 | 13.5096 | 71.1032 | 2024-01-01 03:55 | 2023-12-31 22:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 8.2954 | 7.1103 | 11.67% | 10% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 6.7548 | 13.5096 | 71.1032 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 63.9929 | 62.8078 | 90% | 88.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 6.7548 | 13.5096 | 71.1032 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 62.8078 | 61.6228 | 88.33% | 86.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 6.7548 | 13.5096 | 71.1032 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 61.6228 | 60.4377 | 86.67% | 85% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 6.7548 | 13.5096 | 71.1032 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 60.4377 | 59.2527 | 85% | 83.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 6.7548 | 13.5096 | 71.1032 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 59.2527 | 58.0676 | 83.33% | 81.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 6.7548 | 13.5096 | 71.1032 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 58.0676 | 56.8826 | 81.67% | 80% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 6.7548 | 13.5096 | 71.1032 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 56.8826 | 55.6975 | 80% | 78.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 6.7548 | 13.5096 | 71.1032 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 55.6975 | 54.5125 | 78.33% | 76.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 6.7548 | 13.5096 | 71.1032 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 54.5125 | 53.3274 | 76.67% | 75% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 6.7548 | 13.5096 | 71.1032 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 53.3274 | 52.1423 | 75% | 73.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 6.7548 | 13.5096 | 71.1032 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 52.1423 | 50.9573 | 73.33% | 71.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 6.7548 | 13.5096 | 71.1032 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 50.9573 | 49.7722 | 71.67% | 70% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 6.7548 | 13.5096 | 71.1032 | 2024-01-01 01:00 | 2023-12-31 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 49.7722 | 48.5872 | 70% | 68.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 6.7548 | 13.5096 | 71.1032 | 2024-01-01 01:05 | 2023-12-31 20:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 48.5872 | 47.4021 | 68.33% | 66.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 6.7548 | 13.5096 | 71.1032 | 2024-01-01 01:10 | 2023-12-31 20:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 47.4021 | 46.2171 | 66.67% | 65% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 6.7548 | 13.5096 | 71.1032 | 2024-01-01 01:15 | 2023-12-31 20:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 46.2171 | 45.032 | 65% | 63.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 6.7548 | 13.5096 | 71.1032 | 2024-01-01 01:20 | 2023-12-31 20:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 45.032 | 43.847 | 63.33% | 61.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 6.7548 | 13.5096 | 71.1032 | 2024-01-01 01:25 | 2023-12-31 20:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 43.847 | 42.6619 | 61.67% | 60% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 6.7548 | 13.5096 | 71.1032 | 2024-01-01 01:30 | 2023-12-31 20:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 42.6619 | 41.4769 | 60% | 58.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 6.7548 | 13.5096 | 71.1032 | 2024-01-01 01:35 | 2023-12-31 20:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 41.4769 | 40.2918 | 58.33% | 56.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 6.7548 | 13.5096 | 71.1032 | 2024-01-01 01:40 | 2023-12-31 20:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 40.2918 | 39.1068 | 56.67% | 55% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 6.7548 | 13.5096 | 71.1032 | 2024-01-01 01:45 | 2023-12-31 20:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 39.1068 | 37.9217 | 55% | 53.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 6.7548 | 13.5096 | 71.1032 | 2024-01-01 01:50 | 2023-12-31 20:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 37.9217 | 36.7367 | 53.33% | 51.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 6.7548 | 13.5096 | 71.1032 | 2024-01-01 01:55 | 2023-12-31 20:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 36.7367 | 35.5516 | 51.67% | 50% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 6.7548 | 13.5096 | 71.1032 | 2024-01-01 02:00 | 2023-12-31 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 35.5516 | 34.3665 | 50% | 48.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 6.7548 | 13.5096 | 71.1032 | 2024-01-01 02:05 | 2023-12-31 21:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 34.3665 | 33.1815 | 48.33% | 46.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 6.7548 | 13.5096 | 71.1032 | 2024-01-01 02:10 | 2023-12-31 21:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 33.1815 | 31.9964 | 46.67% | 45% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 6.7548 | 13.5096 | 71.1032 | 2024-01-01 02:15 | 2023-12-31 21:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 31.9964 | 30.8114 | 45% | 43.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 6.7548 | 13.5096 | 71.1032 | 2024-01-01 02:20 | 2023-12-31 21:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 30.8114 | 29.6263 | 43.33% | 41.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 6.7548 | 13.5096 | 71.1032 | 2024-01-01 02:25 | 2023-12-31 21:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 29.6263 | 28.4413 | 41.67% | 40% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 6.7548 | 13.5096 | 71.1032 | 2024-01-01 02:30 | 2023-12-31 21:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 28.4413 | 27.2562 | 40% | 38.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 6.7548 | 13.5096 | 71.1032 | 2024-01-01 02:35 | 2023-12-31 21:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 27.2562 | 26.0712 | 38.33% | 36.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 6.7548 | 13.5096 | 71.1032 | 2024-01-01 02:40 | 2023-12-31 21:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 26.0712 | 24.8861 | 36.67% | 35% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 6.7548 | 13.5096 | 71.1032 | 2024-01-01 02:45 | 2023-12-31 21:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 24.8861 | 23.7011 | 35% | 33.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 6.7548 | 13.5096 | 71.1032 | 2024-01-01 02:50 | 2023-12-31 21:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 23.7011 | 22.516 | 33.33% | 31.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 6.7548 | 13.5096 | 71.1032 | 2024-01-01 02:55 | 2023-12-31 21:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 22.516 | 21.331 | 31.67% | 30% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 6.7548 | 13.5096 | 71.1032 | 2024-01-01 03:00 | 2023-12-31 22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 21.331 | 20.1459 | 30% | 28.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 6.7548 | 13.5096 | 71.1032 | 2024-01-01 03:05 | 2023-12-31 22:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 20.1459 | 18.9609 | 28.33% | 26.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 6.7548 | 13.5096 | 71.1032 | 2024-01-01 03:10 | 2023-12-31 22:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 18.9609 | 17.7758 | 26.67% | 25% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 6.7548 | 13.5096 | 71.1032 | 2024-01-01 03:15 | 2023-12-31 22:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 17.7758 | 16.5907 | 25% | 23.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 6.7548 | 13.5096 | 71.1032 | 2024-01-01 03:20 | 2023-12-31 22:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 16.5907 | 15.4057 | 23.33% | 21.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 6.7548 | 13.5096 | 71.1032 | 2024-01-01 03:25 | 2023-12-31 22:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 15.4057 | 14.2206 | 21.67% | 20% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 6.7548 | 13.5096 | 71.1032 | 2024-01-01 03:30 | 2023-12-31 22:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 14.2206 | 13.0356 | 20% | 18.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 6.7548 | 13.5096 | 71.1032 | 2024-01-01 03:35 | 2023-12-31 22:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 13.0356 | 11.8505 | 18.33% | 16.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 6.7548 | 13.5096 | 71.1032 | 2024-01-01 03:40 | 2023-12-31 22:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 11.8505 | 10.6655 | 16.67% | 15% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 6.7548 | 13.5096 | 71.1032 | 2024-01-01 03:45 | 2023-12-31 22:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 10.6655 | 9.4804 | 15% | 13.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 6.7548 | 13.5096 | 71.1032 | 2024-01-01 03:50 | 2023-12-31 22:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 9.4804 | 8.2954 | 13.33% | 11.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 6.7548 | 13.5096 | 71.1032 | 2024-01-01 03:55 | 2023-12-31 22:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 8.2954 | 7.1103 | 11.67% | 10% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 10.1322 | 13.5096 | 71.1032 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 63.9929 | 62.8078 | 90% | 88.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 10.1322 | 13.5096 | 71.1032 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 62.8078 | 61.6228 | 88.33% | 86.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 10.1322 | 13.5096 | 71.1032 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 61.6228 | 60.4377 | 86.67% | 85% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 10.1322 | 13.5096 | 71.1032 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 60.4377 | 59.2527 | 85% | 83.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 10.1322 | 13.5096 | 71.1032 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 59.2527 | 58.0676 | 83.33% | 81.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 10.1322 | 13.5096 | 71.1032 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 58.0676 | 56.8826 | 81.67% | 80% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 10.1322 | 13.5096 | 71.1032 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 56.8826 | 55.6975 | 80% | 78.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 10.1322 | 13.5096 | 71.1032 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 55.6975 | 54.5125 | 78.33% | 76.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 10.1322 | 13.5096 | 71.1032 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 54.5125 | 53.3274 | 76.67% | 75% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 10.1322 | 13.5096 | 71.1032 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 53.3274 | 52.1423 | 75% | 73.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 10.1322 | 13.5096 | 71.1032 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 52.1423 | 50.9573 | 73.33% | 71.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 10.1322 | 13.5096 | 71.1032 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 50.9573 | 49.7722 | 71.67% | 70% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 10.1322 | 13.5096 | 71.1032 | 2024-01-01 01:00 | 2023-12-31 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 49.7722 | 48.5872 | 70% | 68.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 10.1322 | 13.5096 | 71.1032 | 2024-01-01 01:05 | 2023-12-31 20:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 48.5872 | 47.4021 | 68.33% | 66.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 10.1322 | 13.5096 | 71.1032 | 2024-01-01 01:10 | 2023-12-31 20:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 47.4021 | 46.2171 | 66.67% | 65% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 10.1322 | 13.5096 | 71.1032 | 2024-01-01 01:15 | 2023-12-31 20:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 46.2171 | 45.032 | 65% | 63.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 10.1322 | 13.5096 | 71.1032 | 2024-01-01 01:20 | 2023-12-31 20:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 45.032 | 43.847 | 63.33% | 61.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 10.1322 | 13.5096 | 71.1032 | 2024-01-01 01:25 | 2023-12-31 20:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 43.847 | 42.6619 | 61.67% | 60% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 10.1322 | 13.5096 | 71.1032 | 2024-01-01 01:30 | 2023-12-31 20:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 42.6619 | 41.4769 | 60% | 58.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 10.1322 | 13.5096 | 71.1032 | 2024-01-01 01:35 | 2023-12-31 20:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 41.4769 | 40.2918 | 58.33% | 56.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 10.1322 | 13.5096 | 71.1032 | 2024-01-01 01:40 | 2023-12-31 20:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 40.2918 | 39.1068 | 56.67% | 55% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 10.1322 | 13.5096 | 71.1032 | 2024-01-01 01:45 | 2023-12-31 20:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 39.1068 | 37.9217 | 55% | 53.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 10.1322 | 13.5096 | 71.1032 | 2024-01-01 01:50 | 2023-12-31 20:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 37.9217 | 36.7367 | 53.33% | 51.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 10.1322 | 13.5096 | 71.1032 | 2024-01-01 01:55 | 2023-12-31 20:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 36.7367 | 35.5516 | 51.67% | 50% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 10.1322 | 13.5096 | 71.1032 | 2024-01-01 02:00 | 2023-12-31 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 35.5516 | 34.3665 | 50% | 48.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 10.1322 | 13.5096 | 71.1032 | 2024-01-01 02:05 | 2023-12-31 21:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 34.3665 | 33.1815 | 48.33% | 46.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 10.1322 | 13.5096 | 71.1032 | 2024-01-01 02:10 | 2023-12-31 21:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 33.1815 | 31.9964 | 46.67% | 45% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 10.1322 | 13.5096 | 71.1032 | 2024-01-01 02:15 | 2023-12-31 21:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 31.9964 | 30.8114 | 45% | 43.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 10.1322 | 13.5096 | 71.1032 | 2024-01-01 02:20 | 2023-12-31 21:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 30.8114 | 29.6263 | 43.33% | 41.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 10.1322 | 13.5096 | 71.1032 | 2024-01-01 02:25 | 2023-12-31 21:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 29.6263 | 28.4413 | 41.67% | 40% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 10.1322 | 13.5096 | 71.1032 | 2024-01-01 02:30 | 2023-12-31 21:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 28.4413 | 27.2562 | 40% | 38.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 10.1322 | 13.5096 | 71.1032 | 2024-01-01 02:35 | 2023-12-31 21:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 27.2562 | 26.0712 | 38.33% | 36.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 10.1322 | 13.5096 | 71.1032 | 2024-01-01 02:40 | 2023-12-31 21:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 26.0712 | 24.8861 | 36.67% | 35% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 10.1322 | 13.5096 | 71.1032 | 2024-01-01 02:45 | 2023-12-31 21:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 24.8861 | 23.7011 | 35% | 33.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 10.1322 | 13.5096 | 71.1032 | 2024-01-01 02:50 | 2023-12-31 21:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 23.7011 | 22.516 | 33.33% | 31.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 10.1322 | 13.5096 | 71.1032 | 2024-01-01 02:55 | 2023-12-31 21:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 22.516 | 21.331 | 31.67% | 30% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 10.1322 | 13.5096 | 71.1032 | 2024-01-01 03:00 | 2023-12-31 22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 21.331 | 20.1459 | 30% | 28.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 10.1322 | 13.5096 | 71.1032 | 2024-01-01 03:05 | 2023-12-31 22:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 20.1459 | 18.9609 | 28.33% | 26.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 10.1322 | 13.5096 | 71.1032 | 2024-01-01 03:10 | 2023-12-31 22:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 18.9609 | 17.7758 | 26.67% | 25% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 10.1322 | 13.5096 | 71.1032 | 2024-01-01 03:15 | 2023-12-31 22:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 17.7758 | 16.5907 | 25% | 23.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 10.1322 | 13.5096 | 71.1032 | 2024-01-01 03:20 | 2023-12-31 22:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 16.5907 | 15.4057 | 23.33% | 21.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 10.1322 | 13.5096 | 71.1032 | 2024-01-01 03:25 | 2023-12-31 22:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 15.4057 | 14.2206 | 21.67% | 20% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 10.1322 | 13.5096 | 71.1032 | 2024-01-01 03:30 | 2023-12-31 22:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 14.2206 | 13.0356 | 20% | 18.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 10.1322 | 13.5096 | 71.1032 | 2024-01-01 03:35 | 2023-12-31 22:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 13.0356 | 11.8505 | 18.33% | 16.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 10.1322 | 13.5096 | 71.1032 | 2024-01-01 03:40 | 2023-12-31 22:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 11.8505 | 10.6655 | 16.67% | 15% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 10.1322 | 13.5096 | 71.1032 | 2024-01-01 03:45 | 2023-12-31 22:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 10.6655 | 9.4804 | 15% | 13.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 10.1322 | 13.5096 | 71.1032 | 2024-01-01 03:50 | 2023-12-31 22:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 9.4804 | 8.2954 | 13.33% | 11.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 10.1322 | 13.5096 | 71.1032 | 2024-01-01 03:55 | 2023-12-31 22:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 8.2954 | 7.1103 | 11.67% | 10% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 13.5096 | 13.5096 | 71.1032 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 63.9929 | 62.8078 | 90% | 88.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 13.5096 | 13.5096 | 71.1032 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 62.8078 | 61.6228 | 88.33% | 86.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 13.5096 | 13.5096 | 71.1032 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 61.6228 | 60.4377 | 86.67% | 85% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 13.5096 | 13.5096 | 71.1032 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 60.4377 | 59.2527 | 85% | 83.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 13.5096 | 13.5096 | 71.1032 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 59.2527 | 58.0676 | 83.33% | 81.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 13.5096 | 13.5096 | 71.1032 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 58.0676 | 56.8826 | 81.67% | 80% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 13.5096 | 13.5096 | 71.1032 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 56.8826 | 55.6975 | 80% | 78.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 13.5096 | 13.5096 | 71.1032 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 55.6975 | 54.5125 | 78.33% | 76.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 13.5096 | 13.5096 | 71.1032 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 54.5125 | 53.3274 | 76.67% | 75% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 13.5096 | 13.5096 | 71.1032 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 53.3274 | 52.1423 | 75% | 73.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 13.5096 | 13.5096 | 71.1032 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 52.1423 | 50.9573 | 73.33% | 71.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 13.5096 | 13.5096 | 71.1032 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 50.9573 | 49.7722 | 71.67% | 70% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 13.5096 | 13.5096 | 71.1032 | 2024-01-01 01:00 | 2023-12-31 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 49.7722 | 48.5872 | 70% | 68.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 13.5096 | 13.5096 | 71.1032 | 2024-01-01 01:05 | 2023-12-31 20:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 48.5872 | 47.4021 | 68.33% | 66.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 13.5096 | 13.5096 | 71.1032 | 2024-01-01 01:10 | 2023-12-31 20:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 47.4021 | 46.2171 | 66.67% | 65% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 13.5096 | 13.5096 | 71.1032 | 2024-01-01 01:15 | 2023-12-31 20:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 46.2171 | 45.032 | 65% | 63.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 13.5096 | 13.5096 | 71.1032 | 2024-01-01 01:20 | 2023-12-31 20:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 45.032 | 43.847 | 63.33% | 61.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 13.5096 | 13.5096 | 71.1032 | 2024-01-01 01:25 | 2023-12-31 20:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 43.847 | 42.6619 | 61.67% | 60% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 13.5096 | 13.5096 | 71.1032 | 2024-01-01 01:30 | 2023-12-31 20:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 42.6619 | 41.4769 | 60% | 58.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 13.5096 | 13.5096 | 71.1032 | 2024-01-01 01:35 | 2023-12-31 20:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 41.4769 | 40.2918 | 58.33% | 56.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 13.5096 | 13.5096 | 71.1032 | 2024-01-01 01:40 | 2023-12-31 20:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 40.2918 | 39.1068 | 56.67% | 55% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 13.5096 | 13.5096 | 71.1032 | 2024-01-01 01:45 | 2023-12-31 20:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 39.1068 | 37.9217 | 55% | 53.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 13.5096 | 13.5096 | 71.1032 | 2024-01-01 01:50 | 2023-12-31 20:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 37.9217 | 36.7367 | 53.33% | 51.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 13.5096 | 13.5096 | 71.1032 | 2024-01-01 01:55 | 2023-12-31 20:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 36.7367 | 35.5516 | 51.67% | 50% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 13.5096 | 13.5096 | 71.1032 | 2024-01-01 02:00 | 2023-12-31 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 35.5516 | 34.3665 | 50% | 48.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 13.5096 | 13.5096 | 71.1032 | 2024-01-01 02:05 | 2023-12-31 21:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 34.3665 | 33.1815 | 48.33% | 46.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 13.5096 | 13.5096 | 71.1032 | 2024-01-01 02:10 | 2023-12-31 21:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 33.1815 | 31.9964 | 46.67% | 45% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 13.5096 | 13.5096 | 71.1032 | 2024-01-01 02:15 | 2023-12-31 21:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 31.9964 | 30.8114 | 45% | 43.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 13.5096 | 13.5096 | 71.1032 | 2024-01-01 02:20 | 2023-12-31 21:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 30.8114 | 29.6263 | 43.33% | 41.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 13.5096 | 13.5096 | 71.1032 | 2024-01-01 02:25 | 2023-12-31 21:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 29.6263 | 28.4413 | 41.67% | 40% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 13.5096 | 13.5096 | 71.1032 | 2024-01-01 02:30 | 2023-12-31 21:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 28.4413 | 27.2562 | 40% | 38.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 13.5096 | 13.5096 | 71.1032 | 2024-01-01 02:35 | 2023-12-31 21:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 27.2562 | 26.0712 | 38.33% | 36.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 13.5096 | 13.5096 | 71.1032 | 2024-01-01 02:40 | 2023-12-31 21:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 26.0712 | 24.8861 | 36.67% | 35% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 13.5096 | 13.5096 | 71.1032 | 2024-01-01 02:45 | 2023-12-31 21:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 24.8861 | 23.7011 | 35% | 33.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 13.5096 | 13.5096 | 71.1032 | 2024-01-01 02:50 | 2023-12-31 21:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 23.7011 | 22.516 | 33.33% | 31.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 13.5096 | 13.5096 | 71.1032 | 2024-01-01 02:55 | 2023-12-31 21:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 22.516 | 21.331 | 31.67% | 30% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 13.5096 | 13.5096 | 71.1032 | 2024-01-01 03:00 | 2023-12-31 22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 21.331 | 20.1459 | 30% | 28.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 13.5096 | 13.5096 | 71.1032 | 2024-01-01 03:05 | 2023-12-31 22:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 20.1459 | 18.9609 | 28.33% | 26.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 13.5096 | 13.5096 | 71.1032 | 2024-01-01 03:10 | 2023-12-31 22:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 18.9609 | 17.7758 | 26.67% | 25% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 13.5096 | 13.5096 | 71.1032 | 2024-01-01 03:15 | 2023-12-31 22:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 17.7758 | 16.5907 | 25% | 23.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 13.5096 | 13.5096 | 71.1032 | 2024-01-01 03:20 | 2023-12-31 22:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 16.5907 | 15.4057 | 23.33% | 21.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 13.5096 | 13.5096 | 71.1032 | 2024-01-01 03:25 | 2023-12-31 22:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 15.4057 | 14.2206 | 21.67% | 20% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 13.5096 | 13.5096 | 71.1032 | 2024-01-01 03:30 | 2023-12-31 22:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 14.2206 | 13.0356 | 20% | 18.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 13.5096 | 13.5096 | 71.1032 | 2024-01-01 03:35 | 2023-12-31 22:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 13.0356 | 11.8505 | 18.33% | 16.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 13.5096 | 13.5096 | 71.1032 | 2024-01-01 03:40 | 2023-12-31 22:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 11.8505 | 10.6655 | 16.67% | 15% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 13.5096 | 13.5096 | 71.1032 | 2024-01-01 03:45 | 2023-12-31 22:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 10.6655 | 9.4804 | 15% | 13.33% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 13.5096 | 13.5096 | 71.1032 | 2024-01-01 03:50 | 2023-12-31 22:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 9.4804 | 8.2954 | 13.33% | 11.67% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 4 | 13.5096 | 13.5096 | 71.1032 | 2024-01-01 03:55 | 2023-12-31 22:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 8.2954 | 7.1103 | 11.67% | 10% | 7.1103 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 127.9858 | 126.8007 | 90% | 89.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 126.8007 | 125.6157 | 89.17% | 88.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 125.6157 | 124.4306 | 88.33% | 87.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 124.4306 | 123.2455 | 87.5% | 86.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 123.2455 | 122.0605 | 86.67% | 85.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 122.0605 | 120.8754 | 85.83% | 85% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 120.8754 | 119.6904 | 85% | 84.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 119.6904 | 118.5053 | 84.17% | 83.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 118.5053 | 117.3203 | 83.33% | 82.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 117.3203 | 116.1352 | 82.5% | 81.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 116.1352 | 114.9502 | 81.67% | 80.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 114.9502 | 113.7651 | 80.83% | 80% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 01:00 | 2023-12-31 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 113.7651 | 112.5801 | 80% | 79.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 01:05 | 2023-12-31 20:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 112.5801 | 111.395 | 79.17% | 78.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 01:10 | 2023-12-31 20:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 111.395 | 110.21 | 78.33% | 77.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 01:15 | 2023-12-31 20:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 110.21 | 109.0249 | 77.5% | 76.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 01:20 | 2023-12-31 20:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 109.0249 | 107.8399 | 76.67% | 75.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 01:25 | 2023-12-31 20:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 107.8399 | 106.6548 | 75.83% | 75% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 01:30 | 2023-12-31 20:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 106.6548 | 105.4697 | 75% | 74.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 01:35 | 2023-12-31 20:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 105.4697 | 104.2847 | 74.17% | 73.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 01:40 | 2023-12-31 20:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 104.2847 | 103.0996 | 73.33% | 72.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 01:45 | 2023-12-31 20:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 103.0996 | 101.9146 | 72.5% | 71.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 01:50 | 2023-12-31 20:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 101.9146 | 100.7295 | 71.67% | 70.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 01:55 | 2023-12-31 20:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 100.7295 | 99.5445 | 70.83% | 70% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 02:00 | 2023-12-31 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 99.5445 | 98.3594 | 70% | 69.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 02:05 | 2023-12-31 21:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 98.3594 | 97.1744 | 69.17% | 68.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 02:10 | 2023-12-31 21:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 97.1744 | 95.9893 | 68.33% | 67.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 02:15 | 2023-12-31 21:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 95.9893 | 94.8043 | 67.5% | 66.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 02:20 | 2023-12-31 21:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 94.8043 | 93.6192 | 66.67% | 65.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 02:25 | 2023-12-31 21:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 93.6192 | 92.4342 | 65.83% | 65% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 02:30 | 2023-12-31 21:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 92.4342 | 91.2491 | 65% | 64.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 02:35 | 2023-12-31 21:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 91.2491 | 90.0641 | 64.17% | 63.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 02:40 | 2023-12-31 21:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 90.0641 | 88.879 | 63.33% | 62.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 02:45 | 2023-12-31 21:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 88.879 | 87.6939 | 62.5% | 61.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 02:50 | 2023-12-31 21:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 87.6939 | 86.5089 | 61.67% | 60.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 02:55 | 2023-12-31 21:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 86.5089 | 85.3238 | 60.83% | 60% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 03:00 | 2023-12-31 22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 85.3238 | 84.1388 | 60% | 59.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 03:05 | 2023-12-31 22:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 84.1388 | 82.9537 | 59.17% | 58.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 03:10 | 2023-12-31 22:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 82.9537 | 81.7687 | 58.33% | 57.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 03:15 | 2023-12-31 22:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 81.7687 | 80.5836 | 57.5% | 56.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 03:20 | 2023-12-31 22:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 80.5836 | 79.3986 | 56.67% | 55.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 03:25 | 2023-12-31 22:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 79.3986 | 78.2135 | 55.83% | 55% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 03:30 | 2023-12-31 22:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 78.2135 | 77.0285 | 55% | 54.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 03:35 | 2023-12-31 22:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 77.0285 | 75.8434 | 54.17% | 53.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 03:40 | 2023-12-31 22:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 75.8434 | 74.6584 | 53.33% | 52.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 03:45 | 2023-12-31 22:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 74.6584 | 73.4733 | 52.5% | 51.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 03:50 | 2023-12-31 22:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 73.4733 | 72.2883 | 51.67% | 50.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 03:55 | 2023-12-31 22:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 72.2883 | 71.1032 | 50.83% | 50% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 04:00 | 2023-12-31 23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 71.1032 | 69.9181 | 50% | 49.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 04:05 | 2023-12-31 23:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 69.9181 | 68.7331 | 49.17% | 48.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 04:10 | 2023-12-31 23:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 68.7331 | 67.548 | 48.33% | 47.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 04:15 | 2023-12-31 23:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 67.548 | 66.363 | 47.5% | 46.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 04:20 | 2023-12-31 23:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 66.363 | 65.1779 | 46.67% | 45.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 04:25 | 2023-12-31 23:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 65.1779 | 63.9929 | 45.83% | 45% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 04:30 | 2023-12-31 23:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 63.9929 | 62.8078 | 45% | 44.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 04:35 | 2023-12-31 23:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 62.8078 | 61.6228 | 44.17% | 43.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 04:40 | 2023-12-31 23:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 61.6228 | 60.4377 | 43.33% | 42.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 04:45 | 2023-12-31 23:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 60.4377 | 59.2527 | 42.5% | 41.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 04:50 | 2023-12-31 23:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 59.2527 | 58.0676 | 41.67% | 40.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 04:55 | 2023-12-31 23:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 58.0676 | 56.8826 | 40.83% | 40% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 05:00 | 2024-01-01 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 56.8826 | 55.6975 | 40% | 39.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 05:05 | 2024-01-01 00:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 55.6975 | 54.5125 | 39.17% | 38.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 05:10 | 2024-01-01 00:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 54.5125 | 53.3274 | 38.33% | 37.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 05:15 | 2024-01-01 00:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 53.3274 | 52.1423 | 37.5% | 36.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 05:20 | 2024-01-01 00:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 52.1423 | 50.9573 | 36.67% | 35.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 05:25 | 2024-01-01 00:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 50.9573 | 49.7722 | 35.83% | 35% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 05:30 | 2024-01-01 00:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 49.7722 | 48.5872 | 35% | 34.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 05:35 | 2024-01-01 00:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 48.5872 | 47.4021 | 34.17% | 33.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 05:40 | 2024-01-01 00:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 47.4021 | 46.2171 | 33.33% | 32.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 05:45 | 2024-01-01 00:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 46.2171 | 45.032 | 32.5% | 31.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 05:50 | 2024-01-01 00:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 45.032 | 43.847 | 31.67% | 30.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 05:55 | 2024-01-01 00:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 43.847 | 42.6619 | 30.83% | 30% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 06:00 | 2024-01-01 01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 42.6619 | 41.4769 | 30% | 29.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 06:05 | 2024-01-01 01:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 41.4769 | 40.2918 | 29.17% | 28.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 06:10 | 2024-01-01 01:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 40.2918 | 39.1068 | 28.33% | 27.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 06:15 | 2024-01-01 01:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 39.1068 | 37.9217 | 27.5% | 26.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 06:20 | 2024-01-01 01:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 37.9217 | 36.7367 | 26.67% | 25.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 06:25 | 2024-01-01 01:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 36.7367 | 35.5516 | 25.83% | 25% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 06:30 | 2024-01-01 01:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 35.5516 | 34.3665 | 25% | 24.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 06:35 | 2024-01-01 01:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 34.3665 | 33.1815 | 24.17% | 23.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 06:40 | 2024-01-01 01:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 33.1815 | 31.9964 | 23.33% | 22.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 06:45 | 2024-01-01 01:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 31.9964 | 30.8114 | 22.5% | 21.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 06:50 | 2024-01-01 01:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 30.8114 | 29.6263 | 21.67% | 20.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 06:55 | 2024-01-01 01:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 29.6263 | 28.4413 | 20.83% | 20% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 07:00 | 2024-01-01 02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 28.4413 | 27.2562 | 20% | 19.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 07:05 | 2024-01-01 02:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 27.2562 | 26.0712 | 19.17% | 18.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 07:10 | 2024-01-01 02:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 26.0712 | 24.8861 | 18.33% | 17.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 07:15 | 2024-01-01 02:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 24.8861 | 23.7011 | 17.5% | 16.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 07:20 | 2024-01-01 02:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 23.7011 | 22.516 | 16.67% | 15.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 07:25 | 2024-01-01 02:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 22.516 | 21.331 | 15.83% | 15% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 07:30 | 2024-01-01 02:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 21.331 | 20.1459 | 15% | 14.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 07:35 | 2024-01-01 02:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 20.1459 | 18.9609 | 14.17% | 13.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 07:40 | 2024-01-01 02:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 18.9609 | 17.7758 | 13.33% | 12.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 07:45 | 2024-01-01 02:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 17.7758 | 16.5907 | 12.5% | 11.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 07:50 | 2024-01-01 02:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 16.5907 | 15.4057 | 11.67% | 10.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 0 | 13.5096 | 142.2064 | 2024-01-01 07:55 | 2024-01-01 02:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 15.4057 | 14.2206 | 10.83% | 10% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 127.9858 | 126.8007 | 90% | 89.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 126.8007 | 125.6157 | 89.17% | 88.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 125.6157 | 124.4306 | 88.33% | 87.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 124.4306 | 123.2455 | 87.5% | 86.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 123.2455 | 122.0605 | 86.67% | 85.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 122.0605 | 120.8754 | 85.83% | 85% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 120.8754 | 119.6904 | 85% | 84.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 119.6904 | 118.5053 | 84.17% | 83.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 118.5053 | 117.3203 | 83.33% | 82.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 117.3203 | 116.1352 | 82.5% | 81.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 116.1352 | 114.9502 | 81.67% | 80.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 114.9502 | 113.7651 | 80.83% | 80% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 01:00 | 2023-12-31 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 113.7651 | 112.5801 | 80% | 79.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 01:05 | 2023-12-31 20:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 112.5801 | 111.395 | 79.17% | 78.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 01:10 | 2023-12-31 20:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 111.395 | 110.21 | 78.33% | 77.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 01:15 | 2023-12-31 20:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 110.21 | 109.0249 | 77.5% | 76.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 01:20 | 2023-12-31 20:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 109.0249 | 107.8399 | 76.67% | 75.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 01:25 | 2023-12-31 20:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 107.8399 | 106.6548 | 75.83% | 75% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 01:30 | 2023-12-31 20:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 106.6548 | 105.4697 | 75% | 74.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 01:35 | 2023-12-31 20:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 105.4697 | 104.2847 | 74.17% | 73.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 01:40 | 2023-12-31 20:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 104.2847 | 103.0996 | 73.33% | 72.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 01:45 | 2023-12-31 20:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 103.0996 | 101.9146 | 72.5% | 71.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 01:50 | 2023-12-31 20:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 101.9146 | 100.7295 | 71.67% | 70.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 01:55 | 2023-12-31 20:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 100.7295 | 99.5445 | 70.83% | 70% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 02:00 | 2023-12-31 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 99.5445 | 98.3594 | 70% | 69.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 02:05 | 2023-12-31 21:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 98.3594 | 97.1744 | 69.17% | 68.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 02:10 | 2023-12-31 21:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 97.1744 | 95.9893 | 68.33% | 67.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 02:15 | 2023-12-31 21:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 95.9893 | 94.8043 | 67.5% | 66.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 02:20 | 2023-12-31 21:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 94.8043 | 93.6192 | 66.67% | 65.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 02:25 | 2023-12-31 21:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 93.6192 | 92.4342 | 65.83% | 65% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 02:30 | 2023-12-31 21:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 92.4342 | 91.2491 | 65% | 64.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 02:35 | 2023-12-31 21:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 91.2491 | 90.0641 | 64.17% | 63.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 02:40 | 2023-12-31 21:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 90.0641 | 88.879 | 63.33% | 62.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 02:45 | 2023-12-31 21:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 88.879 | 87.6939 | 62.5% | 61.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 02:50 | 2023-12-31 21:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 87.6939 | 86.5089 | 61.67% | 60.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 02:55 | 2023-12-31 21:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 86.5089 | 85.3238 | 60.83% | 60% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 03:00 | 2023-12-31 22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 85.3238 | 84.1388 | 60% | 59.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 03:05 | 2023-12-31 22:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 84.1388 | 82.9537 | 59.17% | 58.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 03:10 | 2023-12-31 22:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 82.9537 | 81.7687 | 58.33% | 57.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 03:15 | 2023-12-31 22:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 81.7687 | 80.5836 | 57.5% | 56.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 03:20 | 2023-12-31 22:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 80.5836 | 79.3986 | 56.67% | 55.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 03:25 | 2023-12-31 22:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 79.3986 | 78.2135 | 55.83% | 55% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 03:30 | 2023-12-31 22:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 78.2135 | 77.0285 | 55% | 54.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 03:35 | 2023-12-31 22:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 77.0285 | 75.8434 | 54.17% | 53.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 03:40 | 2023-12-31 22:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 75.8434 | 74.6584 | 53.33% | 52.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 03:45 | 2023-12-31 22:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 74.6584 | 73.4733 | 52.5% | 51.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 03:50 | 2023-12-31 22:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 73.4733 | 72.2883 | 51.67% | 50.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 03:55 | 2023-12-31 22:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 72.2883 | 71.1032 | 50.83% | 50% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 04:00 | 2023-12-31 23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 71.1032 | 69.9181 | 50% | 49.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 04:05 | 2023-12-31 23:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 69.9181 | 68.7331 | 49.17% | 48.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 04:10 | 2023-12-31 23:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 68.7331 | 67.548 | 48.33% | 47.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 04:15 | 2023-12-31 23:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 67.548 | 66.363 | 47.5% | 46.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 04:20 | 2023-12-31 23:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 66.363 | 65.1779 | 46.67% | 45.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 04:25 | 2023-12-31 23:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 65.1779 | 63.9929 | 45.83% | 45% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 04:30 | 2023-12-31 23:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 63.9929 | 62.8078 | 45% | 44.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 04:35 | 2023-12-31 23:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 62.8078 | 61.6228 | 44.17% | 43.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 04:40 | 2023-12-31 23:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 61.6228 | 60.4377 | 43.33% | 42.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 04:45 | 2023-12-31 23:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 60.4377 | 59.2527 | 42.5% | 41.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 04:50 | 2023-12-31 23:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 59.2527 | 58.0676 | 41.67% | 40.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 04:55 | 2023-12-31 23:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 58.0676 | 56.8826 | 40.83% | 40% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 05:00 | 2024-01-01 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 56.8826 | 55.6975 | 40% | 39.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 05:05 | 2024-01-01 00:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 55.6975 | 54.5125 | 39.17% | 38.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 05:10 | 2024-01-01 00:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 54.5125 | 53.3274 | 38.33% | 37.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 05:15 | 2024-01-01 00:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 53.3274 | 52.1423 | 37.5% | 36.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 05:20 | 2024-01-01 00:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 52.1423 | 50.9573 | 36.67% | 35.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 05:25 | 2024-01-01 00:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 50.9573 | 49.7722 | 35.83% | 35% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 05:30 | 2024-01-01 00:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 49.7722 | 48.5872 | 35% | 34.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 05:35 | 2024-01-01 00:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 48.5872 | 47.4021 | 34.17% | 33.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 05:40 | 2024-01-01 00:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 47.4021 | 46.2171 | 33.33% | 32.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 05:45 | 2024-01-01 00:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 46.2171 | 45.032 | 32.5% | 31.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 05:50 | 2024-01-01 00:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 45.032 | 43.847 | 31.67% | 30.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 05:55 | 2024-01-01 00:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 43.847 | 42.6619 | 30.83% | 30% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 06:00 | 2024-01-01 01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 42.6619 | 41.4769 | 30% | 29.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 06:05 | 2024-01-01 01:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 41.4769 | 40.2918 | 29.17% | 28.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 06:10 | 2024-01-01 01:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 40.2918 | 39.1068 | 28.33% | 27.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 06:15 | 2024-01-01 01:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 39.1068 | 37.9217 | 27.5% | 26.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 06:20 | 2024-01-01 01:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 37.9217 | 36.7367 | 26.67% | 25.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 06:25 | 2024-01-01 01:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 36.7367 | 35.5516 | 25.83% | 25% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 06:30 | 2024-01-01 01:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 35.5516 | 34.3665 | 25% | 24.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 06:35 | 2024-01-01 01:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 34.3665 | 33.1815 | 24.17% | 23.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 06:40 | 2024-01-01 01:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 33.1815 | 31.9964 | 23.33% | 22.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 06:45 | 2024-01-01 01:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 31.9964 | 30.8114 | 22.5% | 21.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 06:50 | 2024-01-01 01:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 30.8114 | 29.6263 | 21.67% | 20.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 06:55 | 2024-01-01 01:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 29.6263 | 28.4413 | 20.83% | 20% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 07:00 | 2024-01-01 02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 28.4413 | 27.2562 | 20% | 19.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 07:05 | 2024-01-01 02:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 27.2562 | 26.0712 | 19.17% | 18.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 07:10 | 2024-01-01 02:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 26.0712 | 24.8861 | 18.33% | 17.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 07:15 | 2024-01-01 02:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 24.8861 | 23.7011 | 17.5% | 16.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 07:20 | 2024-01-01 02:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 23.7011 | 22.516 | 16.67% | 15.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 07:25 | 2024-01-01 02:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 22.516 | 21.331 | 15.83% | 15% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 07:30 | 2024-01-01 02:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 21.331 | 20.1459 | 15% | 14.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 07:35 | 2024-01-01 02:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 20.1459 | 18.9609 | 14.17% | 13.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 07:40 | 2024-01-01 02:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 18.9609 | 17.7758 | 13.33% | 12.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 07:45 | 2024-01-01 02:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 17.7758 | 16.5907 | 12.5% | 11.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 07:50 | 2024-01-01 02:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 16.5907 | 15.4057 | 11.67% | 10.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 3.3774 | 13.5096 | 142.2064 | 2024-01-01 07:55 | 2024-01-01 02:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 15.4057 | 14.2206 | 10.83% | 10% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 127.9858 | 126.8007 | 90% | 89.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 126.8007 | 125.6157 | 89.17% | 88.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 125.6157 | 124.4306 | 88.33% | 87.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 124.4306 | 123.2455 | 87.5% | 86.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 123.2455 | 122.0605 | 86.67% | 85.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 122.0605 | 120.8754 | 85.83% | 85% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 120.8754 | 119.6904 | 85% | 84.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 119.6904 | 118.5053 | 84.17% | 83.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 118.5053 | 117.3203 | 83.33% | 82.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 117.3203 | 116.1352 | 82.5% | 81.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 116.1352 | 114.9502 | 81.67% | 80.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 114.9502 | 113.7651 | 80.83% | 80% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 01:00 | 2023-12-31 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 113.7651 | 112.5801 | 80% | 79.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 01:05 | 2023-12-31 20:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 112.5801 | 111.395 | 79.17% | 78.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 01:10 | 2023-12-31 20:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 111.395 | 110.21 | 78.33% | 77.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 01:15 | 2023-12-31 20:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 110.21 | 109.0249 | 77.5% | 76.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 01:20 | 2023-12-31 20:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 109.0249 | 107.8399 | 76.67% | 75.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 01:25 | 2023-12-31 20:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 107.8399 | 106.6548 | 75.83% | 75% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 01:30 | 2023-12-31 20:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 106.6548 | 105.4697 | 75% | 74.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 01:35 | 2023-12-31 20:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 105.4697 | 104.2847 | 74.17% | 73.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 01:40 | 2023-12-31 20:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 104.2847 | 103.0996 | 73.33% | 72.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 01:45 | 2023-12-31 20:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 103.0996 | 101.9146 | 72.5% | 71.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 01:50 | 2023-12-31 20:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 101.9146 | 100.7295 | 71.67% | 70.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 01:55 | 2023-12-31 20:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 100.7295 | 99.5445 | 70.83% | 70% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 02:00 | 2023-12-31 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 99.5445 | 98.3594 | 70% | 69.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 02:05 | 2023-12-31 21:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 98.3594 | 97.1744 | 69.17% | 68.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 02:10 | 2023-12-31 21:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 97.1744 | 95.9893 | 68.33% | 67.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 02:15 | 2023-12-31 21:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 95.9893 | 94.8043 | 67.5% | 66.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 02:20 | 2023-12-31 21:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 94.8043 | 93.6192 | 66.67% | 65.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 02:25 | 2023-12-31 21:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 93.6192 | 92.4342 | 65.83% | 65% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 02:30 | 2023-12-31 21:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 92.4342 | 91.2491 | 65% | 64.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 02:35 | 2023-12-31 21:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 91.2491 | 90.0641 | 64.17% | 63.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 02:40 | 2023-12-31 21:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 90.0641 | 88.879 | 63.33% | 62.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 02:45 | 2023-12-31 21:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 88.879 | 87.6939 | 62.5% | 61.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 02:50 | 2023-12-31 21:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 87.6939 | 86.5089 | 61.67% | 60.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 02:55 | 2023-12-31 21:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 86.5089 | 85.3238 | 60.83% | 60% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 03:00 | 2023-12-31 22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 85.3238 | 84.1388 | 60% | 59.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 03:05 | 2023-12-31 22:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 84.1388 | 82.9537 | 59.17% | 58.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 03:10 | 2023-12-31 22:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 82.9537 | 81.7687 | 58.33% | 57.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 03:15 | 2023-12-31 22:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 81.7687 | 80.5836 | 57.5% | 56.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 03:20 | 2023-12-31 22:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 80.5836 | 79.3986 | 56.67% | 55.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 03:25 | 2023-12-31 22:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 79.3986 | 78.2135 | 55.83% | 55% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 03:30 | 2023-12-31 22:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 78.2135 | 77.0285 | 55% | 54.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 03:35 | 2023-12-31 22:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 77.0285 | 75.8434 | 54.17% | 53.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 03:40 | 2023-12-31 22:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 75.8434 | 74.6584 | 53.33% | 52.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 03:45 | 2023-12-31 22:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 74.6584 | 73.4733 | 52.5% | 51.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 03:50 | 2023-12-31 22:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 73.4733 | 72.2883 | 51.67% | 50.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 03:55 | 2023-12-31 22:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 72.2883 | 71.1032 | 50.83% | 50% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 04:00 | 2023-12-31 23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 71.1032 | 69.9181 | 50% | 49.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 04:05 | 2023-12-31 23:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 69.9181 | 68.7331 | 49.17% | 48.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 04:10 | 2023-12-31 23:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 68.7331 | 67.548 | 48.33% | 47.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 04:15 | 2023-12-31 23:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 67.548 | 66.363 | 47.5% | 46.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 04:20 | 2023-12-31 23:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 66.363 | 65.1779 | 46.67% | 45.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 04:25 | 2023-12-31 23:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 65.1779 | 63.9929 | 45.83% | 45% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 04:30 | 2023-12-31 23:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 63.9929 | 62.8078 | 45% | 44.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 04:35 | 2023-12-31 23:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 62.8078 | 61.6228 | 44.17% | 43.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 04:40 | 2023-12-31 23:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 61.6228 | 60.4377 | 43.33% | 42.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 04:45 | 2023-12-31 23:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 60.4377 | 59.2527 | 42.5% | 41.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 04:50 | 2023-12-31 23:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 59.2527 | 58.0676 | 41.67% | 40.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 04:55 | 2023-12-31 23:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 58.0676 | 56.8826 | 40.83% | 40% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 05:00 | 2024-01-01 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 56.8826 | 55.6975 | 40% | 39.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 05:05 | 2024-01-01 00:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 55.6975 | 54.5125 | 39.17% | 38.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 05:10 | 2024-01-01 00:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 54.5125 | 53.3274 | 38.33% | 37.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 05:15 | 2024-01-01 00:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 53.3274 | 52.1423 | 37.5% | 36.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 05:20 | 2024-01-01 00:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 52.1423 | 50.9573 | 36.67% | 35.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 05:25 | 2024-01-01 00:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 50.9573 | 49.7722 | 35.83% | 35% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 05:30 | 2024-01-01 00:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 49.7722 | 48.5872 | 35% | 34.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 05:35 | 2024-01-01 00:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 48.5872 | 47.4021 | 34.17% | 33.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 05:40 | 2024-01-01 00:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 47.4021 | 46.2171 | 33.33% | 32.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 05:45 | 2024-01-01 00:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 46.2171 | 45.032 | 32.5% | 31.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 05:50 | 2024-01-01 00:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 45.032 | 43.847 | 31.67% | 30.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 05:55 | 2024-01-01 00:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 43.847 | 42.6619 | 30.83% | 30% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 06:00 | 2024-01-01 01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 42.6619 | 41.4769 | 30% | 29.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 06:05 | 2024-01-01 01:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 41.4769 | 40.2918 | 29.17% | 28.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 06:10 | 2024-01-01 01:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 40.2918 | 39.1068 | 28.33% | 27.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 06:15 | 2024-01-01 01:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 39.1068 | 37.9217 | 27.5% | 26.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 06:20 | 2024-01-01 01:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 37.9217 | 36.7367 | 26.67% | 25.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 06:25 | 2024-01-01 01:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 36.7367 | 35.5516 | 25.83% | 25% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 06:30 | 2024-01-01 01:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 35.5516 | 34.3665 | 25% | 24.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 06:35 | 2024-01-01 01:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 34.3665 | 33.1815 | 24.17% | 23.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 06:40 | 2024-01-01 01:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 33.1815 | 31.9964 | 23.33% | 22.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 06:45 | 2024-01-01 01:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 31.9964 | 30.8114 | 22.5% | 21.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 06:50 | 2024-01-01 01:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 30.8114 | 29.6263 | 21.67% | 20.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 06:55 | 2024-01-01 01:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 29.6263 | 28.4413 | 20.83% | 20% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 07:00 | 2024-01-01 02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 28.4413 | 27.2562 | 20% | 19.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 07:05 | 2024-01-01 02:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 27.2562 | 26.0712 | 19.17% | 18.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 07:10 | 2024-01-01 02:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 26.0712 | 24.8861 | 18.33% | 17.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 07:15 | 2024-01-01 02:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 24.8861 | 23.7011 | 17.5% | 16.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 07:20 | 2024-01-01 02:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 23.7011 | 22.516 | 16.67% | 15.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 07:25 | 2024-01-01 02:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 22.516 | 21.331 | 15.83% | 15% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 07:30 | 2024-01-01 02:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 21.331 | 20.1459 | 15% | 14.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 07:35 | 2024-01-01 02:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 20.1459 | 18.9609 | 14.17% | 13.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 07:40 | 2024-01-01 02:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 18.9609 | 17.7758 | 13.33% | 12.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 07:45 | 2024-01-01 02:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 17.7758 | 16.5907 | 12.5% | 11.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 07:50 | 2024-01-01 02:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 16.5907 | 15.4057 | 11.67% | 10.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 6.7548 | 13.5096 | 142.2064 | 2024-01-01 07:55 | 2024-01-01 02:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 15.4057 | 14.2206 | 10.83% | 10% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 127.9858 | 126.8007 | 90% | 89.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 126.8007 | 125.6157 | 89.17% | 88.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 125.6157 | 124.4306 | 88.33% | 87.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 124.4306 | 123.2455 | 87.5% | 86.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 123.2455 | 122.0605 | 86.67% | 85.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 122.0605 | 120.8754 | 85.83% | 85% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 120.8754 | 119.6904 | 85% | 84.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 119.6904 | 118.5053 | 84.17% | 83.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 118.5053 | 117.3203 | 83.33% | 82.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 117.3203 | 116.1352 | 82.5% | 81.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 116.1352 | 114.9502 | 81.67% | 80.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 114.9502 | 113.7651 | 80.83% | 80% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 01:00 | 2023-12-31 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 113.7651 | 112.5801 | 80% | 79.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 01:05 | 2023-12-31 20:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 112.5801 | 111.395 | 79.17% | 78.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 01:10 | 2023-12-31 20:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 111.395 | 110.21 | 78.33% | 77.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 01:15 | 2023-12-31 20:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 110.21 | 109.0249 | 77.5% | 76.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 01:20 | 2023-12-31 20:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 109.0249 | 107.8399 | 76.67% | 75.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 01:25 | 2023-12-31 20:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 107.8399 | 106.6548 | 75.83% | 75% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 01:30 | 2023-12-31 20:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 106.6548 | 105.4697 | 75% | 74.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 01:35 | 2023-12-31 20:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 105.4697 | 104.2847 | 74.17% | 73.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 01:40 | 2023-12-31 20:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 104.2847 | 103.0996 | 73.33% | 72.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 01:45 | 2023-12-31 20:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 103.0996 | 101.9146 | 72.5% | 71.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 01:50 | 2023-12-31 20:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 101.9146 | 100.7295 | 71.67% | 70.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 01:55 | 2023-12-31 20:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 100.7295 | 99.5445 | 70.83% | 70% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 02:00 | 2023-12-31 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 99.5445 | 98.3594 | 70% | 69.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 02:05 | 2023-12-31 21:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 98.3594 | 97.1744 | 69.17% | 68.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 02:10 | 2023-12-31 21:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 97.1744 | 95.9893 | 68.33% | 67.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 02:15 | 2023-12-31 21:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 95.9893 | 94.8043 | 67.5% | 66.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 02:20 | 2023-12-31 21:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 94.8043 | 93.6192 | 66.67% | 65.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 02:25 | 2023-12-31 21:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 93.6192 | 92.4342 | 65.83% | 65% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 02:30 | 2023-12-31 21:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 92.4342 | 91.2491 | 65% | 64.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 02:35 | 2023-12-31 21:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 91.2491 | 90.0641 | 64.17% | 63.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 02:40 | 2023-12-31 21:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 90.0641 | 88.879 | 63.33% | 62.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 02:45 | 2023-12-31 21:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 88.879 | 87.6939 | 62.5% | 61.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 02:50 | 2023-12-31 21:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 87.6939 | 86.5089 | 61.67% | 60.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 02:55 | 2023-12-31 21:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 86.5089 | 85.3238 | 60.83% | 60% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 03:00 | 2023-12-31 22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 85.3238 | 84.1388 | 60% | 59.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 03:05 | 2023-12-31 22:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 84.1388 | 82.9537 | 59.17% | 58.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 03:10 | 2023-12-31 22:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 82.9537 | 81.7687 | 58.33% | 57.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 03:15 | 2023-12-31 22:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 81.7687 | 80.5836 | 57.5% | 56.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 03:20 | 2023-12-31 22:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 80.5836 | 79.3986 | 56.67% | 55.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 03:25 | 2023-12-31 22:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 79.3986 | 78.2135 | 55.83% | 55% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 03:30 | 2023-12-31 22:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 78.2135 | 77.0285 | 55% | 54.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 03:35 | 2023-12-31 22:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 77.0285 | 75.8434 | 54.17% | 53.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 03:40 | 2023-12-31 22:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 75.8434 | 74.6584 | 53.33% | 52.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 03:45 | 2023-12-31 22:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 74.6584 | 73.4733 | 52.5% | 51.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 03:50 | 2023-12-31 22:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 73.4733 | 72.2883 | 51.67% | 50.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 03:55 | 2023-12-31 22:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 72.2883 | 71.1032 | 50.83% | 50% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 04:00 | 2023-12-31 23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 71.1032 | 69.9181 | 50% | 49.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 04:05 | 2023-12-31 23:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 69.9181 | 68.7331 | 49.17% | 48.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 04:10 | 2023-12-31 23:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 68.7331 | 67.548 | 48.33% | 47.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 04:15 | 2023-12-31 23:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 67.548 | 66.363 | 47.5% | 46.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 04:20 | 2023-12-31 23:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 66.363 | 65.1779 | 46.67% | 45.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 04:25 | 2023-12-31 23:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 65.1779 | 63.9929 | 45.83% | 45% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 04:30 | 2023-12-31 23:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 63.9929 | 62.8078 | 45% | 44.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 04:35 | 2023-12-31 23:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 62.8078 | 61.6228 | 44.17% | 43.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 04:40 | 2023-12-31 23:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 61.6228 | 60.4377 | 43.33% | 42.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 04:45 | 2023-12-31 23:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 60.4377 | 59.2527 | 42.5% | 41.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 04:50 | 2023-12-31 23:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 59.2527 | 58.0676 | 41.67% | 40.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 04:55 | 2023-12-31 23:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 58.0676 | 56.8826 | 40.83% | 40% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 05:00 | 2024-01-01 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 56.8826 | 55.6975 | 40% | 39.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 05:05 | 2024-01-01 00:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 55.6975 | 54.5125 | 39.17% | 38.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 05:10 | 2024-01-01 00:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 54.5125 | 53.3274 | 38.33% | 37.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 05:15 | 2024-01-01 00:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 53.3274 | 52.1423 | 37.5% | 36.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 05:20 | 2024-01-01 00:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 52.1423 | 50.9573 | 36.67% | 35.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 05:25 | 2024-01-01 00:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 50.9573 | 49.7722 | 35.83% | 35% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 05:30 | 2024-01-01 00:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 49.7722 | 48.5872 | 35% | 34.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 05:35 | 2024-01-01 00:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 48.5872 | 47.4021 | 34.17% | 33.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 05:40 | 2024-01-01 00:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 47.4021 | 46.2171 | 33.33% | 32.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 05:45 | 2024-01-01 00:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 46.2171 | 45.032 | 32.5% | 31.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 05:50 | 2024-01-01 00:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 45.032 | 43.847 | 31.67% | 30.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 05:55 | 2024-01-01 00:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 43.847 | 42.6619 | 30.83% | 30% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 06:00 | 2024-01-01 01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 42.6619 | 41.4769 | 30% | 29.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 06:05 | 2024-01-01 01:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 41.4769 | 40.2918 | 29.17% | 28.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 06:10 | 2024-01-01 01:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 40.2918 | 39.1068 | 28.33% | 27.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 06:15 | 2024-01-01 01:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 39.1068 | 37.9217 | 27.5% | 26.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 06:20 | 2024-01-01 01:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 37.9217 | 36.7367 | 26.67% | 25.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 06:25 | 2024-01-01 01:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 36.7367 | 35.5516 | 25.83% | 25% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 06:30 | 2024-01-01 01:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 35.5516 | 34.3665 | 25% | 24.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 06:35 | 2024-01-01 01:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 34.3665 | 33.1815 | 24.17% | 23.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 06:40 | 2024-01-01 01:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 33.1815 | 31.9964 | 23.33% | 22.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 06:45 | 2024-01-01 01:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 31.9964 | 30.8114 | 22.5% | 21.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 06:50 | 2024-01-01 01:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 30.8114 | 29.6263 | 21.67% | 20.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 06:55 | 2024-01-01 01:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 29.6263 | 28.4413 | 20.83% | 20% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 07:00 | 2024-01-01 02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 28.4413 | 27.2562 | 20% | 19.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 07:05 | 2024-01-01 02:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 27.2562 | 26.0712 | 19.17% | 18.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 07:10 | 2024-01-01 02:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 26.0712 | 24.8861 | 18.33% | 17.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 07:15 | 2024-01-01 02:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 24.8861 | 23.7011 | 17.5% | 16.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 07:20 | 2024-01-01 02:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 23.7011 | 22.516 | 16.67% | 15.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 07:25 | 2024-01-01 02:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 22.516 | 21.331 | 15.83% | 15% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 07:30 | 2024-01-01 02:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 21.331 | 20.1459 | 15% | 14.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 07:35 | 2024-01-01 02:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 20.1459 | 18.9609 | 14.17% | 13.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 07:40 | 2024-01-01 02:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 18.9609 | 17.7758 | 13.33% | 12.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 07:45 | 2024-01-01 02:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 17.7758 | 16.5907 | 12.5% | 11.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 07:50 | 2024-01-01 02:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 16.5907 | 15.4057 | 11.67% | 10.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 10.1322 | 13.5096 | 142.2064 | 2024-01-01 07:55 | 2024-01-01 02:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 15.4057 | 14.2206 | 10.83% | 10% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 | 2023-12-31 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 127.9858 | 126.8007 | 90% | 89.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 00:05 | 2023-12-31 19:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 126.8007 | 125.6157 | 89.17% | 88.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 00:10 | 2023-12-31 19:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 125.6157 | 124.4306 | 88.33% | 87.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 00:15 | 2023-12-31 19:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 124.4306 | 123.2455 | 87.5% | 86.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 00:20 | 2023-12-31 19:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 123.2455 | 122.0605 | 86.67% | 85.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 00:25 | 2023-12-31 19:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 122.0605 | 120.8754 | 85.83% | 85% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 00:30 | 2023-12-31 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 120.8754 | 119.6904 | 85% | 84.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 00:35 | 2023-12-31 19:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 119.6904 | 118.5053 | 84.17% | 83.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 00:40 | 2023-12-31 19:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 118.5053 | 117.3203 | 83.33% | 82.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 00:45 | 2023-12-31 19:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 117.3203 | 116.1352 | 82.5% | 81.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 00:50 | 2023-12-31 19:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 116.1352 | 114.9502 | 81.67% | 80.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 00:55 | 2023-12-31 19:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 114.9502 | 113.7651 | 80.83% | 80% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 01:00 | 2023-12-31 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 113.7651 | 112.5801 | 80% | 79.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 01:05 | 2023-12-31 20:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 112.5801 | 111.395 | 79.17% | 78.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 01:10 | 2023-12-31 20:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 111.395 | 110.21 | 78.33% | 77.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 01:15 | 2023-12-31 20:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 110.21 | 109.0249 | 77.5% | 76.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 01:20 | 2023-12-31 20:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 109.0249 | 107.8399 | 76.67% | 75.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 01:25 | 2023-12-31 20:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 107.8399 | 106.6548 | 75.83% | 75% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 01:30 | 2023-12-31 20:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 106.6548 | 105.4697 | 75% | 74.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 01:35 | 2023-12-31 20:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 105.4697 | 104.2847 | 74.17% | 73.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 01:40 | 2023-12-31 20:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 104.2847 | 103.0996 | 73.33% | 72.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 01:45 | 2023-12-31 20:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 103.0996 | 101.9146 | 72.5% | 71.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 01:50 | 2023-12-31 20:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 101.9146 | 100.7295 | 71.67% | 70.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 01:55 | 2023-12-31 20:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 100.7295 | 99.5445 | 70.83% | 70% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 02:00 | 2023-12-31 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 99.5445 | 98.3594 | 70% | 69.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 02:05 | 2023-12-31 21:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 98.3594 | 97.1744 | 69.17% | 68.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 02:10 | 2023-12-31 21:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 97.1744 | 95.9893 | 68.33% | 67.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 02:15 | 2023-12-31 21:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 95.9893 | 94.8043 | 67.5% | 66.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 02:20 | 2023-12-31 21:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 94.8043 | 93.6192 | 66.67% | 65.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 02:25 | 2023-12-31 21:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 93.6192 | 92.4342 | 65.83% | 65% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 02:30 | 2023-12-31 21:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 92.4342 | 91.2491 | 65% | 64.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 02:35 | 2023-12-31 21:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 91.2491 | 90.0641 | 64.17% | 63.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 02:40 | 2023-12-31 21:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 90.0641 | 88.879 | 63.33% | 62.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 02:45 | 2023-12-31 21:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 88.879 | 87.6939 | 62.5% | 61.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 02:50 | 2023-12-31 21:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 87.6939 | 86.5089 | 61.67% | 60.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 02:55 | 2023-12-31 21:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 86.5089 | 85.3238 | 60.83% | 60% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 03:00 | 2023-12-31 22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 85.3238 | 84.1388 | 60% | 59.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 03:05 | 2023-12-31 22:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 84.1388 | 82.9537 | 59.17% | 58.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 03:10 | 2023-12-31 22:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 82.9537 | 81.7687 | 58.33% | 57.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 03:15 | 2023-12-31 22:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 81.7687 | 80.5836 | 57.5% | 56.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 03:20 | 2023-12-31 22:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 80.5836 | 79.3986 | 56.67% | 55.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 03:25 | 2023-12-31 22:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 79.3986 | 78.2135 | 55.83% | 55% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 03:30 | 2023-12-31 22:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 78.2135 | 77.0285 | 55% | 54.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 03:35 | 2023-12-31 22:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 77.0285 | 75.8434 | 54.17% | 53.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 03:40 | 2023-12-31 22:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 75.8434 | 74.6584 | 53.33% | 52.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 03:45 | 2023-12-31 22:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 74.6584 | 73.4733 | 52.5% | 51.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 03:50 | 2023-12-31 22:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 73.4733 | 72.2883 | 51.67% | 50.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 03:55 | 2023-12-31 22:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 72.2883 | 71.1032 | 50.83% | 50% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 04:00 | 2023-12-31 23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 71.1032 | 69.9181 | 50% | 49.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 04:05 | 2023-12-31 23:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 69.9181 | 68.7331 | 49.17% | 48.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 04:10 | 2023-12-31 23:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 68.7331 | 67.548 | 48.33% | 47.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 04:15 | 2023-12-31 23:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 67.548 | 66.363 | 47.5% | 46.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 04:20 | 2023-12-31 23:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 66.363 | 65.1779 | 46.67% | 45.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 04:25 | 2023-12-31 23:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 65.1779 | 63.9929 | 45.83% | 45% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 04:30 | 2023-12-31 23:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 63.9929 | 62.8078 | 45% | 44.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 04:35 | 2023-12-31 23:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 62.8078 | 61.6228 | 44.17% | 43.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 04:40 | 2023-12-31 23:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 61.6228 | 60.4377 | 43.33% | 42.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 04:45 | 2023-12-31 23:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 60.4377 | 59.2527 | 42.5% | 41.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 04:50 | 2023-12-31 23:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 59.2527 | 58.0676 | 41.67% | 40.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 04:55 | 2023-12-31 23:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 58.0676 | 56.8826 | 40.83% | 40% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 05:00 | 2024-01-01 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 56.8826 | 55.6975 | 40% | 39.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 05:05 | 2024-01-01 00:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 55.6975 | 54.5125 | 39.17% | 38.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 05:10 | 2024-01-01 00:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 54.5125 | 53.3274 | 38.33% | 37.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 05:15 | 2024-01-01 00:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 53.3274 | 52.1423 | 37.5% | 36.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 05:20 | 2024-01-01 00:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 52.1423 | 50.9573 | 36.67% | 35.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 05:25 | 2024-01-01 00:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 50.9573 | 49.7722 | 35.83% | 35% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 05:30 | 2024-01-01 00:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 49.7722 | 48.5872 | 35% | 34.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 05:35 | 2024-01-01 00:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 48.5872 | 47.4021 | 34.17% | 33.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 05:40 | 2024-01-01 00:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 47.4021 | 46.2171 | 33.33% | 32.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 05:45 | 2024-01-01 00:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 46.2171 | 45.032 | 32.5% | 31.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 05:50 | 2024-01-01 00:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 45.032 | 43.847 | 31.67% | 30.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 05:55 | 2024-01-01 00:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 43.847 | 42.6619 | 30.83% | 30% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 06:00 | 2024-01-01 01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 42.6619 | 41.4769 | 30% | 29.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 06:05 | 2024-01-01 01:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 41.4769 | 40.2918 | 29.17% | 28.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 06:10 | 2024-01-01 01:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 40.2918 | 39.1068 | 28.33% | 27.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 06:15 | 2024-01-01 01:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 39.1068 | 37.9217 | 27.5% | 26.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 06:20 | 2024-01-01 01:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 37.9217 | 36.7367 | 26.67% | 25.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 06:25 | 2024-01-01 01:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 36.7367 | 35.5516 | 25.83% | 25% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 06:30 | 2024-01-01 01:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 35.5516 | 34.3665 | 25% | 24.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 06:35 | 2024-01-01 01:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 34.3665 | 33.1815 | 24.17% | 23.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 06:40 | 2024-01-01 01:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 33.1815 | 31.9964 | 23.33% | 22.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 06:45 | 2024-01-01 01:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 31.9964 | 30.8114 | 22.5% | 21.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 06:50 | 2024-01-01 01:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 30.8114 | 29.6263 | 21.67% | 20.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 06:55 | 2024-01-01 01:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 29.6263 | 28.4413 | 20.83% | 20% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 07:00 | 2024-01-01 02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 28.4413 | 27.2562 | 20% | 19.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 07:05 | 2024-01-01 02:05 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 27.2562 | 26.0712 | 19.17% | 18.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 07:10 | 2024-01-01 02:10 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 26.0712 | 24.8861 | 18.33% | 17.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 07:15 | 2024-01-01 02:15 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 24.8861 | 23.7011 | 17.5% | 16.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 07:20 | 2024-01-01 02:20 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 23.7011 | 22.516 | 16.67% | 15.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 07:25 | 2024-01-01 02:25 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 22.516 | 21.331 | 15.83% | 15% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 07:30 | 2024-01-01 02:30 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 21.331 | 20.1459 | 15% | 14.17% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 07:35 | 2024-01-01 02:35 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 20.1459 | 18.9609 | 14.17% | 13.33% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 07:40 | 2024-01-01 02:40 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 18.9609 | 17.7758 | 13.33% | 12.5% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 07:45 | 2024-01-01 02:45 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 17.7758 | 16.5907 | 12.5% | 11.67% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 07:50 | 2024-01-01 02:50 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 16.5907 | 15.4057 | 11.67% | 10.83% | 14.2206 | 13.5096 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 1 | 8 | 13.5096 | 13.5096 | 142.2064 | 2024-01-01 07:55 | 2024-01-01 02:55 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5096 | 15.4057 | 14.2206 | 10.83% | 10% | 14.2206 | 13.5096 | 0 | 0

## Constraint_Generation
Iteration | ActiveWindows | BatteryInstalledMWh | BatteryPowerMW | ViolatingHistoricalWindows | MinimumSOCMarginMWh | MaximumPowerDeficitMW | CandidateKey | ServiceTarget | OutageDurationHours | PVCapacityMW
1 | 12 | 8.8879 | 6.7548 | 0 | 0 | 0 | GSO_122¦line_5852_22 | 0.5 | 1 | 0
1 | 12 | 8.8879 | 6.7548 | 0 | 0 | 0 | GSO_122¦line_5852_22 | 0.5 | 1 | 3.3774
1 | 12 | 8.8879 | 6.7548 | 0 | 0 | 0 | GSO_122¦line_5852_22 | 0.5 | 1 | 6.7548
1 | 12 | 8.8879 | 6.7548 | 0 | 0 | 0 | GSO_122¦line_5852_22 | 0.5 | 1 | 10.1322
1 | 12 | 8.8879 | 6.7548 | 0 | 0 | 0 | GSO_122¦line_5852_22 | 0.5 | 1 | 13.5096
1 | 12 | 17.7758 | 6.7548 | 0 | 0 | 0 | GSO_122¦line_5852_22 | 0.5 | 2 | 0
1 | 12 | 17.7758 | 6.7548 | 0 | 0 | 0 | GSO_122¦line_5852_22 | 0.5 | 2 | 3.3774
1 | 12 | 17.7758 | 6.7548 | 0 | 0 | 0 | GSO_122¦line_5852_22 | 0.5 | 2 | 6.7548
1 | 12 | 17.7758 | 6.7548 | 0 | 0 | 0 | GSO_122¦line_5852_22 | 0.5 | 2 | 10.1322
1 | 12 | 17.7758 | 6.7548 | 0 | 0 | 0 | GSO_122¦line_5852_22 | 0.5 | 2 | 13.5096
1 | 12 | 35.5516 | 6.7548 | 0 | 0 | 0 | GSO_122¦line_5852_22 | 0.5 | 4 | 0
1 | 12 | 35.5516 | 6.7548 | 0 | 0 | 0 | GSO_122¦line_5852_22 | 0.5 | 4 | 3.3774
1 | 12 | 35.5516 | 6.7548 | 0 | 0 | 0 | GSO_122¦line_5852_22 | 0.5 | 4 | 6.7548
1 | 12 | 35.5516 | 6.7548 | 0 | 0 | 0 | GSO_122¦line_5852_22 | 0.5 | 4 | 10.1322
1 | 12 | 35.5516 | 6.7548 | 0 | 0 | 0 | GSO_122¦line_5852_22 | 0.5 | 4 | 13.5096
1 | 12 | 71.1032 | 6.7548 | 0 | 0 | 0 | GSO_122¦line_5852_22 | 0.5 | 8 | 0
1 | 12 | 71.1032 | 6.7548 | 0 | 0 | 0 | GSO_122¦line_5852_22 | 0.5 | 8 | 3.3774
1 | 12 | 71.1032 | 6.7548 | 0 | 0 | 0 | GSO_122¦line_5852_22 | 0.5 | 8 | 6.7548
1 | 12 | 71.1032 | 6.7548 | 0 | 0 | 0 | GSO_122¦line_5852_22 | 0.5 | 8 | 10.1322
1 | 12 | 71.1032 | 6.7548 | 0 | 0 | 0 | GSO_122¦line_5852_22 | 0.5 | 8 | 13.5096
1 | 12 | 13.3319 | 10.1322 | 0 | 1.5543e-15 | 0 | GSO_122¦line_5852_22 | 0.75 | 1 | 0
1 | 12 | 13.3319 | 10.1322 | 0 | 1.5543e-15 | 0 | GSO_122¦line_5852_22 | 0.75 | 1 | 3.3774
1 | 12 | 13.3319 | 10.1322 | 0 | 1.5543e-15 | 0 | GSO_122¦line_5852_22 | 0.75 | 1 | 6.7548
1 | 12 | 13.3319 | 10.1322 | 0 | 1.5543e-15 | 0 | GSO_122¦line_5852_22 | 0.75 | 1 | 10.1322
1 | 12 | 13.3319 | 10.1322 | 0 | 1.5543e-15 | 0 | GSO_122¦line_5852_22 | 0.75 | 1 | 13.5096
1 | 12 | 26.6637 | 10.1322 | 0 | 3.1086e-15 | 0 | GSO_122¦line_5852_22 | 0.75 | 2 | 0
1 | 12 | 26.6637 | 10.1322 | 0 | 3.1086e-15 | 0 | GSO_122¦line_5852_22 | 0.75 | 2 | 3.3774
1 | 12 | 26.6637 | 10.1322 | 0 | 3.1086e-15 | 0 | GSO_122¦line_5852_22 | 0.75 | 2 | 6.7548
1 | 12 | 26.6637 | 10.1322 | 0 | 3.1086e-15 | 0 | GSO_122¦line_5852_22 | 0.75 | 2 | 10.1322
1 | 12 | 26.6637 | 10.1322 | 0 | 3.1086e-15 | 0 | GSO_122¦line_5852_22 | 0.75 | 2 | 13.5096
1 | 12 | 53.3274 | 10.1322 | 0 | -1.6875e-14 | 0 | GSO_122¦line_5852_22 | 0.75 | 4 | 0
1 | 12 | 53.3274 | 10.1322 | 0 | -1.6875e-14 | 0 | GSO_122¦line_5852_22 | 0.75 | 4 | 3.3774
1 | 12 | 53.3274 | 10.1322 | 0 | -1.6875e-14 | 0 | GSO_122¦line_5852_22 | 0.75 | 4 | 6.7548
1 | 12 | 53.3274 | 10.1322 | 0 | -1.6875e-14 | 0 | GSO_122¦line_5852_22 | 0.75 | 4 | 10.1322
1 | 12 | 53.3274 | 10.1322 | 0 | -1.6875e-14 | 0 | GSO_122¦line_5852_22 | 0.75 | 4 | 13.5096
1 | 12 | 106.6548 | 10.1322 | 0 | 4.6185e-14 | 0 | GSO_122¦line_5852_22 | 0.75 | 8 | 0
1 | 12 | 106.6548 | 10.1322 | 0 | 4.6185e-14 | 0 | GSO_122¦line_5852_22 | 0.75 | 8 | 3.3774
1 | 12 | 106.6548 | 10.1322 | 0 | 4.6185e-14 | 0 | GSO_122¦line_5852_22 | 0.75 | 8 | 6.7548
1 | 12 | 106.6548 | 10.1322 | 0 | 4.6185e-14 | 0 | GSO_122¦line_5852_22 | 0.75 | 8 | 10.1322
1 | 12 | 106.6548 | 10.1322 | 0 | 4.6185e-14 | 0 | GSO_122¦line_5852_22 | 0.75 | 8 | 13.5096
1 | 12 | 15.9982 | 12.1586 | 0 | 4.4409e-16 | 0 | GSO_122¦line_5852_22 | 0.9 | 1 | 0
1 | 12 | 15.9982 | 12.1586 | 0 | 4.4409e-16 | 0 | GSO_122¦line_5852_22 | 0.9 | 1 | 3.3774
1 | 12 | 15.9982 | 12.1586 | 0 | 4.4409e-16 | 0 | GSO_122¦line_5852_22 | 0.9 | 1 | 6.7548
1 | 12 | 15.9982 | 12.1586 | 0 | 4.4409e-16 | 0 | GSO_122¦line_5852_22 | 0.9 | 1 | 10.1322
1 | 12 | 15.9982 | 12.1586 | 0 | 4.4409e-16 | 0 | GSO_122¦line_5852_22 | 0.9 | 1 | 13.5096
1 | 12 | 31.9964 | 12.1586 | 0 | 2.2204e-15 | 0 | GSO_122¦line_5852_22 | 0.9 | 2 | 0
1 | 12 | 31.9964 | 12.1586 | 0 | 2.2204e-15 | 0 | GSO_122¦line_5852_22 | 0.9 | 2 | 3.3774
1 | 12 | 31.9964 | 12.1586 | 0 | 2.2204e-15 | 0 | GSO_122¦line_5852_22 | 0.9 | 2 | 6.7548
1 | 12 | 31.9964 | 12.1586 | 0 | 2.2204e-15 | 0 | GSO_122¦line_5852_22 | 0.9 | 2 | 10.1322
1 | 12 | 31.9964 | 12.1586 | 0 | 2.2204e-15 | 0 | GSO_122¦line_5852_22 | 0.9 | 2 | 13.5096
1 | 12 | 63.9929 | 12.1586 | 0 | 1.4211e-14 | 0 | GSO_122¦line_5852_22 | 0.9 | 4 | 0
1 | 12 | 63.9929 | 12.1586 | 0 | 1.4211e-14 | 0 | GSO_122¦line_5852_22 | 0.9 | 4 | 3.3774
1 | 12 | 63.9929 | 12.1586 | 0 | 1.4211e-14 | 0 | GSO_122¦line_5852_22 | 0.9 | 4 | 6.7548
1 | 12 | 63.9929 | 12.1586 | 0 | 1.4211e-14 | 0 | GSO_122¦line_5852_22 | 0.9 | 4 | 10.1322
1 | 12 | 63.9929 | 12.1586 | 0 | 1.4211e-14 | 0 | GSO_122¦line_5852_22 | 0.9 | 4 | 13.5096
1 | 12 | 127.9858 | 12.1586 | 0 | 3.0198e-14 | 0 | GSO_122¦line_5852_22 | 0.9 | 8 | 0
1 | 12 | 127.9858 | 12.1586 | 0 | 3.0198e-14 | 0 | GSO_122¦line_5852_22 | 0.9 | 8 | 3.3774
1 | 12 | 127.9858 | 12.1586 | 0 | 3.0198e-14 | 0 | GSO_122¦line_5852_22 | 0.9 | 8 | 6.7548
1 | 12 | 127.9858 | 12.1586 | 0 | 3.0198e-14 | 0 | GSO_122¦line_5852_22 | 0.9 | 8 | 10.1322
1 | 12 | 127.9858 | 12.1586 | 0 | 3.0198e-14 | 0 | GSO_122¦line_5852_22 | 0.9 | 8 | 13.5096
1 | 12 | 17.7758 | 13.5096 | 0 | 0 | 0 | GSO_122¦line_5852_22 | 1 | 1 | 0
1 | 12 | 17.7758 | 13.5096 | 0 | 0 | 0 | GSO_122¦line_5852_22 | 1 | 1 | 3.3774
1 | 12 | 17.7758 | 13.5096 | 0 | 0 | 0 | GSO_122¦line_5852_22 | 1 | 1 | 6.7548
1 | 12 | 17.7758 | 13.5096 | 0 | 0 | 0 | GSO_122¦line_5852_22 | 1 | 1 | 10.1322
1 | 12 | 17.7758 | 13.5096 | 0 | 0 | 0 | GSO_122¦line_5852_22 | 1 | 1 | 13.5096
1 | 12 | 35.5516 | 13.5096 | 0 | 0 | 0 | GSO_122¦line_5852_22 | 1 | 2 | 0
1 | 12 | 35.5516 | 13.5096 | 0 | 0 | 0 | GSO_122¦line_5852_22 | 1 | 2 | 3.3774
1 | 12 | 35.5516 | 13.5096 | 0 | 0 | 0 | GSO_122¦line_5852_22 | 1 | 2 | 6.7548
1 | 12 | 35.5516 | 13.5096 | 0 | 0 | 0 | GSO_122¦line_5852_22 | 1 | 2 | 10.1322
1 | 12 | 35.5516 | 13.5096 | 0 | 0 | 0 | GSO_122¦line_5852_22 | 1 | 2 | 13.5096
1 | 12 | 71.1032 | 13.5096 | 0 | 0 | 0 | GSO_122¦line_5852_22 | 1 | 4 | 0
1 | 12 | 71.1032 | 13.5096 | 0 | 0 | 0 | GSO_122¦line_5852_22 | 1 | 4 | 3.3774
1 | 12 | 71.1032 | 13.5096 | 0 | 0 | 0 | GSO_122¦line_5852_22 | 1 | 4 | 6.7548
1 | 12 | 71.1032 | 13.5096 | 0 | 0 | 0 | GSO_122¦line_5852_22 | 1 | 4 | 10.1322
1 | 12 | 71.1032 | 13.5096 | 0 | 0 | 0 | GSO_122¦line_5852_22 | 1 | 4 | 13.5096
1 | 12 | 142.2064 | 13.5096 | 0 | 0 | 0 | GSO_122¦line_5852_22 | 1 | 8 | 0
1 | 12 | 142.2064 | 13.5096 | 0 | 0 | 0 | GSO_122¦line_5852_22 | 1 | 8 | 3.3774
1 | 12 | 142.2064 | 13.5096 | 0 | 0 | 0 | GSO_122¦line_5852_22 | 1 | 8 | 6.7548
1 | 12 | 142.2064 | 13.5096 | 0 | 0 | 0 | GSO_122¦line_5852_22 | 1 | 8 | 10.1322
1 | 12 | 142.2064 | 13.5096 | 0 | 0 | 0 | GSO_122¦line_5852_22 | 1 | 8 | 13.5096

## MILP1_Sites
CandidateKey | GridID | SubstationID | CandidateLineID | OriginalFirmHostingMW | ThermalProfileFirmHostingMW | FirmHostingValidationDifferenceMW | FirmHostingValidationMatch | FirmHostingValidationToleranceMW | ModeledIntervals | ModeledHoursEquivalent | RawThermalCoveragePctOfYear | ModeledCommonCoveragePctOfYear | CommonTimestampIntersectionUsed | ThermalIncrementalReserveFactor | SubstationLoadingLimitFraction | ThermalFirmHostingMW | ThermalOnlyReservedFirmMW | SubstationOnlyFirmIncrementalMW | CombinedNoFlexFirmMW | ExistingSystemFirmMW | BaseDCMW | BindingConstraint | AnswerStatus | SubstationCapacityResolved | SubstationCapacityMethod | SubstationCapacitySource | StationLimitingTimestampUTC | StationExistingLoadAtLimitingIntervalMW | CapacityGainFromFlexMW | BatteryPowerMW | BatteryEnergyMWh | BatteryThroughputMWh | PVCapacityMW | PVUsedMWh | FlexibleComputeMWh | DRMWh | EVShiftedMWh | BatteryActive | PVActive | EVActive | DRActive | FlexibleComputeActive | ReliabilityModelEnabled | ReliabilityReady | ReliabilityCapacityMW | ReliabilityOptimizationCreditMW | SelectionEligible | Selected | CapacitySelectionOptimumMW | CoOptimalWithinTolerance | SiteCapacityTieToleranceMW | PrimarySelectionTermination | ReliabilitySecondarySelectionUsed | SecondarySelectionTermination
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 13.5096 | 3.5527e-15 | TRUE | 0.01 | 105348 | 8779 | 99.9431 | 99.9431 | TRUE | 1 | 100% | 13.5096 | 13.5096 |  | 13.5096 | 13.5096 | 13.5096 | FEEDER_PATH_THERMAL_WITH_SUBSTATION_UNRESOLVED | FEEDER_THERMAL_UPPER_BOUND_STATION_UNRESOLVED | FALSE | Unresolved | Review |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE |  | 0 | TRUE | TRUE | 13.5096 | TRUE | 0.001 | optimal | FALSE | NotRun_NoReliabilityRanking

## Assumptions
Item | Value
MILP-1 handoff | Normal-state site and DC MW are fixed from greensboro_final_integrated_milp_results.xlsx. MILP 2 never increases the MILP-1 base load.
Outage model | Utility grid import is unavailable for the full outage. Required served load equals ServiceTarget x BaseDCMW.
Historical robustness | The final battery design is explicitly validated against every complete historical outage start represented by the 2024 PV profile.
Constraint generation | The Pyomo model begins with critical historical windows, solves battery MWh then MW, tests all starts, adds violating windows, and repeats until zero historical violations remain.
PV capacity | New PV is evaluated as explicit capacity scenarios rather than optimized without a defensible cost, land, or interconnection objective.
PV availability | PV production uses the empirical Greensboro normalized availability profile from greensboro_pv_availability_shape_2024.csv.gz; a candidate-substation shape is preferred when available.
PV dispatch | PV serves critical load first. Excess PV may charge the battery up to PCS MW and SOC headroom. Only remaining excess PV is curtailed.
PV islanding requirement | PV outage credit assumes PV/BESS are on the outage-isolated load side with grid-forming/islanding capability. Active=True.
Battery PCS | A single symmetric BatteryPowerMW rating constrains both battery charge and discharge.
Battery SOC | Start=90%, minimum=10%, maximum=100%.
Battery efficiency | Charge=95%; discharge=95%.
Battery sizing objective | Lexicographic: minimize installed/nameplate battery MWh first, then minimize PCS MW while retaining the minimum-MWh solution.
P99/P95/P50 energy diagnostics | These estimate the minimum nameplate energy by historical outage start with unrestricted charge power. The robust Pyomo design remains the governing result.
Not modeled | Battery degradation, temperature derating, black-start transients, inverter overload, generator start sequences, utility protection/islanding approval, land/cost constraints, and post-outage recharge are outside this deterministic stage.
Solver | appsi_highs