## Feeder_Entrance_Audit
ValidatedRank | ProvisionalRank | FeederID | Description | EntranceCapacityConfidence | RecommendedNextStep | BreakerElementID | Latitude | Longitude | BreakerRatingKVA | BreakerRatingMVA | BreakerCapacityMW | AverageLoadMW | P95LoadMW | PeakLoadMW | PeakLoadTimestamp | BreakerAverageUtilizationPct | BreakerP95UtilizationPct | BreakerPeakUtilizationPct | DirectDownstreamElementCount | DirectDownstreamLineCount | DirectDownstreamTransformerCount | DirectDownstreamSwitchCount | EntranceLineCount | EntranceLineSearchDepth | EntranceLinesWithUsableCapacity | EntranceLineIDs | PrimaryEntranceLineID | PrimaryEntranceLineRatingA | PrimaryEntranceLineVoltageKV | PrimaryEntranceLineMVA | PrimaryEntranceLineMW | MinimumEntranceLineMVA | MaximumEntranceLineMVA | SumEntranceLineMVA | MinimumEntranceLineMW | MaximumEntranceLineMW | SumEntranceLineMW | EntranceLineValidationStatus | SCADAAverageVoltage | SCADAMedianVoltage | SCADAP05Voltage | SCADAP95Voltage | SCADAMinimumVoltage | SCADAMaximumVoltage | PhaseAAverageVoltage | PhaseBAverageVoltage | PhaseCAverageVoltage | SCADAVoltageInterpretation | SCADANominalVoltageMatchPct | SCADAVoltageValidationStatus | EntranceThermalCapacityMW | ProvisionalBreakerHeadroomMW | ProvisionalEntranceHeadroomMW | ValidatedEntranceCapacityMW | ValidatedEntranceHeadroomMW | LoadSCADAStatus | VoltageSCADAStatus | Observations | MedianIntervalMinutes | FirstTimestamp | LastTimestamp | GridLastUpdated | ElementType | ElementCustomerType | BreakerPhases | IsProducer | IsConsumer | IsSwitchable | SwitchIsOpen | PowerFlowDirection | UpstreamElementID | Terminal1CN | Terminal2CN | RawBreakerRatingKVA | RawBreakerRatingA | RawBreakerVoltageLevel | BreakerCount | BreakerCandidateRank | AverageIntervalKWh | P95IntervalKWh | PeakIntervalKWh | LoadSourceCount | LoadSourceIDs | LoadSourcePhases | VoltageSourceCount | PhaseAP05Voltage | PhaseAMinimumVoltage | PhaseAMaximumVoltage | PhaseBP05Voltage | PhaseBMinimumVoltage | PhaseBMaximumVoltage | PhaseCP05Voltage | PhaseCMinimumVoltage | PhaseCMaximumVoltage | BreakerVsMinimumLineCapacityRatio | BreakerVsPrimaryLineCapacityRatio | BreakerVsSumEntranceCapacityRatio
1 | 2 | GSO_122 | GSO_122 | High | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis | br_02_22 | 36.083 | -79.9727 | 15000 | 15 | 14.25 | 0.019727 | 0.024036 | 0.03276 | 2024-01-20 07:00 | 0.13844 | 0.16867 | 0.22989 | 1 | 0 | 0 | 1 | 1 | 2 | 1 | line_5852_22 | line_5852_22 | 660 | 12.47 | 14.2551 | 13.5424 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | Single entrance line plausibly supports breaker rating | 7206.9558 | 7202.1623 | 7162.7293 | 7262.722 | 7029.892 | 7398.179 | 7206.9294 | 7206.9385 | 7206.9995 | SCADA interpreted as phase-to-neutral volts | 0.10276 | Strong nominal-voltage agreement | 13.5424 | 14.2172 | 13.5096 | 13.5424 | 13.5096 | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 15000.0 |  | MV | 1 | 1 | 1.6439 | 2.003 | 2.73 | 3 | e63f1c25-1cac-49ae-9929-f96fa015f74e, 4fa57e43-e6c7-4d4b-a312-3fb0e3337ffc, abf746be-5de9-44ac-9f69-a717abe29437 | A, B, C | 3 | 7167.1137 | 7033.548 | 7376.914 | 7166.3363 | 7042.809 | 7386.879 | 7162.7293 | 7029.892 | 7398.179 | 1.0523 | 1.0523 | 1.0523
2 | 3 | GSO_124 | GSO_124 | High | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis | br_04_22 | 36.083 | -79.9727 | 15000 | 15 | 14.25 | 0.077728 | 0.0957 | 0.13387 | 2024-01-22 04:00 | 0.54546 | 0.67158 | 0.93945 | 1 | 0 | 0 | 1 | 1 | 2 | 1 | line_6716_22 | line_6716_22 | 660 | 12.47 | 14.2551 | 13.5424 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | Single entrance line plausibly supports breaker rating | 7208.3181 | 7203.1612 | 7154.8937 | 7269.9309 | 7005.586 | 7387.821 | 7207.2665 | 7206.5732 | 7211.1145 | SCADA interpreted as phase-to-neutral volts | 0.12168 | Strong nominal-voltage agreement | 13.5424 | 14.1161 | 13.4085 | 13.5424 | 13.4085 | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 15000.0 |  | MV | 1 | 1 | 6.4773 | 7.975 | 11.156 | 3 | e9588dba-e5c4-44a0-a87f-6d585846716c, f9dd1e2c-0b53-4323-abbd-c79d2b87bf2e, cbbe0d2b-6245-4a4f-bcc2-e456b3e84669 | A, B, C | 3 | 7165.9279 | 7005.586 | 7378.288 | 7154.8937 | 7057.389 | 7387.123 | 7168.9828 | 7028.827 | 7387.821 | 1.0523 | 1.0523 | 1.0523
3 | 4 | GSO_123 | GSO_123 | High | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis | br_03_22 | 36.083 | -79.9727 | 15000 | 15 | 14.25 | 0.24819 | 0.28877 | 0.36464 | 2024-01-22 04:00 | 1.7417 | 2.0264 | 2.5589 | 1 | 0 | 0 | 1 | 1 | 2 | 1 | line_6019_22 | line_6019_22 | 660 | 12.47 | 14.2551 | 13.5424 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | Single entrance line plausibly supports breaker rating | 7209.9826 | 7204.5635 | 7160.7653 | 7270.5913 | 7022.253 | 7383.732 | 7209.9177 | 7210.9486 | 7209.0817 | SCADA interpreted as phase-to-neutral volts | 0.1448 | Strong nominal-voltage agreement | 13.5424 | 13.8854 | 13.1777 | 13.5424 | 13.1777 | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 15000.0 |  | MV | 1 | 1 | 20.6829 | 24.064 | 30.387 | 3 | 22b46d3c-1104-4a6b-baf0-791554532cbe, c84967ed-4e26-4447-aaec-39d0dba00695, 08fe15ea-b154-4270-ad96-7633898d9feb | A, B, C | 3 | 7163.212 | 7022.253 | 7377.317 | 7166.3879 | 7035.194 | 7382.854 | 7160.7653 | 7029.085 | 7383.732 | 1.0523 | 1.0523 | 1.0523
4 | 5 | GSO_144 | GSO_144 | High | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis | br_024_22 | 36.046 | -79.947 | 12000 | 12 | 11.4 | 0.057412 | 0.090084 | 0.13286 | 2024-01-20 21:00 | 0.50361 | 0.79021 | 1.1655 | 1 | 0 | 0 | 1 | 1 | 2 | 1 | line_5978_22 | line_5978_22 | 600 | 12.47 | 12.9592 | 12.3112 | 12.9592 | 12.9592 | 12.9592 | 12.3112 | 12.3112 | 12.3112 | Single entrance line plausibly supports breaker rating | 7217.5112 | 7209.1507 | 7157.1647 | 7296.9693 | 7017.431 | 7389.952 | 7216.3559 |  | 7218.6666 | SCADA interpreted as phase-to-neutral volts | 0.24937 | Strong nominal-voltage agreement | 11.4 | 11.2671 | 11.2671 | 11.4 | 11.2671 | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 12000.0 |  | MV | 1 | 1 | 4.7843 | 7.507 | 11.072 | 3 | cebe0434-4e95-4fd2-8e1e-22573f21abf5, bd7e1df8-2eb1-4167-bee8-930536ce0573, 82536324-6f01-4e66-a011-7b067544a9ac | A, B, C | 3 | 7160.9817 | 7017.431 | 7389.952 |  |  |  | 7157.1647 | 7026.196 | 7366.826 | 0.92598 | 0.92598 | 0.92598
5 | 6 | GSO_141 | GSO_141 | High | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis | br_021_22 | 36.0459 | -79.947 | 12000 | 12 | 11.4 | 0.23482 | 0.29074 | 0.37996 | 2024-01-21 01:00 | 2.0598 | 2.5504 | 3.3329 | 1 | 0 | 0 | 1 | 1 | 2 | 1 | line_4565_22 | line_4565_22 | 660 | 12.47 | 14.2551 | 13.5424 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | Single entrance line plausibly supports breaker rating | 7210.2786 | 7205.3318 | 7159.172 | 7272.2117 | 7014.988 | 7405.181 | 7211.8626 | 7209.5135 | 7209.4599 | SCADA interpreted as phase-to-neutral volts | 0.14891 | Strong nominal-voltage agreement | 11.4 | 11.02 | 11.02 | 11.4 | 11.02 | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 12000.0 |  | MV | 1 | 1 | 19.5682 | 24.2286 | 31.663 | 3 | 78f844cc-a5b4-4d9d-ba33-ef854d68bc8a, b6f787f7-5117-4b48-81f4-ddbe099f96d7, 0b5869b0-b194-4a18-8593-e04336ade6ea | A, B, C | 3 | 7159.172 | 7020.645 | 7365.578 | 7164.8927 | 7041.681 | 7394.606 | 7162.938 | 7014.988 | 7405.181 | 0.8418 | 0.8418 | 0.8418
6 | 10 | GSO_127 | GSO_127 | High | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis | br_07_22 | 36.0974 | -79.9235 | 10000 | 10 | 9.5 | 0.012603 | 0.016656 | 0.025212 | 2024-01-20 21:00 | 0.13266 | 0.17533 | 0.26539 | 1 | 0 | 0 | 1 | 1 | 2 | 1 | line_6871_22 | line_6871_22 | 660 | 12.47 | 14.2551 | 13.5424 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | Single entrance line plausibly supports breaker rating | 7204.8208 | 7201.1828 | 7160.8637 | 7257.6768 | 7003.738 | 7390.05 | 7204.7881 | 7204.7955 | 7204.8787 | SCADA interpreted as phase-to-neutral volts | 0.073101 | Strong nominal-voltage agreement | 9.5 | 9.4748 | 9.4748 | 9.5 | 9.4748 | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 10000.0 |  | MV | 1 | 1 | 1.0502 | 1.388 | 2.101 | 3 | a16d8ea2-fafa-4870-8bff-75e352b48100, 1287cfdf-d61b-4b7d-9c56-4a67e583be03, 9962595a-e18a-4855-ab7a-6bcfb11262e4 | A, B, C | 3 | 7160.8637 | 7003.738 | 7385.541 | 7161.2317 | 7025.791 | 7390.05 | 7160.9694 | 7019.075 | 7384.944 | 0.7015 | 0.7015 | 0.7015
7 | 11 | GSO_73 | GSO_73 | High | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis | br_073_21 | 36.0825 | -79.7708 | 10000 | 10 | 9.5 | 0.053536 | 0.06612 | 0.097896 | 2024-01-20 20:00 | 0.56354 | 0.696 | 1.0305 | 1 | 0 | 0 | 1 | 1 | 2 | 1 | line_129349_21 | line_129349_21 | 600 | 12.47 | 12.9592 | 12.3112 | 12.9592 | 12.9592 | 12.9592 | 12.3112 | 12.3112 | 12.3112 | Single entrance line plausibly supports breaker rating | 7208.3306 | 7201.901 | 7161.2791 | 7273.6752 | 6987.051 | 7403.747 | 7209.9501 | 7207.1411 | 7207.9008 | SCADA interpreted as phase-to-neutral volts | 0.12185 | Strong nominal-voltage agreement | 9.5 | 9.4021 | 9.4021 | 9.5 | 9.4021 | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE3 | S_nSSEE3_12.47 | 10000.0 |  | MV | 1 | 1 | 4.4614 | 5.51 | 8.158 | 3 | dd7e3ea9-a097-46d9-ba3d-e976877c959f, dc0e22aa-9b17-4812-81b9-805e6e2fcea4, 0a5bd7a0-8dda-4ea9-8140-b43dcad4334a | A, B, C | 3 | 7168.1261 | 7039.737 | 7384.712 | 7165.0548 | 7041.153 | 7394.523 | 7161.2791 | 6987.051 | 7403.747 | 0.77165 | 0.77165 | 0.77165
8 | 12 | GSO_128 | GSO_128 | High | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis | br_08_22 | 36.0974 | -79.9234 | 10000 | 10 | 9.5 | 0.096715 | 0.11608 | 0.15013 | 2024-07-16 02:00 | 1.0181 | 1.2219 | 1.5803 | 1 | 0 | 0 | 1 | 1 | 2 | 1 | line_6872_22 | line_6872_22 | 660 | 12.47 | 14.2551 | 13.5424 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | Single entrance line plausibly supports breaker rating | 7209.2014 | 7203.343 | 7164.4391 | 7273.6893 | 7024.028 | 7401.973 | 7210.8994 | 7208.2738 | 7208.431 | SCADA interpreted as phase-to-neutral volts | 0.13395 | Strong nominal-voltage agreement | 9.5 | 9.3499 | 9.3499 | 9.5 | 9.3499 | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 10000.0 |  | MV | 1 | 1 | 8.0596 | 9.673 | 12.511 | 3 | 692be577-442c-4ab0-b1e1-5785854345e2, 6cff9753-e438-465f-8082-4b41468b4f8c, 3d10e996-315d-4229-9b7c-a9b8e0697db8 | A, B, C | 3 | 7164.4391 | 7053.457 | 7401.973 | 7167.6267 | 7024.028 | 7388.792 | 7164.855 | 7046.559 | 7390.925 | 0.7015 | 0.7015 | 0.7015
9 | 13 | GSO_126 | GSO_126 | High | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis | br_06_22 | 36.0974 | -79.9235 | 10000 | 10 | 9.5 | 0.15702 | 0.18904 | 0.24218 | 2024-01-20 21:00 | 1.6529 | 1.9899 | 2.5493 | 1 | 0 | 0 | 1 | 1 | 2 | 1 | line_6387_22 | line_6387_22 | 660 | 12.47 | 14.2551 | 13.5424 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | Single entrance line plausibly supports breaker rating | 7209.3824 | 7203.0248 | 7158.9918 | 7275.944 | 7007.034 | 7404.106 | 7208.8983 | 7210.81 | 7208.439 | SCADA interpreted as phase-to-neutral volts | 0.13646 | Strong nominal-voltage agreement | 9.5 | 9.2578 | 9.2578 | 9.5 | 9.2578 | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 10000.0 |  | MV | 1 | 1 | 13.0851 | 15.753 | 20.182 | 3 | 9006b8b1-eda0-485b-a8d0-426580b8950f, bc3fda03-9c4b-412b-a5ef-6db07eeba8fc, 12d09ac1-fdb6-467e-a1aa-f99f6eed49f6 | A, B, C | 3 | 7160.3681 | 7007.034 | 7391.187 | 7163.7595 | 7031.745 | 7404.106 | 7158.9918 | 7034.591 | 7393.787 | 0.7015 | 0.7015 | 0.7015
10 | 14 | GSO_55 | GSO_55 | High | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis | br_062_21 | 36.0131 | -79.8489 | 10000 | 10 | 9.5 | 0.12347 | 0.19112 | 0.26848 | 2024-01-20 10:00 | 1.2997 | 2.0118 | 2.8261 | 1 | 0 | 0 | 1 | 1 | 2 | 1 | line_128388_21 | line_128388_21 | 600 | 12.47 | 12.9592 | 12.3112 | 12.9592 | 12.9592 | 12.9592 | 12.3112 | 12.3112 | 12.3112 | Single entrance line plausibly supports breaker rating | 7214.4961 | 7206.7808 | 7161.4228 | 7287.5 | 7035.722 | 7395.43 | 7210.8371 | 7215.7627 | 7216.8887 | SCADA interpreted as phase-to-neutral volts | 0.20749 | Strong nominal-voltage agreement | 9.5 | 9.2315 | 9.2315 | 9.5 | 9.2315 | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE17 | S_nSSEE17_12.47 | 10000.0 |  | MV | 1 | 1 | 10.2891 | 15.9266 | 22.373 | 3 | 55b291eb-5761-4e7f-8635-63057f856791, 0d627f19-7146-43b0-9f7b-bac68e9966db, efb7b851-1f6e-4084-9dd6-5a62049b7654 | A, B, C | 3 | 7172.5084 | 7035.722 | 7395.43 | 7161.4228 | 7043.239 | 7364.353 | 7162.8197 | 7044.503 | 7340.372 | 0.77165 | 0.77165 | 0.77165
11 | 16 | GSO_119 | GSO_119 | High | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis | br_0119_21 | 36.0426 | -79.8533 | 10000 | 10 | 9.5 | 0.14971 | 0.23111 | 0.33516 | 2024-01-20 22:00 | 1.5759 | 2.4327 | 3.528 | 1 | 0 | 0 | 1 | 1 | 2 | 1 | line_132380_21 | line_132380_21 | 660 | 12.47 | 14.2551 | 13.5424 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | Single entrance line plausibly supports breaker rating | 7217.6371 | 7208.9533 | 7159.6174 | 7295.6686 | 7027.404 | 7375.598 | 7218.6921 | 7216.6741 | 7217.545 | SCADA interpreted as phase-to-neutral volts | 0.25112 | Strong nominal-voltage agreement | 9.5 | 9.1648 | 9.1648 | 9.5 | 9.1648 | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE9 | S_nSSEE9_12.47 | 10000.0 |  | MV | 1 | 1 | 12.4758 | 19.259 | 27.93 | 3 | 1a46aa48-ac4e-4046-aa43-a61c07c816d6, faec1da7-65b2-4b86-be90-e4357dfde1ce, 3aad3364-ed36-4087-b7d0-6d3b3fa6f823 | A, B, C | 3 | 7159.6174 | 7027.404 | 7371.066 | 7163.2609 | 7051.481 | 7370.381 | 7162.5343 | 7031.642 | 7375.598 | 0.7015 | 0.7015 | 0.7015
12 | 23 | GSO_131 | GSO_131 | High | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis | br_011_22 | 36.0811 | -79.94 | 8571.4 | 8.5714 | 8.1428 | 0.04523 | 0.053576 | 0.073452 | 2024-01-20 18:00 | 0.55545 | 0.65796 | 0.90205 | 1 | 0 | 0 | 1 | 1 | 2 | 1 | line_4538_22 | line_4538_22 | 660 | 12.47 | 14.2551 | 13.5424 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | Single entrance line plausibly supports breaker rating | 7209.3212 | 7203.5 | 7165.9882 | 7265.7639 | 6987.82 | 7394.459 | 7209.2825 | 7209.4486 | 7209.2326 | SCADA interpreted as phase-to-neutral volts | 0.13561 | Strong nominal-voltage agreement | 8.1428 | 8.0694 | 8.0694 | 8.1428 | 8.0694 | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 8571.4 |  | MV | 1 | 1 | 3.7691 | 4.4646 | 6.121 | 3 | 434fff6c-2804-492a-a7e9-8c978d0dc8e3, 1a6f96c2-84f7-4c0d-b1a3-ee2364b2f450, 618c145a-b95c-4f8d-9e8d-9389861004d6 | A, B, C | 3 | 7166.6618 | 7010.312 | 7387.689 | 7166.3811 | 7001.625 | 7386.858 | 7165.9882 | 6987.82 | 7394.459 | 0.60129 | 0.60129 | 0.60129
13 | 25 | GSO_129 | GSO_129 | High | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis | br_09_22 | 36.0811 | -79.94 | 8571.4 | 8.5714 | 8.1428 | 0.17276 | 0.20905 | 0.26306 | 2024-01-22 04:00 | 2.1216 | 2.5673 | 3.2306 | 1 | 0 | 0 | 1 | 1 | 2 | 1 | line_3574_22 | line_3574_22 | 660 | 12.47 | 14.2551 | 13.5424 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | Single entrance line plausibly supports breaker rating | 7211.198 | 7205.0408 | 7160.769 | 7281.385 | 7013.679 | 7397.262 | 7213.2723 | 7210.6698 | 7209.6521 | SCADA interpreted as phase-to-neutral volts | 0.16168 | Strong nominal-voltage agreement | 8.1428 | 7.8798 | 7.8798 | 8.1428 | 7.8798 | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 8571.4 |  | MV | 1 | 1 | 14.3968 | 17.421 | 21.922 | 3 | 686b2171-718b-454f-a63f-7a08af910b78, 066b1670-e5b9-40c9-bd97-907fe78b74e9, ca9fa130-fc7c-477e-8464-326c962a06af | A, B, C | 3 | 7160.769 | 7013.679 | 7390.702 | 7162.8377 | 7041.943 | 7390.199 | 7163.1615 | 7020.903 | 7397.262 | 0.60129 | 0.60129 | 0.60129
14 | 29 | GSO_132 | GSO_132 | High | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis | br_012_22 | 36.0811 | -79.94 | 8571.4 | 8.5714 | 8.1428 | 0.32331 | 0.37998 | 0.45876 | 2024-01-20 21:00 | 3.9705 | 4.6664 | 5.6339 | 1 | 0 | 0 | 1 | 1 | 2 | 1 | line_4993_22 | line_4993_22 | 660 | 12.47 | 14.2551 | 13.5424 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | Single entrance line plausibly supports breaker rating | 7210.7364 | 7204.5092 | 7159.8988 | 7279.6497 | 7025.031 | 7404.132 | 7213.453 | 7209.726 | 7209.0302 | SCADA interpreted as phase-to-neutral volts | 0.15527 | Strong nominal-voltage agreement | 8.1428 | 7.6841 | 7.6841 | 8.1428 | 7.6841 | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 8571.4 |  | MV | 1 | 1 | 26.9423 | 31.6646 | 38.23 | 3 | 935c3854-ba34-4cf1-b241-c865be78d3bf, 0716ea38-77d5-4d34-bc24-820dc14d344a, 8eae3b99-7252-4faf-9a4e-4abe914bc30e | A, B, C | 3 | 7163.2874 | 7053.594 | 7404.132 | 7159.8988 | 7025.913 | 7385.751 | 7159.9821 | 7025.031 | 7394.927 | 0.60129 | 0.60129 | 0.60129
15 | 34 | GSO_31 | GSO_31 | High | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis | br_038_21 | 36.1038 | -79.7639 | 7500 | 7.5 | 7.125 | 0.014254 | 0.022212 | 0.036228 | 2024-07-15 08:00 | 0.20005 | 0.31175 | 0.50846 | 1 | 0 | 0 | 1 | 1 | 2 | 1 | line_132463_21 | line_132463_21 | 660 | 12.47 | 14.2551 | 13.5424 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | Single entrance line plausibly supports breaker rating | 7205.575 | 7202.019 | 7162.3874 | 7253.6983 | 7007.792 | 7400.844 | 7205.6752 | 7205.5093 | 7205.5404 | SCADA interpreted as phase-to-neutral volts | 0.083576 | Strong nominal-voltage agreement | 7.125 | 7.0888 | 7.0888 | 7.125 | 7.0888 | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE13 | S_nSSEE13_12.47 | 7500.0 |  | MV | 1 | 1 | 1.1878 | 1.851 | 3.019 | 3 | dbd51660-93ed-49dc-b484-ac1a2ff93751, c4bbbd0b-e3cc-4312-b11b-48dca067f34f, f5f51af7-9112-4286-adaa-37e4589d054a | A, B, C | 3 | 7162.9195 | 7007.792 | 7399.343 | 7162.492 | 7042.522 | 7400.844 | 7162.3874 | 7031.065 | 7394.573 | 0.52613 | 0.52613 | 0.52613
16 | 35 | GSO_149 | GSO_149 | High | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis | br_029_22 | 36.114 | -79.9604 | 7500 | 7.5 | 7.125 | 0.056658 | 0.069716 | 0.091644 | 2024-01-17 05:00 | 0.7952 | 0.97848 | 1.2862 | 1 | 0 | 0 | 1 | 1 | 2 | 1 | line_6853_22 | line_6853_22 | 660 | 12.47 | 14.2551 | 13.5424 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | Single entrance line plausibly supports breaker rating | 7210.2175 | 7203.7413 | 7163.1871 | 7279.0988 | 7024.226 | 7401.624 | 7208.2833 | 7208.816 | 7213.5533 | SCADA interpreted as phase-to-neutral volts | 0.14806 | Strong nominal-voltage agreement | 7.125 | 7.0334 | 7.0334 | 7.125 | 7.0334 | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 7500.0 |  | MV | 1 | 1 | 4.7215 | 5.8096 | 7.637 | 3 | 54f22dd6-dae8-4d6f-8c00-4ee16cc1bce1, a7d55959-39f6-4006-8a75-2ac4375060d6, 22ef08a2-8b87-47bf-912f-a49f8dbe4e0e | A, B, C | 3 | 7165.231 | 7024.226 | 7392.547 | 7163.1871 | 7025.5 | 7401.624 | 7165.2724 | 7041.983 | 7380.284 | 0.52613 | 0.52613 | 0.52613
17 | 36 | GSO_28 | GSO_28 | High | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis | br_035_21 | 36.1038 | -79.7639 | 7500 | 7.5 | 7.125 | 0.062273 | 0.079944 | 0.11803 | 2024-01-20 11:00 | 0.874 | 1.122 | 1.6566 | 1 | 0 | 0 | 1 | 1 | 2 | 1 | line_114507_21 | line_114507_21 | 660 | 12.47 | 14.2551 | 13.5424 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | Single entrance line plausibly supports breaker rating | 7207.1091 | 7202.8208 | 7164.2104 | 7262.7566 | 7029.148 | 7397.887 | 7207.8215 | 7208.8662 | 7204.6396 | SCADA interpreted as phase-to-neutral volts | 0.10488 | Strong nominal-voltage agreement | 7.125 | 7.007 | 7.007 | 7.125 | 7.007 | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE13 | S_nSSEE13_12.47 | 7500.0 |  | MV | 1 | 1 | 5.1894 | 6.662 | 9.836 | 3 | c3250712-a026-44dc-83b1-ab0b7bd1cef0, 4cc07d73-767d-4a92-aa56-8d6f6139433c, 4b1de06e-7ccd-42bd-ba7d-141a0d6eed10 | A, B, C | 3 | 7165.3747 | 7048.269 | 7385.741 | 7164.2104 | 7029.148 | 7397.887 | 7165.0645 | 7038.083 | 7386.067 | 0.52613 | 0.52613 | 0.52613
18 | 39 | GSO_113 | GSO_113 | High | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis | br_0113_21 | 36.0543 | -79.8942 | 7142.9 | 7.1429 | 6.7858 | 0.053802 | 0.065088 | 0.091248 | 2024-01-20 20:00 | 0.79287 | 0.95919 | 1.3447 | 1 | 0 | 0 | 1 | 1 | 2 | 1 | line_128560_21 | line_128560_21 | 660 | 12.47 | 14.2551 | 13.5424 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | Single entrance line plausibly supports breaker rating | 7207.7258 | 7202.7598 | 7166.094 | 7265.2236 | 7003.726 | 7393.634 | 7205.9252 | 7209.7353 | 7207.5169 | SCADA interpreted as phase-to-neutral volts | 0.11345 | Strong nominal-voltage agreement | 6.7858 | 6.6945 | 6.6945 | 6.7858 | 6.6945 | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE8 | S_nSSEE8_12.47 | 7142.9 |  | MV | 1 | 1 | 4.4835 | 5.424 | 7.604 | 3 | f8ddca03-2f28-483b-97fe-a4538d6c4e2b, a9bc380c-ca71-4a2b-b314-0f03f9f76581, bdf27366-2b21-4e21-8946-86b299b81d14 | A, B, C | 3 | 7167.059 | 7003.726 | 7393.634 | 7167.5237 | 7042.923 | 7389.602 | 7166.094 | 7024.062 | 7389.029 | 0.50108 | 0.50108 | 0.50108
19 | 42 | GSO_76 | GSO_76 | High | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis | br_076_21 | 36.0719 | -79.8252 | 6666.7 | 6.6667 | 6.3334 | 0.02376 | 0.036908 | 0.052824 | 2024-01-20 23:00 | 0.37515 | 0.58276 | 0.83406 | 1 | 0 | 0 | 1 | 1 | 2 | 1 | line_116886_21 | line_116886_21 | 600 | 12.47 | 12.9592 | 12.3112 | 12.9592 | 12.9592 | 12.9592 | 12.3112 | 12.3112 | 12.3112 | Single entrance line plausibly supports breaker rating | 7215.5004 | 7207.7875 | 7164.72 | 7281.96 | 7058.493 | 7370.531 |  |  | 7215.5004 | SCADA interpreted as phase-to-neutral volts | 0.22144 | Strong nominal-voltage agreement | 6.3334 | 6.2805 | 6.2805 | 6.3334 | 6.2805 | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV | 1 | 1 | 1.98 | 3.0756 | 4.402 | 3 | 89cbe802-faf3-4709-b370-afa1154a5b70, fd14c6a3-6658-4039-a0b8-c00ab26e307c, a61580ad-490f-42dd-919c-3cfdfb775908 | A, B, C | 3 | [6 empty] | 7164.72 | 7058.493 | 7370.531 | 0.51444 | 0.51444 | 0.51444
20 | 45 | GSO_78 | GSO_78 | High | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis | br_078_21 | 36.0719 | -79.8252 | 6666.7 | 6.6667 | 6.3334 | 0.16943 | 0.24664 | 0.32894 | 2024-01-18 04:00 | 2.6752 | 3.8944 | 5.1938 | 1 | 0 | 0 | 1 | 1 | 2 | 1 | line_121156_21 | line_121156_21 | 600 | 12.47 | 12.9592 | 12.3112 | 12.9592 | 12.9592 | 12.9592 | 12.3112 | 12.3112 | 12.3112 | Single entrance line plausibly supports breaker rating | 7218.1923 | 7208.7643 | 7158.4231 | 7296.0196 | 7019.933 | 7383.27 | 7218.3944 | 7217.9901 |  | SCADA interpreted as phase-to-neutral volts | 0.25883 | Strong nominal-voltage agreement | 6.3334 | 6.0044 | 6.0044 | 6.3334 | 6.0044 | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV | 1 | 1 | 14.1194 | 20.5536 | 27.412 | 3 | c0ddba19-fbd3-4341-bb7c-f8d96301d889, 648e5aaa-f39d-4756-9d09-ca5503bbc225, 838a2e79-8d23-4760-9eab-eb6ed2d38b4c | A, B, C | 3 | 7161.9514 | 7019.933 | 7383.27 | 7158.4231 | 7041.958 | 7371.452 |  |  |  | 0.51444 | 0.51444 | 0.51444
21 | 51 | GSO_152 | GSO_152 | High | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis | br_032_22 | 36.0823 | -79.9238 | 6000 | 6 | 5.7 | 0.012 | 0.01728 | 0.0261 | 2024-01-20 16:00 | 0.21052 | 0.30316 | 0.45789 | 1 | 0 | 0 | 1 | 1 | 2 | 1 | line_6573_22 | line_6573_22 | 660 | 12.47 | 14.2551 | 13.5424 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | Single entrance line plausibly supports breaker rating | 7204.4128 | 7202.2422 | 7159.6395 | 7251.687 | 7028.385 | 7411.777 | 7204.3444 | 7204.4102 | 7204.484 | SCADA interpreted as phase-to-neutral volts | 0.067435 | Strong nominal-voltage agreement | 5.7 | 5.6739 | 5.6739 | 5.7 | 5.6739 | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE6 | S_nSSEE6_12.47 | 6000.0 |  | MV | 1 | 1 | 0.99999 | 1.44 | 2.175 | 3 | 3f75484a-66ad-416b-bdfc-429bf783f99d, ab723fc3-e0cb-4dbc-8181-5681e5ac3348, 3b38bb39-6b77-49e7-b0c7-d3c699da74dc | A, B, C | 3 | 7159.6449 | 7028.385 | 7386.467 | 7159.6395 | 7032.64 | 7398.936 | 7159.6744 | 7033.175 | 7411.777 | 0.4209 | 0.4209 | 0.4209
22 | 52 | GSO_38 | GSO_38 | High | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis | br_045_21 | 36.121 | -79.8612 | 6000 | 6 | 5.7 | 0.015622 | 0.024204 | 0.042336 | 2024-01-20 09:00 | 0.27407 | 0.42463 | 0.74274 | 1 | 0 | 0 | 1 | 1 | 2 | 1 | line_107900_21 | line_107900_21 | 660 | 12.47 | 14.2551 | 13.5424 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | Single entrance line plausibly supports breaker rating | 7215.0596 | 7207.5355 | 7170.1838 | 7276.2219 | 7064.572 | 7342.778 | 7215.0596 |  |  | SCADA interpreted as phase-to-neutral volts | 0.21531 | Strong nominal-voltage agreement | 5.7 | 5.6577 | 5.6577 | 5.7 | 5.6577 | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE15 | S_nSSEE15_12.47 | 6000.0 |  | MV | 1 | 1 | 1.3018 | 2.017 | 3.528 | 3 | 9c1dc66a-d26b-42ae-9fa5-d4e46c87f492, 31c14863-6ede-40c4-86a5-41eadc729ac2, 15e8162e-962b-481f-923b-b2fe7c7ce432 | A, B, C | 3 | 7170.1838 | 7064.572 | 7342.778 | [6 empty] | 0.4209 | 0.4209 | 0.4209
23 | 55 | GSO_150 | GSO_150 | High | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis | br_030_22 | 36.0823 | -79.9238 | 6000 | 6 | 5.7 | 0.13007 | 0.15808 | 0.22006 | 2024-01-20 11:00 | 2.2819 | 2.7733 | 3.8606 | 1 | 0 | 0 | 1 | 1 | 2 | 1 | line_4767_22 | line_4767_22 | 660 | 12.47 | 14.2551 | 13.5424 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | Single entrance line plausibly supports breaker rating | 7211.1571 | 7204.4073 | 7163.9424 | 7272.6516 | 7013.469 | 7394.933 | 7210.7203 | 7211.7125 | 7211.0384 | SCADA interpreted as phase-to-neutral volts | 0.16111 | Strong nominal-voltage agreement | 5.7 | 5.4799 | 5.4799 | 5.7 | 5.4799 | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE6 | S_nSSEE6_12.47 | 6000.0 |  | MV | 1 | 1 | 10.8391 | 13.173 | 18.338 | 3 | 99ca8035-36a9-410b-844c-06c1ddb4c66b, 97ae36fa-2e65-4c6d-8a11-b6c4ba921c0d, e18873a3-19e0-4c86-abaf-03f1ea49ef98 | A, B, C | 3 | 7166.3364 | 7039.77 | 7380.158 | 7168.0683 | 7013.469 | 7378.148 | 7163.9424 | 7039.447 | 7394.933 | 0.4209 | 0.4209 | 0.4209
24 | 56 | GSO_33 | GSO_33 | High | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis | br_040_21 | 36.0466 | -79.7995 | 6666.7 | 6.6667 | 6.3334 | 0.5803 | 0.70153 | 0.88399 | 2024-01-20 15:00 | 9.1626 | 11.0768 | 13.9577 | 1 | 0 | 0 | 1 | 1 | 2 | 1 | line_111181_21 | line_111181_21 | 660 | 12.47 | 14.2551 | 13.5424 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | Single entrance line plausibly supports breaker rating | 7212.8077 | 7206.0918 | 7162.3044 | 7283.099 | 7025.724 | 7403.903 | 7210.837 | 7214.7614 | 7212.8247 | SCADA interpreted as phase-to-neutral volts | 0.18404 | Strong nominal-voltage agreement | 6.3334 | 5.4494 | 5.4494 | 6.3334 | 5.4494 | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE14 | S_nSSEE14_12.47 | 6666.7 |  | MV | 1 | 1 | 48.3582 | 58.461 | 73.666 | 3 | ee1a565e-ae8b-4984-9f7a-cab15b5447c3, 2bcc2cc5-82f5-4040-ac32-a00d0d07de51, d858a33a-1b66-4073-aed2-4b1a30ad837b | A, B, C | 3 | 7163.6324 | 7034.404 | 7351.762 | 7165.1263 | 7045.968 | 7388.206 | 7162.3044 | 7025.724 | 7403.903 | 0.46767 | 0.46767 | 0.46767
25 | 58 | GSO_137 | GSO_137 | High | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis | br_017_22 | 36.0705 | -79.9557 | 6000 | 6 | 5.7 | 0.21405 | 0.25138 | 0.30721 | 2024-01-20 18:00 | 3.7553 | 4.4101 | 5.3897 | 1 | 0 | 0 | 1 | 1 | 2 | 1 | line_5445_22 | line_5445_22 | 660 | 12.47 | 14.2551 | 13.5424 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | Single entrance line plausibly supports breaker rating | 7212.3065 | 7205.9177 | 7160.45 | 7281.0173 | 7030.635 | 7392.03 | 7213.852 | 7211.1325 | 7211.9349 | SCADA interpreted as phase-to-neutral volts | 0.17707 | Strong nominal-voltage agreement | 5.7 | 5.3928 | 5.3928 | 5.7 | 5.3928 | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE3 | S_nSSEE3_12.47 | 6000.0 |  | MV | 1 | 1 | 17.8375 | 20.948 | 25.601 | 3 | cf094241-cd71-4a00-ae80-c341e78225f3, d0f42d15-cf63-4976-b310-0a7f21c9a7fc, bb261d99-e16f-41bf-90d2-05acc7b4f39c | A, B, C | 3 | 7160.45 | 7030.635 | 7384.785 | 7161.4777 | 7034.534 | 7378.7 | 7162.634 | 7038.113 | 7392.03 | 0.4209 | 0.4209 | 0.4209
26 | 60 | GSO_3 | GSO_3 | High | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis | br_03_21 | 36.0852 | -79.8826 | 5714.3 | 5.7143 | 5.4286 | 0.014119 | 0.021876 | 0.038244 | 2024-07-15 08:00 | 0.26008 | 0.40298 | 0.70449 | 1 | 0 | 0 | 1 | 1 | 2 | 1 | line_118795_21 | line_118795_21 | 600 | 12.47 | 12.9592 | 12.3112 | 12.9592 | 12.9592 | 12.9592 | 12.3112 | 12.3112 | 12.3112 | Single entrance line plausibly supports breaker rating | 7217.7714 | 7208.2625 | 7171.604 | 7286.2557 | 7053.453 | 7383.62 | 7217.7714 |  |  | SCADA interpreted as phase-to-neutral volts | 0.25298 | Strong nominal-voltage agreement | 5.4286 | 5.3903 | 5.3903 | 5.4286 | 5.3903 | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 5714.3 |  | MV | 1 | 1 | 1.1766 | 1.823 | 3.187 | 3 | cabb02b4-86e3-4261-87ef-66f06902bb61, 262d1506-d23e-42d2-a938-f15cb2f35365, 861d3fe8-4f6d-46b5-bb00-6d79ddaf889d | A, B, C | 3 | 7171.604 | 7053.453 | 7383.62 | [6 empty] | 0.44095 | 0.44095 | 0.44095
27 | 62 | GSO_102 | GSO_102 | High | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis | br_0102_21 | 36.0872 | -79.897 | 5714.3 | 5.7143 | 5.4286 | 0.021543 | 0.0333 | 0.05448 | 2024-07-15 23:00 | 0.39685 | 0.61342 | 1.0036 | 1 | 0 | 0 | 1 | 1 | 2 | 1 | line_127499_21 | line_127499_21 | 660 | 12.47 | 14.2551 | 13.5424 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | Single entrance line plausibly supports breaker rating | 7216.7715 | 7207.7722 | 7163.308 | 7289.008 | 7050.956 | 7390.816 | 7215.2337 |  | 7218.3094 | SCADA interpreted as phase-to-neutral volts | 0.23909 | Strong nominal-voltage agreement | 5.4286 | 5.3741 | 5.3741 | 5.4286 | 5.3741 | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE7 | S_nSSEE7_12.47 | 5714.3 |  | MV | 1 | 1 | 1.7953 | 2.775 | 4.54 | 3 | aaef163c-bdc4-464e-9864-b0c0ebdf8662, 3f11f59f-b6f2-44fe-8a16-f4a87144ca07, 58383f3b-39ee-41c1-9a45-f21c6b309b7c | A, B, C | 3 | 7163.308 | 7050.956 | 7388.052 |  |  |  | 7174.9384 | 7054.77 | 7390.816 | 0.40086 | 0.40086 | 0.40086
28 | 63 | GSO_161 | GSO_161 | High | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis | br_07_23 | 36.2604 | -79.5886 | 5714.3 | 5.7143 | 5.4286 | 0.028877 | 0.044532 | 0.06714 | 2024-01-20 21:00 | 0.53194 | 0.82032 | 1.2368 | 1 | 0 | 0 | 1 | 1 | 2 | 1 | line_12976_23 | line_12976_23 | 660 | 12.47 | 14.2551 | 13.5424 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | Single entrance line plausibly supports breaker rating | 7216.0198 | 7207.331 | 7166.9864 | 7301.8819 | 7029.94 | 7392.414 | 7210.751 |  | 7221.2886 | SCADA interpreted as phase-to-neutral volts | 0.22865 | Strong nominal-voltage agreement | 5.4286 | 5.3614 | 5.3614 | 5.4286 | 5.3614 | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 5714.3 |  | MV | 1 | 1 | 2.4064 | 3.711 | 5.595 | 3 | 89a3b24a-887f-4195-8344-51f18a00dbf7, c4eee589-eb1d-4947-bc9b-3f547ec858d4, e61fb2d3-e704-4d3f-bf86-8b04c3724fd7 | A, B, C | 3 | 7169.174 | 7029.94 | 7388.204 |  |  |  | 7166.9864 | 7061.061 | 7392.414 | 0.40086 | 0.40086 | 0.40086
29 | 64 | GSO_136 | GSO_136 | High | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis | br_016_22 | 36.0705 | -79.9556 | 6000 | 6 | 5.7 | 0.22044 | 0.26099 | 0.34441 | 2024-01-17 16:00 | 3.8674 | 4.5787 | 6.0423 | 1 | 0 | 0 | 1 | 1 | 2 | 1 | line_4976_22 | line_4976_22 | 660 | 12.47 | 14.2551 | 13.5424 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | Single entrance line plausibly supports breaker rating | 7209.1278 | 7203.8727 | 7162.9973 | 7270.215 | 7007.673 | 7388.402 | 7208.1837 | 7210.4734 | 7208.7264 | SCADA interpreted as phase-to-neutral volts | 0.13292 | Strong nominal-voltage agreement | 5.7 | 5.3556 | 5.3556 | 5.7 | 5.3556 | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE3 | S_nSSEE3_12.47 | 6000.0 |  | MV | 1 | 1 | 18.3703 | 21.749 | 28.701 | 3 | 04ce7e89-fb0f-4fb3-9752-836af1c7ab9e, 1985324e-e67a-4d01-bf4e-cbc1776ba800, 66b785ca-af8e-4a6a-8af7-ff9241ec96a5 | A, B, C | 3 | 7162.9973 | 7026.756 | 7382.77 | 7165.3344 | 7007.673 | 7388.402 | 7163.9968 | 7022.48 | 7377.629 | 0.4209 | 0.4209 | 0.4209
30 | 66 | GSO_106 | GSO_106 | High | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis | br_0106_21 | 36.0872 | -79.897 | 5714.3 | 5.7143 | 5.4286 | 0.041269 | 0.064536 | 0.09288 | 2024-01-20 10:00 | 0.76021 | 1.1888 | 1.7109 | 1 | 0 | 0 | 1 | 1 | 2 | 1 | line_131696_21 | line_131696_21 | 660 | 12.47 | 14.2551 | 13.5424 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | Single entrance line plausibly supports breaker rating | 7219.7757 | 7209.4073 | 7161.0111 | 7301.3522 | 7029.431 | 7401.993 | 7219.34 |  | 7220.2115 | SCADA interpreted as phase-to-neutral volts | 0.28082 | Strong nominal-voltage agreement | 5.4286 | 5.3357 | 5.3357 | 5.4286 | 5.3357 | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE7 | S_nSSEE7_12.47 | 5714.3 |  | MV | 1 | 1 | 3.439 | 5.378 | 7.74 | 3 | 1523bf59-c426-49d7-add2-e9b831978748, e37ebffe-ff65-4277-a7e0-2315cac8c267, f0643cc7-b03a-4328-82d5-2924a650f97f | A, B, C | 3 | 7161.0111 | 7046.926 | 7388.014 |  |  |  | 7162.2897 | 7029.431 | 7401.993 | 0.40086 | 0.40086 | 0.40086
31 | 68 | GSO_107 | GSO_107 | High | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis | br_0107_21 | 36.0872 | -79.897 | 5714.3 | 5.7143 | 5.4286 | 0.068935 | 0.08376 | 0.11552 | 2024-07-16 01:00 | 1.2699 | 1.5429 | 2.1281 | 1 | 0 | 0 | 1 | 1 | 2 | 1 | line_132043_21 | line_132043_21 | 660 | 12.47 | 14.2551 | 13.5424 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | Single entrance line plausibly supports breaker rating | 7207.0077 | 7202.351 | 7166.9631 | 7258.7276 | 7022.37 | 7395.225 | 7208.5988 | 7206.0329 | 7206.3914 | SCADA interpreted as phase-to-neutral volts | 0.10348 | Strong nominal-voltage agreement | 5.4286 | 5.3131 | 5.3131 | 5.4286 | 5.3131 | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE7 | S_nSSEE7_12.47 | 5714.3 |  | MV | 1 | 1 | 5.7446 | 6.98 | 9.627 | 3 | 4113937f-0ce2-415a-9249-ce7327d121f7, 5d59abb9-0bac-4fa7-a891-4e9d4e794c88, b1339292-267a-4146-8873-ecfc9cb1a82e | A, B, C | 3 | 7170.413 | 7051.932 | 7387.587 | 7170.9994 | 7036.44 | 7392.051 | 7166.9631 | 7022.37 | 7395.225 | 0.40086 | 0.40086 | 0.40086
32 | 69 | GSO_138 | GSO_138 | High | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis | br_018_22 | 36.0705 | -79.9556 | 6000 | 6 | 5.7 | 0.22654 | 0.29495 | 0.38712 | 2024-01-21 04:00 | 3.9743 | 5.1745 | 6.7916 | 1 | 0 | 0 | 1 | 1 | 2 | 1 | line_5493_22 | line_5493_22 | 660 | 12.47 | 14.2551 | 13.5424 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | Single entrance line plausibly supports breaker rating | 7213.9852 | 7206.6448 | 7159.0362 | 7286.9579 | 7047.309 | 7388.782 | 7212.8076 | 7213.1858 | 7215.9621 | SCADA interpreted as phase-to-neutral volts | 0.20039 | Strong nominal-voltage agreement | 5.7 | 5.3129 | 5.3129 | 5.7 | 5.3129 | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE3 | S_nSSEE3_12.47 | 6000.0 |  | MV | 1 | 1 | 18.878 | 24.579 | 32.26 | 3 | c812a09e-5775-4fbc-93b7-37aa020f3a4a, b91b7108-02a6-4c8f-9294-9075747bf3d2, 8cf34f38-0fdb-4d44-9870-a7c9c5b5c3b4 | A, B, C | 3 | 7159.0362 | 7047.488 | 7388.782 | 7165.1264 | 7047.309 | 7385.392 | 7162.0994 | 7057.249 | 7356.492 | 0.4209 | 0.4209 | 0.4209
33 | 71 | GSO_8 | GSO_8 | High | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis | br_022_21 | 36.1003 | -79.8075 | 5555.6 | 5.5556 | 5.2778 | 0.022721 | 0.034476 | 0.058212 | 2024-01-20 17:00 | 0.43051 | 0.65322 | 1.103 | 1 | 0 | 0 | 1 | 1 | 2 | 1 | line_115508_21 | line_115508_21 | 660 | 12.47 | 14.2551 | 13.5424 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | Single entrance line plausibly supports breaker rating | 7214.2242 | 7206.8805 | 7166.1623 | 7277.7167 | 7023.839 | 7356.725 |  |  | 7214.2242 | SCADA interpreted as phase-to-neutral volts | 0.20371 | Strong nominal-voltage agreement | 5.2778 | 5.2196 | 5.2196 | 5.2778 | 5.2196 | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE10 | S_nSSEE10_12.47 | 5555.6 |  | MV | 1 | 1 | 1.8934 | 2.873 | 4.851 | 3 | 9e0bf50d-94bd-4e5d-9a43-95a506f4c534, 14a29c10-6f6b-4045-834c-a8cdccfa7fe8, 674756f5-28ec-40f8-8ece-cd6c8a394c18 | A, B, C | 3 | [6 empty] | 7166.1623 | 7023.839 | 7356.725 | 0.38973 | 0.38973 | 0.38973
34 | 72 | GSO_139 | GSO_139 | High | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis | br_019_22 | 36.0705 | -79.9557 | 6000 | 6 | 5.7 | 0.30302 | 0.3653 | 0.50093 | 2024-01-21 04:00 | 5.3161 | 6.4088 | 8.7882 | 1 | 0 | 0 | 1 | 1 | 2 | 1 | line_6094_22 | line_6094_22 | 660 | 12.47 | 14.2551 | 13.5424 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | Single entrance line plausibly supports breaker rating | 7208.9415 | 7204.6222 | 7165.2004 | 7263.2199 | 7002.039 | 7396.818 | 7210.2124 | 7210.0069 | 7206.6053 | SCADA interpreted as phase-to-neutral volts | 0.13034 | Strong nominal-voltage agreement | 5.7 | 5.1991 | 5.1991 | 5.7 | 5.1991 | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE3 | S_nSSEE3_12.47 | 6000.0 |  | MV | 1 | 1 | 25.2516 | 30.442 | 41.744 | 3 | 8781de87-205d-4b90-963f-449d72c41e8c, 2a67f2a3-ad9e-4413-af20-999870d5694e, 6ec0fb64-8f9d-48b6-81ae-63048adca78a | A, B, C | 3 | 7165.2004 | 7012.353 | 7396.818 | 7166.6663 | 7005.025 | 7389.219 | 7165.261 | 7002.039 | 7395.536 | 0.4209 | 0.4209 | 0.4209
35 | 74 | GSO_50 | GSO_50 | High | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis | br_057_21 | 36.0168 | -79.7965 | 5454.5 | 5.4545 | 5.1818 | 0.027447 | 0.042684 | 0.06354 | 2024-01-21 | 0.52969 | 0.82373 | 1.2262 | 1 | 0 | 0 | 1 | 1 | 2 | 1 | line_116016_21 | line_116016_21 | 600 | 12.47 | 12.9592 | 12.3112 | 12.9592 | 12.9592 | 12.9592 | 12.3112 | 12.3112 | 12.3112 | Single entrance line plausibly supports breaker rating | 7217.4479 | 7208.345 | 7162.6087 | 7289.8403 | 7048.205 | 7382.127 |  | 7217.4479 |  | SCADA interpreted as phase-to-neutral volts | 0.24849 | Strong nominal-voltage agreement | 5.1818 | 5.1182 | 5.1182 | 5.1818 | 5.1182 | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV | 1 | 1 | 2.2873 | 3.557 | 5.295 | 3 | 4d9bb5e2-1e06-49ed-b322-273c65c7ea12, 02cb60eb-e56b-45c0-871a-7d5da5072e9a, ceeee8fb-13b1-43c7-9caf-4433648f6846 | A, B, C | 3 |  |  |  | 7162.6087 | 7048.205 | 7382.127 |  |  |  | 0.4209 | 0.4209 | 0.4209
36 | 75 | GSO_44 | GSO_44 | High | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis | br_051_21 | 36.0168 | -79.7965 | 5454.5 | 5.4545 | 5.1818 | 0.026957 | 0.04086 | 0.065292 | 2024-01-21 | 0.52022 | 0.78853 | 1.26 | 1 | 0 | 0 | 1 | 1 | 2 | 1 | line_107855_21 | line_107855_21 | 600 | 12.47 | 12.9592 | 12.3112 | 12.9592 | 12.9592 | 12.9592 | 12.3112 | 12.3112 | 12.3112 | Single entrance line plausibly supports breaker rating | 7213.2403 | 7206.3675 | 7163.1437 | 7286.0943 | 7028.315 | 7393.058 |  | 7215.7217 | 7210.7588 | SCADA interpreted as phase-to-neutral volts | 0.19005 | Strong nominal-voltage agreement | 5.1818 | 5.1165 | 5.1165 | 5.1818 | 5.1165 | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV | 1 | 1 | 2.2464 | 3.405 | 5.441 | 3 | ae9708d6-58e3-48d8-b469-2b865749bda5, 9de5605e-2be3-4478-8321-ec1cfdb77d3e, c206a6a0-74a2-4aa0-b700-0397b158b47c | A, B, C | 3 |  |  |  | 7163.1437 | 7028.315 | 7393.058 | 7170.8424 | 7037.943 | 7358.573 | 0.4209 | 0.4209 | 0.4209
37 | 77 | GSO_49 | GSO_49 | High | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis | br_056_21 | 36.0168 | -79.7965 | 5454.5 | 5.4545 | 5.1818 | 0.12927 | 0.15506 | 0.19782 | 2024-06-27 03:00 | 2.4946 | 2.9925 | 3.8176 | 1 | 0 | 0 | 1 | 1 | 2 | 1 | line_112897_21 | line_112897_21 | 660 | 12.47 | 14.2551 | 13.5424 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | Single entrance line plausibly supports breaker rating | 7212.2652 | 7205.3488 | 7166.8527 | 7280.1449 | 7043.116 | 7392.594 | 7213.7994 | 7215.1717 | 7207.8245 | SCADA interpreted as phase-to-neutral volts | 0.1765 | Strong nominal-voltage agreement | 5.1818 | 4.984 | 4.984 | 5.1818 | 4.984 | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV | 1 | 1 | 10.7723 | 12.922 | 16.485 | 3 | 904a534b-b4de-47cc-9111-a909cdd75ff6, cf17223b-5ef6-40ff-aa3f-7eaa71fa5ab1, 4e486c1d-6969-466b-bb85-e868d8c69d96 | A, B, C | 3 | 7167.0694 | 7057.402 | 7392.594 | 7169.6101 | 7043.116 | 7379.586 | 7166.8527 | 7046.812 | 7380.813 | 0.38263 | 0.38263 | 0.38263
38 | 78 | GSO_151 | GSO_151 | High | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis | br_031_22 | 36.0823 | -79.9238 | 6000 | 6 | 5.7 | 0.42541 | 0.54888 | 0.73038 | 2024-01-21 04:00 | 7.4633 | 9.6295 | 12.8137 | 1 | 0 | 0 | 1 | 1 | 2 | 1 | line_5462_22 | line_5462_22 | 660 | 12.47 | 14.2551 | 13.5424 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | Single entrance line plausibly supports breaker rating | 7212.8096 | 7206.9083 | 7156.7407 | 7283.7486 | 7022.59 | 7376.851 | 7214.8052 | 7212.121 | 7211.5027 | SCADA interpreted as phase-to-neutral volts | 0.18406 | Strong nominal-voltage agreement | 5.7 | 4.9696 | 4.9696 | 5.7 | 4.9696 | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE6 | S_nSSEE6_12.47 | 6000.0 |  | MV | 1 | 1 | 35.4508 | 45.74 | 60.865 | 3 | 5b53a681-1338-4fee-9587-71b3e65506cb, 051f7584-2010-41f8-9415-9183657a8ae0, 0542d836-ab02-49aa-a8b7-a4265443a1c4 | A, B, C | 3 | 7158.1074 | 7032.846 | 7376.851 | 7163.1771 | 7035.46 | 7372.07 | 7156.7407 | 7022.59 | 7357.022 | 0.4209 | 0.4209 | 0.4209
39 | 80 | GSO_153 | GSO_153 | High | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis | br_033_22 | 36.0823 | -79.9238 | 6000 | 6 | 5.7 | 0.59934 | 0.69708 | 0.84121 | 2024-07-15 10:00 | 10.5147 | 12.2295 | 14.7581 | 1 | 0 | 0 | 1 | 1 | 2 | 1 | line_6823_22 | line_6823_22 | 660 | 12.47 | 14.2551 | 13.5424 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | Single entrance line plausibly supports breaker rating | 7213.2136 | 7206.5713 | 7160.7353 | 7281.2086 | 7038.833 | 7408.669 | 7213.9751 | 7211.8507 | 7213.8151 | SCADA interpreted as phase-to-neutral volts | 0.18967 | Strong nominal-voltage agreement | 5.7 | 4.8588 | 4.8588 | 5.7 | 4.8588 | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE6 | S_nSSEE6_12.47 | 6000.0 |  | MV | 1 | 1 | 49.9449 | 58.09 | 70.101 | 3 | 0d3f8e19-033b-4d8c-a34b-ff04747bd082, 5e1ed7ac-1e16-4c51-bb12-e8d8b8c244c4, 07ea0bf7-442d-4e77-b98a-b9e2c8d50114 | A, B, C | 3 | 7162.1052 | 7038.833 | 7391.64 | 7160.7353 | 7039.361 | 7408.669 | 7161.8237 | 7039.416 | 7398.191 | 0.4209 | 0.4209 | 0.4209
40 | 83 | GSO_47 | GSO_47 | High | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis | br_054_21 | 36.0168 | -79.7965 | 5454.5 | 5.4545 | 5.1818 | 0.21699 | 0.27116 | 0.35389 | 2024-07-16 03:00 | 4.1875 | 5.233 | 6.8296 | 1 | 0 | 0 | 1 | 1 | 2 | 1 | line_111700_21 | line_111700_21 | 660 | 12.47 | 14.2551 | 13.5424 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | Single entrance line plausibly supports breaker rating | 7208.4652 | 7203.4427 | 7162.8767 | 7281.3782 | 7028.672 | 7383.433 | 7214.5003 | 7204.873 | 7206.0224 | SCADA interpreted as phase-to-neutral volts | 0.12372 | Strong nominal-voltage agreement | 5.1818 | 4.8279 | 4.8279 | 5.1818 | 4.8279 | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV | 1 | 1 | 18.0821 | 22.5966 | 29.491 | 3 | 44d72b2b-4d39-442e-969c-28bfa609a6ca, df231f2b-7e74-4562-8026-e0248f99acb1, 73020989-8b85-4f2f-ae5e-b46034dccc36 | A, B, C | 3 | 7162.8767 | 7029.892 | 7366.855 | 7163.0414 | 7028.672 | 7367.518 | 7166.046 | 7042.72 | 7383.433 | 0.38263 | 0.38263 | 0.38263
41 | 87 | GSO_1 | GSO_1 | High | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis | br_01_21 | 36.0852 | -79.8827 | 5714.3 | 5.7143 | 5.4286 | 0.57147 | 0.69786 | 0.83644 | 2024-01-20 19:00 | 10.527 | 12.8553 | 15.408 | 1 | 0 | 0 | 1 | 1 | 2 | 1 | line_107866_21 | line_107866_21 | 600 | 12.47 | 12.9592 | 12.3112 | 12.9592 | 12.9592 | 12.9592 | 12.3112 | 12.3112 | 12.3112 | Single entrance line plausibly supports breaker rating | 7215.5052 | 7207.8373 | 7157.5324 | 7293.2092 | 7025.575 | 7404.224 | 7216.7574 | 7212.1779 | 7217.5801 | SCADA interpreted as phase-to-neutral volts | 0.2215 | Strong nominal-voltage agreement | 5.4286 | 4.5921 | 4.5921 | 5.4286 | 4.5921 | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 5714.3 |  | MV | 1 | 1 | 47.6222 | 58.155 | 69.703 | 3 | b1e8c057-fded-4c70-8f86-a33db401b6d1, ba6970aa-af7f-428e-9a4f-7826618684b4, ea496fcb-6216-4db1-9885-1da5dbf70fa2 | A, B, C | 3 | 7160.1403 | 7042.119 | 7396.429 | 7157.5324 | 7025.575 | 7379.073 | 7160.058 | 7032.508 | 7404.224 | 0.44095 | 0.44095 | 0.44095
42 | 104 | GSO_94 | GSO_94 | High | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis | br_094_21 | 36.0708 | -79.7962 | 4545.5 | 4.5455 | 4.3182 | 0.33065 | 0.40645 | 0.50374 | 2024-01-18 04:00 | 7.6571 | 9.4125 | 11.6653 | 1 | 0 | 0 | 1 | 1 | 2 | 1 | line_126351_21 | line_126351_21 | 600 | 12.47 | 12.9592 | 12.3112 | 12.9592 | 12.9592 | 12.9592 | 12.3112 | 12.3112 | 12.3112 | Single entrance line plausibly supports breaker rating | 7213.9741 | 7206.6622 | 7162.1317 | 7288.347 | 7018.565 | 7396.239 | 7215.8403 | 7212.7389 | 7213.343 | SCADA interpreted as phase-to-neutral volts | 0.20024 | Strong nominal-voltage agreement | 4.3182 | 3.8145 | 3.8145 | 4.3182 | 3.8145 | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV | 1 | 1 | 27.5543 | 33.871 | 41.978 | 3 | f0bd6ef7-dacb-46d2-ad18-589db990b13a, a82b3639-950c-4ba5-8e39-502e435ad83a, c177967e-e6f6-4644-aa50-326a9ebe3d00 | A, B, C | 3 | 7162.1317 | 7024.219 | 7396.239 | 7164.207 | 7038.382 | 7396.168 | 7164.2347 | 7018.565 | 7380.014 | 0.35075 | 0.35075 | 0.35075
43 | 105 | GSO_90 | GSO_90 | High | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis | br_090_21 | 36.0708 | -79.7962 | 4545.5 | 4.5455 | 4.3182 | 0.41465 | 0.50003 | 0.63064 | 2024-01-20 16:00 | 9.6022 | 11.5795 | 14.6041 | 1 | 0 | 0 | 1 | 1 | 2 | 1 | line_120694_21 | line_120694_21 | 660 | 12.47 | 14.2551 | 13.5424 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | Single entrance line plausibly supports breaker rating | 7211.4651 | 7205.1787 | 7161.6914 | 7278.7077 | 7027.269 | 7394.585 | 7211.4057 | 7213.4059 | 7209.5837 | SCADA interpreted as phase-to-neutral volts | 0.16539 | Strong nominal-voltage agreement | 4.3182 | 3.6876 | 3.6876 | 4.3182 | 3.6876 | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV | 1 | 1 | 34.5538 | 41.669 | 52.553 | 3 | ab8abf18-0128-43c3-8213-8fcc30f583d2, 59f75e54-a46d-4153-8855-555945d0a888, f35586be-8010-4ad3-b579-d95b9825cae5 | A, B, C | 3 | 7161.6914 | 7035.345 | 7378.27 | 7162.335 | 7046.696 | 7391.01 | 7163.7253 | 7027.269 | 7394.585 | 0.31887 | 0.31887 | 0.31887
44 | 107 | GSO_93 | GSO_93 | High | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis | br_093_21 | 36.0709 | -79.7962 | 4545.5 | 4.5455 | 4.3182 | 0.45692 | 0.55536 | 0.70237 | 2024-01-21 04:00 | 10.5812 | 12.8608 | 16.2653 | 1 | 0 | 0 | 1 | 1 | 2 | 1 | line_121299_21 | line_121299_21 | 660 | 12.47 | 14.2551 | 13.5424 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | Single entrance line plausibly supports breaker rating | 7214.4987 | 7206.5897 | 7161.8504 | 7288.9437 | 7038.805 | 7413.538 | 7211.8272 | 7216.6256 | 7215.0432 | SCADA interpreted as phase-to-neutral volts | 0.20752 | Strong nominal-voltage agreement | 4.3182 | 3.6159 | 3.6159 | 4.3182 | 3.6159 | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV | 1 | 1 | 38.0767 | 46.28 | 58.531 | 3 | ac7b38f5-50a1-4cc6-bab1-d609ee8f92a4, 75f25960-b76b-4ea6-95b3-22351b5c7fde, 531ef22d-48aa-4ee9-88be-bf0b21101c8d | A, B, C | 3 | 7164.5423 | 7040.381 | 7413.538 | 7161.8504 | 7038.805 | 7377.404 | 7167.271 | 7049.811 | 7383.599 | 0.31887 | 0.31887 | 0.31887
45 | 110 | GSO_70 | GSO_70 | High | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis | br_070_21 | 36.0801 | -79.7573 | 4285.7 | 4.2857 | 4.0714 | 0.35304 | 0.42007 | 0.51608 | 2024-01-20 22:00 | 8.6713 | 10.3175 | 12.6758 | 1 | 0 | 0 | 1 | 1 | 2 | 1 | line_131920_21 | line_131920_21 | 660 | 12.47 | 14.2551 | 13.5424 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | Single entrance line plausibly supports breaker rating | 7210.9731 | 7204.7862 | 7164.59 | 7284.615 | 7033.796 | 7397.636 | 7215.6732 | 7209.016 | 7208.2302 | SCADA interpreted as phase-to-neutral volts | 0.15856 | Strong nominal-voltage agreement | 4.0714 | 3.5553 | 3.5553 | 4.0714 | 3.5553 | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 4285.7 |  | MV | 1 | 1 | 29.4202 | 35.0057 | 43.007 | 3 | ff4d78df-a97d-465a-9270-6b140f05b7ee, 96d35f0d-746b-4c76-8d6d-a22dac3dcfaa, 7a4e8fb6-f007-4d77-bfcb-6a0b0e18561c | A, B, C | 3 | 7164.59 | 7044.224 | 7392.095 | 7169.5691 | 7075.951 | 7397.636 | 7166.832 | 7033.796 | 7381.615 | 0.30064 | 0.30064 | 0.30064
46 | 111 | GSO_20 | GSO_20 | High | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis | br_027_21 | 36.0604 | -79.8599 | 3750 | 3.75 | 3.5625 | 0.0032747 | 0.004752 | 0.007668 | 2024-07-10 19:00 | 0.091922 | 0.13339 | 0.21524 | 1 | 0 | 0 | 1 | 1 | 2 | 1 | line_107423_21 | line_107423_21 | 660 | 12.47 | 14.2551 | 13.5424 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | Single entrance line plausibly supports breaker rating | 7205.7076 | 7200.567 | 7163.416 | 7264.1847 | 7040.882 | 7402.072 | 7205.7076 |  |  | SCADA interpreted as phase-to-neutral volts | 0.085419 | Strong nominal-voltage agreement | 3.5625 | 3.5548 | 3.5548 | 3.5625 | 3.5548 | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE12 | S_nSSEE12_12.47 | 3750.0 |  | MV | 1 | 1 | 0.27289 | 0.396 | 0.639 | 3 | 0367f0a8-b7e5-4ca5-94ae-d44fa9d00bfd, a602edca-8fde-46f7-8d51-40a5f85d6a1d, c9015052-da74-4877-bbf1-9a6c4275c44d | A, B, C | 3 | 7163.416 | 7040.882 | 7402.072 | [6 empty] | 0.26306 | 0.26306 | 0.26306
47 | 113 | GSO_24 | GSO_24 | High | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis | br_031_21 | 36.0603 | -79.8599 | 3750 | 3.75 | 3.5625 | 0.042273 | 0.050748 | 0.067452 | 2024-01-20 16:00 | 1.1866 | 1.4245 | 1.8934 | 1 | 0 | 0 | 1 | 1 | 2 | 1 | line_124522_21 | line_124522_21 | 660 | 12.47 | 14.2551 | 13.5424 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | Single entrance line plausibly supports breaker rating | 7209.9378 | 7203.305 | 7168.0318 | 7267.7802 | 7016.239 | 7398.253 | 7208.9368 | 7212.0685 | 7208.808 | SCADA interpreted as phase-to-neutral volts | 0.14417 | Strong nominal-voltage agreement | 3.5625 | 3.495 | 3.495 | 3.5625 | 3.495 | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE12 | S_nSSEE12_12.47 | 3750.0 |  | MV | 1 | 1 | 3.5228 | 4.229 | 5.621 | 3 | 8866ae0d-1645-4e1d-85a9-520a2b057093, 0e740376-b7d0-46f1-8238-50979ff53b86, 3abd341d-8629-4be0-888c-4405cbd18a68 | A, B, C | 3 | 7174.7004 | 7033.155 | 7377.447 | 7171.7341 | 7043.772 | 7384.643 | 7168.0318 | 7016.239 | 7398.253 | 0.26306 | 0.26306 | 0.26306
| 1 | GSO_121 | GSO_121 | Low | Inspect downstream topology and line metadata before capacity use | br_01_22 | 36.083 | -79.9727 | 15000 | 15 | 14.25 | 0.24467 | 0.30456 | 0.38162 | 2024-01-17 23:00 | 1.717 | 2.1372 | 2.6781 | [19 empty] | No usable entrance-line capacity | 7213.9157 | 7206.4652 | 7160.5141 | 7282.7945 | 7029.038 | 7396.153 | 7214.2313 | 7213.0706 | 7214.4454 | Unavailable |  | Insufficient voltage data | 14.25 | 13.8684 | 13.8684 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 15000.0 |  | MV | 1 | 1 | 20.3889 | 25.3796 | 31.802 | 3 | 0eb7ef08-0441-4661-84d4-63da9255ea41, 36cfcc10-f3c4-4989-ae21-5fdd2aa20962, 423b0798-4793-4a14-a787-72bb51fb4cef | A, B, C | 3 | 7165.2033 | 7039.781 | 7394.362 | 7162.4387 | 7029.038 | 7396.153 | 7160.5141 | 7035.078 | 7386.541
| 7 | GSO_145 | GSO_145 | Low | Inspect downstream topology and line metadata before capacity use | br_025_22 | 36.046 | -79.947 | 12000 | 12 | 11.4 | 0.4405 | 0.56032 | 0.73442 | 2024-01-21 04:00 | 3.8641 | 4.9151 | 6.4423 | [19 empty] | No usable entrance-line capacity | 7213.5739 | 7206.7195 | 7159.5153 | 7283.6208 | 7038.239 | 7396.884 | 7215.5132 | 7213.7589 | 7211.4496 | Unavailable |  | Insufficient voltage data | 11.4 | 10.6656 | 10.6656 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 12000.0 |  | MV | 1 | 1 | 36.7087 | 46.6936 | 61.202 | 3 | e8f52edb-11b6-4a01-8cb4-dde6abb481d7, 5042bbb0-cc21-499d-9106-09bd8c86b439, 039cb766-152c-4467-9ec0-94180921a657 | A, B, C | 3 | 7164.282 | 7038.239 | 7393.921 | 7160.3044 | 7040.76 | 7396.884 | 7159.5153 | 7041.154 | 7376.019
| 8 | GSO_142 | GSO_142 | Low | Inspect downstream topology and line metadata before capacity use | br_022_22 | 36.0459 | -79.947 | 12000 | 12 | 11.4 | 0.52512 | 0.62478 | 0.79259 | 2024-07-09 | 4.6063 | 5.4805 | 6.9525 | [19 empty] | No usable entrance-line capacity | 7211.9059 | 7205.0028 | 7167.963 | 7272.627 | 7052.771 | 7399.344 | 7211.974 | 7212.3415 | 7211.4021 | Unavailable |  | Insufficient voltage data | 11.4 | 10.6074 | 10.6074 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 12000.0 |  | MV | 1 | 1 | 43.7603 | 52.0646 | 66.049 | 3 | 5c50320a-6541-43e1-a0eb-b3cc85335f92, d8586197-7e6c-42e3-af81-89d0f76301f9, aeed6de5-7aca-4fa3-a5ca-b1f32ee717c2 | A, B, C | 3 | 7167.963 | 7055.092 | 7382.303 | 7169.0873 | 7054.939 | 7399.344 | 7170.084 | 7052.771 | 7378.542
| 9 | GSO_18 | GSO_18 | Low | Inspect downstream topology and line metadata before capacity use | br_025_21 | 36.0264 | -79.8286 | 13333.3 | 13.3333 | 12.6666 | 1.1891 | 1.713 | 2.2897 | 2024-01-21 | 9.3875 | 13.5241 | 18.0768 | [19 empty] | No usable entrance-line capacity | 7214.2621 | 7207.255 | 7159.347 | 7295.8883 | 7035.527 | 7371.574 | 7218.1791 | 7206.1489 | 7218.4581 | Unavailable |  | Insufficient voltage data | 12.6666 | 10.3769 | 10.3769 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE11 | S_nSSEE11_12.47 | 13333.3 |  | MV | 1 | 1 | 99.0903 | 142.754 | 190.81 | 3 | 34cac5e4-313a-4454-a92d-abc9047eadc8, 90d3f27c-2599-462f-8abb-58371a03ece5, 08eb7b30-b593-4a81-854f-d7a00d46db1e | A, B, C | 3 | 7161.4057 | 7052.055 | 7355.37 | 7159.347 | 7035.527 | 7289.948 | 7160.459 | 7036.625 | 7371.574
| 15 | GSO_125 | GSO_125 | Low | Inspect downstream topology and line metadata before capacity use | br_05_22 | 36.0974 | -79.9235 | 10000 | 10 | 9.5 | 0.20672 | 0.25126 | 0.3241 | 2024-01-20 11:00 | 2.176 | 2.6449 | 3.4115 | [19 empty] | No usable entrance-line capacity | 7211.4318 | 7205.7533 | 7161.9564 | 7271.5392 | 7024.71 | 7385.96 | 7212.0974 | 7211.6453 | 7210.5525 | Unavailable |  | Insufficient voltage data | 9.5 | 9.1759 | 9.1759 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 10000.0 |  | MV | 1 | 1 | 17.2263 | 20.9386 | 27.008 | 3 | cd7fbbb9-9a6f-4dd9-891c-e37a9557fa12, 16682194-aa4b-49e9-acf2-9c6562595352, 99cabfd6-b964-4658-8155-1699ad43459b | A, B, C | 3 | 7166.3797 | 7044.963 | 7382.54 | 7162.6512 | 7024.71 | 7385.96 | 7161.9564 | 7044.728 | 7370.4
| 17 | GSO_17 | GSO_17 | Low | Inspect downstream topology and line metadata before capacity use | br_024_21 | 36.0264 | -79.8286 | 13333.3 | 13.3333 | 12.6666 | 1.8182 | 2.6953 | 3.5366 | 2024-01-21 04:05 | 14.3546 | 21.2787 | 27.9204 | [19 empty] | No usable entrance-line capacity | 7213.2163 | 7206.991 | 7155.4172 | 7290.7966 | 7020.65 | 7359.735 | 7207.7383 | 7215.6723 | 7216.2382 | Unavailable |  | Insufficient voltage data | 12.6666 | 9.1301 | 9.1301 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE11 | S_nSSEE11_12.47 | 13333.3 |  | MV | 1 | 1 | 151.5207 | 224.6077 | 294.715 | 3 | 3a2af09c-baa8-4dbe-95ab-fb397036b19d, 883c59a4-ab46-45e2-b36d-e1959b7c89b6, f0a67506-31bf-4b47-9614-f559c928646a | A, B, C | 3 | 7157.2234 | 7032.735 | 7298.912 | 7155.4172 | 7020.65 | 7340.337 | 7157.0243 | 7035.227 | 7359.735
| 18 | GSO_143 | GSO_143 | Low | Inspect downstream topology and line metadata before capacity use | br_023_22 | 36.0459 | -79.947 | 12000 | 12 | 11.4 | 1.249 | 1.8959 | 2.5408 | 2024-01-21 04:00 | 10.9559 | 16.6311 | 22.2874 | [19 empty] | No usable entrance-line capacity | 7218.1091 | 7209.214 | 7154.5197 | 7301.246 | 7026.719 | 7356.242 | 7218.4547 | 7217.4549 | 7218.4176 | Unavailable |  | Insufficient voltage data | 11.4 | 8.8592 | 8.8592 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 12000.0 |  | MV | 1 | 1 | 104.0809 | 157.9957 | 211.73 | 3 | b2362459-63fa-42c8-b75d-cdff666f2190, 15ee4200-f93f-4884-ab81-e52eb3d0b73c, ef7cab0d-e432-4fb1-aab4-46e5068286b4 | A, B, C | 3 | 7156.2924 | 7033.818 | 7356.242 | 7155.772 | 7034.698 | 7350.395 | 7154.5197 | 7026.719 | 7352.954
| 19 | GSO_56 | GSO_56 | Low | Inspect downstream topology and line metadata before capacity use | br_063_21 | 36.0131 | -79.8489 | 10000 | 10 | 9.5 | 0.45164 | 0.62017 | 0.80917 | 2024-01-21 04:00 | 4.7541 | 6.5281 | 8.5176 | [19 empty] | No usable entrance-line capacity | 7216.9616 | 7208.0357 | 7160.4985 | 7299.8013 | 7029.815 | 7379.176 | 7219.8583 | 7214.0309 | 7216.9956 | Unavailable |  | Insufficient voltage data | 9.5 | 8.6908 | 8.6908 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE17 | S_nSSEE17_12.47 | 10000.0 |  | MV | 1 | 1 | 37.6367 | 51.681 | 67.431 | 3 | d5be6516-e14a-46ab-a02a-0650b74a5159, 748858e9-a0e0-4bc6-a0b7-f4e67d7c9ecd, 620a8a0d-bcbd-4f44-be97-24244e308366 | A, B, C | 3 | 7163.0233 | 7043.719 | 7379.13 | 7160.8063 | 7034.107 | 7379.176 | 7160.4985 | 7029.815 | 7359.505
| 20 | GSO_75 | GSO_75 | Low | Inspect downstream topology and line metadata before capacity use | br_075_21 | 36.0825 | -79.7708 | 10000 | 10 | 9.5 | 0.43085 | 0.58537 | 0.81054 | 2024-01-18 04:00 | 4.5353 | 6.1618 | 8.532 | [19 empty] | No usable entrance-line capacity | 7214.6269 | 7207.1745 | 7160.8418 | 7292.2406 | 7027.191 | 7392.568 | 7212.8538 | 7217.721 | 7213.3058 | Unavailable |  | Insufficient voltage data | 9.5 | 8.6895 | 8.6895 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE3 | S_nSSEE3_12.47 | 10000.0 |  | MV | 1 | 1 | 35.9045 | 48.781 | 67.545 | 3 | 74ba07cb-a526-4618-b499-1a430d0286b7, dc09ae69-e1ee-4c83-9c04-e09da568c6ab, 8cfdaf81-8e59-4486-ba2f-4e450a23c876 | A, B, C | 3 | 7160.8418 | 7030.621 | 7371.015 | 7162.0597 | 7027.191 | 7392.568 | 7164.9014 | 7027.838 | 7373.57
| 21 | GSO_74 | GSO_74 | Low | Inspect downstream topology and line metadata before capacity use | br_074_21 | 36.0825 | -79.7708 | 10000 | 10 | 9.5 | 0.71292 | 0.87569 | 1.0535 | 2024-01-20 23:25 | 7.5044 | 9.2178 | 11.0898 | [19 empty] | No usable entrance-line capacity | 7216.604 | 7207.8483 | 7161.1087 | 7294.6044 | 7039.079 | 7405.794 | 7217.9543 | 7215.0811 | 7216.7767 | Unavailable |  | Insufficient voltage data | 9.5 | 8.4465 | 8.4465 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE3 | S_nSSEE3_12.47 | 10000.0 |  | MV | 1 | 1 | 59.4096 | 72.9743 | 87.794 | 3 | 4cb9db9e-b9c3-473e-878d-2df2932f4dcf, 2be1e40d-d971-44eb-9f8e-1f362b00491f, b4794b85-7397-40b2-a7b2-50c82c66983d | A, B, C | 3 | 7163.689 | 7055.504 | 7401.805 | 7161.1087 | 7039.079 | 7352.326 | 7165.0408 | 7049.876 | 7405.794
| 22 | GSO_116 | GSO_116 | Low | Inspect downstream topology and line metadata before capacity use | br_0116_21 | 36.0426 | -79.8533 | 10000 | 10 | 9.5 | 0.64103 | 0.8443 | 1.0806 | 2024-01-20 16:00 | 6.7476 | 8.8874 | 11.3751 | [19 empty] | No usable entrance-line capacity | 7214.5854 | 7207.1007 | 7158.2792 | 7289.1399 | 7015.91 | 7380.441 | 7212.1272 | 7215.2665 | 7216.3624 | Unavailable |  | Insufficient voltage data | 9.5 | 8.4194 | 8.4194 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE9 | S_nSSEE9_12.47 | 10000.0 |  | MV | 1 | 1 | 53.4188 | 70.3586 | 90.053 | 3 | 2a93f307-f837-4de0-9089-b308bde0f0fd, ba9bd088-fa13-4d76-ba16-6dba6a8b45de, e9542020-950f-403c-af95-965f8434a9f8 | A, B, C | 3 | 7163.6835 | 7032.298 | 7378.893 | 7159.7711 | 7015.91 | 7380.441 | 7158.2792 | 7042.425 | 7351.179
| 24 | GSO_118 | GSO_118 | Low | Inspect downstream topology and line metadata before capacity use | br_0118_21 | 36.0426 | -79.8533 | 10000 | 10 | 9.5 | 0.92656 | 1.2453 | 1.5724 | 2024-01-20 21:00 | 9.7533 | 13.1084 | 16.5512 | [19 empty] | No usable entrance-line capacity | 7215.0042 | 7207.7745 | 7156.5658 | 7292.1447 | 7021.733 | 7388.318 | 7215.3234 | 7212.7426 | 7216.9467 | Unavailable |  | Insufficient voltage data | 9.5 | 7.9276 | 7.9276 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE9 | S_nSSEE9_12.47 | 10000.0 |  | MV | 1 | 1 | 77.2137 | 103.7746 | 131.03 | 3 | b2273af8-cb6e-4178-93e7-36fab6dbf2c0, cb23fba1-b5a8-477f-b388-dcbc14cf56b2, 7b9e37f6-9e61-405e-8bc5-9d79097397f4 | A, B, C | 3 | 7160.0714 | 7046.957 | 7388.318 | 7163.0617 | 7054.647 | 7348.819 | 7156.5658 | 7021.733 | 7349.313
| 26 | GSO_130 | GSO_130 | Low | Inspect downstream topology and line metadata before capacity use | br_010_22 | 36.0811 | -79.94 | 8571.4 | 8.5714 | 8.1428 | 0.21103 | 0.24804 | 0.31823 | 2024-01-22 04:00 | 2.5916 | 3.0461 | 3.9081 | [19 empty] | No usable entrance-line capacity | 7210.0993 | 7204.219 | 7159.6044 | 7271.0877 | 7027.936 | 7383.214 | 7211.2124 | 7209.0908 | 7209.9946 | Unavailable |  | Insufficient voltage data | 8.1428 | 7.8246 | 7.8246 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 8571.4 |  | MV | 1 | 1 | 17.5856 | 20.67 | 26.519 | 3 | ec2f67d6-3e29-40e6-b3db-279de5aeb3e1, 0820aaeb-7057-4894-a6ba-7624e83ee1a7, cab2ab50-4b8d-4ecb-98f8-73c155d0b547 | A, B, C | 3 | 7167.3361 | 7050.508 | 7383.214 | 7159.6044 | 7031.164 | 7377.911 | 7167.9577 | 7027.936 | 7367.223
| 27 | GSO_134 | GSO_134 | Low | Inspect downstream topology and line metadata before capacity use | br_014_22 | 36.0811 | -79.94 | 8571.4 | 8.5714 | 8.1428 | 0.22056 | 0.26444 | 0.32862 | 2024-01-20 09:00 | 2.7086 | 3.2476 | 4.0357 | [19 empty] | No usable entrance-line capacity | 7206.0917 | 7201.8808 | 7153.3993 | 7267.3596 | 7010.309 | 7395.425 | 7208.2063 | 7207.283 | 7202.7857 | Unavailable |  | Insufficient voltage data | 8.1428 | 7.8142 | 7.8142 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 8571.4 |  | MV | 1 | 1 | 18.38 | 22.037 | 27.385 | 3 | 4091c3a2-55c3-4b7e-8d9d-a8e4affed314, 57c2fa84-53da-4153-9d01-3c3ac5b2144e, 7325e088-181d-4e0d-b15b-2dd1fbda83f0 | A, B, C | 3 | 7160.0073 | 7024.842 | 7386.148 | 7158.5871 | 7010.309 | 7395.425 | 7153.3993 | 7023.807 | 7381.334
| 28 | GSO_72 | GSO_72 | Low | Inspect downstream topology and line metadata before capacity use | br_072_21 | 36.0825 | -79.7708 | 10000 | 10 | 9.5 | 0.95133 | 1.3238 | 1.741 | 2024-01-21 04:00 | 10.014 | 13.9352 | 18.3268 | [19 empty] | No usable entrance-line capacity | 7214.397 | 7207.3822 | 7157.703 | 7290.686 | 7030.388 | 7365.66 | 7217.0323 | 7212.2769 | 7213.8818 | Unavailable |  | Insufficient voltage data | 9.5 | 7.759 | 7.759 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE3 | S_nSSEE3_12.47 | 10000.0 |  | MV | 1 | 1 | 79.2778 | 110.32 | 145.087 | 3 | 2f6074d9-3367-424b-9912-3b54ba3842dc, 5be2e72a-f9e3-4662-bcdd-f6914b127473, ceb3c16f-b2c1-4384-83e5-47eb8d9787a9 | A, B, C | 3 | 7159.8799 | 7035.943 | 7365.66 | 7157.703 | 7036.086 | 7318.722 | 7158.2641 | 7030.388 | 7345.54
| 30 | GSO_135 | GSO_135 | Low | Inspect downstream topology and line metadata before capacity use | br_015_22 | 36.0811 | -79.94 | 8571.4 | 8.5714 | 8.1428 | 0.36821 | 0.42978 | 0.52656 | 2024-01-20 23:05 | 4.5219 | 5.278 | 6.4665 | [19 empty] | No usable entrance-line capacity | 7208.264 | 7203.0272 | 7156.4443 | 7274.795 | 7044.488 | 7398.005 | 7204.0232 | 7211.6993 | 7209.0694 | Unavailable |  | Insufficient voltage data | 8.1428 | 7.6163 | 7.6163 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 8571.4 |  | MV | 1 | 1 | 30.6842 | 35.815 | 43.88 | 3 | c3ac0e33-1470-42fd-9a70-99015f289563, 306b628e-5350-43cc-bd44-5524b56eb0e1, cb036569-e3a3-4f9a-ab6b-ada0cfc7f7a2 | A, B, C | 3 | 7156.4443 | 7044.488 | 7382.455 | 7163.139 | 7052.077 | 7391.839 | 7163.648 | 7048.886 | 7398.005
| 31 | GSO_19 | GSO_19 | Low | Inspect downstream topology and line metadata before capacity use | br_026_21 | 36.0264 | -79.8286 | 13333.3 | 13.3333 | 12.6666 | 2.5101 | 3.8361 | 5.1626 | 2024-01-18 04:00 | 19.8163 | 30.2854 | 40.7575 | [19 empty] | No usable entrance-line capacity | 7217.1733 | 7208.4697 | 7156.5428 | 7294.6037 | 7031.45 | 7357.445 | 7216.7248 | 7217.6476 | 7217.1475 | Unavailable |  | Insufficient voltage data | 12.6666 | 7.504 | 7.504 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE11 | S_nSSEE11_12.47 | 13333.3 |  | MV | 1 | 1 | 209.1713 | 319.6785 | 430.217 | 3 | d5920248-7472-436e-b060-c7c2ff9ef29d, cf54e8e6-a9a5-4011-b2be-1226fbdc86cb, a03bc8be-0c7b-4ca4-b625-79f7823155e9 | A, B, C | 3 | 7157.4247 | 7031.45 | 7357.445 | 7157.72 | 7037.628 | 7337.216 | 7156.5428 | 7035.338 | 7339.54
| 32 | GSO_133 | GSO_133 | Low | Inspect downstream topology and line metadata before capacity use | br_013_22 | 36.0811 | -79.94 | 8571.4 | 8.5714 | 8.1428 | 0.44721 | 0.52895 | 0.6777 | 2024-01-20 11:00 | 5.4921 | 6.4959 | 8.3227 | [19 empty] | No usable entrance-line capacity | 7210.8249 | 7205.0537 | 7160.7667 | 7276.089 | 7025.626 | 7409.839 | 7208.546 | 7211.8404 | 7212.0883 | Unavailable |  | Insufficient voltage data | 8.1428 | 7.4651 | 7.4651 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 8571.4 |  | MV | 1 | 1 | 37.2676 | 44.079 | 56.475 | 3 | dddfb629-b710-4a70-b13f-4f342bc8fe74, 4d344901-644b-4ea0-b7f1-b381d39a7879, c086c5c8-dc85-4746-8b0a-d8e23067358a | A, B, C | 3 | 7164.2847 | 7027.764 | 7384.006 | 7160.7667 | 7037.181 | 7386.89 | 7162.0651 | 7025.626 | 7409.839
| 33 | GSO_115 | GSO_115 | Low | Inspect downstream topology and line metadata before capacity use | br_0115_21 | 36.0426 | -79.8533 | 10000 | 10 | 9.5 | 1.1974 | 1.7258 | 2.2713 | 2024-01-21 04:00 | 12.6046 | 18.1659 | 23.908 | [19 empty] | No usable entrance-line capacity | 7216.7108 | 7208.4273 | 7156.9744 | 7293.8006 | 7021.72 | 7347.676 | 7215.565 | 7217.2403 | 7217.3271 | Unavailable |  | Insufficient voltage data | 9.5 | 7.2287 | 7.2287 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE9 | S_nSSEE9_12.47 | 10000.0 |  | MV | 1 | 1 | 99.7864 | 143.813 | 189.272 | 3 | d3645b59-a71d-4848-9deb-b044c307c52a, 820fcd78-48b0-467d-8925-554a0333f605, 58786ac1-7ac2-4287-bd8f-add68a4ea208 | A, B, C | 3 | 7157.2431 | 7021.72 | 7339.975 | 7156.9744 | 7023.039 | 7347.676 | 7159.5944 | 7049.57 | 7347.212
| 37 | GSO_147 | GSO_147 | Low | Inspect downstream topology and line metadata before capacity use | br_027_22 | 36.114 | -79.9604 | 7500 | 7.5 | 7.125 | 0.16253 | 0.21618 | 0.29234 | 2024-01-21 04:00 | 2.2811 | 3.0341 | 4.1031 | [19 empty] | No usable entrance-line capacity | 7212.2558 | 7206.2862 | 7162.0871 | 7282.8139 | 7035.176 | 7400.18 | 7215.2158 | 7207.9179 | 7213.6337 | Unavailable |  | Insufficient voltage data | 7.125 | 6.8327 | 6.8327 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 7500.0 |  | MV | 1 | 1 | 13.544 | 18.0146 | 24.362 | 3 | 783419bf-1c8f-4783-a364-729c4d25328a, b05dca4b-f167-46ba-b479-77fc9d306c98, a6c68db1-932a-455f-9961-2001628d137a | A, B, C | 3 | 7162.0871 | 7035.176 | 7400.18 | 7163.5644 | 7041.5 | 7389.222 | 7162.2787 | 7052.141 | 7381.174
| 38 | GSO_100 | GSO_100 | Low | Inspect downstream topology and line metadata before capacity use | br_097_21 | 36.0611 | -79.7715 | 7500 | 7.5 | 7.125 | 0.17463 | 0.26832 | 0.37085 | 2024-01-20 07:05 | 2.451 | 3.7659 | 5.2049 | [19 empty] | No usable entrance-line capacity | 7216.7476 | 7208.478 | 7158.3004 | 7292.7356 | 7002.413 | 7364.021 |  | 7217.1997 | 7216.2955 | Unavailable |  | Insufficient voltage data | 7.125 | 6.7542 | 6.7542 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE6 | S_nSSEE6_12.47 | 7500.0 |  | MV | 1 | 1 | 14.5529 | 22.36 | 30.904 | 3 | 564551fe-ec45-4b6c-a7df-ebfa29a0a242, 3125b67a-cbd0-47b3-94b6-a60b38de7e8b, cc6f9a7e-ea1b-4cdb-9c85-6c672b845068 | A, B, C | 3 |  |  |  | 7158.3004 | 7025.233 | 7359.802 | 7162.5811 | 7002.413 | 7364.021
| 40 | GSO_148 | GSO_148 | Low | Inspect downstream topology and line metadata before capacity use | br_028_22 | 36.114 | -79.9604 | 7500 | 7.5 | 7.125 | 0.29922 | 0.37366 | 0.49594 | 2024-01-21 01:00 | 4.1996 | 5.2443 | 6.9605 | [19 empty] | No usable entrance-line capacity | 7214.7673 | 7207.3495 | 7160.161 | 7288.0593 | 6997.271 | 7404.952 | 7215.742 | 7213.0273 | 7215.5326 | Unavailable |  | Insufficient voltage data | 7.125 | 6.6291 | 6.6291 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 7500.0 |  | MV | 1 | 1 | 24.9351 | 31.138 | 41.328 | 3 | f209db33-c63a-4eeb-9470-44a070b1f980, e51bd3d2-27db-4e8c-85b3-94bb36fdecb2, 9cb02ef5-7d31-4690-b5cc-1c8ff7465b94 | A, B, C | 3 | 7160.4744 | 7011.396 | 7382.448 | 7161.9858 | 6997.271 | 7398.382 | 7160.161 | 7036.014 | 7404.952
| 41 | GSO_162 | GSO_162 | Low | Inspect downstream topology and line metadata before capacity use | br_08_23 | 36.1644 | -79.7079 | 8000 | 8 | 7.6 | 0.50804 | 0.75386 | 1.0057 | 2024-01-20 23:00 | 6.6847 | 9.9192 | 13.2327 | [19 empty] | No usable entrance-line capacity | 7215.1432 | 7207.6575 | 7160.6244 | 7285.1353 | 7032.312 | 7354.077 | 7215.4735 | 7215.8371 | 7214.1189 | Unavailable |  | Insufficient voltage data | 7.6 | 6.5943 | 6.5943 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 8000.0 |  | MV | 1 | 1 | 42.3363 | 62.8216 | 83.807 | 3 | f620b838-2134-4f66-a112-15e5f46318b0, f4ffa257-f9a9-48e6-8ef7-945f8e687e83, 4bfd3a0a-1178-4983-b63c-76c387206a99 | A, B, C | 3 | 7160.6244 | 7032.312 | 7348.664 | 7161.476 | 7042.811 | 7354.077 | 7161.3027 | 7035.953 | 7352.461
| 43 | GSO_146 | GSO_146 | Low | Inspect downstream topology and line metadata before capacity use | br_026_22 | 36.114 | -79.9604 | 7500 | 7.5 | 7.125 | 0.5382 | 0.72909 | 0.97618 | 2024-01-21 04:00 | 7.5538 | 10.2328 | 13.7007 | [19 empty] | No usable entrance-line capacity | 7218.1211 | 7208.7093 | 7155.441 | 7307.3026 | 7032.141 | 7382.472 | 7220.9475 | 7219.2106 | 7214.2051 | Unavailable |  | Insufficient voltage data | 7.125 | 6.1488 | 6.1488 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 7500.0 |  | MV | 1 | 1 | 44.8504 | 60.7569 | 81.348 | 3 | 45141e3c-ee87-445b-a8cd-53eaf3cf8ac6, d4d03355-620e-4213-a24e-266e873f3f79, 9c3aa61d-fdd8-4e3a-a859-786b34331466 | A, B, C | 3 | 7158.1368 | 7034.108 | 7381.47 | 7155.441 | 7032.141 | 7373.949 | 7160.9004 | 7047.821 | 7382.472
| 44 | GSO_112 | GSO_112 | Low | Inspect downstream topology and line metadata before capacity use | br_0112_21 | 36.0543 | -79.8942 | 7142.9 | 7.1429 | 6.7858 | 0.47836 | 0.58066 | 0.77134 | 2024-01-21 04:00 | 7.0495 | 8.557 | 11.367 | [19 empty] | No usable entrance-line capacity | 7207.9653 | 7203.8973 | 7164.223 | 7277.3857 | 7046.776 | 7396.822 | 7213.0353 | 7197.6072 | 7213.2535 | Unavailable |  | Insufficient voltage data | 6.7858 | 6.0144 | 6.0144 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE8 | S_nSSEE8_12.47 | 7142.9 |  | MV | 1 | 1 | 39.8632 | 48.388 | 64.278 | 3 | 407ea9ca-a495-4119-a139-1d1233852fdc, 99fe4744-38fc-4467-902b-d97556b6d295, e1fd2b67-b072-4575-9f5d-c24af5f52b11 | A, B, C | 3 | 7164.6551 | 7048.228 | 7376.669 | 7164.223 | 7046.776 | 7273.008 | 7166.0987 | 7047.055 | 7396.822
| 46 | GSO_117 | GSO_117 | Low | Inspect downstream topology and line metadata before capacity use | br_0117_21 | 36.0426 | -79.8533 | 10000 | 10 | 9.5 | 1.821 | 2.682 | 3.528 | 2024-01-18 04:00 | 19.1685 | 28.2312 | 37.1373 | [19 empty] | No usable entrance-line capacity | 7216.184 | 7208.2262 | 7154.8054 | 7296.203 | 7028.852 | 7350.549 | 7215.3729 | 7215.3451 | 7217.8339 | Unavailable |  | Insufficient voltage data | 9.5 | 5.972 | 5.972 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE9 | S_nSSEE9_12.47 | 10000.0 |  | MV | 1 | 1 | 151.7502 | 223.4966 | 294.004 | 3 | 20ca2ff7-1194-405d-9098-d4544944a36d, 127d58d0-da5d-47a0-a219-b8c1834a136a, 79b91384-9645-42ed-940d-37fdffcc31a0 | A, B, C | 3 | 7154.8054 | 7028.852 | 7346.952 | 7155.5291 | 7030.75 | 7336.216 | 7156.4973 | 7034.986 | 7350.549
| 47 | GSO_84 | GSO_84 | Low | Inspect downstream topology and line metadata before capacity use | br_084_21 | 36.0719 | -79.8252 | 6666.7 | 6.6667 | 6.3334 | 0.1731 | 0.26237 | 0.36289 | 2024-01-20 06:05 | 2.7331 | 4.1426 | 5.7298 | [19 empty] | No usable entrance-line capacity | 7216.3921 | 7207.8645 | 7159.738 | 7296.5661 | 7017.501 | 7399.196 | 7218.608 | 7214.7766 | 7215.7919 | Unavailable |  | Insufficient voltage data | 6.3334 | 5.9705 | 5.9705 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV | 1 | 1 | 14.425 | 21.864 | 30.241 | 3 | d4454767-7751-4c58-9cbd-79e943f45acf, 4cc5af87-12cf-4fd1-a89c-0318dc07c068, b63c8e73-fffc-4e69-ad08-995c149ebeaa | A, B, C | 3 | 7159.738 | 7036.604 | 7369.501 | 7167.39 | 7058 | 7399.196 | 7165.288 | 7017.501 | 7365.089
| 48 | GSO_155 | GSO_155 | Low | Inspect downstream topology and line metadata before capacity use | br_01_23 | 36.1928 | -79.6069 | 7500 | 7.5 | 7.125 | 0.64645 | 0.94631 | 1.2782 | 2024-01-21 04:00 | 9.0729 | 13.2815 | 17.9392 | [19 empty] | No usable entrance-line capacity | 7216.092 | 7208.117 | 7155.7764 | 7290.2095 | 7029.768 | 7369.265 | 7215.3974 | 7216.1464 | 7216.7323 | Unavailable |  | Insufficient voltage data | 7.125 | 5.8468 | 5.8468 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 7500.0 |  | MV | 1 | 1 | 53.8705 | 78.859 | 106.514 | 3 | 033ba35a-0e88-44c7-ae68-9ef721532ab3, ecb9c3ef-513f-492a-821c-4bff92c1df9c, d1e45bf7-a00b-40dc-a6ec-c751080a13c9 | A, B, C | 3 | 7159.7618 | 7032.614 | 7369.265 | 7155.7764 | 7031.508 | 7337.762 | 7161.6021 | 7029.768 | 7359.138
| 49 | GSO_36 | GSO_36 | Low | Inspect downstream topology and line metadata before capacity use | br_043_21 | 36.0466 | -79.7995 | 6666.7 | 6.6667 | 6.3334 | 0.34312 | 0.40406 | 0.4952 | 2024-01-20 05:00 | 5.4176 | 6.3799 | 7.819 | [19 empty] | No usable entrance-line capacity | 7203.9172 | 7201.8702 | 7161.6212 | 7254.6047 | 7030.326 | 7337.693 | 7203.4892 | 7206.3728 | 7201.8895 | Unavailable |  | Insufficient voltage data | 6.3334 | 5.8382 | 5.8382 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE14 | S_nSSEE14_12.47 | 6666.7 |  | MV | 1 | 1 | 28.5929 | 33.6716 | 41.267 | 3 | a492b914-7377-4047-b30b-90aa78dc94d3, c95edbeb-bfcc-48be-abeb-7c6ceba7bdae, 1ede274a-9246-4aec-acc0-17642c07af97 | A, B, C | 3 | 7170.5691 | 7061.322 | 7306.786 | 7161.8934 | 7053.819 | 7337.693 | 7161.6212 | 7030.326 | 7330.966
| 50 | GSO_63 | GSO_63 | Low | Inspect downstream topology and line metadata before capacity use | br_014_21 | 36.0873 | -79.8446 | 6122.4 | 6.1224 | 5.8163 | 0.059226 | 0.090528 | 0.12385 | 2024-07-15 09:00 | 1.0183 | 1.5565 | 2.1294 | [19 empty] | No usable entrance-line capacity | 7215.4477 | 7207.3035 | 7163.6707 | 7288.9791 | 7036.219 | 7389.248 | 7213.9656 | 7214.9811 | 7217.3964 | Unavailable |  | Insufficient voltage data | 5.8163 | 5.6924 | 5.6924 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 6122.4 |  | MV | 1 | 1 | 4.9355 | 7.544 | 10.321 | 3 | 676b1650-044c-43bf-bea6-3dced2a612c6, abbc8c51-7785-4d04-a735-eb965d943d5a, 167b629e-ae1a-4acd-a435-a9faf6b8f0b1 | A, B, C | 3 | 7170.2834 | 7076.604 | 7389.248 | 7163.6707 | 7036.219 | 7367.344 | 7165.0408 | 7039.605 | 7374.976
| 53 | GSO_111 | GSO_111 | Low | Inspect downstream topology and line metadata before capacity use | br_0111_21 | 36.0543 | -79.8942 | 7142.9 | 7.1429 | 6.7858 | 0.65645 | 0.90895 | 1.156 | 2024-01-18 04:00 | 9.674 | 13.395 | 17.0358 | [19 empty] | No usable entrance-line capacity | 7208.1469 | 7205.3898 | 7152.4801 | 7298.7433 | 7022.906 | 7370.484 | 7203.5009 | 7202.15 | 7218.7898 | Unavailable |  | Insufficient voltage data | 6.7858 | 5.6297 | 5.6297 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE8 | S_nSSEE8_12.47 | 7142.9 |  | MV | 1 | 1 | 54.7044 | 75.746 | 96.334 | 3 | f8549391-d242-43a9-9a34-33f872443611, 3488e4fc-fa59-4bcf-b967-3b7a890f6c3c, e60c92cc-e283-4345-87b0-ba3a9fd78005 | A, B, C | 3 | 7153.9956 | 7030.373 | 7294.406 | 7152.4801 | 7022.906 | 7274.06 | 7158.0204 | 7035.072 | 7370.484
| 54 | GSO_85 | GSO_85 | Low | Inspect downstream topology and line metadata before capacity use | br_085_21 | 36.0719 | -79.8252 | 6666.7 | 6.6667 | 6.3334 | 0.46705 | 0.6065 | 0.78437 | 2024-01-21 04:00 | 7.3744 | 9.5763 | 12.3847 | [19 empty] | No usable entrance-line capacity | 7215.3864 | 7207.4985 | 7161.4787 | 7289.5313 | 7029.753 | 7401.007 | 7216.8278 | 7215.8186 | 7213.5127 | Unavailable |  | Insufficient voltage data | 6.3334 | 5.549 | 5.549 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV | 1 | 1 | 38.9205 | 50.5416 | 65.364 | 3 | 6fcd01be-d3d1-4df7-bec8-4f8b1042aac0, 4fc59078-b2c4-42d5-b129-faa7a3f54cac, ac192c64-42ef-423f-814b-c8b837b8f5d2 | A, B, C | 3 | 7161.4787 | 7034.763 | 7386.337 | 7161.5458 | 7039.173 | 7401.007 | 7161.7433 | 7029.753 | 7379.724
| 57 | GSO_154 | GSO_154 | Low | Inspect downstream topology and line metadata before capacity use | br_034_22 | 36.0823 | -79.9238 | 6000 | 6 | 5.7 | 0.16112 | 0.19657 | 0.26084 | 2024-01-21 04:00 | 2.8267 | 3.4486 | 4.5762 | [19 empty] | No usable entrance-line capacity | 7211.3765 | 7204.9182 | 7160.4874 | 7281.0932 | 7021.844 | 7392.101 | 7209.9585 | 7209.7008 | 7214.4702 | Unavailable |  | Insufficient voltage data | 5.7 | 5.4392 | 5.4392 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE6 | S_nSSEE6_12.47 | 6000.0 |  | MV | 1 | 1 | 13.4266 | 16.381 | 21.737 | 3 | 6eba73e4-418d-4cd1-96b6-60b826ae450c, 70369b74-10d7-4556-af26-c0ccb8f01935, 0840b23d-66b0-48cf-856c-1f62526c7d6e | A, B, C | 3 | 7167.741 | 7024.989 | 7389.302 | 7160.4874 | 7021.844 | 7389.229 | 7163.432 | 7051.985 | 7392.101
| 59 | GSO_140 | GSO_140 | Low | Inspect downstream topology and line metadata before capacity use | br_020_22 | 36.0705 | -79.9556 | 6000 | 6 | 5.7 | 0.20816 | 0.2472 | 0.30924 | 2024-07-15 20:00 | 3.6519 | 4.3368 | 5.4253 | [19 empty] | No usable entrance-line capacity | 7211.9884 | 7205.5185 | 7163.6488 | 7280.6359 | 7033.355 | 7409.054 | 7213.2403 | 7208.8107 | 7213.9141 | Unavailable |  | Insufficient voltage data | 5.7 | 5.3908 | 5.3908 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE3 | S_nSSEE3_12.47 | 6000.0 |  | MV | 1 | 1 | 17.3466 | 20.6 | 25.77 | 3 | b6e43aeb-290f-443d-917c-933a0af02698, 7ac282db-535a-4cda-bcc4-f62230cc0be1, 52cf19cb-d2f9-48a0-a5d7-3d345a429c59 | A, B, C | 3 | 7165.7147 | 7038.585 | 7390.538 | 7164.6677 | 7035.544 | 7409.054 | 7163.6488 | 7033.355 | 7395.942
| 61 | GSO_114 | GSO_114 | Low | Inspect downstream topology and line metadata before capacity use | br_0114_21 | 36.0543 | -79.8942 | 7142.9 | 7.1429 | 6.7858 | 0.75285 | 1.0582 | 1.4064 | 2024-01-20 14:00 | 11.0946 | 15.594 | 20.7258 | [19 empty] | No usable entrance-line capacity | 7217.5015 | 7209.1627 | 7156.8274 | 7305.5036 | 7034.026 | 7375.435 | 7217.5945 | 7214.2928 | 7220.6173 | Unavailable |  | Insufficient voltage data | 6.7858 | 5.3794 | 5.3794 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE8 | S_nSSEE8_12.47 | 7142.9 |  | MV | 1 | 1 | 62.7375 | 88.1806 | 117.2 | 3 | 34c2c476-7801-4ae6-ba1f-ca1a602925b3, 156d4241-1525-4089-8367-effd61eb4969, 3128527e-a25b-4b2c-9d88-b40eb600580e | A, B, C | 3 | 7158.642 | 7034.026 | 7359.088 | 7157.2792 | 7034.57 | 7348.25 | 7156.8274 | 7037.237 | 7375.435
| 65 | GSO_7 | GSO_7 | Low | Inspect downstream topology and line metadata before capacity use | br_07_21 | 36.0852 | -79.8826 | 5714.3 | 5.7143 | 5.4286 | 0.029079 | 0.0468 | 0.073416 | 2024-01-21 | 0.53566 | 0.8621 | 1.3524 | [19 empty] | No usable entrance-line capacity | 7200.8526 | 7200.2707 | 7151.5238 | 7265.9657 | 7021.114 | 7394.917 |  | 7205.8972 | 7195.8081 | Unavailable |  | Insufficient voltage data | 5.4286 | 5.3552 | 5.3552 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 5714.3 |  | MV | 1 | 1 | 2.4232 | 3.9 | 6.118 | 3 | 874fce3a-0ddc-405e-8b4d-496bf1208ffa, 7c4e0a27-0ba8-4589-8efa-9d78e22aeea7, b3997dcd-0479-4422-904f-1e86aedb3b49 | A, B, C | 3 |  |  |  | 7161.7451 | 7021.114 | 7394.917 | 7151.5238 | 7035.899 | 7258.936
| 67 | GSO_30 | GSO_30 | Low | Inspect downstream topology and line metadata before capacity use | br_037_21 | 36.1038 | -79.7639 | 7500 | 7.5 | 7.125 | 0.94227 | 1.3691 | 1.8068 | 2024-01-20 09:05 | 13.2248 | 19.2155 | 25.3585 | [19 empty] | No usable entrance-line capacity | 7217.0197 | 7208.4425 | 7156.416 | 7300.6631 | 7033.038 | 7370.04 | 7219.4871 | 7216.1758 | 7215.3962 | Unavailable |  | Insufficient voltage data | 7.125 | 5.3182 | 5.3182 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE13 | S_nSSEE13_12.47 | 7500.0 |  | MV | 1 | 1 | 78.5223 | 114.0916 | 150.566 | 3 | 80a38063-4b58-4c05-9631-c9f20eaae49f, 07afe75d-2efa-4a63-8500-f5eed954ebc4, 4339844d-f7f4-4af5-a7ce-ff1e206a4bfc | A, B, C | 3 | 7159.5577 | 7040.468 | 7370.04 | 7157.2861 | 7034.824 | 7340.439 | 7156.416 | 7033.038 | 7357.223
| 70 | GSO_9 | GSO_9 | Low | Inspect downstream topology and line metadata before capacity use | br_023_21 | 36.1003 | -79.8075 | 5555.6 | 5.5556 | 5.2778 | 0.014247 | 0.022788 | 0.038448 | 2024-01-21 01:00 | 0.26995 | 0.43177 | 0.72848 | [19 empty] | No usable entrance-line capacity | 7211.7125 | 7204.7278 | 7168.3966 | 7274.7069 | 7036.314 | 7398.067 |  | 7213.8407 | 7209.5842 | Unavailable |  | Insufficient voltage data | 5.2778 | 5.2394 | 5.2394 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE10 | S_nSSEE10_12.47 | 5555.6 |  | MV | 1 | 1 | 1.1873 | 1.899 | 3.204 | 3 | c7e10126-bd63-4bd3-96ab-07587af29378, f631ee12-3be7-417b-ad19-901e9ad68684, 9b89dc0e-e258-4610-b60b-484b1b02a312 | A, B, C | 3 |  |  |  | 7169.3564 | 7036.314 | 7398.067 | 7168.3966 | 7063.268 | 7375.544
| 73 | GSO_29 | GSO_29 | Low | Inspect downstream topology and line metadata before capacity use | br_036_21 | 36.1038 | -79.7639 | 7500 | 7.5 | 7.125 | 1.0643 | 1.5256 | 1.9875 | 2024-01-20 05:00 | 14.9374 | 21.4125 | 27.8944 | [19 empty] | No usable entrance-line capacity | 7217.2307 | 7208.4595 | 7158.0898 | 7296.5195 | 7026.696 | 7361.989 | 7218.8008 | 7216.7843 | 7216.1072 | Unavailable |  | Insufficient voltage data | 7.125 | 5.1375 | 5.1375 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE13 | S_nSSEE13_12.47 | 7500.0 |  | MV | 1 | 1 | 88.6911 | 127.1367 | 165.623 | 3 | 53ac9d88-ec7e-422c-9547-7b65d0e1b05c, bbdb1c8c-b61b-4af3-a00d-d34e99f936e8, 37be8bbe-3fc1-42ac-aa14-512831f011d9 | A, B, C | 3 | 7161.3853 | 7026.696 | 7361.989 | 7158.0898 | 7034.163 | 7350.564 | 7158.3643 | 7044.896 | 7343.326
| 76 | GSO_32 | GSO_32 | Low | Inspect downstream topology and line metadata before capacity use | br_039_21 | 36.0466 | -79.7995 | 6666.7 | 6.6667 | 6.3334 | 0.70222 | 0.94806 | 1.2177 | 2024-01-21 | 11.0876 | 14.9692 | 19.2262 | [19 empty] | No usable entrance-line capacity | 7218.7084 | 7209.0225 | 7159.3655 | 7300.1693 | 7028.782 | 7384.644 | 7219.6019 | 7217.9812 | 7218.5421 | Unavailable |  | Insufficient voltage data | 6.3334 | 5.1157 | 5.1157 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE14 | S_nSSEE14_12.47 | 6666.7 |  | MV | 1 | 1 | 58.5184 | 79.0046 | 101.472 | 3 | 049d0b94-e086-4825-b104-d454ffd3dc7c, 81e832b4-cd01-4844-b4d8-6ff81d95dbe4, 934aabc4-8b42-44e6-82dc-1b3261dc29d9 | A, B, C | 3 | 7160.3207 | 7047.206 | 7384.644 | 7161.8561 | 7055.197 | 7353.839 | 7159.3655 | 7028.782 | 7367.974
| 79 | GSO_62 | GSO_62 | Low | Inspect downstream topology and line metadata before capacity use | br_013_21 | 36.0873 | -79.8446 | 6122.4 | 6.1224 | 5.8163 | 0.40929 | 0.62888 | 0.85519 | 2024-01-21 04:00 | 7.0371 | 10.8124 | 14.7034 | [19 empty] | No usable entrance-line capacity | 7210.4934 | 7205.6455 | 7155.6228 | 7285.659 | 7024.907 | 7347.292 | 7200.9471 | 7215.9623 | 7214.571 | Unavailable |  | Insufficient voltage data | 5.8163 | 4.9611 | 4.9611 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 6122.4 |  | MV | 1 | 1 | 34.1079 | 52.4066 | 71.266 | 3 | 2c8910bb-0c41-4c36-8a5f-d8ffc5e65938, 3f59d58a-b780-49d5-86ae-b0b0f01c076d, decddce1-9f0e-44c6-a3bd-24fdb9cf1a60 | A, B, C | 3 | 7162.9904 | 7050.523 | 7265.269 | 7164.2574 | 7057.297 | 7347.292 | 7155.6228 | 7024.907 | 7342.584
| 81 | GSO_79 | GSO_79 | Low | Inspect downstream topology and line metadata before capacity use | br_079_21 | 36.0719 | -79.8252 | 6666.7 | 6.6667 | 6.3334 | 0.85586 | 1.1479 | 1.4952 | 2024-01-21 04:00 | 13.5135 | 18.1249 | 23.6075 | [19 empty] | No usable entrance-line capacity | 7217.6827 | 7208.2548 | 7158.9527 | 7310.2322 | 7031.057 | 7392.982 | 7221.4765 | 7215.6318 | 7215.9397 | Unavailable |  | Insufficient voltage data | 6.3334 | 4.8382 | 4.8382 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV | 1 | 1 | 71.3217 | 95.6596 | 124.596 | 3 | dfd547e9-e06c-4fe7-8842-913f0b3f7d52, f68a1c8a-5406-4783-b8ae-a255bce0e795, 02d224d1-8d1b-45bb-98ed-ebc20c74318a | A, B, C | 3 | 7160.1835 | 7042.092 | 7392.982 | 7160.591 | 7042.367 | 7377.536 | 7158.9527 | 7031.057 | 7344.135
| 82 | GSO_51 | GSO_51 | Low | Inspect downstream topology and line metadata before capacity use | br_058_21 | 36.0168 | -79.7965 | 5454.5 | 5.4545 | 5.1818 | 0.24078 | 0.2792 | 0.35236 | 2024-01-20 15:00 | 4.6466 | 5.3882 | 6.7999 | [19 empty] | No usable entrance-line capacity | 7212.0441 | 7205.4118 | 7164.7827 | 7274.673 | 7031.074 | 7393.478 | 7212.4391 | 7210.7764 | 7212.9168 | Unavailable |  | Insufficient voltage data | 5.1818 | 4.8294 | 4.8294 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV | 1 | 1 | 20.0647 | 23.267 | 29.363 | 3 | 2dabfa67-e633-42fb-88f8-b99c8c81ce3f, 40e658e9-710a-4f81-b823-ce3b23d76208, 100d5254-7678-4ba2-a678-ffa8ba0ac8ce | A, B, C | 3 | 7164.7827 | 7043.323 | 7388.971 | 7165.321 | 7031.074 | 7393.478 | 7168.6754 | 7032.18 | 7379.251
| 84 | GSO_57 | GSO_57 | Low | Inspect downstream topology and line metadata before capacity use | br_08_21 | 36.0872 | -79.8446 | 6122.4 | 6.1224 | 5.8163 | 0.53196 | 0.75041 | 1.0327 | 2024-01-20 10:05 | 9.146 | 12.9019 | 17.7546 | [19 empty] | No usable entrance-line capacity | 7215.7428 | 7207.529 | 7159.9155 | 7299.3301 | 7020.914 | 7366.094 | 7215.334 | 7219.1604 | 7212.7341 | Unavailable |  | Insufficient voltage data | 5.8163 | 4.7836 | 4.7836 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 6122.4 |  | MV | 1 | 1 | 44.3296 | 62.5339 | 86.055 | 3 | 27046833-12e1-4f55-aeb1-743d3fddc9b4, e2d61ac2-432e-446d-b560-32b75aebceed, 08dafb35-ef6e-48c6-89ef-1f3412fa5f7e | A, B, C | 3 | 7161.7144 | 7020.914 | 7360.007 | 7159.9155 | 7026.914 | 7366.094 | 7164.8823 | 7041 | 7362.109
| 85 | GSO_48 | GSO_48 | Low | Inspect downstream topology and line metadata before capacity use | br_055_21 | 36.0168 | -79.7965 | 5454.5 | 5.4545 | 5.1818 | 0.34809 | 0.40578 | 0.50413 | 2024-01-17 21:00 | 6.7177 | 7.8308 | 9.7289 | [19 empty] | No usable entrance-line capacity | 7213.2816 | 7205.8092 | 7165.3937 | 7278.9082 | 7037.298 | 7400.607 | 7214.1262 | 7213.2 | 7212.5187 | Unavailable |  | Insufficient voltage data | 5.1818 | 4.6776 | 4.6776 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV | 1 | 1 | 29.0078 | 33.8146 | 42.011 | 3 | caead5dd-6652-4002-9205-bf1f5d7841a2, 2756c12d-de33-427b-a20e-a7524bf8ba2a, d501232c-0e9b-4aed-b1c7-0711f51fd12c | A, B, C | 3 | 7168.9937 | 7040.019 | 7386.898 | 7166.5917 | 7050.165 | 7396.08 | 7165.3937 | 7037.298 | 7400.607
| 86 | GSO_6 | GSO_6 | Low | Inspect downstream topology and line metadata before capacity use | br_06_21 | 36.0852 | -79.8827 | 5714.3 | 5.7143 | 5.4286 | 0.44327 | 0.637 | 0.82657 | 2024-01-18 04:00 | 8.1654 | 11.7343 | 15.2263 | [19 empty] | No usable entrance-line capacity | 7217.8812 | 7209.1932 | 7155.3929 | 7298.5753 | 7019.858 | 7377.444 | 7217.975 | 7218.6368 | 7217.0318 | Unavailable |  | Insufficient voltage data | 5.4286 | 4.602 | 4.602 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 5714.3 |  | MV | 1 | 1 | 36.9389 | 53.0836 | 68.881 | 3 | 145f4423-0120-41c0-a961-6f6b453e91a7, 120599d7-eee0-4966-bd20-36d9e2e8b089, a5d804f2-bcf0-4e70-ad7f-9ffc889ca71a | A, B, C | 3 | 7157.262 | 7019.858 | 7360.712 | 7158.5274 | 7040.707 | 7377.444 | 7155.3929 | 7038.448 | 7368.328
| 88 | GSO_109 | GSO_109 | Low | Inspect downstream topology and line metadata before capacity use | br_0109_21 | 36.0543 | -79.8942 | 7142.9 | 7.1429 | 6.7858 | 1.16 | 1.6922 | 2.2226 | 2024-01-20 13:00 | 17.0952 | 24.9371 | 32.754 | [19 empty] | No usable entrance-line capacity | 7218.2454 | 7209.5723 | 7154.3264 | 7301.8462 | 7013.79 | 7376.767 | 7219.2755 | 7219.1168 | 7216.3438 | Unavailable |  | Insufficient voltage data | 6.7858 | 4.5632 | 4.5632 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE8 | S_nSSEE8_12.47 | 7142.9 |  | MV | 1 | 1 | 96.6701 | 141.014 | 185.217 | 3 | 0c75d1f1-8237-436b-a2c8-c9b6fdc7a116, ec8ad3c4-a39d-4acb-8788-e7435be58cb7, e6350d88-56d8-492b-bc1e-dcd90fcca31f | A, B, C | 3 | 7158.4793 | 7039.526 | 7361.076 | 7154.3264 | 7013.79 | 7376.767 | 7159.2487 | 7027.561 | 7356.999
| 89 | GSO_158 | GSO_158 | Low | Inspect downstream topology and line metadata before capacity use | br_04_23 | 36.1929 | -79.6068 | 7500 | 7.5 | 7.125 | 1.3735 | 2.0512 | 2.6914 | 2024-01-20 21:00 | 19.2773 | 28.7881 | 37.7736 | [19 empty] | No usable entrance-line capacity | 7215.4466 | 7207.759 | 7154.9717 | 7290.3876 | 7026.375 | 7347.627 | 7216.7902 | 7214.5335 | 7215.016 | Unavailable |  | Insufficient voltage data | 7.125 | 4.4336 | 4.4336 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 7500.0 |  | MV | 1 | 1 | 114.4589 | 170.9293 | 224.281 | 3 | 8e1d3060-4f17-4027-bb48-9326d72d1f5e, b84e6ee7-bc4b-467a-884d-e5dac0fbac0b, 5320e9a7-8d71-4f75-b9c9-3a6a37f707db | A, B, C | 3 | 7159.2145 | 7040.748 | 7347.627 | 7154.9717 | 7026.375 | 7339.706 | 7158.9634 | 7039.11 | 7340.412
| 90 | GSO_163 | GSO_163 | Low | Inspect downstream topology and line metadata before capacity use | br_09_23 | 36.1644 | -79.708 | 8000 | 8 | 7.6 | 1.6046 | 2.3743 | 3.1708 | 2024-01-18 04:00 | 21.1132 | 31.2405 | 41.7216 | [19 empty] | No usable entrance-line capacity | 7217.4868 | 7208.479 | 7158.293 | 7296.5459 | 7025.692 | 7350.74 | 7216.7281 | 7218.3244 | 7217.4077 | Unavailable |  | Insufficient voltage data | 7.6 | 4.4292 | 4.4292 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 8000.0 |  | MV | 1 | 1 | 133.7168 | 197.8567 | 264.237 | 3 | d90170cc-5eec-43f7-a5d9-cb91dca851cb, 9018e821-338d-4aa5-bb0d-3e9aa19f5a3b, 0d2e0f05-d1e8-46f2-953d-daf9b517d3b5 | A, B, C | 3 | 7158.9996 | 7029.88 | 7349.323 | 7159.2007 | 7036.651 | 7344.524 | 7158.293 | 7025.692 | 7350.74
| 91 | GSO_54 | GSO_54 | Low | Inspect downstream topology and line metadata before capacity use | br_061_21 | 36.0131 | -79.8489 | 10000 | 10 | 9.5 | 2.5084 | 3.7884 | 5.0799 | 2024-01-21 04:00 | 26.4037 | 39.8781 | 53.4723 | [19 empty] | No usable entrance-line capacity | 7217.0048 | 7208.6732 | 7155.3215 | 7294.5482 | 7020.097 | 7345.299 | 7217.0266 | 7216.9324 | 7217.0555 | Unavailable |  | Insufficient voltage data | 9.5 | 4.4201 | 4.4201 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE17 | S_nSSEE17_12.47 | 10000.0 |  | MV | 1 | 1 | 209.0296 | 315.702 | 423.322 | 3 | c70624cc-3511-421e-bcd3-4f74ee43c80f, 0c2d5da7-8b73-4e99-a2ec-e1bd371c44f1, b486465e-b5c3-4f46-9979-e961ceb9df52 | A, B, C | 3 | 7155.3215 | 7029.599 | 7345.299 | 7156.9081 | 7039.188 | 7339.95 | 7156.2487 | 7020.097 | 7342.938
| 92 | GSO_80 | GSO_80 | Low | Inspect downstream topology and line metadata before capacity use | br_080_21 | 36.0719 | -79.8252 | 6666.7 | 6.6667 | 6.3334 | 1.0636 | 1.4855 | 1.9457 | 2024-01-21 02:00 | 16.7929 | 23.4556 | 30.7217 | [19 empty] | No usable entrance-line capacity | 7213.9295 | 7207.3892 | 7156.3121 | 7296.8136 | 7029.388 | 7360.017 | 7206.9182 | 7216.6189 | 7218.2514 | Unavailable |  | Insufficient voltage data | 6.3334 | 4.3876 | 4.3876 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV | 1 | 1 | 88.6299 | 123.794 | 162.143 | 3 | 4fb9d568-cec8-4d2c-b185-503c8441a94f, 48527915-ef6b-4d16-9525-f6d17fae71ba, e4842198-5ba7-4542-9415-20f0a87511ac | A, B, C | 3 | 7158.3421 | 7038.262 | 7295.787 | 7156.3121 | 7029.388 | 7349.599 | 7158.4853 | 7042.835 | 7360.017
| 93 | GSO_5 | GSO_5 | Low | Inspect downstream topology and line metadata before capacity use | br_05_21 | 36.0852 | -79.8827 | 5714.3 | 5.7143 | 5.4286 | 0.6801 | 0.83893 | 1.0512 | 2024-01-20 15:00 | 12.5282 | 15.454 | 19.3644 | [19 empty] | No usable entrance-line capacity | 7213.7876 | 7206.87 | 7158.2647 | 7285.5193 | 7021.195 | 7403.876 | 7215.1929 | 7213.7879 | 7212.3819 | Unavailable |  | Insufficient voltage data | 5.4286 | 4.3774 | 4.3774 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 5714.3 |  | MV | 1 | 1 | 56.6751 | 69.911 | 87.601 | 3 | 1a7b2ce3-8ce4-43f0-822c-bae88f338574, fdea0e08-11f9-40c1-bd4a-4dfdb8ea2803, 921b5057-9802-4094-b921-551288ad3d2e | A, B, C | 3 | 7158.2647 | 7021.195 | 7377.471 | 7160.3127 | 7043.416 | 7390.02 | 7159.8977 | 7022.957 | 7403.876
| 94 | GSO_101 | GSO_101 | Low | Inspect downstream topology and line metadata before capacity use | br_0101_21 | 36.0872 | -79.897 | 5714.3 | 5.7143 | 5.4286 | 0.66936 | 0.87754 | 1.1216 | 2024-01-21 04:00 | 12.3302 | 16.1651 | 20.6613 | [19 empty] | No usable entrance-line capacity | 7215.8272 | 7208.2232 | 7154.528 | 7295.7893 | 7015.109 | 7397.203 | 7217.5121 | 7215.0523 | 7214.917 | Unavailable |  | Insufficient voltage data | 5.4286 | 4.307 | 4.307 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE7 | S_nSSEE7_12.47 | 5714.3 |  | MV | 1 | 1 | 55.7798 | 73.128 | 93.468 | 3 | f32aafa6-4f97-40b9-85a1-6516b7a34fb0, 8f1038a0-f3d5-4f15-bedf-b8f1215601f3, 6c559f06-b888-4a9d-ba0f-901b0b19b354 | A, B, C | 3 | 7154.528 | 7032.468 | 7354.335 | 7161.6221 | 7015.109 | 7367.048 | 7160.318 | 7041.751 | 7397.203
| 95 | GSO_108 | GSO_108 | Low | Inspect downstream topology and line metadata before capacity use | br_0108_21 | 36.0543 | -79.8942 | 7142.9 | 7.1429 | 6.7858 | 1.2795 | 1.9144 | 2.4922 | 2024-01-20 23:30 | 18.8557 | 28.2116 | 36.7274 | [19 empty] | No usable entrance-line capacity | 7218.5029 | 7209.4222 | 7152.0488 | 7303.3036 | 7018.219 | 7377.273 | 7217.0711 | 7218.7109 | 7219.7267 | Unavailable |  | Insufficient voltage data | 6.7858 | 4.2935 | 4.2935 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE8 | S_nSSEE8_12.47 | 7142.9 |  | MV | 1 | 1 | 106.625 | 159.5309 | 207.686 | 3 | e867a5e4-d5f1-4fdf-98c8-da37424315a6, c0036365-6459-4cc7-b7b1-ed8933515338, 1886a888-6918-466c-929d-0c8f16370dda | A, B, C | 3 | 7152.0488 | 7020.781 | 7374.353 | 7153.8113 | 7018.219 | 7373.962 | 7156.2754 | 7027.699 | 7377.273
| 96 | GSO_81 | GSO_81 | Low | Inspect downstream topology and line metadata before capacity use | br_081_21 | 36.0719 | -79.8252 | 6666.7 | 6.6667 | 6.3334 | 1.1689 | 1.5889 | 2.07 | 2024-01-21 04:00 | 18.4566 | 25.0875 | 32.6835 | [19 empty] | No usable entrance-line capacity | 7217.7392 | 7208.4933 | 7158.627 | 7300.9326 | 7028.924 | 7379.533 | 7218.1871 | 7215.0403 | 7219.9903 | Unavailable |  | Insufficient voltage data | 6.3334 | 4.2634 | 4.2634 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV | 1 | 1 | 97.4105 | 132.4067 | 172.497 | 3 | 9a5c0969-f68d-4cea-a13e-ef351a3d3730, a8a2fc9d-e642-4554-abad-f2610eb29b51, 27bb62b3-e552-4996-874d-31dcad547987 | A, B, C | 3 | 7162.2 | 7056.459 | 7376.401 | 7158.627 | 7028.924 | 7364.172 | 7162.3398 | 7031.609 | 7379.533
| 97 | GSO_157 | GSO_157 | Low | Inspect downstream topology and line metadata before capacity use | br_03_23 | 36.1929 | -79.6068 | 7500 | 7.5 | 7.125 | 1.4377 | 2.1269 | 2.889 | 2024-01-21 04:00 | 20.1776 | 29.851 | 40.5472 | [19 empty] | No usable entrance-line capacity | 7216.654 | 7208.3397 | 7156.273 | 7299.0265 | 7025.898 | 7357.982 | 7219.391 | 7215.246 | 7215.325 | Unavailable |  | Insufficient voltage data | 7.125 | 4.236 | 4.236 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 7500.0 |  | MV | 1 | 1 | 119.8044 | 177.2403 | 240.749 | 3 | d76a1565-b995-4235-9508-12ae427ed548, b96622f9-34da-4d3a-a144-a82c9e2d84a9, 962e5ace-7f13-49d9-a1bd-65973f2adfac | A, B, C | 3 | 7161.1953 | 7047.317 | 7356.89 | 7156.273 | 7025.898 | 7352.525 | 7158.6673 | 7036.145 | 7357.982
| 98 | GSO_34 | GSO_34 | Low | Inspect downstream topology and line metadata before capacity use | br_041_21 | 36.0466 | -79.7995 | 6666.7 | 6.6667 | 6.3334 | 1.1591 | 1.6717 | 2.2167 | 2024-01-18 04:00 | 18.3008 | 26.3956 | 35.0005 | [19 empty] | No usable entrance-line capacity | 7218.4838 | 7208.9707 | 7156.6527 | 7300.8283 | 7015.072 | 7367.529 | 7217.9172 | 7218.5452 | 7218.989 | Unavailable |  | Insufficient voltage data | 6.3334 | 4.1167 | 4.1167 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE14 | S_nSSEE14_12.47 | 6666.7 |  | MV | 1 | 1 | 96.588 | 139.3106 | 184.726 | 3 | deb58541-2cca-43d5-86c5-55264c6041d3, 179024ab-8e49-42be-b943-761705fb5abd, 0cbf9200-98b4-43c7-934d-2cc30d8ab63b | A, B, C | 3 | 7157.6891 | 7028.229 | 7367.529 | 7158.2614 | 7018.694 | 7361.218 | 7156.6527 | 7015.072 | 7362.113
| 99 | GSO_156 | GSO_156 | Low | Inspect downstream topology and line metadata before capacity use | br_02_23 | 36.1929 | -79.6068 | 7500 | 7.5 | 7.125 | 1.5909 | 2.3544 | 3.0797 | 2024-01-21 04:00 | 22.3279 | 33.0441 | 43.2239 | [19 empty] | No usable entrance-line capacity | 7215.7447 | 7207.9257 | 7155.3354 | 7290.1816 | 7026.036 | 7362.545 | 7215.8325 | 7215.6363 | 7215.7653 | Unavailable |  | Insufficient voltage data | 7.125 | 4.0453 | 4.0453 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 7500.0 |  | MV | 1 | 1 | 132.5721 | 196.1993 | 256.642 | 3 | 2ec12710-cbb3-4ac0-ae81-f21bc775b59d, 17343a92-f390-4c00-96dd-aa4c8e6f2cf5, 12b55d36-db8c-475f-838b-08caf84b6421 | A, B, C | 3 | 7155.3354 | 7034.959 | 7348.881 | 7159.5538 | 7038.91 | 7362.545 | 7156.5434 | 7026.036 | 7345.388
| 100 | GSO_71 | GSO_71 | Low | Inspect downstream topology and line metadata before capacity use | br_071_21 | 36.0825 | -79.7708 | 10000 | 10 | 9.5 | 2.7774 | 4.1681 | 5.5004 | 2024-01-21 02:00 | 29.2357 | 43.8752 | 57.8994 | [19 empty] | No usable entrance-line capacity | 7215.6696 | 7208.074 | 7154.7971 | 7290.003 | 7025.2 | 7350.03 | 7215.7755 | 7215.2592 | 7215.9741 | Unavailable |  | Insufficient voltage data | 9.5 | 3.9996 | 3.9996 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE3 | S_nSSEE3_12.47 | 10000.0 |  | MV | 1 | 1 | 231.4489 | 347.345 | 458.37 | 3 | 7dec81b6-3b82-498d-bfaa-f44bf5d9581d, 4ff8b560-0d8d-46ca-aa4f-48e616d84a8c, 828a3353-455f-43cc-a9b0-71980deae8fd | A, B, C | 3 | 7157.0324 | 7031.212 | 7350.03 | 7155.167 | 7025.2 | 7338.632 | 7154.7971 | 7029.863 | 7346.146
| 101 | GSO_53 | GSO_53 | Low | Inspect downstream topology and line metadata before capacity use | br_060_21 | 36.0168 | -79.7965 | 5454.5 | 5.4545 | 5.1818 | 0.72043 | 0.99739 | 1.3206 | 2024-01-21 04:00 | 13.9032 | 19.2481 | 25.4852 | [19 empty] | No usable entrance-line capacity | 7215.8519 | 7207.7742 | 7158.51 | 7299.8983 | 7024.857 | 7371.023 | 7218.6815 | 7219.8617 | 7209.0126 | Unavailable |  | Insufficient voltage data | 5.1818 | 3.8612 | 3.8612 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV | 1 | 1 | 60.036 | 83.116 | 110.049 | 3 | 77c08208-993b-4559-b9e2-42c4c772997c, 4b800952-fa1b-4668-ba63-4244710bab3c, 3b012ead-fe04-4b66-8c50-59d42334a89c | A, B, C | 3 | 7158.9707 | 7030.684 | 7354.242 | 7162.7831 | 7039.365 | 7371.023 | 7158.51 | 7024.857 | 7312.744
| 102 | GSO_65 | GSO_65 | Low | Inspect downstream topology and line metadata before capacity use | br_065_21 | 36.0801 | -79.7573 | 4285.7 | 4.2857 | 4.0714 | 0.14171 | 0.16918 | 0.21571 | 2024-01-21 04:00 | 3.4806 | 4.1552 | 5.2982 | [19 empty] | No usable entrance-line capacity | 7207.1599 | 7202.0145 | 7162.1424 | 7269.2626 | 7026.92 | 7399.487 | 7206.1207 | 7209.0513 | 7206.3077 | Unavailable |  | Insufficient voltage data | 4.0714 | 3.8557 | 3.8557 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 4285.7 |  | MV | 1 | 1 | 11.8091 | 14.098 | 17.976 | 3 | a8421f63-1fb7-4386-80d1-558a9049f658, c0caf65c-2d30-471b-9a8c-36e1484ba877, a2d74127-91f7-4d1b-a98b-b3f287f80eec | A, B, C | 3 | 7163.0298 | 7028.381 | 7393.974 | 7162.1424 | 7026.92 | 7395.691 | 7163.1053 | 7032.335 | 7399.487
| 103 | GSO_41 | GSO_41 | Low | Inspect downstream topology and line metadata before capacity use | br_048_21 | 36.121 | -79.8612 | 6000 | 6 | 5.7 | 0.89469 | 1.3503 | 1.859 | 2024-01-18 04:00 | 15.6963 | 23.6894 | 32.6147 | [19 empty] | No usable entrance-line capacity | 7218.0995 | 7208.4733 | 7158.0634 | 7298.8416 | 7026.979 | 7371.369 | 7217.7383 | 7218.6123 | 7217.9478 | Unavailable |  | Insufficient voltage data | 5.7 | 3.841 | 3.841 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE15 | S_nSSEE15_12.47 | 6000.0 |  | MV | 1 | 1 | 74.5573 | 112.5246 | 154.92 | 3 | 4f3f10ee-748f-4c21-b9c3-8ac51c8d41f6, d7d6e014-1cd2-4cb5-84bb-a00b2cad42e3, e1cda877-0a5c-49b1-bd5f-ad8449fb0e0c | A, B, C | 3 | 7159.4495 | 7026.979 | 7362.056 | 7158.0634 | 7038.393 | 7371.369 | 7160.848 | 7036.775 | 7358.559
| 106 | GSO_40 | GSO_40 | Low | Inspect downstream topology and line metadata before capacity use | br_047_21 | 36.121 | -79.8612 | 6000 | 6 | 5.7 | 1.0344 | 1.5401 | 2.0837 | 2024-01-20 20:00 | 18.1481 | 27.0187 | 36.5566 | [19 empty] | No usable entrance-line capacity | 7215.8568 | 7208.104 | 7157.5942 | 7289.3843 | 7022.226 | 7348.687 | 7215.8721 | 7215.088 | 7216.6102 | Unavailable |  | Insufficient voltage data | 5.7 | 3.6163 | 3.6163 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE15 | S_nSSEE15_12.47 | 6000.0 |  | MV | 1 | 1 | 86.2034 | 128.3382 | 173.644 | 3 | ee7aaead-b8fb-40d3-8a03-8ab58a542fdc, 58cd6faf-3139-48ff-a9ef-b152b7ebf778, 79202d32-8dca-417a-9d59-fc14f3bcaf5f | A, B, C | 3 | 7158.4064 | 7030.971 | 7348.687 | 7157.5942 | 7022.226 | 7344.815 | 7159.8832 | 7038.791 | 7343.286
| 108 | GSO_69 | GSO_69 | Low | Inspect downstream topology and line metadata before capacity use | br_069_21 | 36.0801 | -79.7573 | 4285.7 | 4.2857 | 4.0714 | 0.29078 | 0.38227 | 0.49324 | 2024-01-21 04:00 | 7.1421 | 9.3892 | 12.1146 | [19 empty] | No usable entrance-line capacity | 7214.1835 | 7207.179 | 7160.1162 | 7282.3762 | 7040.442 | 7404.695 | 7214.1648 | 7215.0953 | 7213.2902 | Unavailable |  | Insufficient voltage data | 4.0714 | 3.5782 | 3.5782 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 4285.7 |  | MV | 1 | 1 | 24.2321 | 31.856 | 41.103 | 3 | 16e446fe-cce5-4d4b-abd0-d9bf98278835, 3f69baec-6464-4c01-91c1-171903c224f7, 9255af13-2569-446c-b326-8de2942e3a26 | A, B, C | 3 | 7160.1162 | 7040.442 | 7404.695 | 7163.2573 | 7048.365 | 7380.163 | 7160.9632 | 7046.617 | 7370.48
| 109 | GSO_16 | GSO_16 | Low | Inspect downstream topology and line metadata before capacity use | br_021_21 | 36.1003 | -79.8075 | 5555.6 | 5.5556 | 5.2778 | 0.91765 | 1.2917 | 1.7095 | 2024-01-21 | 17.3868 | 24.4742 | 32.39 | [19 empty] | No usable entrance-line capacity | 7213.9837 | 7207.3443 | 7158.3023 | 7281.415 | 7027.004 | 7350.634 | 7213.8776 | 7213.8768 | 7214.1967 | Unavailable |  | Insufficient voltage data | 5.2778 | 3.5683 | 3.5683 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE10 | S_nSSEE10_12.47 | 5555.6 |  | MV | 1 | 1 | 76.4704 | 107.642 | 142.457 | 3 | e4f24c66-81cd-48f4-b9a3-a8aaa9fe8c98, b5d738a6-79bd-43f6-b4e4-0fb4de70abfd, 2b3c0835-4f9e-453c-86b3-35847ab5af94 | A, B, C | 3 | 7161.1866 | 7031.904 | 7350.634 | 7158.3023 | 7027.004 | 7349.272 | 7158.5815 | 7028.886 | 7346.423
| 112 | GSO_92 | GSO_92 | Low | Inspect downstream topology and line metadata before capacity use | br_092_21 | 36.0708 | -79.7962 | 4545.5 | 4.5455 | 4.3182 | 0.50669 | 0.61804 | 0.76915 | 2024-01-21 04:00 | 11.7337 | 14.3123 | 17.8118 | [19 empty] | No usable entrance-line capacity | 7212.9872 | 7205.9122 | 7160.4825 | 7288.4225 | 7032.834 | 7398.959 | 7216.6166 | 7211.5031 | 7210.842 | Unavailable |  | Insufficient voltage data | 4.3182 | 3.5491 | 3.5491 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV | 1 | 1 | 42.2238 | 51.503 | 64.096 | 3 | a984179e-ff24-4a5b-9bff-44fa02582a26, fbe573a4-e81d-4315-b9c9-510a65c98be6, 9e7256be-44ac-40e3-95c4-e604f1b5b6ea | A, B, C | 3 | 7163.626 | 7044.05 | 7398.959 | 7164.3354 | 7032.834 | 7390.946 | 7160.4825 | 7042.616 | 7371.121
| 114 | GSO_10 | GSO_10 | Low | Inspect downstream topology and line metadata before capacity use | br_015_21 | 36.1003 | -79.8075 | 5555.6 | 5.5556 | 5.2778 | 0.9939 | 1.3981 | 1.894 | 2024-01-21 04:00 | 18.8317 | 26.4892 | 35.8853 | [19 empty] | No usable entrance-line capacity | 7214.6024 | 7207.4963 | 7157.2806 | 7287.425 | 7029.711 | 7360.154 | 7215.7135 | 7213.7068 | 7214.3869 | Unavailable |  | Insufficient voltage data | 5.2778 | 3.3839 | 3.3839 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE10 | S_nSSEE10_12.47 | 5555.6 |  | MV | 1 | 1 | 82.8253 | 116.5043 | 157.83 | 3 | d140ab36-31a8-40c7-820d-c3a2df82604a, b315ece6-7341-4cdf-a1c9-70a8dbfe93ff, 396f73e2-6041-46ac-90d5-a9439aef50d8 | A, B, C | 3 | 7157.2806 | 7036.492 | 7360.154 | 7159.8699 | 7029.851 | 7347.808 | 7158.904 | 7029.711 | 7336.52
| 115 | GSO_39 | GSO_39 | Low | Inspect downstream topology and line metadata before capacity use | br_046_21 | 36.121 | -79.8612 | 6000 | 6 | 5.7 | 1.194 | 1.7841 | 2.3656 | 2024-01-21 04:00 | 20.9467 | 31.3007 | 41.5025 | [19 empty] | No usable entrance-line capacity | 7215.1734 | 7207.7432 | 7155.6604 | 7289.2733 | 7027.455 | 7357.045 | 7214.3461 | 7215.8886 | 7215.2854 | Unavailable |  | Insufficient voltage data | 5.7 | 3.3344 | 3.3344 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE15 | S_nSSEE15_12.47 | 6000.0 |  | MV | 1 | 1 | 99.4969 | 148.6783 | 197.137 | 3 | 93658bef-4bd5-4300-8424-5c388155968b, 1ef359a3-1b23-4781-b7f6-73e5a4c4559f, 77ff5585-562a-45e7-a281-464e98737abb | A, B, C | 3 | 7156.4961 | 7027.455 | 7347.233 | 7156.372 | 7032.851 | 7357.045 | 7155.6604 | 7030.602 | 7350.951
| 116 | GSO_2 | GSO_2 | Low | Inspect downstream topology and line metadata before capacity use | br_02_21 | 36.0852 | -79.8827 | 5714.3 | 5.7143 | 5.4286 | 1.2027 | 1.7331 | 2.2932 | 2024-01-20 08:10 | 22.1555 | 31.9248 | 42.2426 | [19 empty] | No usable entrance-line capacity | 7217.7143 | 7209.0305 | 7154.6143 | 7299.3899 | 7014.129 | 7363.589 | 7217.7415 | 7218.2129 | 7217.1885 | Unavailable |  | Insufficient voltage data | 5.4286 | 3.1354 | 3.1354 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 5714.3 |  | MV | 1 | 1 | 100.2277 | 144.422 | 191.098 | 3 | e16fe26a-3331-4e10-bcda-3d5b4cfc42bc, f5b81547-937f-4c70-92ba-8a0fb6594394, a28c1752-7f45-48c2-b058-b7cdc091e5d6 | A, B, C | 3 | 7155.0175 | 7014.129 | 7363.589 | 7155.274 | 7032.373 | 7355.642 | 7154.6143 | 7020.742 | 7363.238
| 117 | GSO_11 | GSO_11 | Low | Inspect downstream topology and line metadata before capacity use | br_016_21 | 36.1003 | -79.8075 | 5555.6 | 5.5556 | 5.2778 | 1.2134 | 1.7004 | 2.1962 | 2024-01-21 04:00 | 22.9909 | 32.2172 | 41.612 | [19 empty] | No usable entrance-line capacity | 7213.5801 | 7206.9057 | 7155.8687 | 7286.1987 | 7021.29 | 7361.658 | 7215.4504 | 7213.2752 | 7212.0148 | Unavailable |  | Insufficient voltage data | 5.2778 | 3.0816 | 3.0816 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE10 | S_nSSEE10_12.47 | 5555.6 |  | MV | 1 | 1 | 101.1181 | 141.697 | 183.017 | 3 | 469868d0-2f60-42bd-aa67-be26d6eae0eb, 9cdbec33-569a-438b-ac44-23b272ad169b, dfea635f-2a86-40f1-9367-d78b6dd6c309 | A, B, C | 3 | 7158.1775 | 7031.483 | 7361.658 | 7156.9751 | 7031.188 | 7341.442 | 7155.8687 | 7021.29 | 7337.258
| 118 | GSO_89 | GSO_89 | Low | Inspect downstream topology and line metadata before capacity use | br_089_21 | 36.0708 | -79.7962 | 4545.5 | 4.5455 | 4.3182 | 0.76922 | 1.013 | 1.3116 | 2024-01-21 04:00 | 17.8134 | 23.458 | 30.3739 | [19 empty] | No usable entrance-line capacity | 7204.3218 | 7203.054 | 7155.416 | 7263.6473 | 7028.922 | 7316.769 | 7203.4131 | 7201.3506 | 7208.2017 | Unavailable |  | Insufficient voltage data | 4.3182 | 3.0066 | 3.0066 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV | 1 | 1 | 64.1018 | 84.414 | 109.301 | 3 | d629f58a-fb37-4300-b174-4dadcd7fdef5, c6e42508-1e1b-4a8d-ad6c-5ed17230666d, a59c7bce-fb93-4255-8dac-4024e2c3a1c9 | A, B, C | 3 | 7157.0953 | 7043.136 | 7305.109 | 7159.0577 | 7037.101 | 7280.262 | 7155.416 | 7028.922 | 7316.769
| 119 | GSO_96 | GSO_96 | Low | Inspect downstream topology and line metadata before capacity use | br_096_21 | 36.0708 | -79.7962 | 4545.5 | 4.5455 | 4.3182 | 0.81239 | 1.0681 | 1.358 | 2024-01-20 06:00 | 18.813 | 24.7358 | 31.4471 | [19 empty] | No usable entrance-line capacity | 7216.1074 | 7207.7803 | 7156.9344 | 7295.4159 | 7016.661 | 7389.602 | 7215.6623 | 7217.6007 | 7215.0591 | Unavailable |  | Insufficient voltage data | 4.3182 | 2.9603 | 2.9603 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV | 1 | 1 | 67.699 | 89.0123 | 113.163 | 3 | 1b5731fb-ced8-4f58-b1ab-d0ee4f8ea875, fcbaf392-5711-44ee-86c0-792317753d2f, fad28770-b3f6-4478-87a1-3b095d264a87 | A, B, C | 3 | 7161.264 | 7016.661 | 7387.063 | 7156.9344 | 7025.591 | 7365.089 | 7163.269 | 7043.704 | 7389.602
| 120 | GSO_60 | GSO_60 | Low | Inspect downstream topology and line metadata before capacity use | br_011_21 | 36.0873 | -79.8446 | 6122.4 | 6.1224 | 5.8163 | 1.3871 | 2.0963 | 2.859 | 2024-01-21 04:00 | 23.8491 | 36.042 | 49.1553 | [19 empty] | No usable entrance-line capacity | 7216.1349 | 7208.225 | 7156.5718 | 7290.5723 | 7031.344 | 7353.708 | 7216.191 | 7216.3915 | 7215.8221 | Unavailable |  | Insufficient voltage data | 5.8163 | 2.9573 | 2.9573 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 6122.4 |  | MV | 1 | 1 | 115.5942 | 174.692 | 238.251 | 3 | 229fce16-0cb2-401d-957b-9d0d3c2ac1cc, fc187080-4278-4699-8d7f-ded10dc27448, 52980b4f-3c73-4c68-8631-e69ccc722a34 | A, B, C | 3 | 7156.5718 | 7031.844 | 7349.984 | 7158.6387 | 7037.086 | 7353.708 | 7159.2185 | 7031.344 | 7340.735
| 121 | GSO_88 | GSO_88 | Low | Inspect downstream topology and line metadata before capacity use | br_088_21 | 36.0708 | -79.7962 | 4545.5 | 4.5455 | 4.3182 | 0.76138 | 1.0329 | 1.3613 | 2024-01-18 04:00 | 17.6318 | 23.9186 | 31.5235 | [19 empty] | No usable entrance-line capacity | 7216.6743 | 7208.0308 | 7157.903 | 7293.8588 | 7024.557 | 7398.63 | 7217.5829 | 7214.7847 | 7217.6553 | Unavailable |  | Insufficient voltage data | 4.3182 | 2.957 | 2.957 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV | 1 | 1 | 63.4485 | 86.0716 | 113.438 | 3 | 93986b58-113b-4798-b153-eda6e8924352, 73bea406-8df3-48d6-99e8-780c9ba74d8d, b1fd8626-d75b-4f57-95d8-5e0f995f6548 | A, B, C | 3 | 7157.903 | 7036.979 | 7355.502 | 7160.2295 | 7034.854 | 7398.63 | 7162.7731 | 7024.557 | 7386.5
| 122 | GSO_97 | GSO_97 | Low | Inspect downstream topology and line metadata before capacity use | br_098_21 | 36.061 | -79.7714 | 7500 | 7.5 | 7.125 | 2.111 | 3.1628 | 4.1702 | 2024-01-21 04:00 | 29.6287 | 44.3902 | 58.5288 | [19 empty] | No usable entrance-line capacity | 7215.8654 | 7208.143 | 7154.7981 | 7292.9456 | 7027.295 | 7349.288 | 7216.8698 | 7215.4802 | 7215.246 | Unavailable |  | Insufficient voltage data | 7.125 | 2.9548 | 2.9548 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE6 | S_nSSEE6_12.47 | 7500.0 |  | MV | 1 | 1 | 175.9206 | 263.5666 | 347.515 | 3 | 003a8d77-c248-43c2-af2f-1f5f30595e2b, b3f7a58f-66bb-4c73-a447-90250ee96029, 3b017716-3815-48f3-bf37-e278bd03cc9d | A, B, C | 3 | 7156.487 | 7035.922 | 7341.841 | 7154.7981 | 7027.295 | 7337.104 | 7157.232 | 7029.951 | 7349.288
| 123 | GSO_82 | GSO_82 | Low | Inspect downstream topology and line metadata before capacity use | br_082_21 | 36.0719 | -79.8252 | 6666.7 | 6.6667 | 6.3334 | 1.6447 | 2.5113 | 3.3849 | 2024-01-21 | 25.9693 | 39.6522 | 53.4463 | [19 empty] | No usable entrance-line capacity | 7216.1838 | 7208.2807 | 7155.9567 | 7291.4052 | 7016.762 | 7348.626 | 7216.6384 | 7216.2977 | 7215.6152 | Unavailable |  | Insufficient voltage data | 6.3334 | 2.9484 | 2.9484 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV | 1 | 1 | 137.0611 | 209.2763 | 282.079 | 3 | a890d29a-0380-4cd2-8cff-f9826e3ff07b, 918cae00-7f70-4556-9d40-35da1f05977d, 93c33640-e4a0-470f-a164-89c99ae69984 | A, B, C | 3 | 7155.9567 | 7016.762 | 7348.626 | 7159.058 | 7018.098 | 7336.403 | 7157.9453 | 7043.608 | 7345.808
| 124 | GSO_25 | GSO_25 | Low | Inspect downstream topology and line metadata before capacity use | br_032_21 | 36.0603 | -79.8599 | 3750 | 3.75 | 3.5625 | 0.406 | 0.49246 | 0.62447 | 2024-01-21 04:00 | 11.3964 | 13.8233 | 17.5289 | [19 empty] | No usable entrance-line capacity | 7213.2093 | 7206.3355 | 7161.046 | 7285.556 | 7038.822 | 7398.15 | 7215.3822 | 7209.5937 | 7214.6519 | Unavailable |  | Insufficient voltage data | 3.5625 | 2.938 | 2.938 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE12 | S_nSSEE12_12.47 | 3750.0 |  | MV | 1 | 1 | 33.8332 | 41.038 | 52.039 | 3 | 8c0cf450-9297-450e-b468-8396988be79f, d4f80b32-222c-49ea-bb38-81080bcb0826, 6a2617f0-409e-448d-8ce4-c1175edcf36a | A, B, C | 3 | 7161.046 | 7050.075 | 7391.01 | 7162.9505 | 7038.822 | 7398.15 | 7163.2867 | 7041.124 | 7396.496
| 125 | GSO_35 | GSO_35 | Low | Inspect downstream topology and line metadata before capacity use | br_042_21 | 36.0466 | -79.7995 | 6666.7 | 6.6667 | 6.3334 | 1.7539 | 2.6524 | 3.5443 | 2024-01-21 00:05 | 27.6931 | 41.8801 | 55.9627 | [19 empty] | No usable entrance-line capacity | 7216.6833 | 7208.3607 | 7155.425 | 7297.4489 | 7020.614 | 7365.567 | 7216.5678 | 7215.3526 | 7218.1296 | Unavailable |  | Insufficient voltage data | 6.3334 | 2.789 | 2.789 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE14 | S_nSSEE14_12.47 | 6666.7 |  | MV | 1 | 1 | 146.1585 | 221.035 | 295.36 | 3 | efc37dec-e402-4c7d-81af-aa9cb2729757, d7ccdfd6-6a7d-4338-9666-e79b11f003a9, 6d4ede07-2601-4246-903b-56124df12172 | A, B, C | 3 | 7156.8781 | 7020.614 | 7365.567 | 7155.425 | 7025.555 | 7343.82 | 7157.0082 | 7027.167 | 7353.833
| 126 | GSO_12 | GSO_12 | Low | Inspect downstream topology and line metadata before capacity use | br_017_21 | 36.1003 | -79.8075 | 5555.6 | 5.5556 | 5.2778 | 1.2344 | 1.896 | 2.4984 | 2024-01-18 04:00 | 23.3877 | 35.9233 | 47.3368 | [19 empty] | No usable entrance-line capacity | 7216.2476 | 7208.2533 | 7154.6751 | 7292.8687 | 7027.606 | 7344.314 | 7217.2488 | 7216.1738 | 7215.3203 | Unavailable |  | Insufficient voltage data | 5.2778 | 2.7795 | 2.7795 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE10 | S_nSSEE10_12.47 | 5555.6 |  | MV | 1 | 1 | 102.8633 | 157.9969 | 208.196 | 3 | e263a729-e360-4716-9561-679bf6b5d16a, ede6f7c6-f426-4d65-bfe0-7dac24a794c1, 4c1ed359-972e-4bdd-a0cd-1159d7a32c07 | A, B, C | 3 | 7158.415 | 7027.606 | 7344.314 | 7155.9948 | 7033.07 | 7344.067 | 7154.6751 | 7027.993 | 7342.148
| 127 | GSO_13 | GSO_13 | Low | Inspect downstream topology and line metadata before capacity use | br_018_21 | 36.1003 | -79.8075 | 5555.6 | 5.5556 | 5.2778 | 1.3096 | 1.9149 | 2.5309 | 2024-01-21 04:00 | 24.8124 | 36.2823 | 47.9543 | [19 empty] | No usable entrance-line capacity | 7211.3179 | 7206.4673 | 7156.4895 | 7289.176 | 7029.021 | 7357.057 | 7215.9378 | 7214.4965 | 7203.5194 | Unavailable |  | Insufficient voltage data | 5.2778 | 2.7469 | 2.7469 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE10 | S_nSSEE10_12.47 | 5555.6 |  | MV | 1 | 1 | 109.1296 | 159.5763 | 210.912 | 3 | 28993f84-c3b9-4382-b199-7eae1602f7b5, d4524dc1-a63b-454b-a0d9-1683a9db619b, 538bb977-c069-4a72-a1f5-79ade89be85e | A, B, C | 3 | 7156.4895 | 7035.417 | 7345.131 | 7157.6534 | 7029.021 | 7357.057 | 7158.538 | 7032.707 | 7271.453
| 128 | GSO_91 | GSO_91 | Low | Inspect downstream topology and line metadata before capacity use | br_091_21 | 36.0708 | -79.7962 | 4545.5 | 4.5455 | 4.3182 | 0.96936 | 1.2713 | 1.6821 | 2024-01-21 | 22.4482 | 29.4405 | 38.9535 | [19 empty] | No usable entrance-line capacity | 7218.0043 | 7208.535 | 7161.9621 | 7293.9873 | 7032.754 | 7381.484 | 7218.63 | 7217.8125 | 7217.5705 | Unavailable |  | Insufficient voltage data | 4.3182 | 2.6361 | 2.6361 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV | 1 | 1 | 80.7802 | 105.9423 | 140.175 | 3 | 11eec288-b107-4b0d-8513-8e0e8b097ff9, 66b6c9ff-fe2f-4708-83aa-26715afe7d27, 2494a26c-ddcb-40f8-8643-7c936424dfc0 | A, B, C | 3 | 7164.3295 | 7056.984 | 7368.059 | 7161.9621 | 7032.754 | 7381.484 | 7162.6808 | 7054.194 | 7349.135
| 129 | GSO_59 | GSO_59 | Low | Inspect downstream topology and line metadata before capacity use | br_010_21 | 36.0873 | -79.8446 | 6122.4 | 6.1224 | 5.8163 | 1.5447 | 2.377 | 3.1957 | 2024-01-21 04:00 | 26.5586 | 40.8684 | 54.9442 | [19 empty] | No usable entrance-line capacity | 7216.5114 | 7208.3147 | 7155.6714 | 7292.9023 | 7029.813 | 7360.041 | 7215.7952 | 7216.9801 | 7216.759 | Unavailable |  | Insufficient voltage data | 5.8163 | 2.6206 | 2.6206 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 6122.4 |  | MV | 1 | 1 | 128.7271 | 198.0846 | 266.309 | 3 | 4529fb6d-421e-4f02-9b11-c956a4443f8e, 1231155d-ed13-4563-8801-fa08388d11cd, 1b822839-e89f-49f2-b2a9-69df27011548 | A, B, C | 3 | 7155.6714 | 7030.333 | 7343.653 | 7156.827 | 7029.813 | 7360.041 | 7157.5878 | 7032.205 | 7336.569
| 130 | GSO_99 | GSO_99 | Low | Inspect downstream topology and line metadata before capacity use | br_0100_21 | 36.061 | -79.7715 | 7500 | 7.5 | 7.125 | 2.3225 | 3.3894 | 4.525 | 2024-01-21 04:00 | 32.5971 | 47.5704 | 63.5094 | [19 empty] | No usable entrance-line capacity | 7217.6853 | 7208.632 | 7156.4087 | 7298.442 | 7024.329 | 7349.561 | 7218.8637 | 7217.0449 | 7217.1472 | Unavailable |  | Insufficient voltage data | 7.125 | 2.6 | 2.6 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE6 | S_nSSEE6_12.47 | 7500.0 |  | MV | 1 | 1 | 193.545 | 282.449 | 377.087 | 3 | a3c897bb-ba13-4a0b-af16-81acabf20ccd, 667e5144-bfb1-4543-a81f-7a88e26190c7, 9d892d7c-e138-4107-8084-bbde890e1cc4 | A, B, C | 3 | 7159.1861 | 7024.329 | 7349.561 | 7157.6944 | 7028.516 | 7343.945 | 7156.4087 | 7030.285 | 7340.956
| 131 | GSO_14 | GSO_14 | Low | Inspect downstream topology and line metadata before capacity use | br_019_21 | 36.1003 | -79.8075 | 5555.6 | 5.5556 | 5.2778 | 1.403 | 2.0384 | 2.6885 | 2024-01-21 04:00 | 26.582 | 38.6214 | 50.9392 | [19 empty] | No usable entrance-line capacity | 7213.1081 | 7206.9928 | 7156.9538 | 7292.3547 | 7025.833 | 7347.666 | 7217.0892 | 7216.695 | 7205.5401 | Unavailable |  | Insufficient voltage data | 5.2778 | 2.5893 | 2.5893 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE10 | S_nSSEE10_12.47 | 5555.6 |  | MV | 1 | 1 | 116.9126 | 169.864 | 224.04 | 3 | 9df35035-201c-43e2-9c0f-29f5652d20b6, 4f0a9de3-7d5d-4d74-841a-ad368a655ddc, 37a8aff5-f4d5-48d1-b094-f7ff7add641f | A, B, C | 3 | 7157.7784 | 7025.833 | 7347.666 | 7157.2648 | 7027.14 | 7341.296 | 7156.9538 | 7032.766 | 7284.781
| 132 | GSO_87 | GSO_87 | Low | Inspect downstream topology and line metadata before capacity use | br_087_21 | 36.0709 | -79.7962 | 4545.5 | 4.5455 | 4.3182 | 1.0482 | 1.4151 | 1.8016 | 2024-01-21 04:00 | 24.2732 | 32.7701 | 41.721 | [19 empty] | No usable entrance-line capacity | 7214.9529 | 7207.6065 | 7157.6638 | 7289.0616 | 7023.684 | 7363.641 | 7213.3463 | 7216.8372 | 7214.6752 | Unavailable |  | Insufficient voltage data | 4.3182 | 2.5166 | 2.5166 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV | 1 | 1 | 87.3478 | 117.9236 | 150.134 | 3 | e7689375-373b-4d7a-b001-0fa11239a327, 589e4f98-7742-4541-b2c3-6b108b7f9d4d, d9c84a3d-b565-4642-a7d4-3c9df307b1c8 | A, B, C | 3 | 7157.6638 | 7040.907 | 7339.709 | 7161.6505 | 7051.221 | 7363.641 | 7157.7194 | 7023.684 | 7359.829
| 133 | GSO_23 | GSO_23 | Low | Inspect downstream topology and line metadata before capacity use | br_030_21 | 36.0604 | -79.8599 | 3750 | 3.75 | 3.5625 | 0.63701 | 0.87494 | 1.1484 | 2024-01-18 04:00 | 17.8809 | 24.5598 | 32.2365 | [19 empty] | No usable entrance-line capacity | 7214.3692 | 7207.0337 | 7157.1451 | 7293.317 | 7013.887 | 7392.971 | 7217.5076 | 7215.7757 | 7209.8243 | Unavailable |  | Insufficient voltage data | 3.5625 | 2.4141 | 2.4141 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE12 | S_nSSEE12_12.47 | 3750.0 |  | MV | 1 | 1 | 53.0838 | 72.912 | 95.702 | 3 | 73114768-3396-46b2-8366-027d7f330c2a, 8896d2cc-f5f3-479a-9806-74f9830d0e65, 306a0179-6b1d-4c84-b7ad-c043978706f4 | A, B, C | 3 | 7160.3787 | 7032.392 | 7384.339 | 7158.4472 | 7024.365 | 7368.236 | 7157.1451 | 7013.887 | 7392.971
| 134 | GSO_86 | GSO_86 | Low | Inspect downstream topology and line metadata before capacity use | br_086_21 | 36.0708 | -79.7962 | 4545.5 | 4.5455 | 4.3182 | 1.0764 | 1.5183 | 1.9608 | 2024-01-20 23:00 | 24.9268 | 35.1594 | 45.4078 | [19 empty] | No usable entrance-line capacity | 7216.3646 | 7208.1698 | 7157.4523 | 7292.4896 | 7020.439 | 7364.76 | 7214.4339 | 7217.2619 | 7217.3979 | Unavailable |  | Insufficient voltage data | 4.3182 | 2.3574 | 2.3574 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV | 1 | 1 | 89.6995 | 126.522 | 163.401 | 3 | 492c962b-e2b7-4edd-afe9-20606e4114f6, 6182a628-fb52-41b9-8b93-90488a51a0fe, 6927b6e8-4d14-436e-8236-19dc4cdad934 | A, B, C | 3 | 7157.7648 | 7037.464 | 7361.588 | 7158.2443 | 7020.439 | 7361.105 | 7157.4523 | 7031.181 | 7364.76
| 135 | GSO_110 | GSO_110 | Low | Inspect downstream topology and line metadata before capacity use | br_0110_21 | 36.0543 | -79.8942 | 7142.9 | 7.1429 | 6.7858 | 2.1945 | 3.3579 | 4.5154 | 2024-01-21 04:00 | 32.3391 | 49.484 | 66.5421 | [19 empty] | No usable entrance-line capacity | 7218.5578 | 7209.5133 | 7154.3927 | 7303.0236 | 7032.828 | 7366.994 | 7217.5903 | 7219.8296 | 7218.2535 | Unavailable |  | Insufficient voltage data | 6.7858 | 2.2704 | 2.2704 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE8 | S_nSSEE8_12.47 | 7142.9 |  | MV | 1 | 1 | 182.8709 | 279.822 | 376.282 | 3 | 1e111a58-963a-4906-b1f6-e2d03049b19a, 8a0dd243-2512-4f92-afd7-db6e79d7496e, ca02189c-f89b-417b-a469-ef0366d6da6e | A, B, C | 3 | 7156.5028 | 7038.304 | 7349.554 | 7156.978 | 7039.344 | 7366.994 | 7154.3927 | 7032.828 | 7357.523
| 136 | GSO_46 | GSO_46 | Low | Inspect downstream topology and line metadata before capacity use | br_053_21 | 36.0168 | -79.7965 | 5454.5 | 5.4545 | 5.1818 | 1.4964 | 2.2132 | 2.9347 | 2024-01-21 04:00 | 28.8781 | 42.7115 | 56.6359 | [19 empty] | No usable entrance-line capacity | 7216.6055 | 7208.448 | 7155.0724 | 7294.1416 | 7019.875 | 7356.714 | 7217.5134 | 7216.3368 | 7215.9663 | Unavailable |  | Insufficient voltage data | 5.1818 | 2.247 | 2.247 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV | 1 | 1 | 124.6999 | 184.4341 | 244.562 | 3 | 425e9895-3ec9-4ecf-a2de-00e847c9f5d0, e8d1fc00-bcf6-4d05-b6b9-7f38e6915ce5, 0b8f662d-5bc3-42fe-a24e-070da09bdd80 | A, B, C | 3 | 7157.3281 | 7030.403 | 7350.663 | 7155.0724 | 7019.875 | 7356.714 | 7155.7057 | 7022.197 | 7335.577
| 137 | GSO_83 | GSO_83 | Low | Inspect downstream topology and line metadata before capacity use | br_083_21 | 36.0719 | -79.8252 | 6666.7 | 6.6667 | 6.3334 | 2.0902 | 3.158 | 4.2004 | 2024-01-18 04:00 | 33.0035 | 49.8623 | 66.3213 | [19 empty] | No usable entrance-line capacity | 7216.4286 | 7208.2788 | 7155.2625 | 7292.5603 | 7023.24 | 7352.078 | 7216.4992 | 7215.7309 | 7217.0556 | Unavailable |  | Insufficient voltage data | 6.3334 | 2.133 | 2.133 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV | 1 | 1 | 174.186 | 263.1632 | 350.031 | 3 | af9148e3-1b4f-4f27-b409-3654c3f953f5, 48c0048d-65ab-48a8-8cd9-833258bee864, 8c265c14-8e0f-4c74-9519-46da2dff7cd1 | A, B, C | 3 | 7155.936 | 7027.94 | 7343.715 | 7155.2625 | 7023.24 | 7339.323 | 7156.4478 | 7024.316 | 7352.078
| 138 | GSO_52 | GSO_52 | Low | Inspect downstream topology and line metadata before capacity use | br_059_21 | 36.0168 | -79.7965 | 5454.5 | 5.4545 | 5.1818 | 1.5455 | 2.3443 | 3.1697 | 2024-01-21 04:00 | 29.8254 | 45.242 | 61.17 | [19 empty] | No usable entrance-line capacity | 7216.349 | 7208.1567 | 7154.95 | 7292.7946 | 7020.362 | 7355.853 | 7217.1545 | 7216.0559 | 7215.8365 | Unavailable |  | Insufficient voltage data | 5.1818 | 2.0121 | 2.0121 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV | 1 | 1 | 128.7905 | 195.3616 | 264.141 | 3 | 148e241f-8dca-40c2-bc4c-9bba11acb600, 740ff96c-6171-4486-bb6a-904851da7f68, 54cc7298-372e-4f46-9c94-d78d3e7e3368 | A, B, C | 3 | 7158.2074 | 7037.862 | 7348.919 | 7154.95 | 7020.362 | 7334.09 | 7156.0314 | 7022.008 | 7355.853
| 139 | GSO_159 | GSO_159 | Low | Inspect downstream topology and line metadata before capacity use | br_05_23 | 36.2604 | -79.5886 | 5714.3 | 5.7143 | 5.4286 | 1.722 | 2.5527 | 3.469 | 2024-01-21 04:00 | 31.7218 | 47.0236 | 63.9024 | [19 empty] | No usable entrance-line capacity | 7217.7217 | 7208.8765 | 7157.4357 | 7299.2863 | 7027.018 | 7364.047 | 7216.8027 | 7218.9435 | 7217.4187 | Unavailable |  | Insufficient voltage data | 5.4286 | 1.9596 | 1.9596 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 5714.3 |  | MV | 1 | 1 | 143.5038 | 212.7262 | 289.083 | 3 | 83f2cd36-180e-4d9a-9105-62a32f68ab85, 96fae847-ae01-4905-9884-47b324a88934, 2e882994-3bef-4961-988c-cd677efd6410 | A, B, C | 3 | 7158.2941 | 7032.868 | 7339.673 | 7157.4357 | 7027.018 | 7364.047 | 7157.6084 | 7035.231 | 7350.518
| 140 | GSO_15 | GSO_15 | Low | Inspect downstream topology and line metadata before capacity use | br_020_21 | 36.1003 | -79.8075 | 5555.6 | 5.5556 | 5.2778 | 1.6994 | 2.5284 | 3.3588 | 2024-01-21 04:00 | 32.1984 | 47.9068 | 63.6399 | [19 empty] | No usable entrance-line capacity | 7216.43 | 7208.3982 | 7156.2973 | 7293.6556 | 7028.82 | 7351.676 | 7217.7713 | 7215.5321 | 7215.9867 | Unavailable |  | Insufficient voltage data | 5.2778 | 1.919 | 1.919 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE10 | S_nSSEE10_12.47 | 5555.6 |  | MV | 1 | 1 | 141.6145 | 210.703 | 279.9 | 3 | 2dfc9022-cd2d-4071-a0ed-f7aa4dbf29b5, 34fb9785-294c-4580-94c1-92b57cb0e642, dd9e89fb-3f9a-4966-a494-c19ab9432a67 | A, B, C | 3 | 7159.7277 | 7035.467 | 7347.419 | 7156.2973 | 7028.82 | 7333.648 | 7158.4497 | 7032.503 | 7351.676
| 141 | GSO_21 | GSO_21 | Low | Inspect downstream topology and line metadata before capacity use | br_028_21 | 36.0604 | -79.8599 | 3750 | 3.75 | 3.5625 | 0.9294 | 1.2838 | 1.6817 | 2024-01-18 04:00 | 26.0883 | 36.0354 | 47.2064 | [19 empty] | No usable entrance-line capacity | 7219.2358 | 7209.0887 | 7156.8127 | 7305.799 | 7026.492 | 7381.687 | 7221.1011 | 7217.251 | 7219.3554 | Unavailable |  | Insufficient voltage data | 3.5625 | 1.8808 | 1.8808 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE12 | S_nSSEE12_12.47 | 3750.0 |  | MV | 1 | 1 | 77.4498 | 106.98 | 140.144 | 3 | 6f7a2c02-ca5d-4d73-a76d-82f0fe3158c9, 39b0a939-9afe-4c84-bfda-5eec318bc35e, a49c303e-bacd-45af-8754-babfb2545a48 | A, B, C | 3 | 7161.1557 | 7050.7 | 7381.687 | 7156.8127 | 7026.492 | 7355.105 | 7157.5594 | 7030.65 | 7376.374
| 142 | GSO_22 | GSO_22 | Low | Inspect downstream topology and line metadata before capacity use | br_029_21 | 36.0604 | -79.8599 | 3750 | 3.75 | 3.5625 | 0.94167 | 1.3475 | 1.7494 | 2024-01-18 04:00 | 26.4329 | 37.8235 | 49.1055 | [19 empty] | No usable entrance-line capacity | 7216.9853 | 7208.496 | 7156.3248 | 7298.5923 | 7028.584 | 7385.958 | 7215.6541 | 7216.2422 | 7219.0595 | Unavailable |  | Insufficient voltage data | 3.5625 | 1.8131 | 1.8131 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE12 | S_nSSEE12_12.47 | 3750.0 |  | MV | 1 | 1 | 78.4727 | 112.2883 | 145.782 | 3 | f1fcda72-2c9e-4219-9a68-e344865344e1, c13495f3-7436-4771-9d8e-028fe398e677, 60e175bd-dd8d-424f-b541-e6c27675c2ee | A, B, C | 3 | 7156.3248 | 7028.584 | 7343.157 | 7156.6637 | 7031.264 | 7385.958 | 7159.4587 | 7042.669 | 7360.393
| 143 | GSO_45 | GSO_45 | Low | Inspect downstream topology and line metadata before capacity use | br_052_21 | 36.0168 | -79.7965 | 5454.5 | 5.4545 | 5.1818 | 1.6229 | 2.498 | 3.3731 | 2024-01-18 04:00 | 31.3198 | 48.2067 | 65.0955 | [19 empty] | No usable entrance-line capacity | 7217.0144 | 7208.4208 | 7155.8524 | 7297.333 | 7025.158 | 7348.097 | 7215.9133 | 7218.619 | 7216.511 | Unavailable |  | Insufficient voltage data | 5.1818 | 1.8087 | 1.8087 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV | 1 | 1 | 135.2434 | 208.1636 | 281.092 | 3 | 0a36e22d-cb96-45c8-8d47-74ede8f433bd, ac9dddc3-7cae-427c-a129-87d3008b8362, 87af0485-ac3b-4ef1-bd8e-39742bb1311b | A, B, C | 3 | 7157.1122 | 7030.966 | 7329.357 | 7159.9844 | 7046.351 | 7348.097 | 7155.8524 | 7025.158 | 7341.13
| 144 | GSO_105 | GSO_105 | Low | Inspect downstream topology and line metadata before capacity use | br_0105_21 | 36.0872 | -79.897 | 5714.3 | 5.7143 | 5.4286 | 1.8088 | 2.7735 | 3.66 | 2024-01-21 04:00 | 33.3201 | 51.0907 | 67.4209 | [19 empty] | No usable entrance-line capacity | 7218.4899 | 7209.6347 | 7153.4294 | 7304.0023 | 7026.907 | 7361.976 | 7219.6787 | 7218.4431 | 7217.3479 | Unavailable |  | Insufficient voltage data | 5.4286 | 1.7686 | 1.7686 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE7 | S_nSSEE7_12.47 | 5714.3 |  | MV | 1 | 1 | 150.7342 | 231.125 | 305 | 3 | 3943a935-55e7-44b5-a61e-08789763be18, 11bf4c6d-205c-4caf-b572-7246ab210632, 98dc0614-4560-469e-93e2-97b3c41b5000 | A, B, C | 3 | 7156.0454 | 7038.264 | 7361.976 | 7156.994 | 7041.808 | 7350.941 | 7153.4294 | 7026.907 | 7349.655
| 145 | GSO_68 | GSO_68 | Low | Inspect downstream topology and line metadata before capacity use | br_068_21 | 36.0801 | -79.7573 | 4285.7 | 4.2857 | 4.0714 | 1.2841 | 1.8094 | 2.3491 | 2024-01-21 04:00 | 31.5406 | 44.4408 | 57.6985 | [19 empty] | No usable entrance-line capacity | 7217.103 | 7208.4122 | 7156.8834 | 7300.4956 | 7022.938 | 7378.702 | 7216.1525 | 7219.5354 | 7215.621 | Unavailable |  | Insufficient voltage data | 4.0714 | 1.7223 | 1.7223 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 4285.7 |  | MV | 1 | 1 | 107.0124 | 150.7806 | 195.762 | 3 | 6abb0433-d7c1-47cb-b500-310c0966ae29, b14a51cb-21cb-48f4-91a6-564663c5a923, f2986696-35a7-4d1e-a7dd-8b01d8d6756a | A, B, C | 3 | 7157.0565 | 7033.7 | 7345.095 | 7160.5258 | 7022.938 | 7378.702 | 7156.8834 | 7024.239 | 7349.637
| 146 | GSO_64 | GSO_64 | Low | Inspect downstream topology and line metadata before capacity use | br_064_21 | 36.0801 | -79.7573 | 4285.7 | 4.2857 | 4.0714 | 1.2676 | 1.8163 | 2.3845 | 2024-01-21 04:00 | 31.1334 | 44.6103 | 58.5671 | [19 empty] | No usable entrance-line capacity | 7216.3105 | 7208.2628 | 7157.4191 | 7292.6235 | 7025.429 | 7366.352 | 7215.9508 | 7215.9033 | 7217.0775 | Unavailable |  | Insufficient voltage data | 4.0714 | 1.6869 | 1.6869 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 4285.7 |  | MV | 1 | 1 | 105.6309 | 151.3556 | 198.709 | 3 | aa668afa-9003-4c02-b068-76a760cba7c4, 8ec9092e-c513-4856-b139-17b0f244b287, 96d7ca9d-a8a7-4620-beb4-015993e1495f | A, B, C | 3 | 7157.4191 | 7039.797 | 7364.542 | 7159.1644 | 7025.429 | 7366.352 | 7157.8661 | 7025.686 | 7349.755
| 147 | GSO_26 | GSO_26 | Low | Inspect downstream topology and line metadata before capacity use | br_033_21 | 36.0603 | -79.8599 | 3750 | 3.75 | 3.5625 | 1.0473 | 1.4436 | 1.89 | 2024-01-21 04:00 | 29.3981 | 40.5217 | 53.054 | [19 empty] | No usable entrance-line capacity | 7214.6583 | 7207.5343 | 7155.7894 | 7295.49 | 7014.68 | 7361.056 | 7213.9775 | 7212.5453 | 7217.4522 | Unavailable |  | Insufficient voltage data | 3.5625 | 1.6725 | 1.6725 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE12 | S_nSSEE12_12.47 | 3750.0 |  | MV | 1 | 1 | 87.2755 | 120.2986 | 157.504 | 3 | 2ded452d-d964-456f-bc61-891c5e02102b, 123d2e0f-6c7b-4b17-96d2-32d4328dde67, 06410d93-c578-4f9d-86d8-8eb333ba28c9 | A, B, C | 3 | 7159.6718 | 7038.154 | 7333.781 | 7156.2635 | 7014.68 | 7337.245 | 7155.7894 | 7021.552 | 7361.056
| 148 | GSO_58 | GSO_58 | Low | Inspect downstream topology and line metadata before capacity use | br_09_21 | 36.0872 | -79.8446 | 6122.4 | 6.1224 | 5.8163 | 2.002 | 3.0619 | 4.1658 | 2024-01-21 04:00 | 34.4199 | 52.6438 | 71.6239 | [19 empty] | No usable entrance-line capacity | 7216.6127 | 7208.1485 | 7156.4384 | 7293.9913 | 7028.915 | 7340.455 | 7215.8393 | 7216.443 | 7217.5558 | Unavailable |  | Insufficient voltage data | 5.8163 | 1.6504 | 1.6504 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 6122.4 |  | MV | 1 | 1 | 166.8301 | 255.1588 | 347.154 | 3 | cd71f269-7897-4746-9a77-c6bc730114fe, ff232009-b42f-4f71-a769-88a952701609, b8c6df33-b602-4d1c-9dda-e52dfeb41665 | A, B, C | 3 | 7156.5744 | 7028.915 | 7340.455 | 7156.4384 | 7031.447 | 7334.992 | 7160.001 | 7037.994 | 7337.18
| 149 | GSO_42 | GSO_42 | Low | Inspect downstream topology and line metadata before capacity use | br_049_21 | 36.121 | -79.8612 | 6000 | 6 | 5.7 | 1.9506 | 3.0111 | 4.0752 | 2024-01-21 04:00 | 34.2211 | 52.8266 | 71.4956 | [19 empty] | No usable entrance-line capacity | 7218.4544 | 7209.6573 | 7153.5211 | 7303.5955 | 7021.643 | 7364.274 | 7219.4343 | 7217.4051 | 7218.5237 | Unavailable |  | Insufficient voltage data | 5.7 | 1.6248 | 1.6248 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE15 | S_nSSEE15_12.47 | 6000.0 |  | MV | 1 | 1 | 162.5501 | 250.9263 | 339.604 | 3 | 0b1099db-07b7-4a46-831f-0ab42e837cdd, 119ef0a4-9572-4988-9343-96cacd641d11, 0e80773a-a8cc-45a5-8095-4dc9d8b00215 | A, B, C | 3 | 7154.6007 | 7021.643 | 7364.274 | 7153.5211 | 7031.66 | 7348.614 | 7154.4451 | 7023.651 | 7355.515
| 150 | GSO_104 | GSO_104 | Low | Inspect downstream topology and line metadata before capacity use | br_0104_21 | 36.0872 | -79.897 | 5714.3 | 5.7143 | 5.4286 | 1.917 | 2.8894 | 3.8614 | 2024-01-21 04:00 | 35.3125 | 53.2254 | 71.1312 | [19 empty] | No usable entrance-line capacity | 7217.7306 | 7209.3962 | 7153.0402 | 7299.415 | 7017.727 | 7352.66 | 7217.3862 | 7217.7692 | 7218.0364 | Unavailable |  | Insufficient voltage data | 5.4286 | 1.5672 | 1.5672 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE7 | S_nSSEE7_12.47 | 5714.3 |  | MV | 1 | 1 | 159.7475 | 240.7818 | 321.785 | 3 | dbaf906f-b53b-4b15-bd48-42442608214a, 0256f17b-1fde-4e5f-aa42-6a293aa27e64, 4922eba1-a72a-4e22-8a37-912d5f9ac46b | A, B, C | 3 | 7153.0402 | 7017.727 | 7346.738 | 7154.6534 | 7032.591 | 7352.66 | 7154.0648 | 7030.547 | 7352.079
| 151 | GSO_98 | GSO_98 | Low | Inspect downstream topology and line metadata before capacity use | br_099_21 | 36.0611 | -79.7715 | 7500 | 7.5 | 7.125 | 2.6962 | 4.1417 | 5.674 | 2024-01-21 04:00 | 37.841 | 58.1291 | 79.6355 | [19 empty] | No usable entrance-line capacity | 7210.3215 | 7206.2488 | 7155.6829 | 7289.4437 | 7027.973 | 7345.411 | 7215.959 | 7215.8771 | 7199.1284 | Unavailable |  | Insufficient voltage data | 7.125 | 1.451 | 1.451 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE6 | S_nSSEE6_12.47 | 7500.0 |  | MV | 1 | 1 | 224.6811 | 345.1416 | 472.836 | 3 | e19d273e-4ce0-462d-9501-16552f6df1a5, 74d4c75b-fdbd-4356-81ba-130cbea2e530, 43272e40-5062-4f3e-9a6d-0899fa207db5 | A, B, C | 3 | 7155.6829 | 7030.829 | 7338.381 | 7156.3002 | 7027.973 | 7345.411 | 7156.447 | 7029.363 | 7238.012
| 152 | GSO_66 | GSO_66 | Low | Inspect downstream topology and line metadata before capacity use | br_066_21 | 36.0801 | -79.7573 | 4285.7 | 4.2857 | 4.0714 | 1.3628 | 2.0344 | 2.6972 | 2024-01-21 04:00 | 33.4721 | 49.9676 | 66.2473 | [19 empty] | No usable entrance-line capacity | 7216.1698 | 7208.1637 | 7154.9842 | 7295.2833 | 7025.604 | 7359.498 | 7215.1492 | 7217.6025 | 7215.7577 | Unavailable |  | Insufficient voltage data | 4.0714 | 1.3742 | 1.3742 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 4285.7 |  | MV | 1 | 1 | 113.5657 | 169.5323 | 224.767 | 3 | aa212fd9-92d5-4c56-9a9e-3014ccc9a7ce, 0cbf5c43-696f-40b4-ab01-fd3dfd670388, 3f826b2c-284b-4880-a9f1-d5554c1e5213 | A, B, C | 3 | 7154.9842 | 7025.604 | 7345.18 | 7156.3804 | 7026.735 | 7359.498 | 7157.6622 | 7035.16 | 7342.752
| 153 | GSO_103 | GSO_103 | Low | Inspect downstream topology and line metadata before capacity use | br_0103_21 | 36.0872 | -79.897 | 5714.3 | 5.7143 | 5.4286 | 2.0181 | 3.1027 | 4.187 | 2024-01-21 04:00 | 37.1748 | 57.1556 | 77.1282 | [19 empty] | No usable entrance-line capacity | 7217.5838 | 7209.3302 | 7151.807 | 7300.5822 | 7021.579 | 7352.907 | 7216.7061 | 7218.8255 | 7217.2199 | Unavailable |  | Insufficient voltage data | 5.4286 | 1.2416 | 1.2416 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE7 | S_nSSEE7_12.47 | 5714.3 |  | MV | 1 | 1 | 168.1721 | 258.5616 | 348.914 | 3 | d5fd099c-84d4-4965-91b3-bbc0c68d61d1, d53e58ae-230d-449a-b78d-6b5cfa60f56b, a3539c00-7186-4684-93db-03123790cf12 | A, B, C | 3 | 7154.8283 | 7034.039 | 7340.187 | 7155.0603 | 7030.722 | 7352.907 | 7151.807 | 7021.579 | 7342.457
| 154 | GSO_67 | GSO_67 | Low | Inspect downstream topology and line metadata before capacity use | br_067_21 | 36.0801 | -79.7573 | 4285.7 | 4.2857 | 4.0714 | 1.4901 | 2.1371 | 2.8646 | 2024-01-21 04:00 | 36.5994 | 52.4895 | 70.3586 | [19 empty] | No usable entrance-line capacity | 7218.0193 | 7208.8353 | 7157.8504 | 7296.1246 | 7034.765 | 7375.064 | 7217.8583 | 7218.7983 | 7217.4013 | Unavailable |  | Insufficient voltage data | 4.0714 | 1.2068 | 1.2068 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 4285.7 |  | MV | 1 | 1 | 124.1763 | 178.0886 | 238.716 | 3 | fddc71cc-3766-4601-9ca7-c2caab3c7c4d, 5aed073b-49c0-4020-b105-f7e28cfd41ed, 4b3c48a3-9a69-47a9-b110-7d0b18cc7f06 | A, B, C | 3 | 7158.8614 | 7036.498 | 7375.064 | 7160.5464 | 7034.765 | 7362.045 | 7157.8504 | 7036.847 | 7346.959
| 155 | GSO_77 | GSO_77 | Low | Inspect downstream topology and line metadata before capacity use | br_077_21 | 36.0719 | -79.8252 | 6666.7 | 6.6667 | 6.3334 | 2.6294 | 3.9175 | 5.1594 | 2024-01-21 04:00 | 41.516 | 61.8547 | 81.4642 | [19 empty] | No usable entrance-line capacity | 7213.2397 | 7206.9723 | 7155.6683 | 7291.6793 | 7031.704 | 7355.039 | 7216.1447 | 7216.4596 | 7207.1148 | Unavailable |  | Insufficient voltage data | 6.3334 | 1.1739 | 1.1739 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV | 1 | 1 | 219.1131 | 326.4566 | 429.952 | 3 | 04933340-1f7e-4732-a170-31c687c8d71e, da253492-f9e5-4572-a892-8cf7206f5562, 55611621-48c6-40ab-afb0-d76e41a0d5de | A, B, C | 3 | 7156.1053 | 7036.922 | 7355.039 | 7155.6683 | 7031.704 | 7344.783 | 7157.2588 | 7034.795 | 7293.969
| 156 | GSO_27 | GSO_27 | Low | Inspect downstream topology and line metadata before capacity use | br_034_21 | 36.0604 | -79.8599 | 3750 | 3.75 | 3.5625 | 1.2479 | 1.7988 | 2.4046 | 2024-01-21 04:00 | 35.0281 | 50.4916 | 67.4968 | [19 empty] | No usable entrance-line capacity | 7217.3987 | 7208.487 | 7158.0667 | 7298.3846 | 7023.281 | 7409.065 | 7217.5732 | 7215.2699 | 7219.353 | Unavailable |  | Insufficient voltage data | 3.5625 | 1.1579 | 1.1579 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE12 | S_nSSEE12_12.47 | 3750.0 |  | MV | 1 | 1 | 103.9897 | 149.897 | 200.381 | 3 | 6fdd1896-ad74-48a8-9816-85aa01d652d1, d428eae8-d228-4f79-b9ea-91e3a88bb229, 9dbd0f33-80b1-4155-96b0-ea2e0658e691 | A, B, C | 3 | 7158.0667 | 7023.281 | 7347.271 | 7159.5011 | 7035.279 | 7338.875 | 7161.7148 | 7033.663 | 7409.065
| 157 | GSO_37 | GSO_37 | Low | Inspect downstream topology and line metadata before capacity use | br_044_21 | 36.0466 | -79.7995 | 6666.7 | 6.6667 | 6.3334 | 2.635 | 3.9761 | 5.2542 | 2024-01-20 07:05 | 41.605 | 62.7808 | 82.9599 | [19 empty] | No usable entrance-line capacity | 7216.4951 | 7208.4568 | 7155.4433 | 7294.393 | 7022.594 | 7364.044 | 7216.4271 | 7217.1565 | 7215.9018 | Unavailable |  | Insufficient voltage data | 6.3334 | 1.0792 | 1.0792 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE14 | S_nSSEE14_12.47 | 6666.7 |  | MV | 1 | 1 | 219.5832 | 331.3441 | 437.846 | 3 | e72c363a-7373-4a30-a872-329d650d7569, 547c5604-b333-47b9-83ad-6f6fa1e88927, 53f8a349-7f61-440d-ad82-54a7f6d15d3a | A, B, C | 3 | 7156.2827 | 7027.508 | 7333.263 | 7155.4433 | 7022.594 | 7364.044 | 7157.0619 | 7036.377 | 7353.082
| 158 | GSO_95 | GSO_95 | Low | Inspect downstream topology and line metadata before capacity use | br_095_21 | 36.0709 | -79.7962 | 4545.5 | 4.5455 | 4.3182 | 1.708 | 2.5471 | 3.4292 | 2024-01-18 04:00 | 39.553 | 58.9851 | 79.4112 | [19 empty] | No usable entrance-line capacity | 7217.2659 | 7208.5105 | 7156.1458 | 7298.9305 | 7030.294 | 7354.334 | 7215.8261 | 7217.3642 | 7218.6072 | Unavailable |  | Insufficient voltage data | 4.3182 | 0.88907 | 0.88907 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV | 1 | 1 | 142.3321 | 212.2589 | 285.763 | 3 | 859a9ae6-4d75-45f7-af3f-1d1c2c11b96f, ad766f3b-7d19-4707-8a90-38f818011b97, c6b6dfcf-55ed-45e7-9e6a-1ed25774a828 | A, B, C | 3 | 7156.1458 | 7030.294 | 7333.625 | 7158.3047 | 7036.175 | 7350.672 | 7158.7207 | 7035.639 | 7354.334
| 159 | GSO_43 | GSO_43 | Low | Inspect downstream topology and line metadata before capacity use | br_050_21 | 36.0168 | -79.7965 | 5454.5 | 5.4545 | 5.1818 | 2.2069 | 3.2839 | 4.3723 | 2024-01-21 04:00 | 42.5892 | 63.3747 | 84.3786 | [19 empty] | No usable entrance-line capacity | 7216.2435 | 7208.2735 | 7155.4098 | 7291.5136 | 7033.008 | 7346.268 | 7216.6695 | 7216.2767 | 7215.7842 | Unavailable |  | Insufficient voltage data | 5.1818 | 0.80947 | 0.80947 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV | 1 | 1 | 183.9062 | 273.6613 | 364.359 | 3 | 223df89f-b673-46b7-a74d-953aa3cadd02, d8ed1451-4cac-4c54-9238-07312269a3d5, d260c5dc-0f9a-4ff7-a347-cabc3421f531 | A, B, C | 3 | 7156.584 | 7034.626 | 7340.139 | 7158.2243 | 7042.783 | 7346.268 | 7155.4098 | 7033.008 | 7334.648
| 160 | GSO_160 | GSO_160 | Low | Inspect downstream topology and line metadata before capacity use | br_06_23 | 36.2604 | -79.5886 | 5714.3 | 5.7143 | 5.4286 | 2.3408 | 3.4652 | 4.6476 | 2024-01-21 04:00 | 43.1191 | 63.8332 | 85.6144 | [19 empty] | No usable entrance-line capacity | 7216.8784 | 7208.5343 | 7156.3383 | 7296.0655 | 7024.802 | 7351.791 | 7215.9917 | 7218.2373 | 7216.4062 | Unavailable |  | Insufficient voltage data | 5.4286 | 0.78094 | 0.78094 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 5714.3 |  | MV | 1 | 1 | 195.0631 | 288.77 | 387.304 | 3 | b9360429-edfb-4e59-a900-8a457dc83cba, c3e81296-2c1a-4ada-80c1-b847107d5cfb, 47f0ee8f-4288-4af4-b69a-10cebf43b645 | A, B, C | 3 | 7156.3383 | 7024.802 | 7334.072 | 7158.2601 | 7036.423 | 7349.88 | 7157.1128 | 7027.858 | 7351.791
| 161 | GSO_61 | GSO_61 | Low | Inspect downstream topology and line metadata before capacity use | br_012_21 | 36.0872 | -79.8446 | 6122.4 | 6.1224 | 5.8163 | 2.5424 | 3.922 | 5.2018 | 2024-01-20 09:00 | 43.7119 | 67.4314 | 89.4355 | [19 empty] | No usable entrance-line capacity | 7215.4787 | 7208.0417 | 7155.3458 | 7289.509 | 7027.948 | 7346.349 | 7214.9712 | 7215.7097 | 7215.7552 | Unavailable |  | Insufficient voltage data | 5.8163 | 0.61446 | 0.61446 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 6122.4 |  | MV | 1 | 1 | 211.8673 | 326.8333 | 433.485 | 3 | bdb558af-9d90-4dcd-870e-28a86925b8cc, 192ef0e0-59f5-4932-a625-7e967573ec09, 69c0c6b0-aa07-4cdc-9789-b51b223584c4 | A, B, C | 3 | 7155.7443 | 7029.209 | 7333.784 | 7155.564 | 7028.811 | 7346.349 | 7155.3458 | 7027.948 | 7337.657
| 162 | GSO_4 | GSO_4 | Low | Inspect downstream topology and line metadata before capacity use | br_04_21 | 36.0852 | -79.8827 | 5714.3 | 5.7143 | 5.4286 | 2.4126 | 3.721 | 5.0234 | 2024-01-21 04:00 | 44.4431 | 68.5439 | 92.5357 | [19 empty] | No usable entrance-line capacity | 7215.3189 | 7207.9905 | 7153.8733 | 7291.099 | 7020.302 | 7338.272 | 7214.2919 | 7216.5611 | 7215.1035 | Unavailable |  | Insufficient voltage data | 5.4286 | 0.4052 | 0.4052 |  |  | OK | OK | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 5714.3 |  | MV | 1 | 1 | 201.0527 | 310.0799 | 418.615 | 3 | eda55f14-fedc-4eb6-a389-a51a43231405, 67c44f52-c49c-4993-940f-90408b4b9ae5, 1da22d5c-e6b3-4228-b327-ddf40f1f21b6 | A, B, C | 3 | 7155.628 | 7032.587 | 7336.578 | 7156.2722 | 7028.18 | 7338.272 | 7153.8733 | 7020.302 | 7334.194

## Validated_Shortlist
ValidatedRank | ProvisionalRank | FeederID | BreakerElementID | EntranceCapacityConfidence | BreakerCapacityMW | PeakLoadMW | EntranceThermalCapacityMW | ProvisionalEntranceHeadroomMW | ValidatedEntranceHeadroomMW | PrimaryEntranceLineID | PrimaryEntranceLineMVA | EntranceLineCount | EntranceLineValidationStatus | SCADAVoltageValidationStatus | Latitude | Longitude | RecommendedNextStep
1 | 2 | GSO_122 | br_02_22 | High | 14.25 | 0.03276 | 13.5424 | 13.5096 | 13.5096 | line_5852_22 | 14.2551 | 1 | Single entrance line plausibly supports breaker rating | Strong nominal-voltage agreement | 36.083 | -79.9727 | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis
2 | 3 | GSO_124 | br_04_22 | High | 14.25 | 0.13387 | 13.5424 | 13.4085 | 13.4085 | line_6716_22 | 14.2551 | 1 | Single entrance line plausibly supports breaker rating | Strong nominal-voltage agreement | 36.083 | -79.9727 | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis
3 | 4 | GSO_123 | br_03_22 | High | 14.25 | 0.36464 | 13.5424 | 13.1777 | 13.1777 | line_6019_22 | 14.2551 | 1 | Single entrance line plausibly supports breaker rating | Strong nominal-voltage agreement | 36.083 | -79.9727 | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis
4 | 5 | GSO_144 | br_024_22 | High | 11.4 | 0.13286 | 11.4 | 11.2671 | 11.2671 | line_5978_22 | 12.9592 | 1 | Single entrance line plausibly supports breaker rating | Strong nominal-voltage agreement | 36.046 | -79.947 | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis
5 | 6 | GSO_141 | br_021_22 | High | 11.4 | 0.37996 | 11.4 | 11.02 | 11.02 | line_4565_22 | 14.2551 | 1 | Single entrance line plausibly supports breaker rating | Strong nominal-voltage agreement | 36.0459 | -79.947 | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis
6 | 10 | GSO_127 | br_07_22 | High | 9.5 | 0.025212 | 9.5 | 9.4748 | 9.4748 | line_6871_22 | 14.2551 | 1 | Single entrance line plausibly supports breaker rating | Strong nominal-voltage agreement | 36.0974 | -79.9235 | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis
7 | 11 | GSO_73 | br_073_21 | High | 9.5 | 0.097896 | 9.5 | 9.4021 | 9.4021 | line_129349_21 | 12.9592 | 1 | Single entrance line plausibly supports breaker rating | Strong nominal-voltage agreement | 36.0825 | -79.7708 | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis
8 | 12 | GSO_128 | br_08_22 | High | 9.5 | 0.15013 | 9.5 | 9.3499 | 9.3499 | line_6872_22 | 14.2551 | 1 | Single entrance line plausibly supports breaker rating | Strong nominal-voltage agreement | 36.0974 | -79.9234 | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis
9 | 13 | GSO_126 | br_06_22 | High | 9.5 | 0.24218 | 9.5 | 9.2578 | 9.2578 | line_6387_22 | 14.2551 | 1 | Single entrance line plausibly supports breaker rating | Strong nominal-voltage agreement | 36.0974 | -79.9235 | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis
10 | 14 | GSO_55 | br_062_21 | High | 9.5 | 0.26848 | 9.5 | 9.2315 | 9.2315 | line_128388_21 | 12.9592 | 1 | Single entrance line plausibly supports breaker rating | Strong nominal-voltage agreement | 36.0131 | -79.8489 | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis
11 | 16 | GSO_119 | br_0119_21 | High | 9.5 | 0.33516 | 9.5 | 9.1648 | 9.1648 | line_132380_21 | 14.2551 | 1 | Single entrance line plausibly supports breaker rating | Strong nominal-voltage agreement | 36.0426 | -79.8533 | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis
12 | 23 | GSO_131 | br_011_22 | High | 8.1428 | 0.073452 | 8.1428 | 8.0694 | 8.0694 | line_4538_22 | 14.2551 | 1 | Single entrance line plausibly supports breaker rating | Strong nominal-voltage agreement | 36.0811 | -79.94 | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis
13 | 25 | GSO_129 | br_09_22 | High | 8.1428 | 0.26306 | 8.1428 | 7.8798 | 7.8798 | line_3574_22 | 14.2551 | 1 | Single entrance line plausibly supports breaker rating | Strong nominal-voltage agreement | 36.0811 | -79.94 | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis
14 | 29 | GSO_132 | br_012_22 | High | 8.1428 | 0.45876 | 8.1428 | 7.6841 | 7.6841 | line_4993_22 | 14.2551 | 1 | Single entrance line plausibly supports breaker rating | Strong nominal-voltage agreement | 36.0811 | -79.94 | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis
15 | 34 | GSO_31 | br_038_21 | High | 7.125 | 0.036228 | 7.125 | 7.0888 | 7.0888 | line_132463_21 | 14.2551 | 1 | Single entrance line plausibly supports breaker rating | Strong nominal-voltage agreement | 36.1038 | -79.7639 | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis

## Provisional_Shortlist
ValidatedRank | ProvisionalRank | FeederID | BreakerElementID | EntranceCapacityConfidence | BreakerCapacityMW | PeakLoadMW | EntranceThermalCapacityMW | ProvisionalEntranceHeadroomMW | ValidatedEntranceHeadroomMW | PrimaryEntranceLineID | PrimaryEntranceLineMVA | EntranceLineCount | EntranceLineValidationStatus | SCADAVoltageValidationStatus | Latitude | Longitude | RecommendedNextStep
| 1 | GSO_121 | br_01_22 | Low | 14.25 | 0.38162 | 14.25 | 13.8684 |  |  |  |  | No usable entrance-line capacity | Insufficient voltage data | 36.083 | -79.9727 | Inspect downstream topology and line metadata before capacity use
1 | 2 | GSO_122 | br_02_22 | High | 14.25 | 0.03276 | 13.5424 | 13.5096 | 13.5096 | line_5852_22 | 14.2551 | 1 | Single entrance line plausibly supports breaker rating | Strong nominal-voltage agreement | 36.083 | -79.9727 | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis
2 | 3 | GSO_124 | br_04_22 | High | 14.25 | 0.13387 | 13.5424 | 13.4085 | 13.4085 | line_6716_22 | 14.2551 | 1 | Single entrance line plausibly supports breaker rating | Strong nominal-voltage agreement | 36.083 | -79.9727 | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis
3 | 4 | GSO_123 | br_03_22 | High | 14.25 | 0.36464 | 13.5424 | 13.1777 | 13.1777 | line_6019_22 | 14.2551 | 1 | Single entrance line plausibly supports breaker rating | Strong nominal-voltage agreement | 36.083 | -79.9727 | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis
4 | 5 | GSO_144 | br_024_22 | High | 11.4 | 0.13286 | 11.4 | 11.2671 | 11.2671 | line_5978_22 | 12.9592 | 1 | Single entrance line plausibly supports breaker rating | Strong nominal-voltage agreement | 36.046 | -79.947 | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis
5 | 6 | GSO_141 | br_021_22 | High | 11.4 | 0.37996 | 11.4 | 11.02 | 11.02 | line_4565_22 | 14.2551 | 1 | Single entrance line plausibly supports breaker rating | Strong nominal-voltage agreement | 36.0459 | -79.947 | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis
| 7 | GSO_145 | br_025_22 | Low | 11.4 | 0.73442 | 11.4 | 10.6656 |  |  |  |  | No usable entrance-line capacity | Insufficient voltage data | 36.046 | -79.947 | Inspect downstream topology and line metadata before capacity use
| 8 | GSO_142 | br_022_22 | Low | 11.4 | 0.79259 | 11.4 | 10.6074 |  |  |  |  | No usable entrance-line capacity | Insufficient voltage data | 36.0459 | -79.947 | Inspect downstream topology and line metadata before capacity use
| 9 | GSO_18 | br_025_21 | Low | 12.6666 | 2.2897 | 12.6666 | 10.3769 |  |  |  |  | No usable entrance-line capacity | Insufficient voltage data | 36.0264 | -79.8286 | Inspect downstream topology and line metadata before capacity use
6 | 10 | GSO_127 | br_07_22 | High | 9.5 | 0.025212 | 9.5 | 9.4748 | 9.4748 | line_6871_22 | 14.2551 | 1 | Single entrance line plausibly supports breaker rating | Strong nominal-voltage agreement | 36.0974 | -79.9235 | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis
7 | 11 | GSO_73 | br_073_21 | High | 9.5 | 0.097896 | 9.5 | 9.4021 | 9.4021 | line_129349_21 | 12.9592 | 1 | Single entrance line plausibly supports breaker rating | Strong nominal-voltage agreement | 36.0825 | -79.7708 | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis
8 | 12 | GSO_128 | br_08_22 | High | 9.5 | 0.15013 | 9.5 | 9.3499 | 9.3499 | line_6872_22 | 14.2551 | 1 | Single entrance line plausibly supports breaker rating | Strong nominal-voltage agreement | 36.0974 | -79.9234 | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis
9 | 13 | GSO_126 | br_06_22 | High | 9.5 | 0.24218 | 9.5 | 9.2578 | 9.2578 | line_6387_22 | 14.2551 | 1 | Single entrance line plausibly supports breaker rating | Strong nominal-voltage agreement | 36.0974 | -79.9235 | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis
10 | 14 | GSO_55 | br_062_21 | High | 9.5 | 0.26848 | 9.5 | 9.2315 | 9.2315 | line_128388_21 | 12.9592 | 1 | Single entrance line plausibly supports breaker rating | Strong nominal-voltage agreement | 36.0131 | -79.8489 | Carry into detailed path-specific line/transformer bottleneck and hosting-capacity analysis
| 15 | GSO_125 | br_05_22 | Low | 9.5 | 0.3241 | 9.5 | 9.1759 |  |  |  |  | No usable entrance-line capacity | Insufficient voltage data | 36.0974 | -79.9235 | Inspect downstream topology and line metadata before capacity use

## Selected_Breakers
grid_id | BreakerElementID | ElementType | ElementCustomerType | BreakerPhases | IsProducer | IsConsumer | IsSwitchable | SwitchIsOpen | PowerFlowDirection | UpstreamElementID | Terminal1CN | Terminal2CN | RawBreakerRatingKVA | RawBreakerRatingA | RawBreakerVoltageLevel | Latitude | Longitude | BreakerRatingKVA | BreakerRatingMVA | BreakerCapacityMW | BreakerCount | BreakerCandidateRank
GSO_1 | br_01_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 5714.3 |  | MV | 36.0852 | -79.8827 | 5714.3 | 5.7143 | 5.4286 | 1 | 1
GSO_10 | br_015_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE10 | S_nSSEE10_12.47 | 5555.6 |  | MV | 36.1003 | -79.8075 | 5555.6 | 5.5556 | 5.2778 | 1 | 1
GSO_100 | br_097_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE6 | S_nSSEE6_12.47 | 7500.0 |  | MV | 36.0611 | -79.7715 | 7500 | 7.5 | 7.125 | 1 | 1
GSO_101 | br_0101_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE7 | S_nSSEE7_12.47 | 5714.3 |  | MV | 36.0872 | -79.897 | 5714.3 | 5.7143 | 5.4286 | 1 | 1
GSO_102 | br_0102_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE7 | S_nSSEE7_12.47 | 5714.3 |  | MV | 36.0872 | -79.897 | 5714.3 | 5.7143 | 5.4286 | 1 | 1
GSO_103 | br_0103_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE7 | S_nSSEE7_12.47 | 5714.3 |  | MV | 36.0872 | -79.897 | 5714.3 | 5.7143 | 5.4286 | 1 | 1
GSO_104 | br_0104_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE7 | S_nSSEE7_12.47 | 5714.3 |  | MV | 36.0872 | -79.897 | 5714.3 | 5.7143 | 5.4286 | 1 | 1
GSO_105 | br_0105_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE7 | S_nSSEE7_12.47 | 5714.3 |  | MV | 36.0872 | -79.897 | 5714.3 | 5.7143 | 5.4286 | 1 | 1
GSO_106 | br_0106_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE7 | S_nSSEE7_12.47 | 5714.3 |  | MV | 36.0872 | -79.897 | 5714.3 | 5.7143 | 5.4286 | 1 | 1
GSO_107 | br_0107_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE7 | S_nSSEE7_12.47 | 5714.3 |  | MV | 36.0872 | -79.897 | 5714.3 | 5.7143 | 5.4286 | 1 | 1
GSO_108 | br_0108_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE8 | S_nSSEE8_12.47 | 7142.9 |  | MV | 36.0543 | -79.8942 | 7142.9 | 7.1429 | 6.7858 | 1 | 1
GSO_109 | br_0109_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE8 | S_nSSEE8_12.47 | 7142.9 |  | MV | 36.0543 | -79.8942 | 7142.9 | 7.1429 | 6.7858 | 1 | 1
GSO_11 | br_016_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE10 | S_nSSEE10_12.47 | 5555.6 |  | MV | 36.1003 | -79.8075 | 5555.6 | 5.5556 | 5.2778 | 1 | 1
GSO_110 | br_0110_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE8 | S_nSSEE8_12.47 | 7142.9 |  | MV | 36.0543 | -79.8942 | 7142.9 | 7.1429 | 6.7858 | 1 | 1
GSO_111 | br_0111_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE8 | S_nSSEE8_12.47 | 7142.9 |  | MV | 36.0543 | -79.8942 | 7142.9 | 7.1429 | 6.7858 | 1 | 1
GSO_112 | br_0112_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE8 | S_nSSEE8_12.47 | 7142.9 |  | MV | 36.0543 | -79.8942 | 7142.9 | 7.1429 | 6.7858 | 1 | 1
GSO_113 | br_0113_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE8 | S_nSSEE8_12.47 | 7142.9 |  | MV | 36.0543 | -79.8942 | 7142.9 | 7.1429 | 6.7858 | 1 | 1
GSO_114 | br_0114_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE8 | S_nSSEE8_12.47 | 7142.9 |  | MV | 36.0543 | -79.8942 | 7142.9 | 7.1429 | 6.7858 | 1 | 1
GSO_115 | br_0115_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE9 | S_nSSEE9_12.47 | 10000.0 |  | MV | 36.0426 | -79.8533 | 10000 | 10 | 9.5 | 1 | 1
GSO_116 | br_0116_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE9 | S_nSSEE9_12.47 | 10000.0 |  | MV | 36.0426 | -79.8533 | 10000 | 10 | 9.5 | 1 | 1
GSO_117 | br_0117_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE9 | S_nSSEE9_12.47 | 10000.0 |  | MV | 36.0426 | -79.8533 | 10000 | 10 | 9.5 | 1 | 1
GSO_118 | br_0118_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE9 | S_nSSEE9_12.47 | 10000.0 |  | MV | 36.0426 | -79.8533 | 10000 | 10 | 9.5 | 1 | 1
GSO_119 | br_0119_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE9 | S_nSSEE9_12.47 | 10000.0 |  | MV | 36.0426 | -79.8533 | 10000 | 10 | 9.5 | 1 | 1
GSO_12 | br_017_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE10 | S_nSSEE10_12.47 | 5555.6 |  | MV | 36.1003 | -79.8075 | 5555.6 | 5.5556 | 5.2778 | 1 | 1
GSO_121 | br_01_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 15000.0 |  | MV | 36.083 | -79.9727 | 15000 | 15 | 14.25 | 1 | 1
GSO_122 | br_02_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 15000.0 |  | MV | 36.083 | -79.9727 | 15000 | 15 | 14.25 | 1 | 1
GSO_123 | br_03_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 15000.0 |  | MV | 36.083 | -79.9727 | 15000 | 15 | 14.25 | 1 | 1
GSO_124 | br_04_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 15000.0 |  | MV | 36.083 | -79.9727 | 15000 | 15 | 14.25 | 1 | 1
GSO_125 | br_05_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 10000.0 |  | MV | 36.0974 | -79.9235 | 10000 | 10 | 9.5 | 1 | 1
GSO_126 | br_06_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 10000.0 |  | MV | 36.0974 | -79.9235 | 10000 | 10 | 9.5 | 1 | 1
GSO_127 | br_07_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 10000.0 |  | MV | 36.0974 | -79.9235 | 10000 | 10 | 9.5 | 1 | 1
GSO_128 | br_08_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 10000.0 |  | MV | 36.0974 | -79.9234 | 10000 | 10 | 9.5 | 1 | 1
GSO_129 | br_09_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 8571.4 |  | MV | 36.0811 | -79.94 | 8571.4 | 8.5714 | 8.1428 | 1 | 1
GSO_13 | br_018_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE10 | S_nSSEE10_12.47 | 5555.6 |  | MV | 36.1003 | -79.8075 | 5555.6 | 5.5556 | 5.2778 | 1 | 1
GSO_130 | br_010_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 8571.4 |  | MV | 36.0811 | -79.94 | 8571.4 | 8.5714 | 8.1428 | 1 | 1
GSO_131 | br_011_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 8571.4 |  | MV | 36.0811 | -79.94 | 8571.4 | 8.5714 | 8.1428 | 1 | 1
GSO_132 | br_012_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 8571.4 |  | MV | 36.0811 | -79.94 | 8571.4 | 8.5714 | 8.1428 | 1 | 1
GSO_133 | br_013_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 8571.4 |  | MV | 36.0811 | -79.94 | 8571.4 | 8.5714 | 8.1428 | 1 | 1
GSO_134 | br_014_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 8571.4 |  | MV | 36.0811 | -79.94 | 8571.4 | 8.5714 | 8.1428 | 1 | 1
GSO_135 | br_015_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 8571.4 |  | MV | 36.0811 | -79.94 | 8571.4 | 8.5714 | 8.1428 | 1 | 1
GSO_136 | br_016_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE3 | S_nSSEE3_12.47 | 6000.0 |  | MV | 36.0705 | -79.9556 | 6000 | 6 | 5.7 | 1 | 1
GSO_137 | br_017_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE3 | S_nSSEE3_12.47 | 6000.0 |  | MV | 36.0705 | -79.9557 | 6000 | 6 | 5.7 | 1 | 1
GSO_138 | br_018_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE3 | S_nSSEE3_12.47 | 6000.0 |  | MV | 36.0705 | -79.9556 | 6000 | 6 | 5.7 | 1 | 1
GSO_139 | br_019_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE3 | S_nSSEE3_12.47 | 6000.0 |  | MV | 36.0705 | -79.9557 | 6000 | 6 | 5.7 | 1 | 1
GSO_14 | br_019_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE10 | S_nSSEE10_12.47 | 5555.6 |  | MV | 36.1003 | -79.8075 | 5555.6 | 5.5556 | 5.2778 | 1 | 1
GSO_140 | br_020_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE3 | S_nSSEE3_12.47 | 6000.0 |  | MV | 36.0705 | -79.9556 | 6000 | 6 | 5.7 | 1 | 1
GSO_141 | br_021_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 12000.0 |  | MV | 36.0459 | -79.947 | 12000 | 12 | 11.4 | 1 | 1
GSO_142 | br_022_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 12000.0 |  | MV | 36.0459 | -79.947 | 12000 | 12 | 11.4 | 1 | 1
GSO_143 | br_023_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 12000.0 |  | MV | 36.0459 | -79.947 | 12000 | 12 | 11.4 | 1 | 1
GSO_144 | br_024_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 12000.0 |  | MV | 36.046 | -79.947 | 12000 | 12 | 11.4 | 1 | 1
GSO_145 | br_025_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 12000.0 |  | MV | 36.046 | -79.947 | 12000 | 12 | 11.4 | 1 | 1
GSO_146 | br_026_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 7500.0 |  | MV | 36.114 | -79.9604 | 7500 | 7.5 | 7.125 | 1 | 1
GSO_147 | br_027_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 7500.0 |  | MV | 36.114 | -79.9604 | 7500 | 7.5 | 7.125 | 1 | 1
GSO_148 | br_028_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 7500.0 |  | MV | 36.114 | -79.9604 | 7500 | 7.5 | 7.125 | 1 | 1
GSO_149 | br_029_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 7500.0 |  | MV | 36.114 | -79.9604 | 7500 | 7.5 | 7.125 | 1 | 1
GSO_15 | br_020_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE10 | S_nSSEE10_12.47 | 5555.6 |  | MV | 36.1003 | -79.8075 | 5555.6 | 5.5556 | 5.2778 | 1 | 1
GSO_150 | br_030_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE6 | S_nSSEE6_12.47 | 6000.0 |  | MV | 36.0823 | -79.9238 | 6000 | 6 | 5.7 | 1 | 1
GSO_151 | br_031_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE6 | S_nSSEE6_12.47 | 6000.0 |  | MV | 36.0823 | -79.9238 | 6000 | 6 | 5.7 | 1 | 1
GSO_152 | br_032_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE6 | S_nSSEE6_12.47 | 6000.0 |  | MV | 36.0823 | -79.9238 | 6000 | 6 | 5.7 | 1 | 1
GSO_153 | br_033_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE6 | S_nSSEE6_12.47 | 6000.0 |  | MV | 36.0823 | -79.9238 | 6000 | 6 | 5.7 | 1 | 1
GSO_154 | br_034_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE6 | S_nSSEE6_12.47 | 6000.0 |  | MV | 36.0823 | -79.9238 | 6000 | 6 | 5.7 | 1 | 1
GSO_155 | br_01_23 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 7500.0 |  | MV | 36.1928 | -79.6069 | 7500 | 7.5 | 7.125 | 1 | 1
GSO_156 | br_02_23 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 7500.0 |  | MV | 36.1929 | -79.6068 | 7500 | 7.5 | 7.125 | 1 | 1
GSO_157 | br_03_23 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 7500.0 |  | MV | 36.1929 | -79.6068 | 7500 | 7.5 | 7.125 | 1 | 1
GSO_158 | br_04_23 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 7500.0 |  | MV | 36.1929 | -79.6068 | 7500 | 7.5 | 7.125 | 1 | 1
GSO_159 | br_05_23 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 5714.3 |  | MV | 36.2604 | -79.5886 | 5714.3 | 5.7143 | 5.4286 | 1 | 1
GSO_16 | br_021_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE10 | S_nSSEE10_12.47 | 5555.6 |  | MV | 36.1003 | -79.8075 | 5555.6 | 5.5556 | 5.2778 | 1 | 1
GSO_160 | br_06_23 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 5714.3 |  | MV | 36.2604 | -79.5886 | 5714.3 | 5.7143 | 5.4286 | 1 | 1
GSO_161 | br_07_23 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 5714.3 |  | MV | 36.2604 | -79.5886 | 5714.3 | 5.7143 | 5.4286 | 1 | 1
GSO_162 | br_08_23 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 8000.0 |  | MV | 36.1644 | -79.7079 | 8000 | 8 | 7.6 | 1 | 1
GSO_163 | br_09_23 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 8000.0 |  | MV | 36.1644 | -79.708 | 8000 | 8 | 7.6 | 1 | 1
GSO_17 | br_024_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE11 | S_nSSEE11_12.47 | 13333.3 |  | MV | 36.0264 | -79.8286 | 13333.3 | 13.3333 | 12.6666 | 1 | 1
GSO_18 | br_025_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE11 | S_nSSEE11_12.47 | 13333.3 |  | MV | 36.0264 | -79.8286 | 13333.3 | 13.3333 | 12.6666 | 1 | 1
GSO_19 | br_026_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE11 | S_nSSEE11_12.47 | 13333.3 |  | MV | 36.0264 | -79.8286 | 13333.3 | 13.3333 | 12.6666 | 1 | 1
GSO_2 | br_02_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 5714.3 |  | MV | 36.0852 | -79.8827 | 5714.3 | 5.7143 | 5.4286 | 1 | 1
GSO_20 | br_027_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE12 | S_nSSEE12_12.47 | 3750.0 |  | MV | 36.0604 | -79.8599 | 3750 | 3.75 | 3.5625 | 1 | 1
GSO_21 | br_028_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE12 | S_nSSEE12_12.47 | 3750.0 |  | MV | 36.0604 | -79.8599 | 3750 | 3.75 | 3.5625 | 1 | 1
GSO_22 | br_029_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE12 | S_nSSEE12_12.47 | 3750.0 |  | MV | 36.0604 | -79.8599 | 3750 | 3.75 | 3.5625 | 1 | 1
GSO_23 | br_030_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE12 | S_nSSEE12_12.47 | 3750.0 |  | MV | 36.0604 | -79.8599 | 3750 | 3.75 | 3.5625 | 1 | 1
GSO_24 | br_031_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE12 | S_nSSEE12_12.47 | 3750.0 |  | MV | 36.0603 | -79.8599 | 3750 | 3.75 | 3.5625 | 1 | 1
GSO_25 | br_032_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE12 | S_nSSEE12_12.47 | 3750.0 |  | MV | 36.0603 | -79.8599 | 3750 | 3.75 | 3.5625 | 1 | 1
GSO_26 | br_033_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE12 | S_nSSEE12_12.47 | 3750.0 |  | MV | 36.0603 | -79.8599 | 3750 | 3.75 | 3.5625 | 1 | 1
GSO_27 | br_034_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE12 | S_nSSEE12_12.47 | 3750.0 |  | MV | 36.0604 | -79.8599 | 3750 | 3.75 | 3.5625 | 1 | 1
GSO_28 | br_035_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE13 | S_nSSEE13_12.47 | 7500.0 |  | MV | 36.1038 | -79.7639 | 7500 | 7.5 | 7.125 | 1 | 1
GSO_29 | br_036_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE13 | S_nSSEE13_12.47 | 7500.0 |  | MV | 36.1038 | -79.7639 | 7500 | 7.5 | 7.125 | 1 | 1
GSO_3 | br_03_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 5714.3 |  | MV | 36.0852 | -79.8826 | 5714.3 | 5.7143 | 5.4286 | 1 | 1
GSO_30 | br_037_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE13 | S_nSSEE13_12.47 | 7500.0 |  | MV | 36.1038 | -79.7639 | 7500 | 7.5 | 7.125 | 1 | 1
GSO_31 | br_038_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE13 | S_nSSEE13_12.47 | 7500.0 |  | MV | 36.1038 | -79.7639 | 7500 | 7.5 | 7.125 | 1 | 1
GSO_32 | br_039_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE14 | S_nSSEE14_12.47 | 6666.7 |  | MV | 36.0466 | -79.7995 | 6666.7 | 6.6667 | 6.3334 | 1 | 1
GSO_33 | br_040_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE14 | S_nSSEE14_12.47 | 6666.7 |  | MV | 36.0466 | -79.7995 | 6666.7 | 6.6667 | 6.3334 | 1 | 1
GSO_34 | br_041_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE14 | S_nSSEE14_12.47 | 6666.7 |  | MV | 36.0466 | -79.7995 | 6666.7 | 6.6667 | 6.3334 | 1 | 1
GSO_35 | br_042_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE14 | S_nSSEE14_12.47 | 6666.7 |  | MV | 36.0466 | -79.7995 | 6666.7 | 6.6667 | 6.3334 | 1 | 1
GSO_36 | br_043_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE14 | S_nSSEE14_12.47 | 6666.7 |  | MV | 36.0466 | -79.7995 | 6666.7 | 6.6667 | 6.3334 | 1 | 1
GSO_37 | br_044_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE14 | S_nSSEE14_12.47 | 6666.7 |  | MV | 36.0466 | -79.7995 | 6666.7 | 6.6667 | 6.3334 | 1 | 1
GSO_38 | br_045_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE15 | S_nSSEE15_12.47 | 6000.0 |  | MV | 36.121 | -79.8612 | 6000 | 6 | 5.7 | 1 | 1
GSO_39 | br_046_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE15 | S_nSSEE15_12.47 | 6000.0 |  | MV | 36.121 | -79.8612 | 6000 | 6 | 5.7 | 1 | 1
GSO_4 | br_04_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 5714.3 |  | MV | 36.0852 | -79.8827 | 5714.3 | 5.7143 | 5.4286 | 1 | 1
GSO_40 | br_047_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE15 | S_nSSEE15_12.47 | 6000.0 |  | MV | 36.121 | -79.8612 | 6000 | 6 | 5.7 | 1 | 1
GSO_41 | br_048_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE15 | S_nSSEE15_12.47 | 6000.0 |  | MV | 36.121 | -79.8612 | 6000 | 6 | 5.7 | 1 | 1
GSO_42 | br_049_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE15 | S_nSSEE15_12.47 | 6000.0 |  | MV | 36.121 | -79.8612 | 6000 | 6 | 5.7 | 1 | 1
GSO_43 | br_050_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV | 36.0168 | -79.7965 | 5454.5 | 5.4545 | 5.1818 | 1 | 1
GSO_44 | br_051_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV | 36.0168 | -79.7965 | 5454.5 | 5.4545 | 5.1818 | 1 | 1
GSO_45 | br_052_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV | 36.0168 | -79.7965 | 5454.5 | 5.4545 | 5.1818 | 1 | 1
GSO_46 | br_053_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV | 36.0168 | -79.7965 | 5454.5 | 5.4545 | 5.1818 | 1 | 1
GSO_47 | br_054_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV | 36.0168 | -79.7965 | 5454.5 | 5.4545 | 5.1818 | 1 | 1
GSO_48 | br_055_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV | 36.0168 | -79.7965 | 5454.5 | 5.4545 | 5.1818 | 1 | 1
GSO_49 | br_056_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV | 36.0168 | -79.7965 | 5454.5 | 5.4545 | 5.1818 | 1 | 1
GSO_5 | br_05_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 5714.3 |  | MV | 36.0852 | -79.8827 | 5714.3 | 5.7143 | 5.4286 | 1 | 1
GSO_50 | br_057_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV | 36.0168 | -79.7965 | 5454.5 | 5.4545 | 5.1818 | 1 | 1
GSO_51 | br_058_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV | 36.0168 | -79.7965 | 5454.5 | 5.4545 | 5.1818 | 1 | 1
GSO_52 | br_059_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV | 36.0168 | -79.7965 | 5454.5 | 5.4545 | 5.1818 | 1 | 1
GSO_53 | br_060_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV | 36.0168 | -79.7965 | 5454.5 | 5.4545 | 5.1818 | 1 | 1
GSO_54 | br_061_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE17 | S_nSSEE17_12.47 | 10000.0 |  | MV | 36.0131 | -79.8489 | 10000 | 10 | 9.5 | 1 | 1
GSO_55 | br_062_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE17 | S_nSSEE17_12.47 | 10000.0 |  | MV | 36.0131 | -79.8489 | 10000 | 10 | 9.5 | 1 | 1
GSO_56 | br_063_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE17 | S_nSSEE17_12.47 | 10000.0 |  | MV | 36.0131 | -79.8489 | 10000 | 10 | 9.5 | 1 | 1
GSO_57 | br_08_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 6122.4 |  | MV | 36.0872 | -79.8446 | 6122.4 | 6.1224 | 5.8163 | 1 | 1
GSO_58 | br_09_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 6122.4 |  | MV | 36.0872 | -79.8446 | 6122.4 | 6.1224 | 5.8163 | 1 | 1
GSO_59 | br_010_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 6122.4 |  | MV | 36.0873 | -79.8446 | 6122.4 | 6.1224 | 5.8163 | 1 | 1
GSO_6 | br_06_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 5714.3 |  | MV | 36.0852 | -79.8827 | 5714.3 | 5.7143 | 5.4286 | 1 | 1
GSO_60 | br_011_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 6122.4 |  | MV | 36.0873 | -79.8446 | 6122.4 | 6.1224 | 5.8163 | 1 | 1
GSO_61 | br_012_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 6122.4 |  | MV | 36.0872 | -79.8446 | 6122.4 | 6.1224 | 5.8163 | 1 | 1
GSO_62 | br_013_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 6122.4 |  | MV | 36.0873 | -79.8446 | 6122.4 | 6.1224 | 5.8163 | 1 | 1
GSO_63 | br_014_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 6122.4 |  | MV | 36.0873 | -79.8446 | 6122.4 | 6.1224 | 5.8163 | 1 | 1
GSO_64 | br_064_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 4285.7 |  | MV | 36.0801 | -79.7573 | 4285.7 | 4.2857 | 4.0714 | 1 | 1
GSO_65 | br_065_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 4285.7 |  | MV | 36.0801 | -79.7573 | 4285.7 | 4.2857 | 4.0714 | 1 | 1
GSO_66 | br_066_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 4285.7 |  | MV | 36.0801 | -79.7573 | 4285.7 | 4.2857 | 4.0714 | 1 | 1
GSO_67 | br_067_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 4285.7 |  | MV | 36.0801 | -79.7573 | 4285.7 | 4.2857 | 4.0714 | 1 | 1
GSO_68 | br_068_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 4285.7 |  | MV | 36.0801 | -79.7573 | 4285.7 | 4.2857 | 4.0714 | 1 | 1
GSO_69 | br_069_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 4285.7 |  | MV | 36.0801 | -79.7573 | 4285.7 | 4.2857 | 4.0714 | 1 | 1
GSO_7 | br_07_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 5714.3 |  | MV | 36.0852 | -79.8826 | 5714.3 | 5.7143 | 5.4286 | 1 | 1
GSO_70 | br_070_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 4285.7 |  | MV | 36.0801 | -79.7573 | 4285.7 | 4.2857 | 4.0714 | 1 | 1
GSO_71 | br_071_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE3 | S_nSSEE3_12.47 | 10000.0 |  | MV | 36.0825 | -79.7708 | 10000 | 10 | 9.5 | 1 | 1
GSO_72 | br_072_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE3 | S_nSSEE3_12.47 | 10000.0 |  | MV | 36.0825 | -79.7708 | 10000 | 10 | 9.5 | 1 | 1
GSO_73 | br_073_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE3 | S_nSSEE3_12.47 | 10000.0 |  | MV | 36.0825 | -79.7708 | 10000 | 10 | 9.5 | 1 | 1
GSO_74 | br_074_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE3 | S_nSSEE3_12.47 | 10000.0 |  | MV | 36.0825 | -79.7708 | 10000 | 10 | 9.5 | 1 | 1
GSO_75 | br_075_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE3 | S_nSSEE3_12.47 | 10000.0 |  | MV | 36.0825 | -79.7708 | 10000 | 10 | 9.5 | 1 | 1
GSO_76 | br_076_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV | 36.0719 | -79.8252 | 6666.7 | 6.6667 | 6.3334 | 1 | 1
GSO_77 | br_077_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV | 36.0719 | -79.8252 | 6666.7 | 6.6667 | 6.3334 | 1 | 1
GSO_78 | br_078_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV | 36.0719 | -79.8252 | 6666.7 | 6.6667 | 6.3334 | 1 | 1
GSO_79 | br_079_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV | 36.0719 | -79.8252 | 6666.7 | 6.6667 | 6.3334 | 1 | 1
GSO_8 | br_022_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE10 | S_nSSEE10_12.47 | 5555.6 |  | MV | 36.1003 | -79.8075 | 5555.6 | 5.5556 | 5.2778 | 1 | 1
GSO_80 | br_080_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV | 36.0719 | -79.8252 | 6666.7 | 6.6667 | 6.3334 | 1 | 1
GSO_81 | br_081_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV | 36.0719 | -79.8252 | 6666.7 | 6.6667 | 6.3334 | 1 | 1
GSO_82 | br_082_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV | 36.0719 | -79.8252 | 6666.7 | 6.6667 | 6.3334 | 1 | 1
GSO_83 | br_083_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV | 36.0719 | -79.8252 | 6666.7 | 6.6667 | 6.3334 | 1 | 1
GSO_84 | br_084_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV | 36.0719 | -79.8252 | 6666.7 | 6.6667 | 6.3334 | 1 | 1
GSO_85 | br_085_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV | 36.0719 | -79.8252 | 6666.7 | 6.6667 | 6.3334 | 1 | 1
GSO_86 | br_086_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV | 36.0708 | -79.7962 | 4545.5 | 4.5455 | 4.3182 | 1 | 1
GSO_87 | br_087_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV | 36.0709 | -79.7962 | 4545.5 | 4.5455 | 4.3182 | 1 | 1
GSO_88 | br_088_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV | 36.0708 | -79.7962 | 4545.5 | 4.5455 | 4.3182 | 1 | 1
GSO_89 | br_089_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV | 36.0708 | -79.7962 | 4545.5 | 4.5455 | 4.3182 | 1 | 1
GSO_9 | br_023_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE10 | S_nSSEE10_12.47 | 5555.6 |  | MV | 36.1003 | -79.8075 | 5555.6 | 5.5556 | 5.2778 | 1 | 1
GSO_90 | br_090_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV | 36.0708 | -79.7962 | 4545.5 | 4.5455 | 4.3182 | 1 | 1
GSO_91 | br_091_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV | 36.0708 | -79.7962 | 4545.5 | 4.5455 | 4.3182 | 1 | 1
GSO_92 | br_092_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV | 36.0708 | -79.7962 | 4545.5 | 4.5455 | 4.3182 | 1 | 1
GSO_93 | br_093_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV | 36.0709 | -79.7962 | 4545.5 | 4.5455 | 4.3182 | 1 | 1
GSO_94 | br_094_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV | 36.0708 | -79.7962 | 4545.5 | 4.5455 | 4.3182 | 1 | 1
GSO_95 | br_095_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV | 36.0709 | -79.7962 | 4545.5 | 4.5455 | 4.3182 | 1 | 1
GSO_96 | br_096_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV | 36.0708 | -79.7962 | 4545.5 | 4.5455 | 4.3182 | 1 | 1
GSO_97 | br_098_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE6 | S_nSSEE6_12.47 | 7500.0 |  | MV | 36.061 | -79.7714 | 7500 | 7.5 | 7.125 | 1 | 1
GSO_98 | br_099_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE6 | S_nSSEE6_12.47 | 7500.0 |  | MV | 36.0611 | -79.7715 | 7500 | 7.5 | 7.125 | 1 | 1
GSO_99 | br_0100_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE6 | S_nSSEE6_12.47 | 7500.0 |  | MV | 36.061 | -79.7715 | 7500 | 7.5 | 7.125 | 1 | 1

## Breaker_Candidates
grid_id | BreakerElementID | ElementType | ElementCustomerType | BreakerPhases | IsProducer | IsConsumer | IsSwitchable | SwitchIsOpen | PowerFlowDirection | UpstreamElementID | Terminal1CN | Terminal2CN | RawBreakerRatingKVA | RawBreakerRatingA | RawBreakerVoltageLevel | Latitude | Longitude | BreakerRatingKVA | BreakerRatingMVA | BreakerCapacityMW | BreakerCount | BreakerCandidateRank
GSO_1 | br_01_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 5714.3 |  | MV | 36.0852 | -79.8827 | 5714.3 | 5.7143 | 5.4286 | 1 | 1
GSO_10 | br_015_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE10 | S_nSSEE10_12.47 | 5555.6 |  | MV | 36.1003 | -79.8075 | 5555.6 | 5.5556 | 5.2778 | 1 | 1
GSO_100 | br_097_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE6 | S_nSSEE6_12.47 | 7500.0 |  | MV | 36.0611 | -79.7715 | 7500 | 7.5 | 7.125 | 1 | 1
GSO_101 | br_0101_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE7 | S_nSSEE7_12.47 | 5714.3 |  | MV | 36.0872 | -79.897 | 5714.3 | 5.7143 | 5.4286 | 1 | 1
GSO_102 | br_0102_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE7 | S_nSSEE7_12.47 | 5714.3 |  | MV | 36.0872 | -79.897 | 5714.3 | 5.7143 | 5.4286 | 1 | 1
GSO_103 | br_0103_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE7 | S_nSSEE7_12.47 | 5714.3 |  | MV | 36.0872 | -79.897 | 5714.3 | 5.7143 | 5.4286 | 1 | 1
GSO_104 | br_0104_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE7 | S_nSSEE7_12.47 | 5714.3 |  | MV | 36.0872 | -79.897 | 5714.3 | 5.7143 | 5.4286 | 1 | 1
GSO_105 | br_0105_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE7 | S_nSSEE7_12.47 | 5714.3 |  | MV | 36.0872 | -79.897 | 5714.3 | 5.7143 | 5.4286 | 1 | 1
GSO_106 | br_0106_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE7 | S_nSSEE7_12.47 | 5714.3 |  | MV | 36.0872 | -79.897 | 5714.3 | 5.7143 | 5.4286 | 1 | 1
GSO_107 | br_0107_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE7 | S_nSSEE7_12.47 | 5714.3 |  | MV | 36.0872 | -79.897 | 5714.3 | 5.7143 | 5.4286 | 1 | 1
GSO_108 | br_0108_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE8 | S_nSSEE8_12.47 | 7142.9 |  | MV | 36.0543 | -79.8942 | 7142.9 | 7.1429 | 6.7858 | 1 | 1
GSO_109 | br_0109_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE8 | S_nSSEE8_12.47 | 7142.9 |  | MV | 36.0543 | -79.8942 | 7142.9 | 7.1429 | 6.7858 | 1 | 1
GSO_11 | br_016_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE10 | S_nSSEE10_12.47 | 5555.6 |  | MV | 36.1003 | -79.8075 | 5555.6 | 5.5556 | 5.2778 | 1 | 1
GSO_110 | br_0110_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE8 | S_nSSEE8_12.47 | 7142.9 |  | MV | 36.0543 | -79.8942 | 7142.9 | 7.1429 | 6.7858 | 1 | 1
GSO_111 | br_0111_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE8 | S_nSSEE8_12.47 | 7142.9 |  | MV | 36.0543 | -79.8942 | 7142.9 | 7.1429 | 6.7858 | 1 | 1
GSO_112 | br_0112_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE8 | S_nSSEE8_12.47 | 7142.9 |  | MV | 36.0543 | -79.8942 | 7142.9 | 7.1429 | 6.7858 | 1 | 1
GSO_113 | br_0113_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE8 | S_nSSEE8_12.47 | 7142.9 |  | MV | 36.0543 | -79.8942 | 7142.9 | 7.1429 | 6.7858 | 1 | 1
GSO_114 | br_0114_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE8 | S_nSSEE8_12.47 | 7142.9 |  | MV | 36.0543 | -79.8942 | 7142.9 | 7.1429 | 6.7858 | 1 | 1
GSO_115 | br_0115_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE9 | S_nSSEE9_12.47 | 10000.0 |  | MV | 36.0426 | -79.8533 | 10000 | 10 | 9.5 | 1 | 1
GSO_116 | br_0116_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE9 | S_nSSEE9_12.47 | 10000.0 |  | MV | 36.0426 | -79.8533 | 10000 | 10 | 9.5 | 1 | 1
GSO_117 | br_0117_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE9 | S_nSSEE9_12.47 | 10000.0 |  | MV | 36.0426 | -79.8533 | 10000 | 10 | 9.5 | 1 | 1
GSO_118 | br_0118_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE9 | S_nSSEE9_12.47 | 10000.0 |  | MV | 36.0426 | -79.8533 | 10000 | 10 | 9.5 | 1 | 1
GSO_119 | br_0119_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE9 | S_nSSEE9_12.47 | 10000.0 |  | MV | 36.0426 | -79.8533 | 10000 | 10 | 9.5 | 1 | 1
GSO_12 | br_017_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE10 | S_nSSEE10_12.47 | 5555.6 |  | MV | 36.1003 | -79.8075 | 5555.6 | 5.5556 | 5.2778 | 1 | 1
GSO_121 | br_01_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 15000.0 |  | MV | 36.083 | -79.9727 | 15000 | 15 | 14.25 | 1 | 1
GSO_122 | br_02_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 15000.0 |  | MV | 36.083 | -79.9727 | 15000 | 15 | 14.25 | 1 | 1
GSO_123 | br_03_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 15000.0 |  | MV | 36.083 | -79.9727 | 15000 | 15 | 14.25 | 1 | 1
GSO_124 | br_04_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 15000.0 |  | MV | 36.083 | -79.9727 | 15000 | 15 | 14.25 | 1 | 1
GSO_125 | br_05_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 10000.0 |  | MV | 36.0974 | -79.9235 | 10000 | 10 | 9.5 | 1 | 1
GSO_126 | br_06_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 10000.0 |  | MV | 36.0974 | -79.9235 | 10000 | 10 | 9.5 | 1 | 1
GSO_127 | br_07_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 10000.0 |  | MV | 36.0974 | -79.9235 | 10000 | 10 | 9.5 | 1 | 1
GSO_128 | br_08_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 10000.0 |  | MV | 36.0974 | -79.9234 | 10000 | 10 | 9.5 | 1 | 1
GSO_129 | br_09_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 8571.4 |  | MV | 36.0811 | -79.94 | 8571.4 | 8.5714 | 8.1428 | 1 | 1
GSO_13 | br_018_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE10 | S_nSSEE10_12.47 | 5555.6 |  | MV | 36.1003 | -79.8075 | 5555.6 | 5.5556 | 5.2778 | 1 | 1
GSO_130 | br_010_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 8571.4 |  | MV | 36.0811 | -79.94 | 8571.4 | 8.5714 | 8.1428 | 1 | 1
GSO_131 | br_011_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 8571.4 |  | MV | 36.0811 | -79.94 | 8571.4 | 8.5714 | 8.1428 | 1 | 1
GSO_132 | br_012_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 8571.4 |  | MV | 36.0811 | -79.94 | 8571.4 | 8.5714 | 8.1428 | 1 | 1
GSO_133 | br_013_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 8571.4 |  | MV | 36.0811 | -79.94 | 8571.4 | 8.5714 | 8.1428 | 1 | 1
GSO_134 | br_014_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 8571.4 |  | MV | 36.0811 | -79.94 | 8571.4 | 8.5714 | 8.1428 | 1 | 1
GSO_135 | br_015_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 8571.4 |  | MV | 36.0811 | -79.94 | 8571.4 | 8.5714 | 8.1428 | 1 | 1
GSO_136 | br_016_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE3 | S_nSSEE3_12.47 | 6000.0 |  | MV | 36.0705 | -79.9556 | 6000 | 6 | 5.7 | 1 | 1
GSO_137 | br_017_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE3 | S_nSSEE3_12.47 | 6000.0 |  | MV | 36.0705 | -79.9557 | 6000 | 6 | 5.7 | 1 | 1
GSO_138 | br_018_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE3 | S_nSSEE3_12.47 | 6000.0 |  | MV | 36.0705 | -79.9556 | 6000 | 6 | 5.7 | 1 | 1
GSO_139 | br_019_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE3 | S_nSSEE3_12.47 | 6000.0 |  | MV | 36.0705 | -79.9557 | 6000 | 6 | 5.7 | 1 | 1
GSO_14 | br_019_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE10 | S_nSSEE10_12.47 | 5555.6 |  | MV | 36.1003 | -79.8075 | 5555.6 | 5.5556 | 5.2778 | 1 | 1
GSO_140 | br_020_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE3 | S_nSSEE3_12.47 | 6000.0 |  | MV | 36.0705 | -79.9556 | 6000 | 6 | 5.7 | 1 | 1
GSO_141 | br_021_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 12000.0 |  | MV | 36.0459 | -79.947 | 12000 | 12 | 11.4 | 1 | 1
GSO_142 | br_022_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 12000.0 |  | MV | 36.0459 | -79.947 | 12000 | 12 | 11.4 | 1 | 1
GSO_143 | br_023_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 12000.0 |  | MV | 36.0459 | -79.947 | 12000 | 12 | 11.4 | 1 | 1
GSO_144 | br_024_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 12000.0 |  | MV | 36.046 | -79.947 | 12000 | 12 | 11.4 | 1 | 1
GSO_145 | br_025_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 12000.0 |  | MV | 36.046 | -79.947 | 12000 | 12 | 11.4 | 1 | 1
GSO_146 | br_026_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 7500.0 |  | MV | 36.114 | -79.9604 | 7500 | 7.5 | 7.125 | 1 | 1
GSO_147 | br_027_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 7500.0 |  | MV | 36.114 | -79.9604 | 7500 | 7.5 | 7.125 | 1 | 1
GSO_148 | br_028_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 7500.0 |  | MV | 36.114 | -79.9604 | 7500 | 7.5 | 7.125 | 1 | 1
GSO_149 | br_029_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 7500.0 |  | MV | 36.114 | -79.9604 | 7500 | 7.5 | 7.125 | 1 | 1
GSO_15 | br_020_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE10 | S_nSSEE10_12.47 | 5555.6 |  | MV | 36.1003 | -79.8075 | 5555.6 | 5.5556 | 5.2778 | 1 | 1
GSO_150 | br_030_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE6 | S_nSSEE6_12.47 | 6000.0 |  | MV | 36.0823 | -79.9238 | 6000 | 6 | 5.7 | 1 | 1
GSO_151 | br_031_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE6 | S_nSSEE6_12.47 | 6000.0 |  | MV | 36.0823 | -79.9238 | 6000 | 6 | 5.7 | 1 | 1
GSO_152 | br_032_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE6 | S_nSSEE6_12.47 | 6000.0 |  | MV | 36.0823 | -79.9238 | 6000 | 6 | 5.7 | 1 | 1
GSO_153 | br_033_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE6 | S_nSSEE6_12.47 | 6000.0 |  | MV | 36.0823 | -79.9238 | 6000 | 6 | 5.7 | 1 | 1
GSO_154 | br_034_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE6 | S_nSSEE6_12.47 | 6000.0 |  | MV | 36.0823 | -79.9238 | 6000 | 6 | 5.7 | 1 | 1
GSO_155 | br_01_23 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 7500.0 |  | MV | 36.1928 | -79.6069 | 7500 | 7.5 | 7.125 | 1 | 1
GSO_156 | br_02_23 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 7500.0 |  | MV | 36.1929 | -79.6068 | 7500 | 7.5 | 7.125 | 1 | 1
GSO_157 | br_03_23 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 7500.0 |  | MV | 36.1929 | -79.6068 | 7500 | 7.5 | 7.125 | 1 | 1
GSO_158 | br_04_23 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 7500.0 |  | MV | 36.1929 | -79.6068 | 7500 | 7.5 | 7.125 | 1 | 1
GSO_159 | br_05_23 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 5714.3 |  | MV | 36.2604 | -79.5886 | 5714.3 | 5.7143 | 5.4286 | 1 | 1
GSO_16 | br_021_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE10 | S_nSSEE10_12.47 | 5555.6 |  | MV | 36.1003 | -79.8075 | 5555.6 | 5.5556 | 5.2778 | 1 | 1
GSO_160 | br_06_23 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 5714.3 |  | MV | 36.2604 | -79.5886 | 5714.3 | 5.7143 | 5.4286 | 1 | 1
GSO_161 | br_07_23 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 5714.3 |  | MV | 36.2604 | -79.5886 | 5714.3 | 5.7143 | 5.4286 | 1 | 1
GSO_162 | br_08_23 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 8000.0 |  | MV | 36.1644 | -79.7079 | 8000 | 8 | 7.6 | 1 | 1
GSO_163 | br_09_23 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 8000.0 |  | MV | 36.1644 | -79.708 | 8000 | 8 | 7.6 | 1 | 1
GSO_17 | br_024_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE11 | S_nSSEE11_12.47 | 13333.3 |  | MV | 36.0264 | -79.8286 | 13333.3 | 13.3333 | 12.6666 | 1 | 1
GSO_18 | br_025_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE11 | S_nSSEE11_12.47 | 13333.3 |  | MV | 36.0264 | -79.8286 | 13333.3 | 13.3333 | 12.6666 | 1 | 1
GSO_19 | br_026_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE11 | S_nSSEE11_12.47 | 13333.3 |  | MV | 36.0264 | -79.8286 | 13333.3 | 13.3333 | 12.6666 | 1 | 1
GSO_2 | br_02_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 5714.3 |  | MV | 36.0852 | -79.8827 | 5714.3 | 5.7143 | 5.4286 | 1 | 1
GSO_20 | br_027_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE12 | S_nSSEE12_12.47 | 3750.0 |  | MV | 36.0604 | -79.8599 | 3750 | 3.75 | 3.5625 | 1 | 1
GSO_21 | br_028_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE12 | S_nSSEE12_12.47 | 3750.0 |  | MV | 36.0604 | -79.8599 | 3750 | 3.75 | 3.5625 | 1 | 1
GSO_22 | br_029_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE12 | S_nSSEE12_12.47 | 3750.0 |  | MV | 36.0604 | -79.8599 | 3750 | 3.75 | 3.5625 | 1 | 1
GSO_23 | br_030_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE12 | S_nSSEE12_12.47 | 3750.0 |  | MV | 36.0604 | -79.8599 | 3750 | 3.75 | 3.5625 | 1 | 1
GSO_24 | br_031_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE12 | S_nSSEE12_12.47 | 3750.0 |  | MV | 36.0603 | -79.8599 | 3750 | 3.75 | 3.5625 | 1 | 1
GSO_25 | br_032_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE12 | S_nSSEE12_12.47 | 3750.0 |  | MV | 36.0603 | -79.8599 | 3750 | 3.75 | 3.5625 | 1 | 1
GSO_26 | br_033_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE12 | S_nSSEE12_12.47 | 3750.0 |  | MV | 36.0603 | -79.8599 | 3750 | 3.75 | 3.5625 | 1 | 1
GSO_27 | br_034_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE12 | S_nSSEE12_12.47 | 3750.0 |  | MV | 36.0604 | -79.8599 | 3750 | 3.75 | 3.5625 | 1 | 1
GSO_28 | br_035_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE13 | S_nSSEE13_12.47 | 7500.0 |  | MV | 36.1038 | -79.7639 | 7500 | 7.5 | 7.125 | 1 | 1
GSO_29 | br_036_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE13 | S_nSSEE13_12.47 | 7500.0 |  | MV | 36.1038 | -79.7639 | 7500 | 7.5 | 7.125 | 1 | 1
GSO_3 | br_03_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 5714.3 |  | MV | 36.0852 | -79.8826 | 5714.3 | 5.7143 | 5.4286 | 1 | 1
GSO_30 | br_037_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE13 | S_nSSEE13_12.47 | 7500.0 |  | MV | 36.1038 | -79.7639 | 7500 | 7.5 | 7.125 | 1 | 1
GSO_31 | br_038_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE13 | S_nSSEE13_12.47 | 7500.0 |  | MV | 36.1038 | -79.7639 | 7500 | 7.5 | 7.125 | 1 | 1
GSO_32 | br_039_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE14 | S_nSSEE14_12.47 | 6666.7 |  | MV | 36.0466 | -79.7995 | 6666.7 | 6.6667 | 6.3334 | 1 | 1
GSO_33 | br_040_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE14 | S_nSSEE14_12.47 | 6666.7 |  | MV | 36.0466 | -79.7995 | 6666.7 | 6.6667 | 6.3334 | 1 | 1
GSO_34 | br_041_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE14 | S_nSSEE14_12.47 | 6666.7 |  | MV | 36.0466 | -79.7995 | 6666.7 | 6.6667 | 6.3334 | 1 | 1
GSO_35 | br_042_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE14 | S_nSSEE14_12.47 | 6666.7 |  | MV | 36.0466 | -79.7995 | 6666.7 | 6.6667 | 6.3334 | 1 | 1
GSO_36 | br_043_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE14 | S_nSSEE14_12.47 | 6666.7 |  | MV | 36.0466 | -79.7995 | 6666.7 | 6.6667 | 6.3334 | 1 | 1
GSO_37 | br_044_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE14 | S_nSSEE14_12.47 | 6666.7 |  | MV | 36.0466 | -79.7995 | 6666.7 | 6.6667 | 6.3334 | 1 | 1
GSO_38 | br_045_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE15 | S_nSSEE15_12.47 | 6000.0 |  | MV | 36.121 | -79.8612 | 6000 | 6 | 5.7 | 1 | 1
GSO_39 | br_046_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE15 | S_nSSEE15_12.47 | 6000.0 |  | MV | 36.121 | -79.8612 | 6000 | 6 | 5.7 | 1 | 1
GSO_4 | br_04_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 5714.3 |  | MV | 36.0852 | -79.8827 | 5714.3 | 5.7143 | 5.4286 | 1 | 1
GSO_40 | br_047_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE15 | S_nSSEE15_12.47 | 6000.0 |  | MV | 36.121 | -79.8612 | 6000 | 6 | 5.7 | 1 | 1
GSO_41 | br_048_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE15 | S_nSSEE15_12.47 | 6000.0 |  | MV | 36.121 | -79.8612 | 6000 | 6 | 5.7 | 1 | 1
GSO_42 | br_049_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE15 | S_nSSEE15_12.47 | 6000.0 |  | MV | 36.121 | -79.8612 | 6000 | 6 | 5.7 | 1 | 1
GSO_43 | br_050_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV | 36.0168 | -79.7965 | 5454.5 | 5.4545 | 5.1818 | 1 | 1
GSO_44 | br_051_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV | 36.0168 | -79.7965 | 5454.5 | 5.4545 | 5.1818 | 1 | 1
GSO_45 | br_052_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV | 36.0168 | -79.7965 | 5454.5 | 5.4545 | 5.1818 | 1 | 1
GSO_46 | br_053_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV | 36.0168 | -79.7965 | 5454.5 | 5.4545 | 5.1818 | 1 | 1
GSO_47 | br_054_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV | 36.0168 | -79.7965 | 5454.5 | 5.4545 | 5.1818 | 1 | 1
GSO_48 | br_055_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV | 36.0168 | -79.7965 | 5454.5 | 5.4545 | 5.1818 | 1 | 1
GSO_49 | br_056_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV | 36.0168 | -79.7965 | 5454.5 | 5.4545 | 5.1818 | 1 | 1
GSO_5 | br_05_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 5714.3 |  | MV | 36.0852 | -79.8827 | 5714.3 | 5.7143 | 5.4286 | 1 | 1
GSO_50 | br_057_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV | 36.0168 | -79.7965 | 5454.5 | 5.4545 | 5.1818 | 1 | 1
GSO_51 | br_058_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV | 36.0168 | -79.7965 | 5454.5 | 5.4545 | 5.1818 | 1 | 1
GSO_52 | br_059_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV | 36.0168 | -79.7965 | 5454.5 | 5.4545 | 5.1818 | 1 | 1
GSO_53 | br_060_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV | 36.0168 | -79.7965 | 5454.5 | 5.4545 | 5.1818 | 1 | 1
GSO_54 | br_061_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE17 | S_nSSEE17_12.47 | 10000.0 |  | MV | 36.0131 | -79.8489 | 10000 | 10 | 9.5 | 1 | 1
GSO_55 | br_062_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE17 | S_nSSEE17_12.47 | 10000.0 |  | MV | 36.0131 | -79.8489 | 10000 | 10 | 9.5 | 1 | 1
GSO_56 | br_063_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE17 | S_nSSEE17_12.47 | 10000.0 |  | MV | 36.0131 | -79.8489 | 10000 | 10 | 9.5 | 1 | 1
GSO_57 | br_08_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 6122.4 |  | MV | 36.0872 | -79.8446 | 6122.4 | 6.1224 | 5.8163 | 1 | 1
GSO_58 | br_09_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 6122.4 |  | MV | 36.0872 | -79.8446 | 6122.4 | 6.1224 | 5.8163 | 1 | 1
GSO_59 | br_010_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 6122.4 |  | MV | 36.0873 | -79.8446 | 6122.4 | 6.1224 | 5.8163 | 1 | 1
GSO_6 | br_06_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 5714.3 |  | MV | 36.0852 | -79.8827 | 5714.3 | 5.7143 | 5.4286 | 1 | 1
GSO_60 | br_011_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 6122.4 |  | MV | 36.0873 | -79.8446 | 6122.4 | 6.1224 | 5.8163 | 1 | 1
GSO_61 | br_012_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 6122.4 |  | MV | 36.0872 | -79.8446 | 6122.4 | 6.1224 | 5.8163 | 1 | 1
GSO_62 | br_013_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 6122.4 |  | MV | 36.0873 | -79.8446 | 6122.4 | 6.1224 | 5.8163 | 1 | 1
GSO_63 | br_014_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 6122.4 |  | MV | 36.0873 | -79.8446 | 6122.4 | 6.1224 | 5.8163 | 1 | 1
GSO_64 | br_064_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 4285.7 |  | MV | 36.0801 | -79.7573 | 4285.7 | 4.2857 | 4.0714 | 1 | 1
GSO_65 | br_065_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 4285.7 |  | MV | 36.0801 | -79.7573 | 4285.7 | 4.2857 | 4.0714 | 1 | 1
GSO_66 | br_066_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 4285.7 |  | MV | 36.0801 | -79.7573 | 4285.7 | 4.2857 | 4.0714 | 1 | 1
GSO_67 | br_067_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 4285.7 |  | MV | 36.0801 | -79.7573 | 4285.7 | 4.2857 | 4.0714 | 1 | 1
GSO_68 | br_068_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 4285.7 |  | MV | 36.0801 | -79.7573 | 4285.7 | 4.2857 | 4.0714 | 1 | 1
GSO_69 | br_069_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 4285.7 |  | MV | 36.0801 | -79.7573 | 4285.7 | 4.2857 | 4.0714 | 1 | 1
GSO_7 | br_07_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 5714.3 |  | MV | 36.0852 | -79.8826 | 5714.3 | 5.7143 | 5.4286 | 1 | 1
GSO_70 | br_070_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 4285.7 |  | MV | 36.0801 | -79.7573 | 4285.7 | 4.2857 | 4.0714 | 1 | 1
GSO_71 | br_071_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE3 | S_nSSEE3_12.47 | 10000.0 |  | MV | 36.0825 | -79.7708 | 10000 | 10 | 9.5 | 1 | 1
GSO_72 | br_072_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE3 | S_nSSEE3_12.47 | 10000.0 |  | MV | 36.0825 | -79.7708 | 10000 | 10 | 9.5 | 1 | 1
GSO_73 | br_073_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE3 | S_nSSEE3_12.47 | 10000.0 |  | MV | 36.0825 | -79.7708 | 10000 | 10 | 9.5 | 1 | 1
GSO_74 | br_074_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE3 | S_nSSEE3_12.47 | 10000.0 |  | MV | 36.0825 | -79.7708 | 10000 | 10 | 9.5 | 1 | 1
GSO_75 | br_075_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE3 | S_nSSEE3_12.47 | 10000.0 |  | MV | 36.0825 | -79.7708 | 10000 | 10 | 9.5 | 1 | 1
GSO_76 | br_076_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV | 36.0719 | -79.8252 | 6666.7 | 6.6667 | 6.3334 | 1 | 1
GSO_77 | br_077_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV | 36.0719 | -79.8252 | 6666.7 | 6.6667 | 6.3334 | 1 | 1
GSO_78 | br_078_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV | 36.0719 | -79.8252 | 6666.7 | 6.6667 | 6.3334 | 1 | 1
GSO_79 | br_079_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV | 36.0719 | -79.8252 | 6666.7 | 6.6667 | 6.3334 | 1 | 1
GSO_8 | br_022_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE10 | S_nSSEE10_12.47 | 5555.6 |  | MV | 36.1003 | -79.8075 | 5555.6 | 5.5556 | 5.2778 | 1 | 1
GSO_80 | br_080_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV | 36.0719 | -79.8252 | 6666.7 | 6.6667 | 6.3334 | 1 | 1
GSO_81 | br_081_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV | 36.0719 | -79.8252 | 6666.7 | 6.6667 | 6.3334 | 1 | 1
GSO_82 | br_082_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV | 36.0719 | -79.8252 | 6666.7 | 6.6667 | 6.3334 | 1 | 1
GSO_83 | br_083_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV | 36.0719 | -79.8252 | 6666.7 | 6.6667 | 6.3334 | 1 | 1
GSO_84 | br_084_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV | 36.0719 | -79.8252 | 6666.7 | 6.6667 | 6.3334 | 1 | 1
GSO_85 | br_085_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV | 36.0719 | -79.8252 | 6666.7 | 6.6667 | 6.3334 | 1 | 1
GSO_86 | br_086_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV | 36.0708 | -79.7962 | 4545.5 | 4.5455 | 4.3182 | 1 | 1
GSO_87 | br_087_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV | 36.0709 | -79.7962 | 4545.5 | 4.5455 | 4.3182 | 1 | 1
GSO_88 | br_088_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV | 36.0708 | -79.7962 | 4545.5 | 4.5455 | 4.3182 | 1 | 1
GSO_89 | br_089_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV | 36.0708 | -79.7962 | 4545.5 | 4.5455 | 4.3182 | 1 | 1
GSO_9 | br_023_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE10 | S_nSSEE10_12.47 | 5555.6 |  | MV | 36.1003 | -79.8075 | 5555.6 | 5.5556 | 5.2778 | 1 | 1
GSO_90 | br_090_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV | 36.0708 | -79.7962 | 4545.5 | 4.5455 | 4.3182 | 1 | 1
GSO_91 | br_091_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV | 36.0708 | -79.7962 | 4545.5 | 4.5455 | 4.3182 | 1 | 1
GSO_92 | br_092_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV | 36.0708 | -79.7962 | 4545.5 | 4.5455 | 4.3182 | 1 | 1
GSO_93 | br_093_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV | 36.0709 | -79.7962 | 4545.5 | 4.5455 | 4.3182 | 1 | 1
GSO_94 | br_094_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV | 36.0708 | -79.7962 | 4545.5 | 4.5455 | 4.3182 | 1 | 1
GSO_95 | br_095_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV | 36.0709 | -79.7962 | 4545.5 | 4.5455 | 4.3182 | 1 | 1
GSO_96 | br_096_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV | 36.0708 | -79.7962 | 4545.5 | 4.5455 | 4.3182 | 1 | 1
GSO_97 | br_098_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE6 | S_nSSEE6_12.47 | 7500.0 |  | MV | 36.061 | -79.7714 | 7500 | 7.5 | 7.125 | 1 | 1
GSO_98 | br_099_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE6 | S_nSSEE6_12.47 | 7500.0 |  | MV | 36.0611 | -79.7715 | 7500 | 7.5 | 7.125 | 1 | 1
GSO_99 | br_0100_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE6 | S_nSSEE6_12.47 | 7500.0 |  | MV | 36.061 | -79.7715 | 7500 | 7.5 | 7.125 | 1 | 1

## SCADA_Load
Observations | FirstTimestamp | LastTimestamp | MedianIntervalMinutes | AverageIntervalKWh | P95IntervalKWh | PeakIntervalKWh | AverageLoadMW | P95LoadMW | PeakLoadMW | PeakLoadTimestamp | grid_id | BreakerElementID | LoadSourceCount | LoadSourceIDs | LoadSourcePhases | LoadSCADAStatus
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 47.6222 | 58.155 | 69.703 | 0.57147 | 0.69786 | 0.83644 | 2024-01-20 19:00 | GSO_1 | br_01_21 | 3 | b1e8c057-fded-4c70-8f86-a33db401b6d1, ba6970aa-af7f-428e-9a4f-7826618684b4, ea496fcb-6216-4db1-9885-1da5dbf70fa2 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 82.8253 | 116.5043 | 157.83 | 0.9939 | 1.3981 | 1.894 | 2024-01-21 04:00 | GSO_10 | br_015_21 | 3 | d140ab36-31a8-40c7-820d-c3a2df82604a, b315ece6-7341-4cdf-a1c9-70a8dbfe93ff, 396f73e2-6041-46ac-90d5-a9439aef50d8 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 14.5529 | 22.36 | 30.904 | 0.17463 | 0.26832 | 0.37085 | 2024-01-20 07:05 | GSO_100 | br_097_21 | 3 | 564551fe-ec45-4b6c-a7df-ebfa29a0a242, 3125b67a-cbd0-47b3-94b6-a60b38de7e8b, cc6f9a7e-ea1b-4cdb-9c85-6c672b845068 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 55.7798 | 73.128 | 93.468 | 0.66936 | 0.87754 | 1.1216 | 2024-01-21 04:00 | GSO_101 | br_0101_21 | 3 | f32aafa6-4f97-40b9-85a1-6516b7a34fb0, 8f1038a0-f3d5-4f15-bedf-b8f1215601f3, 6c559f06-b888-4a9d-ba0f-901b0b19b354 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 1.7953 | 2.775 | 4.54 | 0.021543 | 0.0333 | 0.05448 | 2024-07-15 23:00 | GSO_102 | br_0102_21 | 3 | aaef163c-bdc4-464e-9864-b0c0ebdf8662, 3f11f59f-b6f2-44fe-8a16-f4a87144ca07, 58383f3b-39ee-41c1-9a45-f21c6b309b7c | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 168.1721 | 258.5616 | 348.914 | 2.0181 | 3.1027 | 4.187 | 2024-01-21 04:00 | GSO_103 | br_0103_21 | 3 | d5fd099c-84d4-4965-91b3-bbc0c68d61d1, d53e58ae-230d-449a-b78d-6b5cfa60f56b, a3539c00-7186-4684-93db-03123790cf12 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 159.7475 | 240.7818 | 321.785 | 1.917 | 2.8894 | 3.8614 | 2024-01-21 04:00 | GSO_104 | br_0104_21 | 3 | dbaf906f-b53b-4b15-bd48-42442608214a, 0256f17b-1fde-4e5f-aa42-6a293aa27e64, 4922eba1-a72a-4e22-8a37-912d5f9ac46b | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 150.7342 | 231.125 | 305 | 1.8088 | 2.7735 | 3.66 | 2024-01-21 04:00 | GSO_105 | br_0105_21 | 3 | 3943a935-55e7-44b5-a61e-08789763be18, 11bf4c6d-205c-4caf-b572-7246ab210632, 98dc0614-4560-469e-93e2-97b3c41b5000 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 3.439 | 5.378 | 7.74 | 0.041269 | 0.064536 | 0.09288 | 2024-01-20 10:00 | GSO_106 | br_0106_21 | 3 | 1523bf59-c426-49d7-add2-e9b831978748, e37ebffe-ff65-4277-a7e0-2315cac8c267, f0643cc7-b03a-4328-82d5-2924a650f97f | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 5.7446 | 6.98 | 9.627 | 0.068935 | 0.08376 | 0.11552 | 2024-07-16 01:00 | GSO_107 | br_0107_21 | 3 | 4113937f-0ce2-415a-9249-ce7327d121f7, 5d59abb9-0bac-4fa7-a891-4e9d4e794c88, b1339292-267a-4146-8873-ecfc9cb1a82e | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 106.625 | 159.5309 | 207.686 | 1.2795 | 1.9144 | 2.4922 | 2024-01-20 23:30 | GSO_108 | br_0108_21 | 3 | e867a5e4-d5f1-4fdf-98c8-da37424315a6, c0036365-6459-4cc7-b7b1-ed8933515338, 1886a888-6918-466c-929d-0c8f16370dda | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 96.6701 | 141.014 | 185.217 | 1.16 | 1.6922 | 2.2226 | 2024-01-20 13:00 | GSO_109 | br_0109_21 | 3 | 0c75d1f1-8237-436b-a2c8-c9b6fdc7a116, ec8ad3c4-a39d-4acb-8788-e7435be58cb7, e6350d88-56d8-492b-bc1e-dcd90fcca31f | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 101.1181 | 141.697 | 183.017 | 1.2134 | 1.7004 | 2.1962 | 2024-01-21 04:00 | GSO_11 | br_016_21 | 3 | 469868d0-2f60-42bd-aa67-be26d6eae0eb, 9cdbec33-569a-438b-ac44-23b272ad169b, dfea635f-2a86-40f1-9367-d78b6dd6c309 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 182.8709 | 279.822 | 376.282 | 2.1945 | 3.3579 | 4.5154 | 2024-01-21 04:00 | GSO_110 | br_0110_21 | 3 | 1e111a58-963a-4906-b1f6-e2d03049b19a, 8a0dd243-2512-4f92-afd7-db6e79d7496e, ca02189c-f89b-417b-a469-ef0366d6da6e | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 54.7044 | 75.746 | 96.334 | 0.65645 | 0.90895 | 1.156 | 2024-01-18 04:00 | GSO_111 | br_0111_21 | 3 | f8549391-d242-43a9-9a34-33f872443611, 3488e4fc-fa59-4bcf-b967-3b7a890f6c3c, e60c92cc-e283-4345-87b0-ba3a9fd78005 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 39.8632 | 48.388 | 64.278 | 0.47836 | 0.58066 | 0.77134 | 2024-01-21 04:00 | GSO_112 | br_0112_21 | 3 | 407ea9ca-a495-4119-a139-1d1233852fdc, 99fe4744-38fc-4467-902b-d97556b6d295, e1fd2b67-b072-4575-9f5d-c24af5f52b11 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 4.4835 | 5.424 | 7.604 | 0.053802 | 0.065088 | 0.091248 | 2024-01-20 20:00 | GSO_113 | br_0113_21 | 3 | f8ddca03-2f28-483b-97fe-a4538d6c4e2b, a9bc380c-ca71-4a2b-b314-0f03f9f76581, bdf27366-2b21-4e21-8946-86b299b81d14 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 62.7375 | 88.1806 | 117.2 | 0.75285 | 1.0582 | 1.4064 | 2024-01-20 14:00 | GSO_114 | br_0114_21 | 3 | 34c2c476-7801-4ae6-ba1f-ca1a602925b3, 156d4241-1525-4089-8367-effd61eb4969, 3128527e-a25b-4b2c-9d88-b40eb600580e | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 99.7864 | 143.813 | 189.272 | 1.1974 | 1.7258 | 2.2713 | 2024-01-21 04:00 | GSO_115 | br_0115_21 | 3 | d3645b59-a71d-4848-9deb-b044c307c52a, 820fcd78-48b0-467d-8925-554a0333f605, 58786ac1-7ac2-4287-bd8f-add68a4ea208 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 53.4188 | 70.3586 | 90.053 | 0.64103 | 0.8443 | 1.0806 | 2024-01-20 16:00 | GSO_116 | br_0116_21 | 3 | 2a93f307-f837-4de0-9089-b308bde0f0fd, ba9bd088-fa13-4d76-ba16-6dba6a8b45de, e9542020-950f-403c-af95-965f8434a9f8 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 151.7502 | 223.4966 | 294.004 | 1.821 | 2.682 | 3.528 | 2024-01-18 04:00 | GSO_117 | br_0117_21 | 3 | 20ca2ff7-1194-405d-9098-d4544944a36d, 127d58d0-da5d-47a0-a219-b8c1834a136a, 79b91384-9645-42ed-940d-37fdffcc31a0 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 77.2137 | 103.7746 | 131.03 | 0.92656 | 1.2453 | 1.5724 | 2024-01-20 21:00 | GSO_118 | br_0118_21 | 3 | b2273af8-cb6e-4178-93e7-36fab6dbf2c0, cb23fba1-b5a8-477f-b388-dcbc14cf56b2, 7b9e37f6-9e61-405e-8bc5-9d79097397f4 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 12.4758 | 19.259 | 27.93 | 0.14971 | 0.23111 | 0.33516 | 2024-01-20 22:00 | GSO_119 | br_0119_21 | 3 | 1a46aa48-ac4e-4046-aa43-a61c07c816d6, faec1da7-65b2-4b86-be90-e4357dfde1ce, 3aad3364-ed36-4087-b7d0-6d3b3fa6f823 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 102.8633 | 157.9969 | 208.196 | 1.2344 | 1.896 | 2.4984 | 2024-01-18 04:00 | GSO_12 | br_017_21 | 3 | e263a729-e360-4716-9561-679bf6b5d16a, ede6f7c6-f426-4d65-bfe0-7dac24a794c1, 4c1ed359-972e-4bdd-a0cd-1159d7a32c07 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 20.3889 | 25.3796 | 31.802 | 0.24467 | 0.30456 | 0.38162 | 2024-01-17 23:00 | GSO_121 | br_01_22 | 3 | 0eb7ef08-0441-4661-84d4-63da9255ea41, 36cfcc10-f3c4-4989-ae21-5fdd2aa20962, 423b0798-4793-4a14-a787-72bb51fb4cef | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 1.6439 | 2.003 | 2.73 | 0.019727 | 0.024036 | 0.03276 | 2024-01-20 07:00 | GSO_122 | br_02_22 | 3 | e63f1c25-1cac-49ae-9929-f96fa015f74e, 4fa57e43-e6c7-4d4b-a312-3fb0e3337ffc, abf746be-5de9-44ac-9f69-a717abe29437 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 20.6829 | 24.064 | 30.387 | 0.24819 | 0.28877 | 0.36464 | 2024-01-22 04:00 | GSO_123 | br_03_22 | 3 | 22b46d3c-1104-4a6b-baf0-791554532cbe, c84967ed-4e26-4447-aaec-39d0dba00695, 08fe15ea-b154-4270-ad96-7633898d9feb | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 6.4773 | 7.975 | 11.156 | 0.077728 | 0.0957 | 0.13387 | 2024-01-22 04:00 | GSO_124 | br_04_22 | 3 | e9588dba-e5c4-44a0-a87f-6d585846716c, f9dd1e2c-0b53-4323-abbd-c79d2b87bf2e, cbbe0d2b-6245-4a4f-bcc2-e456b3e84669 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 17.2263 | 20.9386 | 27.008 | 0.20672 | 0.25126 | 0.3241 | 2024-01-20 11:00 | GSO_125 | br_05_22 | 3 | cd7fbbb9-9a6f-4dd9-891c-e37a9557fa12, 16682194-aa4b-49e9-acf2-9c6562595352, 99cabfd6-b964-4658-8155-1699ad43459b | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 13.0851 | 15.753 | 20.182 | 0.15702 | 0.18904 | 0.24218 | 2024-01-20 21:00 | GSO_126 | br_06_22 | 3 | 9006b8b1-eda0-485b-a8d0-426580b8950f, bc3fda03-9c4b-412b-a5ef-6db07eeba8fc, 12d09ac1-fdb6-467e-a1aa-f99f6eed49f6 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 1.0502 | 1.388 | 2.101 | 0.012603 | 0.016656 | 0.025212 | 2024-01-20 21:00 | GSO_127 | br_07_22 | 3 | a16d8ea2-fafa-4870-8bff-75e352b48100, 1287cfdf-d61b-4b7d-9c56-4a67e583be03, 9962595a-e18a-4855-ab7a-6bcfb11262e4 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 8.0596 | 9.673 | 12.511 | 0.096715 | 0.11608 | 0.15013 | 2024-07-16 02:00 | GSO_128 | br_08_22 | 3 | 692be577-442c-4ab0-b1e1-5785854345e2, 6cff9753-e438-465f-8082-4b41468b4f8c, 3d10e996-315d-4229-9b7c-a9b8e0697db8 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 14.3968 | 17.421 | 21.922 | 0.17276 | 0.20905 | 0.26306 | 2024-01-22 04:00 | GSO_129 | br_09_22 | 3 | 686b2171-718b-454f-a63f-7a08af910b78, 066b1670-e5b9-40c9-bd97-907fe78b74e9, ca9fa130-fc7c-477e-8464-326c962a06af | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 109.1296 | 159.5763 | 210.912 | 1.3096 | 1.9149 | 2.5309 | 2024-01-21 04:00 | GSO_13 | br_018_21 | 3 | 28993f84-c3b9-4382-b199-7eae1602f7b5, d4524dc1-a63b-454b-a0d9-1683a9db619b, 538bb977-c069-4a72-a1f5-79ade89be85e | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 17.5856 | 20.67 | 26.519 | 0.21103 | 0.24804 | 0.31823 | 2024-01-22 04:00 | GSO_130 | br_010_22 | 3 | ec2f67d6-3e29-40e6-b3db-279de5aeb3e1, 0820aaeb-7057-4894-a6ba-7624e83ee1a7, cab2ab50-4b8d-4ecb-98f8-73c155d0b547 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 3.7691 | 4.4646 | 6.121 | 0.04523 | 0.053576 | 0.073452 | 2024-01-20 18:00 | GSO_131 | br_011_22 | 3 | 434fff6c-2804-492a-a7e9-8c978d0dc8e3, 1a6f96c2-84f7-4c0d-b1a3-ee2364b2f450, 618c145a-b95c-4f8d-9e8d-9389861004d6 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 26.9423 | 31.6646 | 38.23 | 0.32331 | 0.37998 | 0.45876 | 2024-01-20 21:00 | GSO_132 | br_012_22 | 3 | 935c3854-ba34-4cf1-b241-c865be78d3bf, 0716ea38-77d5-4d34-bc24-820dc14d344a, 8eae3b99-7252-4faf-9a4e-4abe914bc30e | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 37.2676 | 44.079 | 56.475 | 0.44721 | 0.52895 | 0.6777 | 2024-01-20 11:00 | GSO_133 | br_013_22 | 3 | dddfb629-b710-4a70-b13f-4f342bc8fe74, 4d344901-644b-4ea0-b7f1-b381d39a7879, c086c5c8-dc85-4746-8b0a-d8e23067358a | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 18.38 | 22.037 | 27.385 | 0.22056 | 0.26444 | 0.32862 | 2024-01-20 09:00 | GSO_134 | br_014_22 | 3 | 4091c3a2-55c3-4b7e-8d9d-a8e4affed314, 57c2fa84-53da-4153-9d01-3c3ac5b2144e, 7325e088-181d-4e0d-b15b-2dd1fbda83f0 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 30.6842 | 35.815 | 43.88 | 0.36821 | 0.42978 | 0.52656 | 2024-01-20 23:05 | GSO_135 | br_015_22 | 3 | c3ac0e33-1470-42fd-9a70-99015f289563, 306b628e-5350-43cc-bd44-5524b56eb0e1, cb036569-e3a3-4f9a-ab6b-ada0cfc7f7a2 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 18.3703 | 21.749 | 28.701 | 0.22044 | 0.26099 | 0.34441 | 2024-01-17 16:00 | GSO_136 | br_016_22 | 3 | 04ce7e89-fb0f-4fb3-9752-836af1c7ab9e, 1985324e-e67a-4d01-bf4e-cbc1776ba800, 66b785ca-af8e-4a6a-8af7-ff9241ec96a5 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 17.8375 | 20.948 | 25.601 | 0.21405 | 0.25138 | 0.30721 | 2024-01-20 18:00 | GSO_137 | br_017_22 | 3 | cf094241-cd71-4a00-ae80-c341e78225f3, d0f42d15-cf63-4976-b310-0a7f21c9a7fc, bb261d99-e16f-41bf-90d2-05acc7b4f39c | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 18.878 | 24.579 | 32.26 | 0.22654 | 0.29495 | 0.38712 | 2024-01-21 04:00 | GSO_138 | br_018_22 | 3 | c812a09e-5775-4fbc-93b7-37aa020f3a4a, b91b7108-02a6-4c8f-9294-9075747bf3d2, 8cf34f38-0fdb-4d44-9870-a7c9c5b5c3b4 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 25.2516 | 30.442 | 41.744 | 0.30302 | 0.3653 | 0.50093 | 2024-01-21 04:00 | GSO_139 | br_019_22 | 3 | 8781de87-205d-4b90-963f-449d72c41e8c, 2a67f2a3-ad9e-4413-af20-999870d5694e, 6ec0fb64-8f9d-48b6-81ae-63048adca78a | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 116.9126 | 169.864 | 224.04 | 1.403 | 2.0384 | 2.6885 | 2024-01-21 04:00 | GSO_14 | br_019_21 | 3 | 9df35035-201c-43e2-9c0f-29f5652d20b6, 4f0a9de3-7d5d-4d74-841a-ad368a655ddc, 37a8aff5-f4d5-48d1-b094-f7ff7add641f | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 17.3466 | 20.6 | 25.77 | 0.20816 | 0.2472 | 0.30924 | 2024-07-15 20:00 | GSO_140 | br_020_22 | 3 | b6e43aeb-290f-443d-917c-933a0af02698, 7ac282db-535a-4cda-bcc4-f62230cc0be1, 52cf19cb-d2f9-48a0-a5d7-3d345a429c59 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 19.5682 | 24.2286 | 31.663 | 0.23482 | 0.29074 | 0.37996 | 2024-01-21 01:00 | GSO_141 | br_021_22 | 3 | 78f844cc-a5b4-4d9d-ba33-ef854d68bc8a, b6f787f7-5117-4b48-81f4-ddbe099f96d7, 0b5869b0-b194-4a18-8593-e04336ade6ea | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 43.7603 | 52.0646 | 66.049 | 0.52512 | 0.62478 | 0.79259 | 2024-07-09 | GSO_142 | br_022_22 | 3 | 5c50320a-6541-43e1-a0eb-b3cc85335f92, d8586197-7e6c-42e3-af81-89d0f76301f9, aeed6de5-7aca-4fa3-a5ca-b1f32ee717c2 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 104.0809 | 157.9957 | 211.73 | 1.249 | 1.8959 | 2.5408 | 2024-01-21 04:00 | GSO_143 | br_023_22 | 3 | b2362459-63fa-42c8-b75d-cdff666f2190, 15ee4200-f93f-4884-ab81-e52eb3d0b73c, ef7cab0d-e432-4fb1-aab4-46e5068286b4 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 4.7843 | 7.507 | 11.072 | 0.057412 | 0.090084 | 0.13286 | 2024-01-20 21:00 | GSO_144 | br_024_22 | 3 | cebe0434-4e95-4fd2-8e1e-22573f21abf5, bd7e1df8-2eb1-4167-bee8-930536ce0573, 82536324-6f01-4e66-a011-7b067544a9ac | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 36.7087 | 46.6936 | 61.202 | 0.4405 | 0.56032 | 0.73442 | 2024-01-21 04:00 | GSO_145 | br_025_22 | 3 | e8f52edb-11b6-4a01-8cb4-dde6abb481d7, 5042bbb0-cc21-499d-9106-09bd8c86b439, 039cb766-152c-4467-9ec0-94180921a657 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 44.8504 | 60.7569 | 81.348 | 0.5382 | 0.72909 | 0.97618 | 2024-01-21 04:00 | GSO_146 | br_026_22 | 3 | 45141e3c-ee87-445b-a8cd-53eaf3cf8ac6, d4d03355-620e-4213-a24e-266e873f3f79, 9c3aa61d-fdd8-4e3a-a859-786b34331466 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 13.544 | 18.0146 | 24.362 | 0.16253 | 0.21618 | 0.29234 | 2024-01-21 04:00 | GSO_147 | br_027_22 | 3 | 783419bf-1c8f-4783-a364-729c4d25328a, b05dca4b-f167-46ba-b479-77fc9d306c98, a6c68db1-932a-455f-9961-2001628d137a | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 24.9351 | 31.138 | 41.328 | 0.29922 | 0.37366 | 0.49594 | 2024-01-21 01:00 | GSO_148 | br_028_22 | 3 | f209db33-c63a-4eeb-9470-44a070b1f980, e51bd3d2-27db-4e8c-85b3-94bb36fdecb2, 9cb02ef5-7d31-4690-b5cc-1c8ff7465b94 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 4.7215 | 5.8096 | 7.637 | 0.056658 | 0.069716 | 0.091644 | 2024-01-17 05:00 | GSO_149 | br_029_22 | 3 | 54f22dd6-dae8-4d6f-8c00-4ee16cc1bce1, a7d55959-39f6-4006-8a75-2ac4375060d6, 22ef08a2-8b87-47bf-912f-a49f8dbe4e0e | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 141.6145 | 210.703 | 279.9 | 1.6994 | 2.5284 | 3.3588 | 2024-01-21 04:00 | GSO_15 | br_020_21 | 3 | 2dfc9022-cd2d-4071-a0ed-f7aa4dbf29b5, 34fb9785-294c-4580-94c1-92b57cb0e642, dd9e89fb-3f9a-4966-a494-c19ab9432a67 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 10.8391 | 13.173 | 18.338 | 0.13007 | 0.15808 | 0.22006 | 2024-01-20 11:00 | GSO_150 | br_030_22 | 3 | 99ca8035-36a9-410b-844c-06c1ddb4c66b, 97ae36fa-2e65-4c6d-8a11-b6c4ba921c0d, e18873a3-19e0-4c86-abaf-03f1ea49ef98 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 35.4508 | 45.74 | 60.865 | 0.42541 | 0.54888 | 0.73038 | 2024-01-21 04:00 | GSO_151 | br_031_22 | 3 | 5b53a681-1338-4fee-9587-71b3e65506cb, 051f7584-2010-41f8-9415-9183657a8ae0, 0542d836-ab02-49aa-a8b7-a4265443a1c4 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 0.99999 | 1.44 | 2.175 | 0.012 | 0.01728 | 0.0261 | 2024-01-20 16:00 | GSO_152 | br_032_22 | 3 | 3f75484a-66ad-416b-bdfc-429bf783f99d, ab723fc3-e0cb-4dbc-8181-5681e5ac3348, 3b38bb39-6b77-49e7-b0c7-d3c699da74dc | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 49.9449 | 58.09 | 70.101 | 0.59934 | 0.69708 | 0.84121 | 2024-07-15 10:00 | GSO_153 | br_033_22 | 3 | 0d3f8e19-033b-4d8c-a34b-ff04747bd082, 5e1ed7ac-1e16-4c51-bb12-e8d8b8c244c4, 07ea0bf7-442d-4e77-b98a-b9e2c8d50114 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 13.4266 | 16.381 | 21.737 | 0.16112 | 0.19657 | 0.26084 | 2024-01-21 04:00 | GSO_154 | br_034_22 | 3 | 6eba73e4-418d-4cd1-96b6-60b826ae450c, 70369b74-10d7-4556-af26-c0ccb8f01935, 0840b23d-66b0-48cf-856c-1f62526c7d6e | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 53.8705 | 78.859 | 106.514 | 0.64645 | 0.94631 | 1.2782 | 2024-01-21 04:00 | GSO_155 | br_01_23 | 3 | 033ba35a-0e88-44c7-ae68-9ef721532ab3, ecb9c3ef-513f-492a-821c-4bff92c1df9c, d1e45bf7-a00b-40dc-a6ec-c751080a13c9 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 132.5721 | 196.1993 | 256.642 | 1.5909 | 2.3544 | 3.0797 | 2024-01-21 04:00 | GSO_156 | br_02_23 | 3 | 2ec12710-cbb3-4ac0-ae81-f21bc775b59d, 17343a92-f390-4c00-96dd-aa4c8e6f2cf5, 12b55d36-db8c-475f-838b-08caf84b6421 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 119.8044 | 177.2403 | 240.749 | 1.4377 | 2.1269 | 2.889 | 2024-01-21 04:00 | GSO_157 | br_03_23 | 3 | d76a1565-b995-4235-9508-12ae427ed548, b96622f9-34da-4d3a-a144-a82c9e2d84a9, 962e5ace-7f13-49d9-a1bd-65973f2adfac | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 114.4589 | 170.9293 | 224.281 | 1.3735 | 2.0512 | 2.6914 | 2024-01-20 21:00 | GSO_158 | br_04_23 | 3 | 8e1d3060-4f17-4027-bb48-9326d72d1f5e, b84e6ee7-bc4b-467a-884d-e5dac0fbac0b, 5320e9a7-8d71-4f75-b9c9-3a6a37f707db | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 143.5038 | 212.7262 | 289.083 | 1.722 | 2.5527 | 3.469 | 2024-01-21 04:00 | GSO_159 | br_05_23 | 3 | 83f2cd36-180e-4d9a-9105-62a32f68ab85, 96fae847-ae01-4905-9884-47b324a88934, 2e882994-3bef-4961-988c-cd677efd6410 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 76.4704 | 107.642 | 142.457 | 0.91765 | 1.2917 | 1.7095 | 2024-01-21 | GSO_16 | br_021_21 | 3 | e4f24c66-81cd-48f4-b9a3-a8aaa9fe8c98, b5d738a6-79bd-43f6-b4e4-0fb4de70abfd, 2b3c0835-4f9e-453c-86b3-35847ab5af94 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 195.0631 | 288.77 | 387.304 | 2.3408 | 3.4652 | 4.6476 | 2024-01-21 04:00 | GSO_160 | br_06_23 | 3 | b9360429-edfb-4e59-a900-8a457dc83cba, c3e81296-2c1a-4ada-80c1-b847107d5cfb, 47f0ee8f-4288-4af4-b69a-10cebf43b645 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 2.4064 | 3.711 | 5.595 | 0.028877 | 0.044532 | 0.06714 | 2024-01-20 21:00 | GSO_161 | br_07_23 | 3 | 89a3b24a-887f-4195-8344-51f18a00dbf7, c4eee589-eb1d-4947-bc9b-3f547ec858d4, e61fb2d3-e704-4d3f-bf86-8b04c3724fd7 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 42.3363 | 62.8216 | 83.807 | 0.50804 | 0.75386 | 1.0057 | 2024-01-20 23:00 | GSO_162 | br_08_23 | 3 | f620b838-2134-4f66-a112-15e5f46318b0, f4ffa257-f9a9-48e6-8ef7-945f8e687e83, 4bfd3a0a-1178-4983-b63c-76c387206a99 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 133.7168 | 197.8567 | 264.237 | 1.6046 | 2.3743 | 3.1708 | 2024-01-18 04:00 | GSO_163 | br_09_23 | 3 | d90170cc-5eec-43f7-a5d9-cb91dca851cb, 9018e821-338d-4aa5-bb0d-3e9aa19f5a3b, 0d2e0f05-d1e8-46f2-953d-daf9b517d3b5 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 151.5207 | 224.6077 | 294.715 | 1.8182 | 2.6953 | 3.5366 | 2024-01-21 04:05 | GSO_17 | br_024_21 | 3 | 3a2af09c-baa8-4dbe-95ab-fb397036b19d, 883c59a4-ab46-45e2-b36d-e1959b7c89b6, f0a67506-31bf-4b47-9614-f559c928646a | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 99.0903 | 142.754 | 190.81 | 1.1891 | 1.713 | 2.2897 | 2024-01-21 | GSO_18 | br_025_21 | 3 | 34cac5e4-313a-4454-a92d-abc9047eadc8, 90d3f27c-2599-462f-8abb-58371a03ece5, 08eb7b30-b593-4a81-854f-d7a00d46db1e | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 209.1713 | 319.6785 | 430.217 | 2.5101 | 3.8361 | 5.1626 | 2024-01-18 04:00 | GSO_19 | br_026_21 | 3 | d5920248-7472-436e-b060-c7c2ff9ef29d, cf54e8e6-a9a5-4011-b2be-1226fbdc86cb, a03bc8be-0c7b-4ca4-b625-79f7823155e9 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 100.2277 | 144.422 | 191.098 | 1.2027 | 1.7331 | 2.2932 | 2024-01-20 08:10 | GSO_2 | br_02_21 | 3 | e16fe26a-3331-4e10-bcda-3d5b4cfc42bc, f5b81547-937f-4c70-92ba-8a0fb6594394, a28c1752-7f45-48c2-b058-b7cdc091e5d6 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 0.27289 | 0.396 | 0.639 | 0.0032747 | 0.004752 | 0.007668 | 2024-07-10 19:00 | GSO_20 | br_027_21 | 3 | 0367f0a8-b7e5-4ca5-94ae-d44fa9d00bfd, a602edca-8fde-46f7-8d51-40a5f85d6a1d, c9015052-da74-4877-bbf1-9a6c4275c44d | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 77.4498 | 106.98 | 140.144 | 0.9294 | 1.2838 | 1.6817 | 2024-01-18 04:00 | GSO_21 | br_028_21 | 3 | 6f7a2c02-ca5d-4d73-a76d-82f0fe3158c9, 39b0a939-9afe-4c84-bfda-5eec318bc35e, a49c303e-bacd-45af-8754-babfb2545a48 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 78.4727 | 112.2883 | 145.782 | 0.94167 | 1.3475 | 1.7494 | 2024-01-18 04:00 | GSO_22 | br_029_21 | 3 | f1fcda72-2c9e-4219-9a68-e344865344e1, c13495f3-7436-4771-9d8e-028fe398e677, 60e175bd-dd8d-424f-b541-e6c27675c2ee | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 53.0838 | 72.912 | 95.702 | 0.63701 | 0.87494 | 1.1484 | 2024-01-18 04:00 | GSO_23 | br_030_21 | 3 | 73114768-3396-46b2-8366-027d7f330c2a, 8896d2cc-f5f3-479a-9806-74f9830d0e65, 306a0179-6b1d-4c84-b7ad-c043978706f4 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 3.5228 | 4.229 | 5.621 | 0.042273 | 0.050748 | 0.067452 | 2024-01-20 16:00 | GSO_24 | br_031_21 | 3 | 8866ae0d-1645-4e1d-85a9-520a2b057093, 0e740376-b7d0-46f1-8238-50979ff53b86, 3abd341d-8629-4be0-888c-4405cbd18a68 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 33.8332 | 41.038 | 52.039 | 0.406 | 0.49246 | 0.62447 | 2024-01-21 04:00 | GSO_25 | br_032_21 | 3 | 8c0cf450-9297-450e-b468-8396988be79f, d4f80b32-222c-49ea-bb38-81080bcb0826, 6a2617f0-409e-448d-8ce4-c1175edcf36a | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 87.2755 | 120.2986 | 157.504 | 1.0473 | 1.4436 | 1.89 | 2024-01-21 04:00 | GSO_26 | br_033_21 | 3 | 2ded452d-d964-456f-bc61-891c5e02102b, 123d2e0f-6c7b-4b17-96d2-32d4328dde67, 06410d93-c578-4f9d-86d8-8eb333ba28c9 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 103.9897 | 149.897 | 200.381 | 1.2479 | 1.7988 | 2.4046 | 2024-01-21 04:00 | GSO_27 | br_034_21 | 3 | 6fdd1896-ad74-48a8-9816-85aa01d652d1, d428eae8-d228-4f79-b9ea-91e3a88bb229, 9dbd0f33-80b1-4155-96b0-ea2e0658e691 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 5.1894 | 6.662 | 9.836 | 0.062273 | 0.079944 | 0.11803 | 2024-01-20 11:00 | GSO_28 | br_035_21 | 3 | c3250712-a026-44dc-83b1-ab0b7bd1cef0, 4cc07d73-767d-4a92-aa56-8d6f6139433c, 4b1de06e-7ccd-42bd-ba7d-141a0d6eed10 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 88.6911 | 127.1367 | 165.623 | 1.0643 | 1.5256 | 1.9875 | 2024-01-20 05:00 | GSO_29 | br_036_21 | 3 | 53ac9d88-ec7e-422c-9547-7b65d0e1b05c, bbdb1c8c-b61b-4af3-a00d-d34e99f936e8, 37be8bbe-3fc1-42ac-aa14-512831f011d9 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 1.1766 | 1.823 | 3.187 | 0.014119 | 0.021876 | 0.038244 | 2024-07-15 08:00 | GSO_3 | br_03_21 | 3 | cabb02b4-86e3-4261-87ef-66f06902bb61, 262d1506-d23e-42d2-a938-f15cb2f35365, 861d3fe8-4f6d-46b5-bb00-6d79ddaf889d | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 78.5223 | 114.0916 | 150.566 | 0.94227 | 1.3691 | 1.8068 | 2024-01-20 09:05 | GSO_30 | br_037_21 | 3 | 80a38063-4b58-4c05-9631-c9f20eaae49f, 07afe75d-2efa-4a63-8500-f5eed954ebc4, 4339844d-f7f4-4af5-a7ce-ff1e206a4bfc | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 1.1878 | 1.851 | 3.019 | 0.014254 | 0.022212 | 0.036228 | 2024-07-15 08:00 | GSO_31 | br_038_21 | 3 | dbd51660-93ed-49dc-b484-ac1a2ff93751, c4bbbd0b-e3cc-4312-b11b-48dca067f34f, f5f51af7-9112-4286-adaa-37e4589d054a | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 58.5184 | 79.0046 | 101.472 | 0.70222 | 0.94806 | 1.2177 | 2024-01-21 | GSO_32 | br_039_21 | 3 | 049d0b94-e086-4825-b104-d454ffd3dc7c, 81e832b4-cd01-4844-b4d8-6ff81d95dbe4, 934aabc4-8b42-44e6-82dc-1b3261dc29d9 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 48.3582 | 58.461 | 73.666 | 0.5803 | 0.70153 | 0.88399 | 2024-01-20 15:00 | GSO_33 | br_040_21 | 3 | ee1a565e-ae8b-4984-9f7a-cab15b5447c3, 2bcc2cc5-82f5-4040-ac32-a00d0d07de51, d858a33a-1b66-4073-aed2-4b1a30ad837b | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 96.588 | 139.3106 | 184.726 | 1.1591 | 1.6717 | 2.2167 | 2024-01-18 04:00 | GSO_34 | br_041_21 | 3 | deb58541-2cca-43d5-86c5-55264c6041d3, 179024ab-8e49-42be-b943-761705fb5abd, 0cbf9200-98b4-43c7-934d-2cc30d8ab63b | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 146.1585 | 221.035 | 295.36 | 1.7539 | 2.6524 | 3.5443 | 2024-01-21 00:05 | GSO_35 | br_042_21 | 3 | efc37dec-e402-4c7d-81af-aa9cb2729757, d7ccdfd6-6a7d-4338-9666-e79b11f003a9, 6d4ede07-2601-4246-903b-56124df12172 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 28.5929 | 33.6716 | 41.267 | 0.34312 | 0.40406 | 0.4952 | 2024-01-20 05:00 | GSO_36 | br_043_21 | 3 | a492b914-7377-4047-b30b-90aa78dc94d3, c95edbeb-bfcc-48be-abeb-7c6ceba7bdae, 1ede274a-9246-4aec-acc0-17642c07af97 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 219.5832 | 331.3441 | 437.846 | 2.635 | 3.9761 | 5.2542 | 2024-01-20 07:05 | GSO_37 | br_044_21 | 3 | e72c363a-7373-4a30-a872-329d650d7569, 547c5604-b333-47b9-83ad-6f6fa1e88927, 53f8a349-7f61-440d-ad82-54a7f6d15d3a | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 1.3018 | 2.017 | 3.528 | 0.015622 | 0.024204 | 0.042336 | 2024-01-20 09:00 | GSO_38 | br_045_21 | 3 | 9c1dc66a-d26b-42ae-9fa5-d4e46c87f492, 31c14863-6ede-40c4-86a5-41eadc729ac2, 15e8162e-962b-481f-923b-b2fe7c7ce432 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 99.4969 | 148.6783 | 197.137 | 1.194 | 1.7841 | 2.3656 | 2024-01-21 04:00 | GSO_39 | br_046_21 | 3 | 93658bef-4bd5-4300-8424-5c388155968b, 1ef359a3-1b23-4781-b7f6-73e5a4c4559f, 77ff5585-562a-45e7-a281-464e98737abb | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 201.0527 | 310.0799 | 418.615 | 2.4126 | 3.721 | 5.0234 | 2024-01-21 04:00 | GSO_4 | br_04_21 | 3 | eda55f14-fedc-4eb6-a389-a51a43231405, 67c44f52-c49c-4993-940f-90408b4b9ae5, 1da22d5c-e6b3-4228-b327-ddf40f1f21b6 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 86.2034 | 128.3382 | 173.644 | 1.0344 | 1.5401 | 2.0837 | 2024-01-20 20:00 | GSO_40 | br_047_21 | 3 | ee7aaead-b8fb-40d3-8a03-8ab58a542fdc, 58cd6faf-3139-48ff-a9ef-b152b7ebf778, 79202d32-8dca-417a-9d59-fc14f3bcaf5f | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 74.5573 | 112.5246 | 154.92 | 0.89469 | 1.3503 | 1.859 | 2024-01-18 04:00 | GSO_41 | br_048_21 | 3 | 4f3f10ee-748f-4c21-b9c3-8ac51c8d41f6, d7d6e014-1cd2-4cb5-84bb-a00b2cad42e3, e1cda877-0a5c-49b1-bd5f-ad8449fb0e0c | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 162.5501 | 250.9263 | 339.604 | 1.9506 | 3.0111 | 4.0752 | 2024-01-21 04:00 | GSO_42 | br_049_21 | 3 | 0b1099db-07b7-4a46-831f-0ab42e837cdd, 119ef0a4-9572-4988-9343-96cacd641d11, 0e80773a-a8cc-45a5-8095-4dc9d8b00215 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 183.9062 | 273.6613 | 364.359 | 2.2069 | 3.2839 | 4.3723 | 2024-01-21 04:00 | GSO_43 | br_050_21 | 3 | 223df89f-b673-46b7-a74d-953aa3cadd02, d8ed1451-4cac-4c54-9238-07312269a3d5, d260c5dc-0f9a-4ff7-a347-cabc3421f531 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 2.2464 | 3.405 | 5.441 | 0.026957 | 0.04086 | 0.065292 | 2024-01-21 | GSO_44 | br_051_21 | 3 | ae9708d6-58e3-48d8-b469-2b865749bda5, 9de5605e-2be3-4478-8321-ec1cfdb77d3e, c206a6a0-74a2-4aa0-b700-0397b158b47c | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 135.2434 | 208.1636 | 281.092 | 1.6229 | 2.498 | 3.3731 | 2024-01-18 04:00 | GSO_45 | br_052_21 | 3 | 0a36e22d-cb96-45c8-8d47-74ede8f433bd, ac9dddc3-7cae-427c-a129-87d3008b8362, 87af0485-ac3b-4ef1-bd8e-39742bb1311b | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 124.6999 | 184.4341 | 244.562 | 1.4964 | 2.2132 | 2.9347 | 2024-01-21 04:00 | GSO_46 | br_053_21 | 3 | 425e9895-3ec9-4ecf-a2de-00e847c9f5d0, e8d1fc00-bcf6-4d05-b6b9-7f38e6915ce5, 0b8f662d-5bc3-42fe-a24e-070da09bdd80 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 18.0821 | 22.5966 | 29.491 | 0.21699 | 0.27116 | 0.35389 | 2024-07-16 03:00 | GSO_47 | br_054_21 | 3 | 44d72b2b-4d39-442e-969c-28bfa609a6ca, df231f2b-7e74-4562-8026-e0248f99acb1, 73020989-8b85-4f2f-ae5e-b46034dccc36 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 29.0078 | 33.8146 | 42.011 | 0.34809 | 0.40578 | 0.50413 | 2024-01-17 21:00 | GSO_48 | br_055_21 | 3 | caead5dd-6652-4002-9205-bf1f5d7841a2, 2756c12d-de33-427b-a20e-a7524bf8ba2a, d501232c-0e9b-4aed-b1c7-0711f51fd12c | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 10.7723 | 12.922 | 16.485 | 0.12927 | 0.15506 | 0.19782 | 2024-06-27 03:00 | GSO_49 | br_056_21 | 3 | 904a534b-b4de-47cc-9111-a909cdd75ff6, cf17223b-5ef6-40ff-aa3f-7eaa71fa5ab1, 4e486c1d-6969-466b-bb85-e868d8c69d96 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 56.6751 | 69.911 | 87.601 | 0.6801 | 0.83893 | 1.0512 | 2024-01-20 15:00 | GSO_5 | br_05_21 | 3 | 1a7b2ce3-8ce4-43f0-822c-bae88f338574, fdea0e08-11f9-40c1-bd4a-4dfdb8ea2803, 921b5057-9802-4094-b921-551288ad3d2e | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 2.2873 | 3.557 | 5.295 | 0.027447 | 0.042684 | 0.06354 | 2024-01-21 | GSO_50 | br_057_21 | 3 | 4d9bb5e2-1e06-49ed-b322-273c65c7ea12, 02cb60eb-e56b-45c0-871a-7d5da5072e9a, ceeee8fb-13b1-43c7-9caf-4433648f6846 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 20.0647 | 23.267 | 29.363 | 0.24078 | 0.2792 | 0.35236 | 2024-01-20 15:00 | GSO_51 | br_058_21 | 3 | 2dabfa67-e633-42fb-88f8-b99c8c81ce3f, 40e658e9-710a-4f81-b823-ce3b23d76208, 100d5254-7678-4ba2-a678-ffa8ba0ac8ce | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 128.7905 | 195.3616 | 264.141 | 1.5455 | 2.3443 | 3.1697 | 2024-01-21 04:00 | GSO_52 | br_059_21 | 3 | 148e241f-8dca-40c2-bc4c-9bba11acb600, 740ff96c-6171-4486-bb6a-904851da7f68, 54cc7298-372e-4f46-9c94-d78d3e7e3368 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 60.036 | 83.116 | 110.049 | 0.72043 | 0.99739 | 1.3206 | 2024-01-21 04:00 | GSO_53 | br_060_21 | 3 | 77c08208-993b-4559-b9e2-42c4c772997c, 4b800952-fa1b-4668-ba63-4244710bab3c, 3b012ead-fe04-4b66-8c50-59d42334a89c | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 209.0296 | 315.702 | 423.322 | 2.5084 | 3.7884 | 5.0799 | 2024-01-21 04:00 | GSO_54 | br_061_21 | 3 | c70624cc-3511-421e-bcd3-4f74ee43c80f, 0c2d5da7-8b73-4e99-a2ec-e1bd371c44f1, b486465e-b5c3-4f46-9979-e961ceb9df52 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 10.2891 | 15.9266 | 22.373 | 0.12347 | 0.19112 | 0.26848 | 2024-01-20 10:00 | GSO_55 | br_062_21 | 3 | 55b291eb-5761-4e7f-8635-63057f856791, 0d627f19-7146-43b0-9f7b-bac68e9966db, efb7b851-1f6e-4084-9dd6-5a62049b7654 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 37.6367 | 51.681 | 67.431 | 0.45164 | 0.62017 | 0.80917 | 2024-01-21 04:00 | GSO_56 | br_063_21 | 3 | d5be6516-e14a-46ab-a02a-0650b74a5159, 748858e9-a0e0-4bc6-a0b7-f4e67d7c9ecd, 620a8a0d-bcbd-4f44-be97-24244e308366 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 44.3296 | 62.5339 | 86.055 | 0.53196 | 0.75041 | 1.0327 | 2024-01-20 10:05 | GSO_57 | br_08_21 | 3 | 27046833-12e1-4f55-aeb1-743d3fddc9b4, e2d61ac2-432e-446d-b560-32b75aebceed, 08dafb35-ef6e-48c6-89ef-1f3412fa5f7e | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 166.8301 | 255.1588 | 347.154 | 2.002 | 3.0619 | 4.1658 | 2024-01-21 04:00 | GSO_58 | br_09_21 | 3 | cd71f269-7897-4746-9a77-c6bc730114fe, ff232009-b42f-4f71-a769-88a952701609, b8c6df33-b602-4d1c-9dda-e52dfeb41665 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 128.7271 | 198.0846 | 266.309 | 1.5447 | 2.377 | 3.1957 | 2024-01-21 04:00 | GSO_59 | br_010_21 | 3 | 4529fb6d-421e-4f02-9b11-c956a4443f8e, 1231155d-ed13-4563-8801-fa08388d11cd, 1b822839-e89f-49f2-b2a9-69df27011548 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 36.9389 | 53.0836 | 68.881 | 0.44327 | 0.637 | 0.82657 | 2024-01-18 04:00 | GSO_6 | br_06_21 | 3 | 145f4423-0120-41c0-a961-6f6b453e91a7, 120599d7-eee0-4966-bd20-36d9e2e8b089, a5d804f2-bcf0-4e70-ad7f-9ffc889ca71a | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 115.5942 | 174.692 | 238.251 | 1.3871 | 2.0963 | 2.859 | 2024-01-21 04:00 | GSO_60 | br_011_21 | 3 | 229fce16-0cb2-401d-957b-9d0d3c2ac1cc, fc187080-4278-4699-8d7f-ded10dc27448, 52980b4f-3c73-4c68-8631-e69ccc722a34 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 211.8673 | 326.8333 | 433.485 | 2.5424 | 3.922 | 5.2018 | 2024-01-20 09:00 | GSO_61 | br_012_21 | 3 | bdb558af-9d90-4dcd-870e-28a86925b8cc, 192ef0e0-59f5-4932-a625-7e967573ec09, 69c0c6b0-aa07-4cdc-9789-b51b223584c4 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 34.1079 | 52.4066 | 71.266 | 0.40929 | 0.62888 | 0.85519 | 2024-01-21 04:00 | GSO_62 | br_013_21 | 3 | 2c8910bb-0c41-4c36-8a5f-d8ffc5e65938, 3f59d58a-b780-49d5-86ae-b0b0f01c076d, decddce1-9f0e-44c6-a3bd-24fdb9cf1a60 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 4.9355 | 7.544 | 10.321 | 0.059226 | 0.090528 | 0.12385 | 2024-07-15 09:00 | GSO_63 | br_014_21 | 3 | 676b1650-044c-43bf-bea6-3dced2a612c6, abbc8c51-7785-4d04-a735-eb965d943d5a, 167b629e-ae1a-4acd-a435-a9faf6b8f0b1 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 105.6309 | 151.3556 | 198.709 | 1.2676 | 1.8163 | 2.3845 | 2024-01-21 04:00 | GSO_64 | br_064_21 | 3 | aa668afa-9003-4c02-b068-76a760cba7c4, 8ec9092e-c513-4856-b139-17b0f244b287, 96d7ca9d-a8a7-4620-beb4-015993e1495f | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 11.8091 | 14.098 | 17.976 | 0.14171 | 0.16918 | 0.21571 | 2024-01-21 04:00 | GSO_65 | br_065_21 | 3 | a8421f63-1fb7-4386-80d1-558a9049f658, c0caf65c-2d30-471b-9a8c-36e1484ba877, a2d74127-91f7-4d1b-a98b-b3f287f80eec | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 113.5657 | 169.5323 | 224.767 | 1.3628 | 2.0344 | 2.6972 | 2024-01-21 04:00 | GSO_66 | br_066_21 | 3 | aa212fd9-92d5-4c56-9a9e-3014ccc9a7ce, 0cbf5c43-696f-40b4-ab01-fd3dfd670388, 3f826b2c-284b-4880-a9f1-d5554c1e5213 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 124.1763 | 178.0886 | 238.716 | 1.4901 | 2.1371 | 2.8646 | 2024-01-21 04:00 | GSO_67 | br_067_21 | 3 | fddc71cc-3766-4601-9ca7-c2caab3c7c4d, 5aed073b-49c0-4020-b105-f7e28cfd41ed, 4b3c48a3-9a69-47a9-b110-7d0b18cc7f06 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 107.0124 | 150.7806 | 195.762 | 1.2841 | 1.8094 | 2.3491 | 2024-01-21 04:00 | GSO_68 | br_068_21 | 3 | 6abb0433-d7c1-47cb-b500-310c0966ae29, b14a51cb-21cb-48f4-91a6-564663c5a923, f2986696-35a7-4d1e-a7dd-8b01d8d6756a | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 24.2321 | 31.856 | 41.103 | 0.29078 | 0.38227 | 0.49324 | 2024-01-21 04:00 | GSO_69 | br_069_21 | 3 | 16e446fe-cce5-4d4b-abd0-d9bf98278835, 3f69baec-6464-4c01-91c1-171903c224f7, 9255af13-2569-446c-b326-8de2942e3a26 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 2.4232 | 3.9 | 6.118 | 0.029079 | 0.0468 | 0.073416 | 2024-01-21 | GSO_7 | br_07_21 | 3 | 874fce3a-0ddc-405e-8b4d-496bf1208ffa, 7c4e0a27-0ba8-4589-8efa-9d78e22aeea7, b3997dcd-0479-4422-904f-1e86aedb3b49 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 29.4202 | 35.0057 | 43.007 | 0.35304 | 0.42007 | 0.51608 | 2024-01-20 22:00 | GSO_70 | br_070_21 | 3 | ff4d78df-a97d-465a-9270-6b140f05b7ee, 96d35f0d-746b-4c76-8d6d-a22dac3dcfaa, 7a4e8fb6-f007-4d77-bfcb-6a0b0e18561c | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 231.4489 | 347.345 | 458.37 | 2.7774 | 4.1681 | 5.5004 | 2024-01-21 02:00 | GSO_71 | br_071_21 | 3 | 7dec81b6-3b82-498d-bfaa-f44bf5d9581d, 4ff8b560-0d8d-46ca-aa4f-48e616d84a8c, 828a3353-455f-43cc-a9b0-71980deae8fd | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 79.2778 | 110.32 | 145.087 | 0.95133 | 1.3238 | 1.741 | 2024-01-21 04:00 | GSO_72 | br_072_21 | 3 | 2f6074d9-3367-424b-9912-3b54ba3842dc, 5be2e72a-f9e3-4662-bcdd-f6914b127473, ceb3c16f-b2c1-4384-83e5-47eb8d9787a9 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 4.4614 | 5.51 | 8.158 | 0.053536 | 0.06612 | 0.097896 | 2024-01-20 20:00 | GSO_73 | br_073_21 | 3 | dd7e3ea9-a097-46d9-ba3d-e976877c959f, dc0e22aa-9b17-4812-81b9-805e6e2fcea4, 0a5bd7a0-8dda-4ea9-8140-b43dcad4334a | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 59.4096 | 72.9743 | 87.794 | 0.71292 | 0.87569 | 1.0535 | 2024-01-20 23:25 | GSO_74 | br_074_21 | 3 | 4cb9db9e-b9c3-473e-878d-2df2932f4dcf, 2be1e40d-d971-44eb-9f8e-1f362b00491f, b4794b85-7397-40b2-a7b2-50c82c66983d | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 35.9045 | 48.781 | 67.545 | 0.43085 | 0.58537 | 0.81054 | 2024-01-18 04:00 | GSO_75 | br_075_21 | 3 | 74ba07cb-a526-4618-b499-1a430d0286b7, dc09ae69-e1ee-4c83-9c04-e09da568c6ab, 8cfdaf81-8e59-4486-ba2f-4e450a23c876 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 1.98 | 3.0756 | 4.402 | 0.02376 | 0.036908 | 0.052824 | 2024-01-20 23:00 | GSO_76 | br_076_21 | 3 | 89cbe802-faf3-4709-b370-afa1154a5b70, fd14c6a3-6658-4039-a0b8-c00ab26e307c, a61580ad-490f-42dd-919c-3cfdfb775908 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 219.1131 | 326.4566 | 429.952 | 2.6294 | 3.9175 | 5.1594 | 2024-01-21 04:00 | GSO_77 | br_077_21 | 3 | 04933340-1f7e-4732-a170-31c687c8d71e, da253492-f9e5-4572-a892-8cf7206f5562, 55611621-48c6-40ab-afb0-d76e41a0d5de | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 14.1194 | 20.5536 | 27.412 | 0.16943 | 0.24664 | 0.32894 | 2024-01-18 04:00 | GSO_78 | br_078_21 | 3 | c0ddba19-fbd3-4341-bb7c-f8d96301d889, 648e5aaa-f39d-4756-9d09-ca5503bbc225, 838a2e79-8d23-4760-9eab-eb6ed2d38b4c | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 71.3217 | 95.6596 | 124.596 | 0.85586 | 1.1479 | 1.4952 | 2024-01-21 04:00 | GSO_79 | br_079_21 | 3 | dfd547e9-e06c-4fe7-8842-913f0b3f7d52, f68a1c8a-5406-4783-b8ae-a255bce0e795, 02d224d1-8d1b-45bb-98ed-ebc20c74318a | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 1.8934 | 2.873 | 4.851 | 0.022721 | 0.034476 | 0.058212 | 2024-01-20 17:00 | GSO_8 | br_022_21 | 3 | 9e0bf50d-94bd-4e5d-9a43-95a506f4c534, 14a29c10-6f6b-4045-834c-a8cdccfa7fe8, 674756f5-28ec-40f8-8ece-cd6c8a394c18 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 88.6299 | 123.794 | 162.143 | 1.0636 | 1.4855 | 1.9457 | 2024-01-21 02:00 | GSO_80 | br_080_21 | 3 | 4fb9d568-cec8-4d2c-b185-503c8441a94f, 48527915-ef6b-4d16-9525-f6d17fae71ba, e4842198-5ba7-4542-9415-20f0a87511ac | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 97.4105 | 132.4067 | 172.497 | 1.1689 | 1.5889 | 2.07 | 2024-01-21 04:00 | GSO_81 | br_081_21 | 3 | 9a5c0969-f68d-4cea-a13e-ef351a3d3730, a8a2fc9d-e642-4554-abad-f2610eb29b51, 27bb62b3-e552-4996-874d-31dcad547987 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 137.0611 | 209.2763 | 282.079 | 1.6447 | 2.5113 | 3.3849 | 2024-01-21 | GSO_82 | br_082_21 | 3 | a890d29a-0380-4cd2-8cff-f9826e3ff07b, 918cae00-7f70-4556-9d40-35da1f05977d, 93c33640-e4a0-470f-a164-89c99ae69984 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 174.186 | 263.1632 | 350.031 | 2.0902 | 3.158 | 4.2004 | 2024-01-18 04:00 | GSO_83 | br_083_21 | 3 | af9148e3-1b4f-4f27-b409-3654c3f953f5, 48c0048d-65ab-48a8-8cd9-833258bee864, 8c265c14-8e0f-4c74-9519-46da2dff7cd1 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 14.425 | 21.864 | 30.241 | 0.1731 | 0.26237 | 0.36289 | 2024-01-20 06:05 | GSO_84 | br_084_21 | 3 | d4454767-7751-4c58-9cbd-79e943f45acf, 4cc5af87-12cf-4fd1-a89c-0318dc07c068, b63c8e73-fffc-4e69-ad08-995c149ebeaa | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 38.9205 | 50.5416 | 65.364 | 0.46705 | 0.6065 | 0.78437 | 2024-01-21 04:00 | GSO_85 | br_085_21 | 3 | 6fcd01be-d3d1-4df7-bec8-4f8b1042aac0, 4fc59078-b2c4-42d5-b129-faa7a3f54cac, ac192c64-42ef-423f-814b-c8b837b8f5d2 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 89.6995 | 126.522 | 163.401 | 1.0764 | 1.5183 | 1.9608 | 2024-01-20 23:00 | GSO_86 | br_086_21 | 3 | 492c962b-e2b7-4edd-afe9-20606e4114f6, 6182a628-fb52-41b9-8b93-90488a51a0fe, 6927b6e8-4d14-436e-8236-19dc4cdad934 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 87.3478 | 117.9236 | 150.134 | 1.0482 | 1.4151 | 1.8016 | 2024-01-21 04:00 | GSO_87 | br_087_21 | 3 | e7689375-373b-4d7a-b001-0fa11239a327, 589e4f98-7742-4541-b2c3-6b108b7f9d4d, d9c84a3d-b565-4642-a7d4-3c9df307b1c8 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 63.4485 | 86.0716 | 113.438 | 0.76138 | 1.0329 | 1.3613 | 2024-01-18 04:00 | GSO_88 | br_088_21 | 3 | 93986b58-113b-4798-b153-eda6e8924352, 73bea406-8df3-48d6-99e8-780c9ba74d8d, b1fd8626-d75b-4f57-95d8-5e0f995f6548 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 64.1018 | 84.414 | 109.301 | 0.76922 | 1.013 | 1.3116 | 2024-01-21 04:00 | GSO_89 | br_089_21 | 3 | d629f58a-fb37-4300-b174-4dadcd7fdef5, c6e42508-1e1b-4a8d-ad6c-5ed17230666d, a59c7bce-fb93-4255-8dac-4024e2c3a1c9 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 1.1873 | 1.899 | 3.204 | 0.014247 | 0.022788 | 0.038448 | 2024-01-21 01:00 | GSO_9 | br_023_21 | 3 | c7e10126-bd63-4bd3-96ab-07587af29378, f631ee12-3be7-417b-ad19-901e9ad68684, 9b89dc0e-e258-4610-b60b-484b1b02a312 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 34.5538 | 41.669 | 52.553 | 0.41465 | 0.50003 | 0.63064 | 2024-01-20 16:00 | GSO_90 | br_090_21 | 3 | ab8abf18-0128-43c3-8213-8fcc30f583d2, 59f75e54-a46d-4153-8855-555945d0a888, f35586be-8010-4ad3-b579-d95b9825cae5 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 80.7802 | 105.9423 | 140.175 | 0.96936 | 1.2713 | 1.6821 | 2024-01-21 | GSO_91 | br_091_21 | 3 | 11eec288-b107-4b0d-8513-8e0e8b097ff9, 66b6c9ff-fe2f-4708-83aa-26715afe7d27, 2494a26c-ddcb-40f8-8643-7c936424dfc0 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 42.2238 | 51.503 | 64.096 | 0.50669 | 0.61804 | 0.76915 | 2024-01-21 04:00 | GSO_92 | br_092_21 | 3 | a984179e-ff24-4a5b-9bff-44fa02582a26, fbe573a4-e81d-4315-b9c9-510a65c98be6, 9e7256be-44ac-40e3-95c4-e604f1b5b6ea | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 38.0767 | 46.28 | 58.531 | 0.45692 | 0.55536 | 0.70237 | 2024-01-21 04:00 | GSO_93 | br_093_21 | 3 | ac7b38f5-50a1-4cc6-bab1-d609ee8f92a4, 75f25960-b76b-4ea6-95b3-22351b5c7fde, 531ef22d-48aa-4ee9-88be-bf0b21101c8d | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 27.5543 | 33.871 | 41.978 | 0.33065 | 0.40645 | 0.50374 | 2024-01-18 04:00 | GSO_94 | br_094_21 | 3 | f0bd6ef7-dacb-46d2-ad18-589db990b13a, a82b3639-950c-4ba5-8e39-502e435ad83a, c177967e-e6f6-4644-aa50-326a9ebe3d00 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 142.3321 | 212.2589 | 285.763 | 1.708 | 2.5471 | 3.4292 | 2024-01-18 04:00 | GSO_95 | br_095_21 | 3 | 859a9ae6-4d75-45f7-af3f-1d1c2c11b96f, ad766f3b-7d19-4707-8a90-38f818011b97, c6b6dfcf-55ed-45e7-9e6a-1ed25774a828 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 67.699 | 89.0123 | 113.163 | 0.81239 | 1.0681 | 1.358 | 2024-01-20 06:00 | GSO_96 | br_096_21 | 3 | 1b5731fb-ced8-4f58-b1ab-d0ee4f8ea875, fcbaf392-5711-44ee-86c0-792317753d2f, fad28770-b3f6-4478-87a1-3b095d264a87 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 175.9206 | 263.5666 | 347.515 | 2.111 | 3.1628 | 4.1702 | 2024-01-21 04:00 | GSO_97 | br_098_21 | 3 | 003a8d77-c248-43c2-af2f-1f5f30595e2b, b3f7a58f-66bb-4c73-a447-90250ee96029, 3b017716-3815-48f3-bf37-e278bd03cc9d | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 224.6811 | 345.1416 | 472.836 | 2.6962 | 4.1417 | 5.674 | 2024-01-21 04:00 | GSO_98 | br_099_21 | 3 | e19d273e-4ce0-462d-9501-16552f6df1a5, 74d4c75b-fdbd-4356-81ba-130cbea2e530, 43272e40-5062-4f3e-9a6d-0899fa207db5 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 193.545 | 282.449 | 377.087 | 2.3225 | 3.3894 | 4.525 | 2024-01-21 04:00 | GSO_99 | br_0100_21 | 3 | a3c897bb-ba13-4a0b-af16-81acabf20ccd, 667e5144-bfb1-4543-a81f-7a88e26190c7, 9d892d7c-e138-4107-8084-bbde890e1cc4 | A, B, C | OK

## SCADA_Voltage_Phases
Observations | FirstTimestamp | LastTimestamp | AverageVoltage | MedianVoltage | P05Voltage | P95Voltage | MinimumVoltage | MaximumVoltage | grid_id | BreakerElementID | DataSourceID | FriendlyID | Phase | VoltageSCADAStatus
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7216.7574 | 7208.094 | 7160.1403 | 7291.9212 | 7042.119 | 7396.429 | GSO_1 | br_01_21 | b1e8c057-fded-4c70-8f86-a33db401b6d1 | br_01_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7212.1779 | 7206.466 | 7157.5324 | 7276.938 | 7025.575 | 7379.073 | GSO_1 | br_01_21 | ba6970aa-af7f-428e-9a4f-7826618684b4 | br_01_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7217.5801 | 7208.952 | 7160.058 | 7293.2092 | 7032.508 | 7404.224 | GSO_1 | br_01_21 | ea496fcb-6216-4db1-9885-1da5dbf70fa2 | br_01_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.7135 | 7208.1125 | 7157.2806 | 7287.425 | 7036.492 | 7360.154 | GSO_10 | br_015_21 | d140ab36-31a8-40c7-820d-c3a2df82604a | br_015_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7213.7068 | 7206.745 | 7159.8699 | 7278.9536 | 7029.851 | 7347.808 | GSO_10 | br_015_21 | b315ece6-7341-4cdf-a1c9-70a8dbfe93ff | br_015_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7214.3869 | 7207.6315 | 7158.904 | 7281.2527 | 7029.711 | 7336.52 | GSO_10 | br_015_21 | 396f73e2-6041-46ac-90d5-a9439aef50d8 | br_015_21.C | C | OK
0 | [8 empty] | GSO_100 | br_097_21 | 564551fe-ec45-4b6c-a7df-ebfa29a0a242 | br_097_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7217.1997 | 7208.615 | 7158.3004 | 7292.7356 | 7025.233 | 7359.802 | GSO_100 | br_097_21 | 3125b67a-cbd0-47b3-94b6-a60b38de7e8b | br_097_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7216.2955 | 7208.341 | 7162.5811 | 7286.27 | 7002.413 | 7364.021 | GSO_100 | br_097_21 | cc6f9a7e-ea1b-4cdb-9c85-6c672b845068 | br_097_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7217.5121 | 7209.406 | 7154.528 | 7295.7893 | 7032.468 | 7354.335 | GSO_101 | br_0101_21 | f32aafa6-4f97-40b9-85a1-6516b7a34fb0 | br_0101_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.0523 | 7207.648 | 7161.6221 | 7283.803 | 7015.109 | 7367.048 | GSO_101 | br_0101_21 | 8f1038a0-f3d5-4f15-bedf-b8f1215601f3 | br_0101_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7214.917 | 7207.6155 | 7160.318 | 7283.3026 | 7041.751 | 7397.203 | GSO_101 | br_0101_21 | 6c559f06-b888-4a9d-ba0f-901b0b19b354 | br_0101_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.2337 | 7207.745 | 7163.308 | 7282.8733 | 7050.956 | 7388.052 | GSO_102 | br_0102_21 | aaef163c-bdc4-464e-9864-b0c0ebdf8662 | br_0102_21.A | A | OK
0 | [8 empty] | GSO_102 | br_0102_21 | 3f11f59f-b6f2-44fe-8a16-f4a87144ca07 | br_0102_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7218.3094 | 7207.7995 | 7174.9384 | 7289.008 | 7054.77 | 7390.816 | GSO_102 | br_0102_21 | 58383f3b-39ee-41c1-9a45-f21c6b309b7c | br_0102_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7216.7061 | 7208.768 | 7154.8283 | 7293.1092 | 7034.039 | 7340.187 | GSO_103 | br_0103_21 | d5fd099c-84d4-4965-91b3-bbc0c68d61d1 | br_0103_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7218.8255 | 7209.816 | 7155.0603 | 7300.5822 | 7030.722 | 7352.907 | GSO_103 | br_0103_21 | d53e58ae-230d-449a-b78d-6b5cfa60f56b | br_0103_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7217.2199 | 7209.4065 | 7151.807 | 7296.9813 | 7021.579 | 7342.457 | GSO_103 | br_0103_21 | a3539c00-7186-4684-93db-03123790cf12 | br_0103_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7217.3862 | 7209.254 | 7153.0402 | 7297.3336 | 7017.727 | 7346.738 | GSO_104 | br_0104_21 | dbaf906f-b53b-4b15-bd48-42442608214a | br_0104_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7217.7692 | 7209.5475 | 7154.6534 | 7296.321 | 7032.591 | 7352.66 | GSO_104 | br_0104_21 | 0256f17b-1fde-4e5f-aa42-6a293aa27e64 | br_0104_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7218.0364 | 7209.387 | 7154.0648 | 7299.415 | 7030.547 | 7352.079 | GSO_104 | br_0104_21 | 4922eba1-a72a-4e22-8a37-912d5f9ac46b | br_0104_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7219.6787 | 7209.899 | 7156.0454 | 7304.0023 | 7038.264 | 7361.976 | GSO_105 | br_0105_21 | 3943a935-55e7-44b5-a61e-08789763be18 | br_0105_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7218.4431 | 7209.6395 | 7156.994 | 7297.9776 | 7041.808 | 7350.941 | GSO_105 | br_0105_21 | 11bf4c6d-205c-4caf-b572-7246ab210632 | br_0105_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7217.3479 | 7209.3655 | 7153.4294 | 7296.4739 | 7026.907 | 7349.655 | GSO_105 | br_0105_21 | 98dc0614-4560-469e-93e2-97b3c41b5000 | br_0105_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7219.34 | 7209.2695 | 7161.0111 | 7299.2837 | 7046.926 | 7388.014 | GSO_106 | br_0106_21 | 1523bf59-c426-49d7-add2-e9b831978748 | br_0106_21.A | A | OK
0 | [8 empty] | GSO_106 | br_0106_21 | e37ebffe-ff65-4277-a7e0-2315cac8c267 | br_0106_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7220.2115 | 7209.545 | 7162.2897 | 7301.3522 | 7029.431 | 7401.993 | GSO_106 | br_0106_21 | f0643cc7-b03a-4328-82d5-2924a650f97f | br_0106_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7208.5988 | 7203.313 | 7170.413 | 7258.7276 | 7051.932 | 7387.587 | GSO_107 | br_0107_21 | 4113937f-0ce2-415a-9249-ce7327d121f7 | br_0107_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7206.0329 | 7201.489 | 7170.9994 | 7251.96 | 7036.44 | 7392.051 | GSO_107 | br_0107_21 | 5d59abb9-0bac-4fa7-a891-4e9d4e794c88 | br_0107_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7206.3914 | 7202.251 | 7166.9631 | 7254.7026 | 7022.37 | 7395.225 | GSO_107 | br_0107_21 | b1339292-267a-4146-8873-ecfc9cb1a82e | br_0107_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7217.0711 | 7209.033 | 7152.0488 | 7297.4397 | 7020.781 | 7374.353 | GSO_108 | br_0108_21 | e867a5e4-d5f1-4fdf-98c8-da37424315a6 | br_0108_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7218.7109 | 7209.722 | 7153.8113 | 7300.975 | 7018.219 | 7373.962 | GSO_108 | br_0108_21 | c0036365-6459-4cc7-b7b1-ed8933515338 | br_0108_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7219.7267 | 7209.5115 | 7156.2754 | 7303.3036 | 7027.699 | 7377.273 | GSO_108 | br_0108_21 | 1886a888-6918-466c-929d-0c8f16370dda | br_0108_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7219.2755 | 7209.8155 | 7158.4793 | 7300.235 | 7039.526 | 7361.076 | GSO_109 | br_0109_21 | 0c75d1f1-8237-436b-a2c8-c9b6fdc7a116 | br_0109_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7219.1168 | 7210.0965 | 7154.3264 | 7301.8462 | 7013.79 | 7376.767 | GSO_109 | br_0109_21 | ec8ad3c4-a39d-4acb-8788-e7435be58cb7 | br_0109_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7216.3438 | 7208.805 | 7159.2487 | 7287.9757 | 7027.561 | 7356.999 | GSO_109 | br_0109_21 | e6350d88-56d8-492b-bc1e-dcd90fcca31f | br_0109_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.4504 | 7207.702 | 7158.1775 | 7286.1987 | 7031.483 | 7361.658 | GSO_11 | br_016_21 | 469868d0-2f60-42bd-aa67-be26d6eae0eb | br_016_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7213.2752 | 7206.957 | 7156.9751 | 7279.2486 | 7031.188 | 7341.442 | GSO_11 | br_016_21 | 9cdbec33-569a-438b-ac44-23b272ad169b | br_016_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7212.0148 | 7206.058 | 7155.8687 | 7276.7859 | 7021.29 | 7337.258 | GSO_11 | br_016_21 | dfea635f-2a86-40f1-9367-d78b6dd6c309 | br_016_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7217.5903 | 7209.105 | 7156.5028 | 7295.5812 | 7038.304 | 7349.554 | GSO_110 | br_0110_21 | 1e111a58-963a-4906-b1f6-e2d03049b19a | br_0110_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7219.8296 | 7209.9735 | 7156.978 | 7303.0236 | 7039.344 | 7366.994 | GSO_110 | br_0110_21 | 8a0dd243-2512-4f92-afd7-db6e79d7496e | br_0110_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7218.2535 | 7209.4615 | 7154.3927 | 7299.153 | 7032.828 | 7357.523 | GSO_110 | br_0110_21 | ca02189c-f89b-417b-a469-ef0366d6da6e | br_0110_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7203.5009 | 7203.571 | 7153.9956 | 7245.1713 | 7030.373 | 7294.406 | GSO_111 | br_0111_21 | f8549391-d242-43a9-9a34-33f872443611 | br_0111_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7202.15 | 7203.106 | 7152.4801 | 7241.312 | 7022.906 | 7274.06 | GSO_111 | br_0111_21 | 3488e4fc-fa59-4bcf-b967-3b7a890f6c3c | br_0111_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7218.7898 | 7209.4925 | 7158.0204 | 7298.7433 | 7035.072 | 7370.484 | GSO_111 | br_0111_21 | e60c92cc-e283-4345-87b0-ba3a9fd78005 | br_0111_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7213.0353 | 7205.793 | 7164.6551 | 7277.0432 | 7048.228 | 7376.669 | GSO_112 | br_0112_21 | 407ea9ca-a495-4119-a139-1d1233852fdc | br_0112_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7197.6072 | 7200.156 | 7164.223 | 7221.2173 | 7046.776 | 7273.008 | GSO_112 | br_0112_21 | 99fe4744-38fc-4467-902b-d97556b6d295 | br_0112_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7213.2535 | 7205.743 | 7166.0987 | 7277.3857 | 7047.055 | 7396.822 | GSO_112 | br_0112_21 | e1fd2b67-b072-4575-9f5d-c24af5f52b11 | br_0112_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7205.9252 | 7202.1105 | 7167.059 | 7252.6706 | 7003.726 | 7393.634 | GSO_113 | br_0113_21 | f8ddca03-2f28-483b-97fe-a4538d6c4e2b | br_0113_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7209.7353 | 7203.745 | 7167.5237 | 7265.2236 | 7042.923 | 7389.602 | GSO_113 | br_0113_21 | a9bc380c-ca71-4a2b-b314-0f03f9f76581 | br_0113_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7207.5169 | 7202.424 | 7166.094 | 7260.6206 | 7024.062 | 7389.029 | GSO_113 | br_0113_21 | bdf27366-2b21-4e21-8946-86b299b81d14 | br_0113_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7217.5945 | 7209.171 | 7158.642 | 7293.6552 | 7034.026 | 7359.088 | GSO_114 | br_0114_21 | 34c2c476-7801-4ae6-ba1f-ca1a602925b3 | br_0114_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7214.2928 | 7207.837 | 7157.2792 | 7282.2633 | 7034.57 | 7348.25 | GSO_114 | br_0114_21 | 156d4241-1525-4089-8367-effd61eb4969 | br_0114_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7220.6173 | 7210.48 | 7156.8274 | 7305.5036 | 7037.237 | 7375.435 | GSO_114 | br_0114_21 | 3128527e-a25b-4b2c-9d88-b40eb600580e | br_0114_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.565 | 7208.0985 | 7157.2431 | 7286.585 | 7021.72 | 7339.975 | GSO_115 | br_0115_21 | d3645b59-a71d-4848-9deb-b044c307c52a | br_0115_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7217.2403 | 7208.642 | 7156.9744 | 7293.8006 | 7023.039 | 7347.676 | GSO_115 | br_0115_21 | 820fcd78-48b0-467d-8925-554a0333f605 | br_0115_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7217.3271 | 7208.5415 | 7159.5944 | 7292.2603 | 7049.57 | 7347.212 | GSO_115 | br_0115_21 | 58786ac1-7ac2-4287-bd8f-add68a4ea208 | br_0115_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7212.1272 | 7205.4815 | 7163.6835 | 7274.8086 | 7032.298 | 7378.893 | GSO_116 | br_0116_21 | 2a93f307-f837-4de0-9089-b308bde0f0fd | br_0116_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.2665 | 7207.5875 | 7159.7711 | 7285.5339 | 7015.91 | 7380.441 | GSO_116 | br_0116_21 | ba9bd088-fa13-4d76-ba16-6dba6a8b45de | br_0116_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7216.3624 | 7208.233 | 7158.2792 | 7289.1399 | 7042.425 | 7351.179 | GSO_116 | br_0116_21 | e9542020-950f-403c-af95-965f8434a9f8 | br_0116_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.3729 | 7207.643 | 7154.8054 | 7289.599 | 7028.852 | 7346.952 | GSO_117 | br_0117_21 | 20ca2ff7-1194-405d-9098-d4544944a36d | br_0117_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.3451 | 7208.187 | 7155.5291 | 7287.5516 | 7030.75 | 7336.216 | GSO_117 | br_0117_21 | 127d58d0-da5d-47a0-a219-b8c1834a136a | br_0117_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7217.8339 | 7208.8485 | 7156.4973 | 7296.203 | 7034.986 | 7350.549 | GSO_117 | br_0117_21 | 79b91384-9645-42ed-940d-37fdffcc31a0 | br_0117_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.3234 | 7207.7875 | 7160.0714 | 7284.7982 | 7046.957 | 7388.318 | GSO_118 | br_0118_21 | b2273af8-cb6e-4178-93e7-36fab6dbf2c0 | br_0118_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7212.7426 | 7206.702 | 7163.0617 | 7273.2416 | 7054.647 | 7348.819 | GSO_118 | br_0118_21 | cb23fba1-b5a8-477f-b388-dcbc14cf56b2 | br_0118_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7216.9467 | 7208.834 | 7156.5658 | 7292.1447 | 7021.733 | 7349.313 | GSO_118 | br_0118_21 | 7b9e37f6-9e61-405e-8bc5-9d79097397f4 | br_0118_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7218.6921 | 7210.072 | 7159.6174 | 7295.6686 | 7027.404 | 7371.066 | GSO_119 | br_0119_21 | 1a46aa48-ac4e-4046-aa43-a61c07c816d6 | br_0119_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7216.6741 | 7207.9705 | 7163.2609 | 7287.6112 | 7051.481 | 7370.381 | GSO_119 | br_0119_21 | faec1da7-65b2-4b86-be90-e4357dfde1ce | br_0119_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7217.545 | 7208.8175 | 7162.5343 | 7290.7323 | 7031.642 | 7375.598 | GSO_119 | br_0119_21 | 3aad3364-ed36-4087-b7d0-6d3b3fa6f823 | br_0119_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7217.2488 | 7208.608 | 7158.415 | 7292.8687 | 7027.606 | 7344.314 | GSO_12 | br_017_21 | e263a729-e360-4716-9561-679bf6b5d16a | br_017_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7216.1738 | 7208.311 | 7155.9948 | 7290.073 | 7033.07 | 7344.067 | GSO_12 | br_017_21 | ede6f7c6-f426-4d65-bfe0-7dac24a794c1 | br_017_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.3203 | 7207.841 | 7154.6751 | 7288.2626 | 7027.993 | 7342.148 | GSO_12 | br_017_21 | 4c1ed359-972e-4bdd-a0cd-1159d7a32c07 | br_017_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7214.2313 | 7206.3025 | 7165.2033 | 7280.4042 | 7039.781 | 7394.362 | GSO_121 | br_01_22 | 0eb7ef08-0441-4661-84d4-63da9255ea41 | br_01_22.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7213.0706 | 7205.7265 | 7162.4387 | 7279.1977 | 7029.038 | 7396.153 | GSO_121 | br_01_22 | 36cfcc10-f3c4-4989-ae21-5fdd2aa20962 | br_01_22.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7214.4454 | 7207.3665 | 7160.5141 | 7282.7945 | 7035.078 | 7386.541 | GSO_121 | br_01_22 | 423b0798-4793-4a14-a787-72bb51fb4cef | br_01_22.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7206.9294 | 7202.101 | 7167.1137 | 7257.117 | 7033.548 | 7376.914 | GSO_122 | br_02_22 | e63f1c25-1cac-49ae-9929-f96fa015f74e | br_02_22.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7206.9385 | 7202.137 | 7166.3363 | 7258.021 | 7042.809 | 7386.879 | GSO_122 | br_02_22 | 4fa57e43-e6c7-4d4b-a312-3fb0e3337ffc | br_02_22.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7206.9995 | 7202.249 | 7162.7293 | 7262.722 | 7029.892 | 7398.179 | GSO_122 | br_02_22 | abf746be-5de9-44ac-9f69-a717abe29437 | br_02_22.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7209.9177 | 7204.507 | 7163.212 | 7267.2029 | 7022.253 | 7377.317 | GSO_123 | br_03_22 | 22b46d3c-1104-4a6b-baf0-791554532cbe | br_03_22.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7210.9486 | 7204.5625 | 7166.3879 | 7270.5913 | 7035.194 | 7382.854 | GSO_123 | br_03_22 | c84967ed-4e26-4447-aaec-39d0dba00695 | br_03_22.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7209.0817 | 7204.621 | 7160.7653 | 7264.8146 | 7029.085 | 7383.732 | GSO_123 | br_03_22 | 08fe15ea-b154-4270-ad96-7633898d9feb | br_03_22.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7207.2665 | 7203.095 | 7165.9279 | 7256.709 | 7005.586 | 7378.288 | GSO_124 | br_04_22 | e9588dba-e5c4-44a0-a87f-6d585846716c | br_04_22.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7206.5732 | 7202.2845 | 7154.8937 | 7266.754 | 7057.389 | 7387.123 | GSO_124 | br_04_22 | f9dd1e2c-0b53-4323-abbd-c79d2b87bf2e | br_04_22.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7211.1145 | 7204.104 | 7168.9828 | 7269.9309 | 7028.827 | 7387.821 | GSO_124 | br_04_22 | cbbe0d2b-6245-4a4f-bcc2-e456b3e84669 | br_04_22.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7212.0974 | 7205.935 | 7166.3797 | 7270.0249 | 7044.963 | 7382.54 | GSO_125 | br_05_22 | cd7fbbb9-9a6f-4dd9-891c-e37a9557fa12 | br_05_22.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7211.6453 | 7205.909 | 7162.6512 | 7271.5392 | 7024.71 | 7385.96 | GSO_125 | br_05_22 | 16682194-aa4b-49e9-acf2-9c6562595352 | br_05_22.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7210.5525 | 7205.416 | 7161.9564 | 7267.8796 | 7044.728 | 7370.4 | GSO_125 | br_05_22 | 99cabfd6-b964-4658-8155-1699ad43459b | br_05_22.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7208.8983 | 7202.992 | 7160.3681 | 7272.0098 | 7007.034 | 7391.187 | GSO_126 | br_06_22 | 9006b8b1-eda0-485b-a8d0-426580b8950f | br_06_22.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7210.81 | 7203.103 | 7163.7595 | 7275.944 | 7031.745 | 7404.106 | GSO_126 | br_06_22 | bc3fda03-9c4b-412b-a5ef-6db07eeba8fc | br_06_22.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7208.439 | 7202.9795 | 7158.9918 | 7270.146 | 7034.591 | 7393.787 | GSO_126 | br_06_22 | 12d09ac1-fdb6-467e-a1aa-f99f6eed49f6 | br_06_22.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7204.7881 | 7201.194 | 7160.8637 | 7256.931 | 7003.738 | 7385.541 | GSO_127 | br_07_22 | a16d8ea2-fafa-4870-8bff-75e352b48100 | br_07_22.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7204.7955 | 7201.171 | 7161.2317 | 7256.684 | 7025.791 | 7390.05 | GSO_127 | br_07_22 | 1287cfdf-d61b-4b7d-9c56-4a67e583be03 | br_07_22.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7204.8787 | 7201.1835 | 7160.9694 | 7257.6768 | 7019.075 | 7384.944 | GSO_127 | br_07_22 | 9962595a-e18a-4855-ab7a-6bcfb11262e4 | br_07_22.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7210.8994 | 7204.28 | 7164.4391 | 7273.6893 | 7053.457 | 7401.973 | GSO_128 | br_08_22 | 692be577-442c-4ab0-b1e1-5785854345e2 | br_08_22.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7208.2738 | 7202.816 | 7167.6267 | 7262.0203 | 7024.028 | 7388.792 | GSO_128 | br_08_22 | 6cff9753-e438-465f-8082-4b41468b4f8c | br_08_22.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7208.431 | 7202.933 | 7164.855 | 7265.1068 | 7046.559 | 7390.925 | GSO_128 | br_08_22 | 3d10e996-315d-4229-9b7c-a9b8e0697db8 | br_08_22.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7213.2723 | 7206.1615 | 7160.769 | 7281.385 | 7013.679 | 7390.702 | GSO_129 | br_09_22 | 686b2171-718b-454f-a63f-7a08af910b78 | br_09_22.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7210.6698 | 7205.044 | 7162.8377 | 7269.2056 | 7041.943 | 7390.199 | GSO_129 | br_09_22 | 066b1670-e5b9-40c9-bd97-907fe78b74e9 | br_09_22.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7209.6521 | 7203.917 | 7163.1615 | 7269.1382 | 7020.903 | 7397.262 | GSO_129 | br_09_22 | ca9fa130-fc7c-477e-8464-326c962a06af | br_09_22.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.9378 | 7208.291 | 7156.4895 | 7289.176 | 7035.417 | 7345.131 | GSO_13 | br_018_21 | 28993f84-c3b9-4382-b199-7eae1602f7b5 | br_018_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7214.4965 | 7207.684 | 7157.6534 | 7282.8666 | 7029.021 | 7357.057 | GSO_13 | br_018_21 | d4524dc1-a63b-454b-a0d9-1683a9db619b | br_018_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7203.5194 | 7203.427 | 7158.538 | 7242.009 | 7032.707 | 7271.453 | GSO_13 | br_018_21 | 538bb977-c069-4a72-a1f5-79ade89be85e | br_018_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7211.2124 | 7204.4695 | 7167.3361 | 7271.0877 | 7050.508 | 7383.214 | GSO_130 | br_010_22 | ec2f67d6-3e29-40e6-b3db-279de5aeb3e1 | br_010_22.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7209.0908 | 7203.9505 | 7159.6044 | 7268.8956 | 7031.164 | 7377.911 | GSO_130 | br_010_22 | 0820aaeb-7057-4894-a6ba-7624e83ee1a7 | br_010_22.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7209.9946 | 7204.237 | 7167.9577 | 7264.1018 | 7027.936 | 7367.223 | GSO_130 | br_010_22 | cab2ab50-4b8d-4ecb-98f8-73c155d0b547 | br_010_22.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7209.2825 | 7203.501 | 7166.6618 | 7264.9838 | 7010.312 | 7387.689 | GSO_131 | br_011_22 | 434fff6c-2804-492a-a7e9-8c978d0dc8e3 | br_011_22.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7209.4486 | 7203.472 | 7166.3811 | 7265.7639 | 7001.625 | 7386.858 | GSO_131 | br_011_22 | 1a6f96c2-84f7-4c0d-b1a3-ee2364b2f450 | br_011_22.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7209.2326 | 7203.527 | 7165.9882 | 7265.2073 | 6987.82 | 7394.459 | GSO_131 | br_011_22 | 618c145a-b95c-4f8d-9e8d-9389861004d6 | br_011_22.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7213.453 | 7205.973 | 7163.2874 | 7279.6497 | 7053.594 | 7404.132 | GSO_132 | br_012_22 | 935c3854-ba34-4cf1-b241-c865be78d3bf | br_012_22.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7209.726 | 7204.6375 | 7159.8988 | 7268.9655 | 7025.913 | 7385.751 | GSO_132 | br_012_22 | 0716ea38-77d5-4d34-bc24-820dc14d344a | br_012_22.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7209.0302 | 7202.917 | 7159.9821 | 7272.1319 | 7025.031 | 7394.927 | GSO_132 | br_012_22 | 8eae3b99-7252-4faf-9a4e-4abe914bc30e | br_012_22.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7208.546 | 7203.84 | 7164.2847 | 7261.7873 | 7027.764 | 7384.006 | GSO_133 | br_013_22 | dddfb629-b710-4a70-b13f-4f342bc8fe74 | br_013_22.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7211.8404 | 7205.3995 | 7160.7667 | 7276.089 | 7037.181 | 7386.89 | GSO_133 | br_013_22 | 4d344901-644b-4ea0-b7f1-b381d39a7879 | br_013_22.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7212.0883 | 7205.9215 | 7162.0651 | 7273.9723 | 7025.626 | 7409.839 | GSO_133 | br_013_22 | c086c5c8-dc85-4746-8b0a-d8e23067358a | br_013_22.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7208.2063 | 7203.328 | 7160.0073 | 7267.3596 | 7024.842 | 7386.148 | GSO_134 | br_014_22 | 4091c3a2-55c3-4b7e-8d9d-a8e4affed314 | br_014_22.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7207.283 | 7202.935 | 7158.5871 | 7265.9212 | 7010.309 | 7395.425 | GSO_134 | br_014_22 | 57c2fa84-53da-4153-9d01-3c3ac5b2144e | br_014_22.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7202.7857 | 7199.3795 | 7153.3993 | 7266.0556 | 7023.807 | 7381.334 | GSO_134 | br_014_22 | 7325e088-181d-4e0d-b15b-2dd1fbda83f0 | br_014_22.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7204.0232 | 7200.188 | 7156.4443 | 7264.4978 | 7044.488 | 7382.455 | GSO_135 | br_015_22 | c3ac0e33-1470-42fd-9a70-99015f289563 | br_015_22.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7211.6993 | 7205.274 | 7163.139 | 7274.795 | 7052.077 | 7391.839 | GSO_135 | br_015_22 | 306b628e-5350-43cc-bd44-5524b56eb0e1 | br_015_22.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7209.0694 | 7203.6195 | 7163.648 | 7267.11 | 7048.886 | 7398.005 | GSO_135 | br_015_22 | cb036569-e3a3-4f9a-ab6b-ada0cfc7f7a2 | br_015_22.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7208.1837 | 7203.715 | 7162.9973 | 7261.957 | 7026.756 | 7382.77 | GSO_136 | br_016_22 | 04ce7e89-fb0f-4fb3-9752-836af1c7ab9e | br_016_22.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7210.4734 | 7204.0825 | 7165.3344 | 7270.215 | 7007.673 | 7388.402 | GSO_136 | br_016_22 | 1985324e-e67a-4d01-bf4e-cbc1776ba800 | br_016_22.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7208.7264 | 7203.8205 | 7163.9968 | 7263.5183 | 7022.48 | 7377.629 | GSO_136 | br_016_22 | 66b785ca-af8e-4a6a-8af7-ff9241ec96a5 | br_016_22.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7213.852 | 7206.893 | 7160.45 | 7281.0173 | 7030.635 | 7384.785 | GSO_137 | br_017_22 | cf094241-cd71-4a00-ae80-c341e78225f3 | br_017_22.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7211.1325 | 7205.876 | 7161.4777 | 7269.7526 | 7034.534 | 7378.7 | GSO_137 | br_017_22 | d0f42d15-cf63-4976-b310-0a7f21c9a7fc | br_017_22.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7211.9349 | 7204.984 | 7162.634 | 7277.3549 | 7038.113 | 7392.03 | GSO_137 | br_017_22 | bb261d99-e16f-41bf-90d2-05acc7b4f39c | br_017_22.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7212.8076 | 7206.808 | 7159.0362 | 7277.1828 | 7047.488 | 7388.782 | GSO_138 | br_018_22 | c812a09e-5775-4fbc-93b7-37aa020f3a4a | br_018_22.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7213.1858 | 7205.249 | 7165.1264 | 7279.31 | 7047.309 | 7385.392 | GSO_138 | br_018_22 | b91b7108-02a6-4c8f-9294-9075747bf3d2 | br_018_22.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.9621 | 7207.8775 | 7162.0994 | 7286.9579 | 7057.249 | 7356.492 | GSO_138 | br_018_22 | 8cf34f38-0fdb-4d44-9870-a7c9c5b5c3b4 | br_018_22.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7210.2124 | 7205.4135 | 7165.2004 | 7263.2199 | 7012.353 | 7396.818 | GSO_139 | br_019_22 | 8781de87-205d-4b90-963f-449d72c41e8c | br_019_22.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7210.0069 | 7204.8695 | 7166.6663 | 7262.7683 | 7005.025 | 7389.219 | GSO_139 | br_019_22 | 2a67f2a3-ad9e-4413-af20-999870d5694e | br_019_22.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7206.6053 | 7203.5835 | 7165.261 | 7252.0686 | 7002.039 | 7395.536 | GSO_139 | br_019_22 | 6ec0fb64-8f9d-48b6-81ae-63048adca78a | br_019_22.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7217.0892 | 7208.278 | 7157.7784 | 7292.3547 | 7025.833 | 7347.666 | GSO_14 | br_019_21 | 9df35035-201c-43e2-9c0f-29f5652d20b6 | br_019_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7216.695 | 7208.4165 | 7157.2648 | 7291.1322 | 7027.14 | 7341.296 | GSO_14 | br_019_21 | 4f0a9de3-7d5d-4d74-841a-ad368a655ddc | br_019_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7205.5401 | 7204.284 | 7156.9538 | 7250.2787 | 7032.766 | 7284.781 | GSO_14 | br_019_21 | 37a8aff5-f4d5-48d1-b094-f7ff7add641f | br_019_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7213.2403 | 7206.066 | 7165.7147 | 7276.187 | 7038.585 | 7390.538 | GSO_140 | br_020_22 | b6e43aeb-290f-443d-917c-933a0af02698 | br_020_22.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7208.8107 | 7204.097 | 7164.6677 | 7263.466 | 7035.544 | 7409.054 | GSO_140 | br_020_22 | 7ac282db-535a-4cda-bcc4-f62230cc0be1 | br_020_22.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7213.9141 | 7206.3925 | 7163.6488 | 7280.6359 | 7033.355 | 7395.942 | GSO_140 | br_020_22 | 52cf19cb-d2f9-48a0-a5d7-3d345a429c59 | br_020_22.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7211.8626 | 7206.868 | 7159.172 | 7272.2117 | 7020.645 | 7365.578 | GSO_141 | br_021_22 | 78f844cc-a5b4-4d9d-ba33-ef854d68bc8a | br_021_22.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7209.5135 | 7204.919 | 7164.8927 | 7262.0853 | 7041.681 | 7394.606 | GSO_141 | br_021_22 | b6f787f7-5117-4b48-81f4-ddbe099f96d7 | br_021_22.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7209.4599 | 7204.2085 | 7162.938 | 7266.9803 | 7014.988 | 7405.181 | GSO_141 | br_021_22 | 0b5869b0-b194-4a18-8593-e04336ade6ea | br_021_22.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7211.974 | 7204.982 | 7167.963 | 7272.627 | 7055.092 | 7382.303 | GSO_142 | br_022_22 | 5c50320a-6541-43e1-a0eb-b3cc85335f92 | br_022_22.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7212.3415 | 7205.35 | 7169.0873 | 7272.2467 | 7054.939 | 7399.344 | GSO_142 | br_022_22 | d8586197-7e6c-42e3-af81-89d0f76301f9 | br_022_22.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7211.4021 | 7204.6765 | 7170.084 | 7268.3623 | 7052.771 | 7378.542 | GSO_142 | br_022_22 | aeed6de5-7aca-4fa3-a5ca-b1f32ee717c2 | br_022_22.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7218.4547 | 7209.4935 | 7156.2924 | 7298.3679 | 7033.818 | 7356.242 | GSO_143 | br_023_22 | b2362459-63fa-42c8-b75d-cdff666f2190 | br_023_22.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7217.4549 | 7209.186 | 7155.772 | 7295.3123 | 7034.698 | 7350.395 | GSO_143 | br_023_22 | 15ee4200-f93f-4884-ab81-e52eb3d0b73c | br_023_22.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7218.4176 | 7208.9625 | 7154.5197 | 7301.246 | 7026.719 | 7352.954 | GSO_143 | br_023_22 | ef7cab0d-e432-4fb1-aab4-46e5068286b4 | br_023_22.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7216.3559 | 7208.3035 | 7160.9817 | 7289.3076 | 7017.431 | 7389.952 | GSO_144 | br_024_22 | cebe0434-4e95-4fd2-8e1e-22573f21abf5 | br_024_22.A | A | OK
0 | [8 empty] | GSO_144 | br_024_22 | bd7e1df8-2eb1-4167-bee8-930536ce0573 | br_024_22.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7218.6666 | 7209.998 | 7157.1647 | 7296.9693 | 7026.196 | 7366.826 | GSO_144 | br_024_22 | 82536324-6f01-4e66-a011-7b067544a9ac | br_024_22.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.5132 | 7207.4625 | 7164.282 | 7283.6208 | 7038.239 | 7393.921 | GSO_145 | br_025_22 | e8f52edb-11b6-4a01-8cb4-dde6abb481d7 | br_025_22.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7213.7589 | 7206.813 | 7160.3044 | 7280.5117 | 7040.76 | 7396.884 | GSO_145 | br_025_22 | 5042bbb0-cc21-499d-9106-09bd8c86b439 | br_025_22.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7211.4496 | 7205.883 | 7159.5153 | 7273.7176 | 7041.154 | 7376.019 | GSO_145 | br_025_22 | 039cb766-152c-4467-9ec0-94180921a657 | br_025_22.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7220.9475 | 7210.065 | 7158.1368 | 7307.3026 | 7034.108 | 7381.47 | GSO_146 | br_026_22 | 45141e3c-ee87-445b-a8cd-53eaf3cf8ac6 | br_026_22.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7219.2106 | 7209.9585 | 7155.441 | 7301.7287 | 7032.141 | 7373.949 | GSO_146 | br_026_22 | d4d03355-620e-4213-a24e-266e873f3f79 | br_026_22.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7214.2051 | 7206.1045 | 7160.9004 | 7283.6407 | 7047.821 | 7382.472 | GSO_146 | br_026_22 | 9c3aa61d-fdd8-4e3a-a859-786b34331466 | br_026_22.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.2158 | 7207.762 | 7162.0871 | 7282.8139 | 7035.176 | 7400.18 | GSO_147 | br_027_22 | 783419bf-1c8f-4783-a364-729c4d25328a | br_027_22.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7207.9179 | 7204.265 | 7163.5644 | 7257.5786 | 7041.5 | 7389.222 | GSO_147 | br_027_22 | b05dca4b-f167-46ba-b479-77fc9d306c98 | br_027_22.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7213.6337 | 7206.8315 | 7162.2787 | 7277.8893 | 7052.141 | 7381.174 | GSO_147 | br_027_22 | a6c68db1-932a-455f-9961-2001628d137a | br_027_22.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.742 | 7207.83 | 7160.4744 | 7288.0593 | 7011.396 | 7382.448 | GSO_148 | br_028_22 | f209db33-c63a-4eeb-9470-44a070b1f980 | br_028_22.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7213.0273 | 7206.195 | 7161.9858 | 7278.5696 | 6997.271 | 7398.382 | GSO_148 | br_028_22 | e51bd3d2-27db-4e8c-85b3-94bb36fdecb2 | br_028_22.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.5326 | 7208.0235 | 7160.161 | 7286.1496 | 7036.014 | 7404.952 | GSO_148 | br_028_22 | 9cb02ef5-7d31-4690-b5cc-1c8ff7465b94 | br_028_22.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7208.2833 | 7202.918 | 7165.231 | 7262.843 | 7024.226 | 7392.547 | GSO_149 | br_029_22 | 54f22dd6-dae8-4d6f-8c00-4ee16cc1bce1 | br_029_22.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7208.816 | 7202.491 | 7163.1871 | 7269.889 | 7025.5 | 7401.624 | GSO_149 | br_029_22 | a7d55959-39f6-4006-8a75-2ac4375060d6 | br_029_22.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7213.5533 | 7205.815 | 7165.2724 | 7279.0988 | 7041.983 | 7380.284 | GSO_149 | br_029_22 | 22ef08a2-8b87-47bf-912f-a49f8dbe4e0e | br_029_22.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7217.7713 | 7208.713 | 7159.7277 | 7293.6556 | 7035.467 | 7347.419 | GSO_15 | br_020_21 | 2dfc9022-cd2d-4071-a0ed-f7aa4dbf29b5 | br_020_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.5321 | 7208.3185 | 7156.2973 | 7286.9276 | 7028.82 | 7333.648 | GSO_15 | br_020_21 | 34fb9785-294c-4580-94c1-92b57cb0e642 | br_020_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.9867 | 7208.163 | 7158.4497 | 7288.0995 | 7032.503 | 7351.676 | GSO_15 | br_020_21 | dd9e89fb-3f9a-4966-a494-c19ab9432a67 | br_020_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7210.7203 | 7203.9665 | 7166.3364 | 7271.7209 | 7039.77 | 7380.158 | GSO_150 | br_030_22 | 99ca8035-36a9-410b-844c-06c1ddb4c66b | br_030_22.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7211.7125 | 7204.612 | 7168.0683 | 7272.6516 | 7013.469 | 7378.148 | GSO_150 | br_030_22 | 97ae36fa-2e65-4c6d-8a11-b6c4ba921c0d | br_030_22.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7211.0384 | 7204.6435 | 7163.9424 | 7272.4979 | 7039.447 | 7394.933 | GSO_150 | br_030_22 | e18873a3-19e0-4c86-abaf-03f1ea49ef98 | br_030_22.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7214.8052 | 7208.055 | 7158.1074 | 7283.7486 | 7032.846 | 7376.851 | GSO_151 | br_031_22 | 5b53a681-1338-4fee-9587-71b3e65506cb | br_031_22.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7212.121 | 7205.82 | 7163.1771 | 7274.0986 | 7035.46 | 7372.07 | GSO_151 | br_031_22 | 051f7584-2010-41f8-9415-9183657a8ae0 | br_031_22.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7211.5027 | 7206.85 | 7156.7407 | 7272.0842 | 7022.59 | 7357.022 | GSO_151 | br_031_22 | 0542d836-ab02-49aa-a8b7-a4265443a1c4 | br_031_22.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7204.3444 | 7202.173 | 7159.6449 | 7250.6789 | 7028.385 | 7386.467 | GSO_152 | br_032_22 | 3f75484a-66ad-416b-bdfc-429bf783f99d | br_032_22.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7204.4102 | 7202.2725 | 7159.6395 | 7251.687 | 7032.64 | 7398.936 | GSO_152 | br_032_22 | ab723fc3-e0cb-4dbc-8181-5681e5ac3348 | br_032_22.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7204.484 | 7202.281 | 7159.6744 | 7251.354 | 7033.175 | 7411.777 | GSO_152 | br_032_22 | 3b38bb39-6b77-49e7-b0c7-d3c699da74dc | br_032_22.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7213.9751 | 7206.9845 | 7162.1052 | 7279.9119 | 7038.833 | 7391.64 | GSO_153 | br_033_22 | 0d3f8e19-033b-4d8c-a34b-ff04747bd082 | br_033_22.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7211.8507 | 7206.0015 | 7160.7353 | 7274.4617 | 7039.361 | 7408.669 | GSO_153 | br_033_22 | 5e1ed7ac-1e16-4c51-bb12-e8d8b8c244c4 | br_033_22.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7213.8151 | 7206.728 | 7161.8237 | 7281.2086 | 7039.416 | 7398.191 | GSO_153 | br_033_22 | 07ea0bf7-442d-4e77-b98a-b9e2c8d50114 | br_033_22.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7209.9585 | 7204.004 | 7167.741 | 7265.2103 | 7024.989 | 7389.302 | GSO_154 | br_034_22 | 6eba73e4-418d-4cd1-96b6-60b826ae450c | br_034_22.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7209.7008 | 7203.788 | 7160.4874 | 7274.343 | 7021.844 | 7389.229 | GSO_154 | br_034_22 | 70369b74-10d7-4556-af26-c0ccb8f01935 | br_034_22.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7214.4702 | 7206.9625 | 7163.432 | 7281.0932 | 7051.985 | 7392.101 | GSO_154 | br_034_22 | 0840b23d-66b0-48cf-856c-1f62526c7d6e | br_034_22.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.3974 | 7207.845 | 7159.7618 | 7284.873 | 7032.614 | 7369.265 | GSO_155 | br_01_23 | 033ba35a-0e88-44c7-ae68-9ef721532ab3 | br_01_23.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7216.1464 | 7208.5435 | 7155.7764 | 7290.2095 | 7031.508 | 7337.762 | GSO_155 | br_01_23 | ecb9c3ef-513f-492a-821c-4bff92c1df9c | br_01_23.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7216.7323 | 7207.9625 | 7161.6021 | 7289.2487 | 7029.768 | 7359.138 | GSO_155 | br_01_23 | d1e45bf7-a00b-40dc-a6ec-c751080a13c9 | br_01_23.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.8325 | 7207.901 | 7155.3354 | 7290.1816 | 7034.959 | 7348.881 | GSO_156 | br_02_23 | 2ec12710-cbb3-4ac0-ae81-f21bc775b59d | br_02_23.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.6363 | 7207.761 | 7159.5538 | 7286.74 | 7038.91 | 7362.545 | GSO_156 | br_02_23 | 17343a92-f390-4c00-96dd-aa4c8e6f2cf5 | br_02_23.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.7653 | 7208.115 | 7156.5434 | 7287.6809 | 7026.036 | 7345.388 | GSO_156 | br_02_23 | 12b55d36-db8c-475f-838b-08caf84b6421 | br_02_23.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7219.391 | 7209.1885 | 7161.1953 | 7299.0265 | 7047.317 | 7356.89 | GSO_157 | br_03_23 | d76a1565-b995-4235-9508-12ae427ed548 | br_03_23.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.246 | 7208.107 | 7156.273 | 7286.532 | 7025.898 | 7352.525 | GSO_157 | br_03_23 | b96622f9-34da-4d3a-a144-a82c9e2d84a9 | br_03_23.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.325 | 7207.7235 | 7158.6673 | 7285.8126 | 7036.145 | 7357.982 | GSO_157 | br_03_23 | 962e5ace-7f13-49d9-a1bd-65973f2adfac | br_03_23.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7216.7902 | 7208.311 | 7159.2145 | 7290.3876 | 7040.748 | 7347.627 | GSO_158 | br_04_23 | 8e1d3060-4f17-4027-bb48-9326d72d1f5e | br_04_23.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7214.5335 | 7207.2965 | 7154.9717 | 7286.2722 | 7026.375 | 7339.706 | GSO_158 | br_04_23 | b84e6ee7-bc4b-467a-884d-e5dac0fbac0b | br_04_23.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.016 | 7207.6695 | 7158.9634 | 7284.046 | 7039.11 | 7340.412 | GSO_158 | br_04_23 | 5320e9a7-8d71-4f75-b9c9-3a6a37f707db | br_04_23.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7216.8027 | 7208.5505 | 7158.2941 | 7291.082 | 7032.868 | 7339.673 | GSO_159 | br_05_23 | 83f2cd36-180e-4d9a-9105-62a32f68ab85 | br_05_23.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7218.9435 | 7209.351 | 7157.4357 | 7299.2863 | 7027.018 | 7364.047 | GSO_159 | br_05_23 | 96fae847-ae01-4905-9884-47b324a88934 | br_05_23.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7217.4187 | 7208.728 | 7157.6084 | 7293.4383 | 7035.231 | 7350.518 | GSO_159 | br_05_23 | 2e882994-3bef-4961-988c-cd677efd6410 | br_05_23.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7213.8776 | 7207.2685 | 7161.1866 | 7278.2493 | 7031.904 | 7350.634 | GSO_16 | br_021_21 | e4f24c66-81cd-48f4-b9a3-a8aaa9fe8c98 | br_021_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7213.8768 | 7207.4225 | 7158.3023 | 7279.8516 | 7027.004 | 7349.272 | GSO_16 | br_021_21 | b5d738a6-79bd-43f6-b4e4-0fb4de70abfd | br_021_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7214.1967 | 7207.342 | 7158.5815 | 7281.415 | 7028.886 | 7346.423 | GSO_16 | br_021_21 | 2b3c0835-4f9e-453c-86b3-35847ab5af94 | br_021_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.9917 | 7208.204 | 7156.3383 | 7289.2563 | 7024.802 | 7334.072 | GSO_160 | br_06_23 | b9360429-edfb-4e59-a900-8a457dc83cba | br_06_23.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7218.2373 | 7208.874 | 7158.2601 | 7296.0655 | 7036.423 | 7349.88 | GSO_160 | br_06_23 | c3e81296-2c1a-4ada-80c1-b847107d5cfb | br_06_23.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7216.4062 | 7208.525 | 7157.1128 | 7289.6526 | 7027.858 | 7351.791 | GSO_160 | br_06_23 | 47f0ee8f-4288-4af4-b69a-10cebf43b645 | br_06_23.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7210.751 | 7204.609 | 7169.174 | 7265.8897 | 7029.94 | 7388.204 | GSO_161 | br_07_23 | 89a3b24a-887f-4195-8344-51f18a00dbf7 | br_07_23.A | A | OK
0 | [8 empty] | GSO_161 | br_07_23 | c4eee589-eb1d-4947-bc9b-3f547ec858d4 | br_07_23.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7221.2886 | 7210.053 | 7166.9864 | 7301.8819 | 7061.061 | 7392.414 | GSO_161 | br_07_23 | e61fb2d3-e704-4d3f-bf86-8b04c3724fd7 | br_07_23.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.4735 | 7207.7705 | 7160.6244 | 7284.6082 | 7032.312 | 7348.664 | GSO_162 | br_08_23 | f620b838-2134-4f66-a112-15e5f46318b0 | br_08_23.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.8371 | 7207.847 | 7161.476 | 7285.1353 | 7042.811 | 7354.077 | GSO_162 | br_08_23 | f4ffa257-f9a9-48e6-8ef7-945f8e687e83 | br_08_23.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7214.1189 | 7207.355 | 7161.3027 | 7280.0393 | 7035.953 | 7352.461 | GSO_162 | br_08_23 | 4bfd3a0a-1178-4983-b63c-76c387206a99 | br_08_23.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7216.7281 | 7207.9915 | 7158.9996 | 7291.4643 | 7029.88 | 7349.323 | GSO_163 | br_09_23 | d90170cc-5eec-43f7-a5d9-cb91dca851cb | br_09_23.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7218.3244 | 7208.7405 | 7159.2007 | 7296.5459 | 7036.651 | 7344.524 | GSO_163 | br_09_23 | 9018e821-338d-4aa5-bb0d-3e9aa19f5a3b | br_09_23.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7217.4077 | 7208.705 | 7158.293 | 7293.5802 | 7025.692 | 7350.74 | GSO_163 | br_09_23 | 0d2e0f05-d1e8-46f2-953d-daf9b517d3b5 | br_09_23.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7207.7383 | 7205.0775 | 7157.2234 | 7258.2287 | 7032.735 | 7298.912 | GSO_17 | br_024_21 | 3a2af09c-baa8-4dbe-95ab-fb397036b19d | br_024_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.6723 | 7207.722 | 7155.4172 | 7290.7966 | 7020.65 | 7340.337 | GSO_17 | br_024_21 | 883c59a4-ab46-45e2-b36d-e1959b7c89b6 | br_024_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7216.2382 | 7208.1735 | 7157.0243 | 7290.394 | 7035.227 | 7359.735 | GSO_17 | br_024_21 | f0a67506-31bf-4b47-9614-f559c928646a | br_024_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7218.1791 | 7208.5785 | 7161.4057 | 7294.2063 | 7052.055 | 7355.37 | GSO_18 | br_025_21 | 34cac5e4-313a-4454-a92d-abc9047eadc8 | br_025_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7206.1489 | 7204.1995 | 7159.347 | 7251.1076 | 7035.527 | 7289.948 | GSO_18 | br_025_21 | 90d3f27c-2599-462f-8abb-58371a03ece5 | br_025_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7218.4581 | 7208.987 | 7160.459 | 7295.8883 | 7036.625 | 7371.574 | GSO_18 | br_025_21 | 08eb7b30-b593-4a81-854f-d7a00d46db1e | br_025_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7216.7248 | 7208.044 | 7157.4247 | 7292.684 | 7031.45 | 7357.445 | GSO_19 | br_026_21 | d5920248-7472-436e-b060-c7c2ff9ef29d | br_026_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7217.6476 | 7208.82 | 7157.72 | 7294.6037 | 7037.628 | 7337.216 | GSO_19 | br_026_21 | cf54e8e6-a9a5-4011-b2be-1226fbdc86cb | br_026_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7217.1475 | 7208.545 | 7156.5428 | 7293.5567 | 7035.338 | 7339.54 | GSO_19 | br_026_21 | a03bc8be-0c7b-4ca4-b625-79f7823155e9 | br_026_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7217.7415 | 7209.318 | 7155.0175 | 7296.2289 | 7014.129 | 7363.589 | GSO_2 | br_02_21 | e16fe26a-3331-4e10-bcda-3d5b4cfc42bc | br_02_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7218.2129 | 7208.9475 | 7155.274 | 7299.3899 | 7032.373 | 7355.642 | GSO_2 | br_02_21 | f5b81547-937f-4c70-92ba-8a0fb6594394 | br_02_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7217.1885 | 7208.826 | 7154.6143 | 7296.169 | 7020.742 | 7363.238 | GSO_2 | br_02_21 | a28c1752-7f45-48c2-b058-b7cdc091e5d6 | br_02_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7205.7076 | 7200.567 | 7163.416 | 7264.1847 | 7040.882 | 7402.072 | GSO_20 | br_027_21 | 0367f0a8-b7e5-4ca5-94ae-d44fa9d00bfd | br_027_21.A | A | OK
0 | [8 empty] | GSO_20 | br_027_21 | a602edca-8fde-46f7-8d51-40a5f85d6a1d | br_027_21.B | B | OK
0 | [8 empty] | GSO_20 | br_027_21 | c9015052-da74-4877-bbf1-9a6c4275c44d | br_027_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7221.1011 | 7209.687 | 7161.1557 | 7305.799 | 7050.7 | 7381.687 | GSO_21 | br_028_21 | 6f7a2c02-ca5d-4d73-a76d-82f0fe3158c9 | br_028_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7217.251 | 7208.311 | 7156.8127 | 7294.2458 | 7026.492 | 7355.105 | GSO_21 | br_028_21 | 39b0a939-9afe-4c84-bfda-5eec318bc35e | br_028_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7219.3554 | 7209.268 | 7157.5594 | 7301.9285 | 7030.65 | 7376.374 | GSO_21 | br_028_21 | a49c303e-bacd-45af-8754-babfb2545a48 | br_028_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.6541 | 7208.2825 | 7156.3248 | 7287.2789 | 7028.584 | 7343.157 | GSO_22 | br_029_21 | f1fcda72-2c9e-4219-9a68-e344865344e1 | br_029_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7216.2422 | 7208.0035 | 7156.6637 | 7290.3637 | 7031.264 | 7385.958 | GSO_22 | br_029_21 | c13495f3-7436-4771-9d8e-028fe398e677 | br_029_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7219.0595 | 7209.202 | 7159.4587 | 7298.5923 | 7042.669 | 7360.393 | GSO_22 | br_029_21 | 60e175bd-dd8d-424f-b541-e6c27675c2ee | br_029_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7217.5076 | 7208.116 | 7160.3787 | 7293.317 | 7032.392 | 7384.339 | GSO_23 | br_030_21 | 73114768-3396-46b2-8366-027d7f330c2a | br_030_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.7757 | 7207.962 | 7158.4472 | 7288.1048 | 7024.365 | 7368.236 | GSO_23 | br_030_21 | 8896d2cc-f5f3-479a-9806-74f9830d0e65 | br_030_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7209.8243 | 7205.023 | 7157.1451 | 7274.093 | 7013.887 | 7392.971 | GSO_23 | br_030_21 | 306a0179-6b1d-4c84-b7ad-c043978706f4 | br_030_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7208.9368 | 7202.386 | 7174.7004 | 7260.5432 | 7033.155 | 7377.447 | GSO_24 | br_031_21 | 8866ae0d-1645-4e1d-85a9-520a2b057093 | br_031_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7212.0685 | 7205.422 | 7171.7341 | 7267.7802 | 7043.772 | 7384.643 | GSO_24 | br_031_21 | 0e740376-b7d0-46f1-8238-50979ff53b86 | br_031_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7208.808 | 7202.107 | 7168.0318 | 7265.8737 | 7016.239 | 7398.253 | GSO_24 | br_031_21 | 3abd341d-8629-4be0-888c-4405cbd18a68 | br_031_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.3822 | 7207.4915 | 7161.046 | 7285.556 | 7050.075 | 7391.01 | GSO_25 | br_032_21 | 8c0cf450-9297-450e-b468-8396988be79f | br_032_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7209.5937 | 7204.7765 | 7162.9505 | 7263.9371 | 7038.822 | 7398.15 | GSO_25 | br_032_21 | d4f80b32-222c-49ea-bb38-81080bcb0826 | br_032_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7214.6519 | 7206.7385 | 7163.2867 | 7284.3436 | 7041.124 | 7396.496 | GSO_25 | br_032_21 | 6a2617f0-409e-448d-8ce4-c1175edcf36a | br_032_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7213.9775 | 7207.5455 | 7159.6718 | 7279.015 | 7038.154 | 7333.781 | GSO_26 | br_033_21 | 2ded452d-d964-456f-bc61-891c5e02102b | br_033_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7212.5453 | 7206.009 | 7156.2635 | 7279.184 | 7014.68 | 7337.245 | GSO_26 | br_033_21 | 123d2e0f-6c7b-4b17-96d2-32d4328dde67 | br_033_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7217.4522 | 7209.0485 | 7155.7894 | 7295.49 | 7021.552 | 7361.056 | GSO_26 | br_033_21 | 06410d93-c578-4f9d-86d8-8eb333ba28c9 | br_033_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7217.5732 | 7208.624 | 7158.0667 | 7295.2993 | 7023.281 | 7347.271 | GSO_27 | br_034_21 | 6fdd1896-ad74-48a8-9816-85aa01d652d1 | br_034_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.2699 | 7207.666 | 7159.5011 | 7284.5917 | 7035.279 | 7338.875 | GSO_27 | br_034_21 | d428eae8-d228-4f79-b9ea-91e3a88bb229 | br_034_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7219.353 | 7209.171 | 7161.7148 | 7298.3846 | 7033.663 | 7409.065 | GSO_27 | br_034_21 | 9dbd0f33-80b1-4155-96b0-ea2e0658e691 | br_034_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7207.8215 | 7202.953 | 7165.3747 | 7260.7203 | 7048.269 | 7385.741 | GSO_28 | br_035_21 | c3250712-a026-44dc-83b1-ab0b7bd1cef0 | br_035_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7208.8662 | 7203.9835 | 7164.2104 | 7262.7566 | 7029.148 | 7397.887 | GSO_28 | br_035_21 | 4cc07d73-767d-4a92-aa56-8d6f6139433c | br_035_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7204.6396 | 7201.526 | 7165.0645 | 7250.201 | 7038.083 | 7386.067 | GSO_28 | br_035_21 | 4b1de06e-7ccd-42bd-ba7d-141a0d6eed10 | br_035_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7218.8008 | 7208.725 | 7161.3853 | 7296.5195 | 7026.696 | 7361.989 | GSO_29 | br_036_21 | 53ac9d88-ec7e-422c-9547-7b65d0e1b05c | br_036_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7216.7843 | 7208.424 | 7158.0898 | 7290.911 | 7034.163 | 7350.564 | GSO_29 | br_036_21 | bbdb1c8c-b61b-4af3-a00d-d34e99f936e8 | br_036_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7216.1072 | 7208.2295 | 7158.3643 | 7288.5603 | 7044.896 | 7343.326 | GSO_29 | br_036_21 | 37be8bbe-3fc1-42ac-aa14-512831f011d9 | br_036_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7217.7714 | 7208.2625 | 7171.604 | 7286.2557 | 7053.453 | 7383.62 | GSO_3 | br_03_21 | cabb02b4-86e3-4261-87ef-66f06902bb61 | br_03_21.A | A | OK
0 | [8 empty] | GSO_3 | br_03_21 | 262d1506-d23e-42d2-a938-f15cb2f35365 | br_03_21.B | B | OK
0 | [8 empty] | GSO_3 | br_03_21 | 861d3fe8-4f6d-46b5-bb00-6d79ddaf889d | br_03_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7219.4871 | 7209.157 | 7159.5577 | 7300.6631 | 7040.468 | 7370.04 | GSO_30 | br_037_21 | 80a38063-4b58-4c05-9631-c9f20eaae49f | br_037_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7216.1758 | 7208.384 | 7157.2861 | 7289.037 | 7034.824 | 7340.439 | GSO_30 | br_037_21 | 07afe75d-2efa-4a63-8500-f5eed954ebc4 | br_037_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.3962 | 7207.7865 | 7156.416 | 7287.5616 | 7033.038 | 7357.223 | GSO_30 | br_037_21 | 4339844d-f7f4-4af5-a7ce-ff1e206a4bfc | br_037_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7205.6752 | 7202.035 | 7162.9195 | 7253.6766 | 7007.792 | 7399.343 | GSO_31 | br_038_21 | dbd51660-93ed-49dc-b484-ac1a2ff93751 | br_038_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7205.5093 | 7201.977 | 7162.492 | 7253.6526 | 7042.522 | 7400.844 | GSO_31 | br_038_21 | c4bbbd0b-e3cc-4312-b11b-48dca067f34f | br_038_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7205.5404 | 7202.045 | 7162.3874 | 7253.6983 | 7031.065 | 7394.573 | GSO_31 | br_038_21 | f5f51af7-9112-4286-adaa-37e4589d054a | br_038_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7219.6019 | 7209.3985 | 7160.3207 | 7300.1693 | 7047.206 | 7384.644 | GSO_32 | br_039_21 | 049d0b94-e086-4825-b104-d454ffd3dc7c | br_039_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7217.9812 | 7208.684 | 7161.8561 | 7292.6112 | 7055.197 | 7353.839 | GSO_32 | br_039_21 | 81e832b4-cd01-4844-b4d8-6ff81d95dbe4 | br_039_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7218.5421 | 7208.985 | 7159.3655 | 7297.0893 | 7028.782 | 7367.974 | GSO_32 | br_039_21 | 934aabc4-8b42-44e6-82dc-1b3261dc29d9 | br_039_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7210.837 | 7205.7135 | 7163.6324 | 7266.503 | 7034.404 | 7351.762 | GSO_33 | br_040_21 | ee1a565e-ae8b-4984-9f7a-cab15b5447c3 | br_040_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7214.7614 | 7206.6265 | 7165.1263 | 7283.099 | 7045.968 | 7388.206 | GSO_33 | br_040_21 | 2bcc2cc5-82f5-4040-ac32-a00d0d07de51 | br_040_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7212.8247 | 7205.9355 | 7162.3044 | 7277.1313 | 7025.724 | 7403.903 | GSO_33 | br_040_21 | d858a33a-1b66-4073-aed2-4b1a30ad837b | br_040_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7217.9172 | 7208.8495 | 7157.6891 | 7295.4646 | 7028.229 | 7367.529 | GSO_34 | br_041_21 | deb58541-2cca-43d5-86c5-55264c6041d3 | br_041_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7218.5452 | 7209.0855 | 7158.2614 | 7297.2086 | 7018.694 | 7361.218 | GSO_34 | br_041_21 | 179024ab-8e49-42be-b943-761705fb5abd | br_041_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7218.989 | 7208.977 | 7156.6527 | 7300.8283 | 7015.072 | 7362.113 | GSO_34 | br_041_21 | 0cbf9200-98b4-43c7-934d-2cc30d8ab63b | br_041_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7216.5678 | 7208.405 | 7156.8781 | 7290.9733 | 7020.614 | 7365.567 | GSO_35 | br_042_21 | efc37dec-e402-4c7d-81af-aa9cb2729757 | br_042_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.3526 | 7207.7755 | 7155.425 | 7288.0498 | 7025.555 | 7343.82 | GSO_35 | br_042_21 | d7ccdfd6-6a7d-4338-9666-e79b11f003a9 | br_042_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7218.1296 | 7208.9015 | 7157.0082 | 7297.4489 | 7027.167 | 7353.833 | GSO_35 | br_042_21 | 6d4ede07-2601-4246-903b-56124df12172 | br_042_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7203.4892 | 7201.505 | 7170.5691 | 7238.4703 | 7061.322 | 7306.786 | GSO_36 | br_043_21 | a492b914-7377-4047-b30b-90aa78dc94d3 | br_043_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7206.3728 | 7203.0695 | 7161.8934 | 7254.6047 | 7053.819 | 7337.693 | GSO_36 | br_043_21 | c95edbeb-bfcc-48be-abeb-7c6ceba7bdae | br_043_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7201.8895 | 7201.036 | 7161.6212 | 7241.6263 | 7030.326 | 7330.966 | GSO_36 | br_043_21 | 1ede274a-9246-4aec-acc0-17642c07af97 | br_043_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7216.4271 | 7208.537 | 7156.2827 | 7291.0522 | 7027.508 | 7333.263 | GSO_37 | br_044_21 | e72c363a-7373-4a30-a872-329d650d7569 | br_044_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7217.1565 | 7208.6415 | 7155.4433 | 7294.393 | 7022.594 | 7364.044 | GSO_37 | br_044_21 | 547c5604-b333-47b9-83ad-6f6fa1e88927 | br_044_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.9018 | 7208.192 | 7157.0619 | 7287.8166 | 7036.377 | 7353.082 | GSO_37 | br_044_21 | 53f8a349-7f61-440d-ad82-54a7f6d15d3a | br_044_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.0596 | 7207.5355 | 7170.1838 | 7276.2219 | 7064.572 | 7342.778 | GSO_38 | br_045_21 | 9c1dc66a-d26b-42ae-9fa5-d4e46c87f492 | br_045_21.A | A | OK
0 | [8 empty] | GSO_38 | br_045_21 | 31c14863-6ede-40c4-86a5-41eadc729ac2 | br_045_21.B | B | OK
0 | [8 empty] | GSO_38 | br_045_21 | 15e8162e-962b-481f-923b-b2fe7c7ce432 | br_045_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7214.3461 | 7207.1485 | 7156.4961 | 7283.9862 | 7027.455 | 7347.233 | GSO_39 | br_046_21 | 93658bef-4bd5-4300-8424-5c388155968b | br_046_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.8886 | 7208.1915 | 7156.372 | 7289.2733 | 7032.851 | 7357.045 | GSO_39 | br_046_21 | 1ef359a3-1b23-4781-b7f6-73e5a4c4559f | br_046_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.2854 | 7207.8895 | 7155.6604 | 7287.6992 | 7030.602 | 7350.951 | GSO_39 | br_046_21 | 77ff5585-562a-45e7-a281-464e98737abb | br_046_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7214.2919 | 7207.4925 | 7155.628 | 7283.9435 | 7032.587 | 7336.578 | GSO_4 | br_04_21 | eda55f14-fedc-4eb6-a389-a51a43231405 | br_04_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7216.5611 | 7208.4265 | 7156.2722 | 7291.099 | 7028.18 | 7338.272 | GSO_4 | br_04_21 | 67c44f52-c49c-4993-940f-90408b4b9ae5 | br_04_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.1035 | 7208.0525 | 7153.8733 | 7287.0285 | 7020.302 | 7334.194 | GSO_4 | br_04_21 | 1da22d5c-e6b3-4228-b327-ddf40f1f21b6 | br_04_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.8721 | 7208.18 | 7158.4064 | 7287.5827 | 7030.971 | 7348.687 | GSO_40 | br_047_21 | ee7aaead-b8fb-40d3-8a03-8ab58a542fdc | br_047_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.088 | 7207.895 | 7157.5942 | 7285.1629 | 7022.226 | 7344.815 | GSO_40 | br_047_21 | 58cd6faf-3139-48ff-a9ef-b152b7ebf778 | br_047_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7216.6102 | 7208.237 | 7159.8832 | 7289.3843 | 7038.791 | 7343.286 | GSO_40 | br_047_21 | 79202d32-8dca-417a-9d59-fc14f3bcaf5f | br_047_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7217.7383 | 7208.573 | 7159.4495 | 7294.1786 | 7026.979 | 7362.056 | GSO_41 | br_048_21 | 4f3f10ee-748f-4c21-b9c3-8ac51c8d41f6 | br_048_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7218.6123 | 7208.8025 | 7158.0634 | 7298.8416 | 7038.393 | 7371.369 | GSO_41 | br_048_21 | d7d6e014-1cd2-4cb5-84bb-a00b2cad42e3 | br_048_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7217.9478 | 7208.0445 | 7160.848 | 7295.384 | 7036.775 | 7358.559 | GSO_41 | br_048_21 | e1cda877-0a5c-49b1-bd5f-ad8449fb0e0c | br_048_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7219.4343 | 7209.971 | 7154.6007 | 7303.5955 | 7021.643 | 7364.274 | GSO_42 | br_049_21 | 0b1099db-07b7-4a46-831f-0ab42e837cdd | br_049_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7217.4051 | 7209.241 | 7153.5211 | 7296.5095 | 7031.66 | 7348.614 | GSO_42 | br_049_21 | 119ef0a4-9572-4988-9343-96cacd641d11 | br_049_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7218.5237 | 7209.76 | 7154.4451 | 7299.929 | 7023.651 | 7355.515 | GSO_42 | br_049_21 | 0e80773a-a8cc-45a5-8095-4dc9d8b00215 | br_049_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7216.6695 | 7208.48 | 7156.584 | 7291.5136 | 7034.626 | 7340.139 | GSO_43 | br_050_21 | 223df89f-b673-46b7-a74d-953aa3cadd02 | br_050_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7216.2767 | 7208.1595 | 7158.2243 | 7288.9399 | 7042.783 | 7346.268 | GSO_43 | br_050_21 | d8ed1451-4cac-4c54-9238-07312269a3d5 | br_050_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.7842 | 7208.181 | 7155.4098 | 7289.3819 | 7033.008 | 7334.648 | GSO_43 | br_050_21 | d260c5dc-0f9a-4ff7-a347-cabc3421f531 | br_050_21.C | C | OK
0 | [8 empty] | GSO_44 | br_051_21 | ae9708d6-58e3-48d8-b469-2b865749bda5 | br_051_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.7217 | 7207.2945 | 7163.1437 | 7286.0943 | 7028.315 | 7393.058 | GSO_44 | br_051_21 | 9de5605e-2be3-4478-8321-ec1cfdb77d3e | br_051_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7210.7588 | 7205.4405 | 7170.8424 | 7261.824 | 7037.943 | 7358.573 | GSO_44 | br_051_21 | c206a6a0-74a2-4aa0-b700-0397b158b47c | br_051_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.9133 | 7208.082 | 7157.1122 | 7288.744 | 7030.966 | 7329.357 | GSO_45 | br_052_21 | 0a36e22d-cb96-45c8-8d47-74ede8f433bd | br_052_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7218.619 | 7208.843 | 7159.9844 | 7297.333 | 7046.351 | 7348.097 | GSO_45 | br_052_21 | ac9dddc3-7cae-427c-a129-87d3008b8362 | br_052_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7216.511 | 7208.3375 | 7155.8524 | 7292.0028 | 7025.158 | 7341.13 | GSO_45 | br_052_21 | 87af0485-ac3b-4ef1-bd8e-39742bb1311b | br_052_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7217.5134 | 7208.8215 | 7157.3281 | 7294.1416 | 7030.403 | 7350.663 | GSO_46 | br_053_21 | 425e9895-3ec9-4ecf-a2de-00e847c9f5d0 | br_053_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7216.3368 | 7208.508 | 7155.0724 | 7291.6299 | 7019.875 | 7356.714 | GSO_46 | br_053_21 | e8d1fc00-bcf6-4d05-b6b9-7f38e6915ce5 | br_053_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.9663 | 7208.0145 | 7155.7057 | 7290.0787 | 7022.197 | 7335.577 | GSO_46 | br_053_21 | 0b8f662d-5bc3-42fe-a24e-070da09bdd80 | br_053_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7214.5003 | 7206.8645 | 7162.8767 | 7281.3782 | 7029.892 | 7366.855 | GSO_47 | br_054_21 | 44d72b2b-4d39-442e-969c-28bfa609a6ca | br_054_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7204.873 | 7201.5215 | 7163.0414 | 7254.2943 | 7028.672 | 7367.518 | GSO_47 | br_054_21 | df231f2b-7e74-4562-8026-e0248f99acb1 | br_054_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7206.0224 | 7201.942 | 7166.046 | 7255.1433 | 7042.72 | 7383.433 | GSO_47 | br_054_21 | 73020989-8b85-4f2f-ae5e-b46034dccc36 | br_054_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7214.1262 | 7206.0645 | 7168.9937 | 7278.9082 | 7040.019 | 7386.898 | GSO_48 | br_055_21 | caead5dd-6652-4002-9205-bf1f5d7841a2 | br_055_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7213.2 | 7205.769 | 7166.5917 | 7276.0028 | 7050.165 | 7396.08 | GSO_48 | br_055_21 | 2756c12d-de33-427b-a20e-a7524bf8ba2a | br_055_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7212.5187 | 7205.594 | 7165.3937 | 7275.377 | 7037.298 | 7400.607 | GSO_48 | br_055_21 | d501232c-0e9b-4aed-b1c7-0711f51fd12c | br_055_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7213.7994 | 7206.27 | 7167.0694 | 7277.2149 | 7057.402 | 7392.594 | GSO_49 | br_056_21 | 904a534b-b4de-47cc-9111-a909cdd75ff6 | br_056_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.1717 | 7206.8115 | 7169.6101 | 7280.1449 | 7043.116 | 7379.586 | GSO_49 | br_056_21 | cf17223b-5ef6-40ff-aa3f-7eaa71fa5ab1 | br_056_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7207.8245 | 7202.965 | 7166.8527 | 7258.5433 | 7046.812 | 7380.813 | GSO_49 | br_056_21 | 4e486c1d-6969-466b-bb85-e868d8c69d96 | br_056_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.1929 | 7208.115 | 7158.2647 | 7285.5193 | 7021.195 | 7377.471 | GSO_5 | br_05_21 | 1a7b2ce3-8ce4-43f0-822c-bae88f338574 | br_05_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7213.7879 | 7206.307 | 7160.3127 | 7282.432 | 7043.416 | 7390.02 | GSO_5 | br_05_21 | fdea0e08-11f9-40c1-bd4a-4dfdb8ea2803 | br_05_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7212.3819 | 7206.188 | 7159.8977 | 7276.9013 | 7022.957 | 7403.876 | GSO_5 | br_05_21 | 921b5057-9802-4094-b921-551288ad3d2e | br_05_21.C | C | OK
0 | [8 empty] | GSO_50 | br_057_21 | 4d9bb5e2-1e06-49ed-b322-273c65c7ea12 | br_057_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7217.4479 | 7208.345 | 7162.6087 | 7289.8403 | 7048.205 | 7382.127 | GSO_50 | br_057_21 | 02cb60eb-e56b-45c0-871a-7d5da5072e9a | br_057_21.B | B | OK
0 | [8 empty] | GSO_50 | br_057_21 | ceeee8fb-13b1-43c7-9caf-4433648f6846 | br_057_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7212.4391 | 7205.7255 | 7164.7827 | 7274.2005 | 7043.323 | 7388.971 | GSO_51 | br_058_21 | 2dabfa67-e633-42fb-88f8-b99c8c81ce3f | br_058_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7210.7764 | 7205.0015 | 7165.321 | 7267.4366 | 7031.074 | 7393.478 | GSO_51 | br_058_21 | 40e658e9-710a-4f81-b823-ce3b23d76208 | br_058_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7212.9168 | 7205.5085 | 7168.6754 | 7274.673 | 7032.18 | 7379.251 | GSO_51 | br_058_21 | 100d5254-7678-4ba2-a678-ffa8ba0ac8ce | br_058_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7217.1545 | 7208.3105 | 7158.2074 | 7292.7946 | 7037.862 | 7348.919 | GSO_52 | br_059_21 | 148e241f-8dca-40c2-bc4c-9bba11acb600 | br_059_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7216.0559 | 7208.2855 | 7154.95 | 7290.8026 | 7020.362 | 7334.09 | GSO_52 | br_059_21 | 740ff96c-6171-4486-bb6a-904851da7f68 | br_059_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.8365 | 7207.874 | 7156.0314 | 7289.212 | 7022.008 | 7355.853 | GSO_52 | br_059_21 | 54cc7298-372e-4f46-9c94-d78d3e7e3368 | br_059_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7218.6815 | 7208.9355 | 7158.9707 | 7297.8285 | 7030.684 | 7354.242 | GSO_53 | br_060_21 | 77c08208-993b-4559-b9e2-42c4c772997c | br_060_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7219.8617 | 7209.19 | 7162.7831 | 7299.8983 | 7039.365 | 7371.023 | GSO_53 | br_060_21 | 4b800952-fa1b-4668-ba63-4244710bab3c | br_060_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7209.0126 | 7205.197 | 7158.51 | 7263.043 | 7024.857 | 7312.744 | GSO_53 | br_060_21 | 3b012ead-fe04-4b66-8c50-59d42334a89c | br_060_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7217.0266 | 7208.63 | 7155.3215 | 7294.5482 | 7029.599 | 7345.299 | GSO_54 | br_061_21 | c70624cc-3511-421e-bcd3-4f74ee43c80f | br_061_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7216.9324 | 7208.7145 | 7156.9081 | 7292.0633 | 7039.188 | 7339.95 | GSO_54 | br_061_21 | 0c2d5da7-8b73-4e99-a2ec-e1bd371c44f1 | br_061_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7217.0555 | 7208.675 | 7156.2487 | 7293.111 | 7020.097 | 7342.938 | GSO_54 | br_061_21 | b486465e-b5c3-4f46-9979-e961ceb9df52 | br_061_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7210.8371 | 7204.223 | 7172.5084 | 7263.9058 | 7035.722 | 7395.43 | GSO_55 | br_062_21 | 55b291eb-5761-4e7f-8635-63057f856791 | br_062_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.7627 | 7207.611 | 7161.4228 | 7285.7467 | 7043.239 | 7364.353 | GSO_55 | br_062_21 | 0d627f19-7146-43b0-9f7b-bac68e9966db | br_062_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7216.8887 | 7208.5085 | 7162.8197 | 7287.5 | 7044.503 | 7340.372 | GSO_55 | br_062_21 | efb7b851-1f6e-4084-9dd6-5a62049b7654 | br_062_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7219.8583 | 7208.9495 | 7163.0233 | 7299.8013 | 7043.719 | 7379.13 | GSO_56 | br_063_21 | d5be6516-e14a-46ab-a02a-0650b74a5159 | br_063_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7214.0309 | 7206.5615 | 7160.8063 | 7282.6201 | 7034.107 | 7379.176 | GSO_56 | br_063_21 | 748858e9-a0e0-4bc6-a0b7-f4e67d7c9ecd | br_063_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7216.9956 | 7208.596 | 7160.4985 | 7289.878 | 7029.815 | 7359.505 | GSO_56 | br_063_21 | 620a8a0d-bcbd-4f44-be97-24244e308366 | br_063_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.334 | 7207.539 | 7161.7144 | 7283.7925 | 7020.914 | 7360.007 | GSO_57 | br_08_21 | 27046833-12e1-4f55-aeb1-743d3fddc9b4 | br_08_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7219.1604 | 7209.017 | 7159.9155 | 7299.3301 | 7026.914 | 7366.094 | GSO_57 | br_08_21 | e2d61ac2-432e-446d-b560-32b75aebceed | br_08_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7212.7341 | 7206.031 | 7164.8823 | 7274.2946 | 7041 | 7362.109 | GSO_57 | br_08_21 | 08dafb35-ef6e-48c6-89ef-1f3412fa5f7e | br_08_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.8393 | 7207.9825 | 7156.5744 | 7288.9357 | 7028.915 | 7340.455 | GSO_58 | br_09_21 | cd71f269-7897-4746-9a77-c6bc730114fe | br_09_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7216.443 | 7208.263 | 7156.4384 | 7291.9369 | 7031.447 | 7334.992 | GSO_58 | br_09_21 | ff232009-b42f-4f71-a769-88a952701609 | br_09_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7217.5558 | 7208.2 | 7160.001 | 7293.9913 | 7037.994 | 7337.18 | GSO_58 | br_09_21 | b8c6df33-b602-4d1c-9dda-e52dfeb41665 | br_09_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.7952 | 7208.1185 | 7155.6714 | 7289.4719 | 7030.333 | 7343.653 | GSO_59 | br_010_21 | 4529fb6d-421e-4f02-9b11-c956a4443f8e | br_010_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7216.9801 | 7208.4025 | 7156.827 | 7292.9023 | 7029.813 | 7360.041 | GSO_59 | br_010_21 | 1231155d-ed13-4563-8801-fa08388d11cd | br_010_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7216.759 | 7208.423 | 7157.5878 | 7290.9132 | 7032.205 | 7336.569 | GSO_59 | br_010_21 | 1b822839-e89f-49f2-b2a9-69df27011548 | br_010_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7217.975 | 7209.198 | 7157.262 | 7295.811 | 7019.858 | 7360.712 | GSO_6 | br_06_21 | 145f4423-0120-41c0-a961-6f6b453e91a7 | br_06_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7218.6368 | 7209.31 | 7158.5274 | 7298.5753 | 7040.707 | 7377.444 | GSO_6 | br_06_21 | 120599d7-eee0-4966-bd20-36d9e2e8b089 | br_06_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7217.0318 | 7209.0715 | 7155.3929 | 7293.5253 | 7038.448 | 7368.328 | GSO_6 | br_06_21 | a5d804f2-bcf0-4e70-ad7f-9ffc889ca71a | br_06_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7216.191 | 7208.03 | 7156.5718 | 7290.5723 | 7031.844 | 7349.984 | GSO_60 | br_011_21 | 229fce16-0cb2-401d-957b-9d0d3c2ac1cc | br_011_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7216.3915 | 7208.4115 | 7158.6387 | 7289.8687 | 7037.086 | 7353.708 | GSO_60 | br_011_21 | fc187080-4278-4699-8d7f-ded10dc27448 | br_011_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.8221 | 7208.2335 | 7159.2185 | 7287.4252 | 7031.344 | 7340.735 | GSO_60 | br_011_21 | 52980b4f-3c73-4c68-8631-e69ccc722a34 | br_011_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7214.9712 | 7207.897 | 7155.7443 | 7286.15 | 7029.209 | 7333.784 | GSO_61 | br_012_21 | bdb558af-9d90-4dcd-870e-28a86925b8cc | br_012_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.7097 | 7207.9955 | 7155.564 | 7289.231 | 7028.811 | 7346.349 | GSO_61 | br_012_21 | 192ef0e0-59f5-4932-a625-7e967573ec09 | br_012_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.7552 | 7208.2325 | 7155.3458 | 7289.509 | 7027.948 | 7337.657 | GSO_61 | br_012_21 | 69c0c6b0-aa07-4cdc-9789-b51b223584c4 | br_012_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7200.9471 | 7201.817 | 7162.9904 | 7231.939 | 7050.523 | 7265.269 | GSO_62 | br_013_21 | 2c8910bb-0c41-4c36-8a5f-d8ffc5e65938 | br_013_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.9623 | 7207.7345 | 7164.2574 | 7284.718 | 7057.297 | 7347.292 | GSO_62 | br_013_21 | 3f59d58a-b780-49d5-86ae-b0b0f01c076d | br_013_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7214.571 | 7207.385 | 7155.6228 | 7285.659 | 7024.907 | 7342.584 | GSO_62 | br_013_21 | decddce1-9f0e-44c6-a3bd-24fdb9cf1a60 | br_013_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7213.9656 | 7206.541 | 7170.2834 | 7275.5522 | 7076.604 | 7389.248 | GSO_63 | br_014_21 | 676b1650-044c-43bf-bea6-3dced2a612c6 | br_014_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7214.9811 | 7207.2055 | 7163.6707 | 7281.8772 | 7036.219 | 7367.344 | GSO_63 | br_014_21 | abbc8c51-7785-4d04-a735-eb965d943d5a | br_014_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7217.3964 | 7208.164 | 7165.0408 | 7288.9791 | 7039.605 | 7374.976 | GSO_63 | br_014_21 | 167b629e-ae1a-4acd-a435-a9faf6b8f0b1 | br_014_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.9508 | 7208.1955 | 7157.4191 | 7288.234 | 7039.797 | 7364.542 | GSO_64 | br_064_21 | aa668afa-9003-4c02-b068-76a760cba7c4 | br_064_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.9033 | 7207.931 | 7159.1644 | 7287.5529 | 7025.429 | 7366.352 | GSO_64 | br_064_21 | 8ec9092e-c513-4856-b139-17b0f244b287 | br_064_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7217.0775 | 7208.662 | 7157.8661 | 7292.6235 | 7025.686 | 7349.755 | GSO_64 | br_064_21 | 96d7ca9d-a8a7-4620-beb4-015993e1495f | br_064_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7206.1207 | 7201.087 | 7163.0298 | 7263.755 | 7028.381 | 7393.974 | GSO_65 | br_065_21 | a8421f63-1fb7-4386-80d1-558a9049f658 | br_065_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7209.0513 | 7203.834 | 7162.1424 | 7269.2626 | 7026.92 | 7395.691 | GSO_65 | br_065_21 | c0caf65c-2d30-471b-9a8c-36e1484ba877 | br_065_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7206.3077 | 7201.1225 | 7163.1053 | 7264.7805 | 7032.335 | 7399.487 | GSO_65 | br_065_21 | a2d74127-91f7-4d1b-a98b-b3f287f80eec | br_065_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.1492 | 7207.6235 | 7154.9842 | 7287.41 | 7025.604 | 7345.18 | GSO_66 | br_066_21 | aa212fd9-92d5-4c56-9a9e-3014ccc9a7ce | br_066_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7217.6025 | 7208.73 | 7156.3804 | 7295.2833 | 7026.735 | 7359.498 | GSO_66 | br_066_21 | 0cbf5c43-696f-40b4-ab01-fd3dfd670388 | br_066_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.7577 | 7208.1375 | 7157.6622 | 7287.2406 | 7035.16 | 7342.752 | GSO_66 | br_066_21 | 3f826b2c-284b-4880-a9f1-d5554c1e5213 | br_066_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7217.8583 | 7208.645 | 7158.8614 | 7295.2951 | 7036.498 | 7375.064 | GSO_67 | br_067_21 | fddc71cc-3766-4601-9ca7-c2caab3c7c4d | br_067_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7218.7983 | 7209.148 | 7160.5464 | 7296.1246 | 7034.765 | 7362.045 | GSO_67 | br_067_21 | 5aed073b-49c0-4020-b105-f7e28cfd41ed | br_067_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7217.4013 | 7208.713 | 7157.8504 | 7293.125 | 7036.847 | 7346.959 | GSO_67 | br_067_21 | 4b3c48a3-9a69-47a9-b110-7d0b18cc7f06 | br_067_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7216.1525 | 7208.25 | 7157.0565 | 7289.2603 | 7033.7 | 7345.095 | GSO_68 | br_068_21 | 6abb0433-d7c1-47cb-b500-310c0966ae29 | br_068_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7219.5354 | 7208.8615 | 7160.5258 | 7300.4956 | 7022.938 | 7378.702 | GSO_68 | br_068_21 | b14a51cb-21cb-48f4-91a6-564663c5a923 | br_068_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.621 | 7208.125 | 7156.8834 | 7287.3149 | 7024.239 | 7349.637 | GSO_68 | br_068_21 | f2986696-35a7-4d1e-a7dd-8b01d8d6756a | br_068_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7214.1648 | 7207.0335 | 7160.1162 | 7282.3762 | 7040.442 | 7404.695 | GSO_69 | br_069_21 | 16e446fe-cce5-4d4b-abd0-d9bf98278835 | br_069_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.0953 | 7207.4945 | 7163.2573 | 7281.6613 | 7048.365 | 7380.163 | GSO_69 | br_069_21 | 3f69baec-6464-4c01-91c1-171903c224f7 | br_069_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7213.2902 | 7207.009 | 7160.9632 | 7276.5626 | 7046.617 | 7370.48 | GSO_69 | br_069_21 | 9255af13-2569-446c-b326-8de2942e3a26 | br_069_21.C | C | OK
0 | [8 empty] | GSO_7 | br_07_21 | 874fce3a-0ddc-405e-8b4d-496bf1208ffa | br_07_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7205.8972 | 7201.097 | 7161.7451 | 7265.9657 | 7021.114 | 7394.917 | GSO_7 | br_07_21 | 7c4e0a27-0ba8-4589-8efa-9d78e22aeea7 | br_07_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7195.8081 | 7199.4445 | 7151.5238 | 7227.334 | 7035.899 | 7258.936 | GSO_7 | br_07_21 | b3997dcd-0479-4422-904f-1e86aedb3b49 | br_07_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.6732 | 7207.49 | 7164.59 | 7284.615 | 7044.224 | 7392.095 | GSO_70 | br_070_21 | ff4d78df-a97d-465a-9270-6b140f05b7ee | br_070_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7209.016 | 7203.6895 | 7169.5691 | 7260.5957 | 7075.951 | 7397.636 | GSO_70 | br_070_21 | 96d35f0d-746b-4c76-8d6d-a22dac3dcfaa | br_070_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7208.2302 | 7203.179 | 7166.832 | 7260.0316 | 7033.796 | 7381.615 | GSO_70 | br_070_21 | 7a4e8fb6-f007-4d77-bfcb-6a0b0e18561c | br_070_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.7755 | 7208.04 | 7157.0324 | 7288.1409 | 7031.212 | 7350.03 | GSO_71 | br_071_21 | 7dec81b6-3b82-498d-bfaa-f44bf5d9581d | br_071_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.2592 | 7207.838 | 7155.167 | 7287.8185 | 7025.2 | 7338.632 | GSO_71 | br_071_21 | 4ff8b560-0d8d-46ca-aa4f-48e616d84a8c | br_071_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.9741 | 7208.344 | 7154.7971 | 7290.003 | 7029.863 | 7346.146 | GSO_71 | br_071_21 | 828a3353-455f-43cc-a9b0-71980deae8fd | br_071_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7217.0323 | 7208.3645 | 7159.8799 | 7290.686 | 7035.943 | 7365.66 | GSO_72 | br_072_21 | 2f6074d9-3367-424b-9912-3b54ba3842dc | br_072_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7212.2769 | 7206.437 | 7157.703 | 7275.5417 | 7036.086 | 7318.722 | GSO_72 | br_072_21 | 5be2e72a-f9e3-4662-bcdd-f6914b127473 | br_072_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7213.8818 | 7207.345 | 7158.2641 | 7280.1039 | 7030.388 | 7345.54 | GSO_72 | br_072_21 | ceb3c16f-b2c1-4384-83e5-47eb8d9787a9 | br_072_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7209.9501 | 7203.232 | 7168.1261 | 7266.9118 | 7039.737 | 7384.712 | GSO_73 | br_073_21 | dd7e3ea9-a097-46d9-ba3d-e976877c959f | br_073_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7207.1411 | 7202.094 | 7165.0548 | 7260.999 | 7041.153 | 7394.523 | GSO_73 | br_073_21 | dc0e22aa-9b17-4812-81b9-805e6e2fcea4 | br_073_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7207.9008 | 7200.377 | 7161.2791 | 7273.6752 | 6987.051 | 7403.747 | GSO_73 | br_073_21 | 0a5bd7a0-8dda-4ea9-8140-b43dcad4334a | br_073_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7217.9543 | 7208.138 | 7163.689 | 7294.6044 | 7055.504 | 7401.805 | GSO_74 | br_074_21 | 4cb9db9e-b9c3-473e-878d-2df2932f4dcf | br_074_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.0811 | 7207.613 | 7161.1087 | 7282.3227 | 7039.079 | 7352.326 | GSO_74 | br_074_21 | 2be1e40d-d971-44eb-9f8e-1f362b00491f | br_074_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7216.7767 | 7207.794 | 7165.0408 | 7288.2063 | 7049.876 | 7405.794 | GSO_74 | br_074_21 | b4794b85-7397-40b2-a7b2-50c82c66983d | br_074_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7212.8538 | 7206.496 | 7160.8418 | 7277.3752 | 7030.621 | 7371.015 | GSO_75 | br_075_21 | 74ba07cb-a526-4618-b499-1a430d0286b7 | br_075_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7217.721 | 7208.4 | 7162.0597 | 7292.2406 | 7027.191 | 7392.568 | GSO_75 | br_075_21 | dc09ae69-e1ee-4c83-9c04-e09da568c6ab | br_075_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7213.3058 | 7206.6275 | 7164.9014 | 7275.0919 | 7027.838 | 7373.57 | GSO_75 | br_075_21 | 8cfdaf81-8e59-4486-ba2f-4e450a23c876 | br_075_21.C | C | OK
0 | [8 empty] | GSO_76 | br_076_21 | 89cbe802-faf3-4709-b370-afa1154a5b70 | br_076_21.A | A | OK
0 | [8 empty] | GSO_76 | br_076_21 | fd14c6a3-6658-4039-a0b8-c00ab26e307c | br_076_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.5004 | 7207.7875 | 7164.72 | 7281.96 | 7058.493 | 7370.531 | GSO_76 | br_076_21 | a61580ad-490f-42dd-919c-3cfdfb775908 | br_076_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7216.1447 | 7207.686 | 7156.1053 | 7291.3597 | 7036.922 | 7355.039 | GSO_77 | br_077_21 | 04933340-1f7e-4732-a170-31c687c8d71e | br_077_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7216.4596 | 7208.278 | 7155.6683 | 7291.6793 | 7031.704 | 7344.783 | GSO_77 | br_077_21 | da253492-f9e5-4572-a892-8cf7206f5562 | br_077_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7207.1148 | 7204.953 | 7157.2588 | 7255.9416 | 7034.795 | 7293.969 | GSO_77 | br_077_21 | 55611621-48c6-40ab-afb0-d76e41a0d5de | br_077_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7218.3944 | 7208.398 | 7161.9514 | 7296.0196 | 7019.933 | 7383.27 | GSO_78 | br_078_21 | c0ddba19-fbd3-4341-bb7c-f8d96301d889 | br_078_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7217.9901 | 7209.1305 | 7158.4231 | 7295.112 | 7041.958 | 7371.452 | GSO_78 | br_078_21 | 648e5aaa-f39d-4756-9d09-ca5503bbc225 | br_078_21.B | B | OK
0 | [8 empty] | GSO_78 | br_078_21 | 838a2e79-8d23-4760-9eab-eb6ed2d38b4c | br_078_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7221.4765 | 7208.9705 | 7160.1835 | 7310.2322 | 7042.092 | 7392.982 | GSO_79 | br_079_21 | dfd547e9-e06c-4fe7-8842-913f0b3f7d52 | br_079_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.6318 | 7207.6855 | 7160.591 | 7285.5147 | 7042.367 | 7377.536 | GSO_79 | br_079_21 | f68a1c8a-5406-4783-b8ae-a255bce0e795 | br_079_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.9397 | 7208.1085 | 7158.9527 | 7287.2906 | 7031.057 | 7344.135 | GSO_79 | br_079_21 | 02d224d1-8d1b-45bb-98ed-ebc20c74318a | br_079_21.C | C | OK
0 | [8 empty] | GSO_8 | br_022_21 | 9e0bf50d-94bd-4e5d-9a43-95a506f4c534 | br_022_21.A | A | OK
0 | [8 empty] | GSO_8 | br_022_21 | 14a29c10-6f6b-4045-834c-a8cdccfa7fe8 | br_022_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7214.2242 | 7206.8805 | 7166.1623 | 7277.7167 | 7023.839 | 7356.725 | GSO_8 | br_022_21 | 674756f5-28ec-40f8-8ece-cd6c8a394c18 | br_022_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7206.9182 | 7204.657 | 7158.3421 | 7254.5779 | 7038.262 | 7295.787 | GSO_80 | br_080_21 | 4fb9d568-cec8-4d2c-b185-503c8441a94f | br_080_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7216.6189 | 7208.465 | 7156.3121 | 7291.9886 | 7029.388 | 7349.599 | GSO_80 | br_080_21 | 48527915-ef6b-4d16-9525-f6d17fae71ba | br_080_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7218.2514 | 7209.0455 | 7158.4853 | 7296.8136 | 7042.835 | 7360.017 | GSO_80 | br_080_21 | e4842198-5ba7-4542-9415-20f0a87511ac | br_080_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7218.1871 | 7208.7565 | 7162.2 | 7294.29 | 7056.459 | 7376.401 | GSO_81 | br_081_21 | 9a5c0969-f68d-4cea-a13e-ef351a3d3730 | br_081_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.0403 | 7207.5515 | 7158.627 | 7285.1249 | 7028.924 | 7364.172 | GSO_81 | br_081_21 | a8a2fc9d-e642-4554-abad-f2610eb29b51 | br_081_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7219.9903 | 7209.172 | 7162.3398 | 7300.9326 | 7031.609 | 7379.533 | GSO_81 | br_081_21 | 27bb62b3-e552-4996-874d-31dcad547987 | br_081_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7216.6384 | 7208.5885 | 7155.9567 | 7291.4052 | 7016.762 | 7348.626 | GSO_82 | br_082_21 | a890d29a-0380-4cd2-8cff-f9826e3ff07b | br_082_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7216.2977 | 7208.259 | 7159.058 | 7288.0413 | 7018.098 | 7336.403 | GSO_82 | br_082_21 | 918cae00-7f70-4556-9d40-35da1f05977d | br_082_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.6152 | 7207.9945 | 7157.9453 | 7286.613 | 7043.608 | 7345.808 | GSO_82 | br_082_21 | 93c33640-e4a0-470f-a164-89c99ae69984 | br_082_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7216.4992 | 7208.1095 | 7155.936 | 7292.5603 | 7027.94 | 7343.715 | GSO_83 | br_083_21 | af9148e3-1b4f-4f27-b409-3654c3f953f5 | br_083_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.7309 | 7207.989 | 7155.2625 | 7289.7127 | 7023.24 | 7339.323 | GSO_83 | br_083_21 | 48c0048d-65ab-48a8-8cd9-833258bee864 | br_083_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7217.0556 | 7208.738 | 7156.4478 | 7292.5132 | 7024.316 | 7352.078 | GSO_83 | br_083_21 | 8c265c14-8e0f-4c74-9519-46da2dff7cd1 | br_083_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7218.608 | 7209.276 | 7159.738 | 7296.5661 | 7036.604 | 7369.501 | GSO_84 | br_084_21 | d4454767-7751-4c58-9cbd-79e943f45acf | br_084_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7214.7766 | 7207.1525 | 7167.39 | 7278.6426 | 7058 | 7399.196 | GSO_84 | br_084_21 | 4cc5af87-12cf-4fd1-a89c-0318dc07c068 | br_084_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.7919 | 7207.165 | 7165.288 | 7285.1753 | 7017.501 | 7365.089 | GSO_84 | br_084_21 | b63c8e73-fffc-4e69-ad08-995c149ebeaa | br_084_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7216.8278 | 7208.261 | 7161.4787 | 7289.5313 | 7034.763 | 7386.337 | GSO_85 | br_085_21 | 6fcd01be-d3d1-4df7-bec8-4f8b1042aac0 | br_085_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.8186 | 7207.4445 | 7161.5458 | 7287.0867 | 7039.173 | 7401.007 | GSO_85 | br_085_21 | 4fc59078-b2c4-42d5-b129-faa7a3f54cac | br_085_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7213.5127 | 7206.79 | 7161.7433 | 7278.275 | 7029.753 | 7379.724 | GSO_85 | br_085_21 | ac192c64-42ef-423f-814b-c8b837b8f5d2 | br_085_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7214.4339 | 7206.9475 | 7157.7648 | 7283.8197 | 7037.464 | 7361.588 | GSO_86 | br_086_21 | 492c962b-e2b7-4edd-afe9-20606e4114f6 | br_086_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7217.2619 | 7208.7005 | 7158.2443 | 7292.1719 | 7020.439 | 7361.105 | GSO_86 | br_086_21 | 6182a628-fb52-41b9-8b93-90488a51a0fe | br_086_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7217.3979 | 7208.8615 | 7157.4523 | 7292.4896 | 7031.181 | 7364.76 | GSO_86 | br_086_21 | 6927b6e8-4d14-436e-8236-19dc4cdad934 | br_086_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7213.3463 | 7206.988 | 7157.6638 | 7279.286 | 7040.907 | 7339.709 | GSO_87 | br_087_21 | e7689375-373b-4d7a-b001-0fa11239a327 | br_087_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7216.8372 | 7208.107 | 7161.6505 | 7289.0616 | 7051.221 | 7363.641 | GSO_87 | br_087_21 | 589e4f98-7742-4541-b2c3-6b108b7f9d4d | br_087_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7214.6752 | 7207.7245 | 7157.7194 | 7283.2983 | 7023.684 | 7359.829 | GSO_87 | br_087_21 | d9c84a3d-b565-4642-a7d4-3c9df307b1c8 | br_087_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7217.5829 | 7208.6525 | 7157.903 | 7293.8588 | 7036.979 | 7355.502 | GSO_88 | br_088_21 | 93986b58-113b-4798-b153-eda6e8924352 | br_088_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7214.7847 | 7206.9745 | 7160.2295 | 7284.5796 | 7034.854 | 7398.63 | GSO_88 | br_088_21 | 73bea406-8df3-48d6-99e8-780c9ba74d8d | br_088_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7217.6553 | 7208.4655 | 7162.7731 | 7291.5716 | 7024.557 | 7386.5 | GSO_88 | br_088_21 | b1fd8626-d75b-4f57-95d8-5e0f995f6548 | br_088_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7203.4131 | 7202.67 | 7157.0953 | 7245.14 | 7043.136 | 7305.109 | GSO_89 | br_089_21 | d629f58a-fb37-4300-b174-4dadcd7fdef5 | br_089_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7201.3506 | 7201.9615 | 7159.0577 | 7236.4586 | 7037.101 | 7280.262 | GSO_89 | br_089_21 | c6e42508-1e1b-4a8d-ad6c-5ed17230666d | br_089_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7208.2017 | 7204.5305 | 7155.416 | 7263.6473 | 7028.922 | 7316.769 | GSO_89 | br_089_21 | a59c7bce-fb93-4255-8dac-4024e2c3a1c9 | br_089_21.C | C | OK
0 | [8 empty] | GSO_9 | br_023_21 | c7e10126-bd63-4bd3-96ab-07587af29378 | br_023_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7213.8407 | 7206.4735 | 7169.3564 | 7274.7069 | 7036.314 | 7398.067 | GSO_9 | br_023_21 | f631ee12-3be7-417b-ad19-901e9ad68684 | br_023_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7209.5842 | 7202.982 | 7168.3966 | 7270.1407 | 7063.268 | 7375.544 | GSO_9 | br_023_21 | 9b89dc0e-e258-4610-b60b-484b1b02a312 | br_023_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7211.4057 | 7205.324 | 7161.6914 | 7274.1723 | 7035.345 | 7378.27 | GSO_90 | br_090_21 | ab8abf18-0128-43c3-8213-8fcc30f583d2 | br_090_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7213.4059 | 7206.617 | 7162.335 | 7278.7077 | 7046.696 | 7391.01 | GSO_90 | br_090_21 | 59f75e54-a46d-4153-8855-555945d0a888 | br_090_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7209.5837 | 7203.595 | 7163.7253 | 7268.963 | 7027.269 | 7394.585 | GSO_90 | br_090_21 | f35586be-8010-4ad3-b579-d95b9825cae5 | br_090_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7218.63 | 7208.619 | 7164.3295 | 7293.9873 | 7056.984 | 7368.059 | GSO_91 | br_091_21 | 11eec288-b107-4b0d-8513-8e0e8b097ff9 | br_091_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7217.8125 | 7208.4565 | 7161.9621 | 7292.8976 | 7032.754 | 7381.484 | GSO_91 | br_091_21 | 66b6c9ff-fe2f-4708-83aa-26715afe7d27 | br_091_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7217.5705 | 7208.5295 | 7162.6808 | 7290.4425 | 7054.194 | 7349.135 | GSO_91 | br_091_21 | 2494a26c-ddcb-40f8-8643-7c936424dfc0 | br_091_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7216.6166 | 7207.6855 | 7163.626 | 7288.4225 | 7044.05 | 7398.959 | GSO_92 | br_092_21 | a984179e-ff24-4a5b-9bff-44fa02582a26 | br_092_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7211.5031 | 7205.219 | 7164.3354 | 7272.4385 | 7032.834 | 7390.946 | GSO_92 | br_092_21 | fbe573a4-e81d-4315-b9c9-510a65c98be6 | br_092_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7210.842 | 7204.832 | 7160.4825 | 7271.903 | 7042.616 | 7371.121 | GSO_92 | br_092_21 | 9e7256be-44ac-40e3-95c4-e604f1b5b6ea | br_092_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7211.8272 | 7205.196 | 7164.5423 | 7273.729 | 7040.381 | 7413.538 | GSO_93 | br_093_21 | ac7b38f5-50a1-4cc6-bab1-d609ee8f92a4 | br_093_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7216.6256 | 7208.177 | 7161.8504 | 7288.9437 | 7038.805 | 7377.404 | GSO_93 | br_093_21 | 75f25960-b76b-4ea6-95b3-22351b5c7fde | br_093_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.0432 | 7206.396 | 7167.271 | 7283.076 | 7049.811 | 7383.599 | GSO_93 | br_093_21 | 531ef22d-48aa-4ee9-88be-bf0b21101c8d | br_093_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.8403 | 7207.15 | 7162.1317 | 7288.347 | 7024.219 | 7396.239 | GSO_94 | br_094_21 | f0bd6ef7-dacb-46d2-ad18-589db990b13a | br_094_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7212.7389 | 7206.354 | 7164.207 | 7273.7439 | 7038.382 | 7396.168 | GSO_94 | br_094_21 | a82b3639-950c-4ba5-8e39-502e435ad83a | br_094_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7213.343 | 7206.4825 | 7164.2347 | 7276.4753 | 7018.565 | 7380.014 | GSO_94 | br_094_21 | c177967e-e6f6-4644-aa50-326a9ebe3d00 | br_094_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.8261 | 7208.193 | 7156.1458 | 7289.1093 | 7030.294 | 7333.625 | GSO_95 | br_095_21 | 859a9ae6-4d75-45f7-af3f-1d1c2c11b96f | br_095_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7217.3642 | 7208.474 | 7158.3047 | 7293.1933 | 7036.175 | 7350.672 | GSO_95 | br_095_21 | ad766f3b-7d19-4707-8a90-38f818011b97 | br_095_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7218.6072 | 7208.8645 | 7158.7207 | 7298.9305 | 7035.639 | 7354.334 | GSO_95 | br_095_21 | c6b6dfcf-55ed-45e7-9e6a-1ed25774a828 | br_095_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.6623 | 7207.555 | 7161.264 | 7286.8817 | 7016.661 | 7387.063 | GSO_96 | br_096_21 | 1b5731fb-ced8-4f58-b1ab-d0ee4f8ea875 | br_096_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7217.6007 | 7208.686 | 7156.9344 | 7295.4159 | 7025.591 | 7365.089 | GSO_96 | br_096_21 | fcbaf392-5711-44ee-86c0-792317753d2f | br_096_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.0591 | 7207.1 | 7163.269 | 7283.2742 | 7043.704 | 7389.602 | GSO_96 | br_096_21 | fad28770-b3f6-4478-87a1-3b095d264a87 | br_096_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7216.8698 | 7208.265 | 7156.487 | 7292.9456 | 7035.922 | 7341.841 | GSO_97 | br_098_21 | 003a8d77-c248-43c2-af2f-1f5f30595e2b | br_098_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.4802 | 7208.238 | 7154.7981 | 7288.0237 | 7027.295 | 7337.104 | GSO_97 | br_098_21 | b3f7a58f-66bb-4c73-a447-90250ee96029 | br_098_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.246 | 7207.926 | 7157.232 | 7285.5802 | 7029.951 | 7349.288 | GSO_97 | br_098_21 | 3b017716-3815-48f3-bf37-e278bd03cc9d | br_098_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.959 | 7208.317 | 7155.6829 | 7289.4437 | 7030.829 | 7338.381 | GSO_98 | br_099_21 | e19d273e-4ce0-462d-9501-16552f6df1a5 | br_099_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7215.8771 | 7208.1175 | 7156.3002 | 7289.4416 | 7027.973 | 7345.411 | GSO_98 | br_099_21 | 74d4c75b-fdbd-4356-81ba-130cbea2e530 | br_099_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7199.1284 | 7202.312 | 7156.447 | 7225.3126 | 7029.363 | 7238.012 | GSO_98 | br_099_21 | 43272e40-5062-4f3e-9a6d-0899fa207db5 | br_099_21.C | C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7218.8637 | 7208.8615 | 7159.1861 | 7298.442 | 7024.329 | 7349.561 | GSO_99 | br_0100_21 | a3c897bb-ba13-4a0b-af16-81acabf20ccd | br_0100_21.A | A | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7217.0449 | 7208.395 | 7157.6944 | 7292.4956 | 7028.516 | 7343.945 | GSO_99 | br_0100_21 | 667e5144-bfb1-4543-a81f-7a88e26190c7 | br_0100_21.B | B | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 7217.1472 | 7208.6395 | 7156.4087 | 7293.6487 | 7030.285 | 7340.956 | GSO_99 | br_0100_21 | 9d892d7c-e138-4107-8084-bbde890e1cc4 | br_0100_21.C | C | OK

## SCADA_Voltage_Summary
grid_id | BreakerElementID | VoltageSourceCount | SCADAAverageVoltage | SCADAMedianVoltage | SCADAP05Voltage | SCADAP95Voltage | SCADAMinimumVoltage | SCADAMaximumVoltage | VoltageSCADAStatus | PhaseAAverageVoltage | PhaseAP05Voltage | PhaseAMinimumVoltage | PhaseAMaximumVoltage | PhaseBAverageVoltage | PhaseBP05Voltage | PhaseBMinimumVoltage | PhaseBMaximumVoltage | PhaseCAverageVoltage | PhaseCP05Voltage | PhaseCMinimumVoltage | PhaseCMaximumVoltage
GSO_1 | br_01_21 | 3 | 7215.5052 | 7207.8373 | 7157.5324 | 7293.2092 | 7025.575 | 7404.224 | OK | 7216.7574 | 7160.1403 | 7042.119 | 7396.429 | 7212.1779 | 7157.5324 | 7025.575 | 7379.073 | 7217.5801 | 7160.058 | 7032.508 | 7404.224
GSO_10 | br_015_21 | 3 | 7214.6024 | 7207.4963 | 7157.2806 | 7287.425 | 7029.711 | 7360.154 | OK | 7215.7135 | 7157.2806 | 7036.492 | 7360.154 | 7213.7068 | 7159.8699 | 7029.851 | 7347.808 | 7214.3869 | 7158.904 | 7029.711 | 7336.52
GSO_100 | br_097_21 | 3 | 7216.7476 | 7208.478 | 7158.3004 | 7292.7356 | 7002.413 | 7364.021 | OK |  |  |  |  | 7217.1997 | 7158.3004 | 7025.233 | 7359.802 | 7216.2955 | 7162.5811 | 7002.413 | 7364.021
GSO_101 | br_0101_21 | 3 | 7215.8272 | 7208.2232 | 7154.528 | 7295.7893 | 7015.109 | 7397.203 | OK | 7217.5121 | 7154.528 | 7032.468 | 7354.335 | 7215.0523 | 7161.6221 | 7015.109 | 7367.048 | 7214.917 | 7160.318 | 7041.751 | 7397.203
GSO_102 | br_0102_21 | 3 | 7216.7715 | 7207.7722 | 7163.308 | 7289.008 | 7050.956 | 7390.816 | OK | 7215.2337 | 7163.308 | 7050.956 | 7388.052 |  |  |  |  | 7218.3094 | 7174.9384 | 7054.77 | 7390.816
GSO_103 | br_0103_21 | 3 | 7217.5838 | 7209.3302 | 7151.807 | 7300.5822 | 7021.579 | 7352.907 | OK | 7216.7061 | 7154.8283 | 7034.039 | 7340.187 | 7218.8255 | 7155.0603 | 7030.722 | 7352.907 | 7217.2199 | 7151.807 | 7021.579 | 7342.457
GSO_104 | br_0104_21 | 3 | 7217.7306 | 7209.3962 | 7153.0402 | 7299.415 | 7017.727 | 7352.66 | OK | 7217.3862 | 7153.0402 | 7017.727 | 7346.738 | 7217.7692 | 7154.6534 | 7032.591 | 7352.66 | 7218.0364 | 7154.0648 | 7030.547 | 7352.079
GSO_105 | br_0105_21 | 3 | 7218.4899 | 7209.6347 | 7153.4294 | 7304.0023 | 7026.907 | 7361.976 | OK | 7219.6787 | 7156.0454 | 7038.264 | 7361.976 | 7218.4431 | 7156.994 | 7041.808 | 7350.941 | 7217.3479 | 7153.4294 | 7026.907 | 7349.655
GSO_106 | br_0106_21 | 3 | 7219.7757 | 7209.4073 | 7161.0111 | 7301.3522 | 7029.431 | 7401.993 | OK | 7219.34 | 7161.0111 | 7046.926 | 7388.014 |  |  |  |  | 7220.2115 | 7162.2897 | 7029.431 | 7401.993
GSO_107 | br_0107_21 | 3 | 7207.0077 | 7202.351 | 7166.9631 | 7258.7276 | 7022.37 | 7395.225 | OK | 7208.5988 | 7170.413 | 7051.932 | 7387.587 | 7206.0329 | 7170.9994 | 7036.44 | 7392.051 | 7206.3914 | 7166.9631 | 7022.37 | 7395.225
GSO_108 | br_0108_21 | 3 | 7218.5029 | 7209.4222 | 7152.0488 | 7303.3036 | 7018.219 | 7377.273 | OK | 7217.0711 | 7152.0488 | 7020.781 | 7374.353 | 7218.7109 | 7153.8113 | 7018.219 | 7373.962 | 7219.7267 | 7156.2754 | 7027.699 | 7377.273
GSO_109 | br_0109_21 | 3 | 7218.2454 | 7209.5723 | 7154.3264 | 7301.8462 | 7013.79 | 7376.767 | OK | 7219.2755 | 7158.4793 | 7039.526 | 7361.076 | 7219.1168 | 7154.3264 | 7013.79 | 7376.767 | 7216.3438 | 7159.2487 | 7027.561 | 7356.999
GSO_11 | br_016_21 | 3 | 7213.5801 | 7206.9057 | 7155.8687 | 7286.1987 | 7021.29 | 7361.658 | OK | 7215.4504 | 7158.1775 | 7031.483 | 7361.658 | 7213.2752 | 7156.9751 | 7031.188 | 7341.442 | 7212.0148 | 7155.8687 | 7021.29 | 7337.258
GSO_110 | br_0110_21 | 3 | 7218.5578 | 7209.5133 | 7154.3927 | 7303.0236 | 7032.828 | 7366.994 | OK | 7217.5903 | 7156.5028 | 7038.304 | 7349.554 | 7219.8296 | 7156.978 | 7039.344 | 7366.994 | 7218.2535 | 7154.3927 | 7032.828 | 7357.523
GSO_111 | br_0111_21 | 3 | 7208.1469 | 7205.3898 | 7152.4801 | 7298.7433 | 7022.906 | 7370.484 | OK | 7203.5009 | 7153.9956 | 7030.373 | 7294.406 | 7202.15 | 7152.4801 | 7022.906 | 7274.06 | 7218.7898 | 7158.0204 | 7035.072 | 7370.484
GSO_112 | br_0112_21 | 3 | 7207.9653 | 7203.8973 | 7164.223 | 7277.3857 | 7046.776 | 7396.822 | OK | 7213.0353 | 7164.6551 | 7048.228 | 7376.669 | 7197.6072 | 7164.223 | 7046.776 | 7273.008 | 7213.2535 | 7166.0987 | 7047.055 | 7396.822
GSO_113 | br_0113_21 | 3 | 7207.7258 | 7202.7598 | 7166.094 | 7265.2236 | 7003.726 | 7393.634 | OK | 7205.9252 | 7167.059 | 7003.726 | 7393.634 | 7209.7353 | 7167.5237 | 7042.923 | 7389.602 | 7207.5169 | 7166.094 | 7024.062 | 7389.029
GSO_114 | br_0114_21 | 3 | 7217.5015 | 7209.1627 | 7156.8274 | 7305.5036 | 7034.026 | 7375.435 | OK | 7217.5945 | 7158.642 | 7034.026 | 7359.088 | 7214.2928 | 7157.2792 | 7034.57 | 7348.25 | 7220.6173 | 7156.8274 | 7037.237 | 7375.435
GSO_115 | br_0115_21 | 3 | 7216.7108 | 7208.4273 | 7156.9744 | 7293.8006 | 7021.72 | 7347.676 | OK | 7215.565 | 7157.2431 | 7021.72 | 7339.975 | 7217.2403 | 7156.9744 | 7023.039 | 7347.676 | 7217.3271 | 7159.5944 | 7049.57 | 7347.212
GSO_116 | br_0116_21 | 3 | 7214.5854 | 7207.1007 | 7158.2792 | 7289.1399 | 7015.91 | 7380.441 | OK | 7212.1272 | 7163.6835 | 7032.298 | 7378.893 | 7215.2665 | 7159.7711 | 7015.91 | 7380.441 | 7216.3624 | 7158.2792 | 7042.425 | 7351.179
GSO_117 | br_0117_21 | 3 | 7216.184 | 7208.2262 | 7154.8054 | 7296.203 | 7028.852 | 7350.549 | OK | 7215.3729 | 7154.8054 | 7028.852 | 7346.952 | 7215.3451 | 7155.5291 | 7030.75 | 7336.216 | 7217.8339 | 7156.4973 | 7034.986 | 7350.549
GSO_118 | br_0118_21 | 3 | 7215.0042 | 7207.7745 | 7156.5658 | 7292.1447 | 7021.733 | 7388.318 | OK | 7215.3234 | 7160.0714 | 7046.957 | 7388.318 | 7212.7426 | 7163.0617 | 7054.647 | 7348.819 | 7216.9467 | 7156.5658 | 7021.733 | 7349.313
GSO_119 | br_0119_21 | 3 | 7217.6371 | 7208.9533 | 7159.6174 | 7295.6686 | 7027.404 | 7375.598 | OK | 7218.6921 | 7159.6174 | 7027.404 | 7371.066 | 7216.6741 | 7163.2609 | 7051.481 | 7370.381 | 7217.545 | 7162.5343 | 7031.642 | 7375.598
GSO_12 | br_017_21 | 3 | 7216.2476 | 7208.2533 | 7154.6751 | 7292.8687 | 7027.606 | 7344.314 | OK | 7217.2488 | 7158.415 | 7027.606 | 7344.314 | 7216.1738 | 7155.9948 | 7033.07 | 7344.067 | 7215.3203 | 7154.6751 | 7027.993 | 7342.148
GSO_121 | br_01_22 | 3 | 7213.9157 | 7206.4652 | 7160.5141 | 7282.7945 | 7029.038 | 7396.153 | OK | 7214.2313 | 7165.2033 | 7039.781 | 7394.362 | 7213.0706 | 7162.4387 | 7029.038 | 7396.153 | 7214.4454 | 7160.5141 | 7035.078 | 7386.541
GSO_122 | br_02_22 | 3 | 7206.9558 | 7202.1623 | 7162.7293 | 7262.722 | 7029.892 | 7398.179 | OK | 7206.9294 | 7167.1137 | 7033.548 | 7376.914 | 7206.9385 | 7166.3363 | 7042.809 | 7386.879 | 7206.9995 | 7162.7293 | 7029.892 | 7398.179
GSO_123 | br_03_22 | 3 | 7209.9826 | 7204.5635 | 7160.7653 | 7270.5913 | 7022.253 | 7383.732 | OK | 7209.9177 | 7163.212 | 7022.253 | 7377.317 | 7210.9486 | 7166.3879 | 7035.194 | 7382.854 | 7209.0817 | 7160.7653 | 7029.085 | 7383.732
GSO_124 | br_04_22 | 3 | 7208.3181 | 7203.1612 | 7154.8937 | 7269.9309 | 7005.586 | 7387.821 | OK | 7207.2665 | 7165.9279 | 7005.586 | 7378.288 | 7206.5732 | 7154.8937 | 7057.389 | 7387.123 | 7211.1145 | 7168.9828 | 7028.827 | 7387.821
GSO_125 | br_05_22 | 3 | 7211.4318 | 7205.7533 | 7161.9564 | 7271.5392 | 7024.71 | 7385.96 | OK | 7212.0974 | 7166.3797 | 7044.963 | 7382.54 | 7211.6453 | 7162.6512 | 7024.71 | 7385.96 | 7210.5525 | 7161.9564 | 7044.728 | 7370.4
GSO_126 | br_06_22 | 3 | 7209.3824 | 7203.0248 | 7158.9918 | 7275.944 | 7007.034 | 7404.106 | OK | 7208.8983 | 7160.3681 | 7007.034 | 7391.187 | 7210.81 | 7163.7595 | 7031.745 | 7404.106 | 7208.439 | 7158.9918 | 7034.591 | 7393.787
GSO_127 | br_07_22 | 3 | 7204.8208 | 7201.1828 | 7160.8637 | 7257.6768 | 7003.738 | 7390.05 | OK | 7204.7881 | 7160.8637 | 7003.738 | 7385.541 | 7204.7955 | 7161.2317 | 7025.791 | 7390.05 | 7204.8787 | 7160.9694 | 7019.075 | 7384.944
GSO_128 | br_08_22 | 3 | 7209.2014 | 7203.343 | 7164.4391 | 7273.6893 | 7024.028 | 7401.973 | OK | 7210.8994 | 7164.4391 | 7053.457 | 7401.973 | 7208.2738 | 7167.6267 | 7024.028 | 7388.792 | 7208.431 | 7164.855 | 7046.559 | 7390.925
GSO_129 | br_09_22 | 3 | 7211.198 | 7205.0408 | 7160.769 | 7281.385 | 7013.679 | 7397.262 | OK | 7213.2723 | 7160.769 | 7013.679 | 7390.702 | 7210.6698 | 7162.8377 | 7041.943 | 7390.199 | 7209.6521 | 7163.1615 | 7020.903 | 7397.262
GSO_13 | br_018_21 | 3 | 7211.3179 | 7206.4673 | 7156.4895 | 7289.176 | 7029.021 | 7357.057 | OK | 7215.9378 | 7156.4895 | 7035.417 | 7345.131 | 7214.4965 | 7157.6534 | 7029.021 | 7357.057 | 7203.5194 | 7158.538 | 7032.707 | 7271.453
GSO_130 | br_010_22 | 3 | 7210.0993 | 7204.219 | 7159.6044 | 7271.0877 | 7027.936 | 7383.214 | OK | 7211.2124 | 7167.3361 | 7050.508 | 7383.214 | 7209.0908 | 7159.6044 | 7031.164 | 7377.911 | 7209.9946 | 7167.9577 | 7027.936 | 7367.223
GSO_131 | br_011_22 | 3 | 7209.3212 | 7203.5 | 7165.9882 | 7265.7639 | 6987.82 | 7394.459 | OK | 7209.2825 | 7166.6618 | 7010.312 | 7387.689 | 7209.4486 | 7166.3811 | 7001.625 | 7386.858 | 7209.2326 | 7165.9882 | 6987.82 | 7394.459
GSO_132 | br_012_22 | 3 | 7210.7364 | 7204.5092 | 7159.8988 | 7279.6497 | 7025.031 | 7404.132 | OK | 7213.453 | 7163.2874 | 7053.594 | 7404.132 | 7209.726 | 7159.8988 | 7025.913 | 7385.751 | 7209.0302 | 7159.9821 | 7025.031 | 7394.927
GSO_133 | br_013_22 | 3 | 7210.8249 | 7205.0537 | 7160.7667 | 7276.089 | 7025.626 | 7409.839 | OK | 7208.546 | 7164.2847 | 7027.764 | 7384.006 | 7211.8404 | 7160.7667 | 7037.181 | 7386.89 | 7212.0883 | 7162.0651 | 7025.626 | 7409.839
GSO_134 | br_014_22 | 3 | 7206.0917 | 7201.8808 | 7153.3993 | 7267.3596 | 7010.309 | 7395.425 | OK | 7208.2063 | 7160.0073 | 7024.842 | 7386.148 | 7207.283 | 7158.5871 | 7010.309 | 7395.425 | 7202.7857 | 7153.3993 | 7023.807 | 7381.334
GSO_135 | br_015_22 | 3 | 7208.264 | 7203.0272 | 7156.4443 | 7274.795 | 7044.488 | 7398.005 | OK | 7204.0232 | 7156.4443 | 7044.488 | 7382.455 | 7211.6993 | 7163.139 | 7052.077 | 7391.839 | 7209.0694 | 7163.648 | 7048.886 | 7398.005
GSO_136 | br_016_22 | 3 | 7209.1278 | 7203.8727 | 7162.9973 | 7270.215 | 7007.673 | 7388.402 | OK | 7208.1837 | 7162.9973 | 7026.756 | 7382.77 | 7210.4734 | 7165.3344 | 7007.673 | 7388.402 | 7208.7264 | 7163.9968 | 7022.48 | 7377.629
GSO_137 | br_017_22 | 3 | 7212.3065 | 7205.9177 | 7160.45 | 7281.0173 | 7030.635 | 7392.03 | OK | 7213.852 | 7160.45 | 7030.635 | 7384.785 | 7211.1325 | 7161.4777 | 7034.534 | 7378.7 | 7211.9349 | 7162.634 | 7038.113 | 7392.03
GSO_138 | br_018_22 | 3 | 7213.9852 | 7206.6448 | 7159.0362 | 7286.9579 | 7047.309 | 7388.782 | OK | 7212.8076 | 7159.0362 | 7047.488 | 7388.782 | 7213.1858 | 7165.1264 | 7047.309 | 7385.392 | 7215.9621 | 7162.0994 | 7057.249 | 7356.492
GSO_139 | br_019_22 | 3 | 7208.9415 | 7204.6222 | 7165.2004 | 7263.2199 | 7002.039 | 7396.818 | OK | 7210.2124 | 7165.2004 | 7012.353 | 7396.818 | 7210.0069 | 7166.6663 | 7005.025 | 7389.219 | 7206.6053 | 7165.261 | 7002.039 | 7395.536
GSO_14 | br_019_21 | 3 | 7213.1081 | 7206.9928 | 7156.9538 | 7292.3547 | 7025.833 | 7347.666 | OK | 7217.0892 | 7157.7784 | 7025.833 | 7347.666 | 7216.695 | 7157.2648 | 7027.14 | 7341.296 | 7205.5401 | 7156.9538 | 7032.766 | 7284.781
GSO_140 | br_020_22 | 3 | 7211.9884 | 7205.5185 | 7163.6488 | 7280.6359 | 7033.355 | 7409.054 | OK | 7213.2403 | 7165.7147 | 7038.585 | 7390.538 | 7208.8107 | 7164.6677 | 7035.544 | 7409.054 | 7213.9141 | 7163.6488 | 7033.355 | 7395.942
GSO_141 | br_021_22 | 3 | 7210.2786 | 7205.3318 | 7159.172 | 7272.2117 | 7014.988 | 7405.181 | OK | 7211.8626 | 7159.172 | 7020.645 | 7365.578 | 7209.5135 | 7164.8927 | 7041.681 | 7394.606 | 7209.4599 | 7162.938 | 7014.988 | 7405.181
GSO_142 | br_022_22 | 3 | 7211.9059 | 7205.0028 | 7167.963 | 7272.627 | 7052.771 | 7399.344 | OK | 7211.974 | 7167.963 | 7055.092 | 7382.303 | 7212.3415 | 7169.0873 | 7054.939 | 7399.344 | 7211.4021 | 7170.084 | 7052.771 | 7378.542
GSO_143 | br_023_22 | 3 | 7218.1091 | 7209.214 | 7154.5197 | 7301.246 | 7026.719 | 7356.242 | OK | 7218.4547 | 7156.2924 | 7033.818 | 7356.242 | 7217.4549 | 7155.772 | 7034.698 | 7350.395 | 7218.4176 | 7154.5197 | 7026.719 | 7352.954
GSO_144 | br_024_22 | 3 | 7217.5112 | 7209.1507 | 7157.1647 | 7296.9693 | 7017.431 | 7389.952 | OK | 7216.3559 | 7160.9817 | 7017.431 | 7389.952 |  |  |  |  | 7218.6666 | 7157.1647 | 7026.196 | 7366.826
GSO_145 | br_025_22 | 3 | 7213.5739 | 7206.7195 | 7159.5153 | 7283.6208 | 7038.239 | 7396.884 | OK | 7215.5132 | 7164.282 | 7038.239 | 7393.921 | 7213.7589 | 7160.3044 | 7040.76 | 7396.884 | 7211.4496 | 7159.5153 | 7041.154 | 7376.019
GSO_146 | br_026_22 | 3 | 7218.1211 | 7208.7093 | 7155.441 | 7307.3026 | 7032.141 | 7382.472 | OK | 7220.9475 | 7158.1368 | 7034.108 | 7381.47 | 7219.2106 | 7155.441 | 7032.141 | 7373.949 | 7214.2051 | 7160.9004 | 7047.821 | 7382.472
GSO_147 | br_027_22 | 3 | 7212.2558 | 7206.2862 | 7162.0871 | 7282.8139 | 7035.176 | 7400.18 | OK | 7215.2158 | 7162.0871 | 7035.176 | 7400.18 | 7207.9179 | 7163.5644 | 7041.5 | 7389.222 | 7213.6337 | 7162.2787 | 7052.141 | 7381.174
GSO_148 | br_028_22 | 3 | 7214.7673 | 7207.3495 | 7160.161 | 7288.0593 | 6997.271 | 7404.952 | OK | 7215.742 | 7160.4744 | 7011.396 | 7382.448 | 7213.0273 | 7161.9858 | 6997.271 | 7398.382 | 7215.5326 | 7160.161 | 7036.014 | 7404.952
GSO_149 | br_029_22 | 3 | 7210.2175 | 7203.7413 | 7163.1871 | 7279.0988 | 7024.226 | 7401.624 | OK | 7208.2833 | 7165.231 | 7024.226 | 7392.547 | 7208.816 | 7163.1871 | 7025.5 | 7401.624 | 7213.5533 | 7165.2724 | 7041.983 | 7380.284
GSO_15 | br_020_21 | 3 | 7216.43 | 7208.3982 | 7156.2973 | 7293.6556 | 7028.82 | 7351.676 | OK | 7217.7713 | 7159.7277 | 7035.467 | 7347.419 | 7215.5321 | 7156.2973 | 7028.82 | 7333.648 | 7215.9867 | 7158.4497 | 7032.503 | 7351.676
GSO_150 | br_030_22 | 3 | 7211.1571 | 7204.4073 | 7163.9424 | 7272.6516 | 7013.469 | 7394.933 | OK | 7210.7203 | 7166.3364 | 7039.77 | 7380.158 | 7211.7125 | 7168.0683 | 7013.469 | 7378.148 | 7211.0384 | 7163.9424 | 7039.447 | 7394.933
GSO_151 | br_031_22 | 3 | 7212.8096 | 7206.9083 | 7156.7407 | 7283.7486 | 7022.59 | 7376.851 | OK | 7214.8052 | 7158.1074 | 7032.846 | 7376.851 | 7212.121 | 7163.1771 | 7035.46 | 7372.07 | 7211.5027 | 7156.7407 | 7022.59 | 7357.022
GSO_152 | br_032_22 | 3 | 7204.4128 | 7202.2422 | 7159.6395 | 7251.687 | 7028.385 | 7411.777 | OK | 7204.3444 | 7159.6449 | 7028.385 | 7386.467 | 7204.4102 | 7159.6395 | 7032.64 | 7398.936 | 7204.484 | 7159.6744 | 7033.175 | 7411.777
GSO_153 | br_033_22 | 3 | 7213.2136 | 7206.5713 | 7160.7353 | 7281.2086 | 7038.833 | 7408.669 | OK | 7213.9751 | 7162.1052 | 7038.833 | 7391.64 | 7211.8507 | 7160.7353 | 7039.361 | 7408.669 | 7213.8151 | 7161.8237 | 7039.416 | 7398.191
GSO_154 | br_034_22 | 3 | 7211.3765 | 7204.9182 | 7160.4874 | 7281.0932 | 7021.844 | 7392.101 | OK | 7209.9585 | 7167.741 | 7024.989 | 7389.302 | 7209.7008 | 7160.4874 | 7021.844 | 7389.229 | 7214.4702 | 7163.432 | 7051.985 | 7392.101
GSO_155 | br_01_23 | 3 | 7216.092 | 7208.117 | 7155.7764 | 7290.2095 | 7029.768 | 7369.265 | OK | 7215.3974 | 7159.7618 | 7032.614 | 7369.265 | 7216.1464 | 7155.7764 | 7031.508 | 7337.762 | 7216.7323 | 7161.6021 | 7029.768 | 7359.138
GSO_156 | br_02_23 | 3 | 7215.7447 | 7207.9257 | 7155.3354 | 7290.1816 | 7026.036 | 7362.545 | OK | 7215.8325 | 7155.3354 | 7034.959 | 7348.881 | 7215.6363 | 7159.5538 | 7038.91 | 7362.545 | 7215.7653 | 7156.5434 | 7026.036 | 7345.388
GSO_157 | br_03_23 | 3 | 7216.654 | 7208.3397 | 7156.273 | 7299.0265 | 7025.898 | 7357.982 | OK | 7219.391 | 7161.1953 | 7047.317 | 7356.89 | 7215.246 | 7156.273 | 7025.898 | 7352.525 | 7215.325 | 7158.6673 | 7036.145 | 7357.982
GSO_158 | br_04_23 | 3 | 7215.4466 | 7207.759 | 7154.9717 | 7290.3876 | 7026.375 | 7347.627 | OK | 7216.7902 | 7159.2145 | 7040.748 | 7347.627 | 7214.5335 | 7154.9717 | 7026.375 | 7339.706 | 7215.016 | 7158.9634 | 7039.11 | 7340.412
GSO_159 | br_05_23 | 3 | 7217.7217 | 7208.8765 | 7157.4357 | 7299.2863 | 7027.018 | 7364.047 | OK | 7216.8027 | 7158.2941 | 7032.868 | 7339.673 | 7218.9435 | 7157.4357 | 7027.018 | 7364.047 | 7217.4187 | 7157.6084 | 7035.231 | 7350.518
GSO_16 | br_021_21 | 3 | 7213.9837 | 7207.3443 | 7158.3023 | 7281.415 | 7027.004 | 7350.634 | OK | 7213.8776 | 7161.1866 | 7031.904 | 7350.634 | 7213.8768 | 7158.3023 | 7027.004 | 7349.272 | 7214.1967 | 7158.5815 | 7028.886 | 7346.423
GSO_160 | br_06_23 | 3 | 7216.8784 | 7208.5343 | 7156.3383 | 7296.0655 | 7024.802 | 7351.791 | OK | 7215.9917 | 7156.3383 | 7024.802 | 7334.072 | 7218.2373 | 7158.2601 | 7036.423 | 7349.88 | 7216.4062 | 7157.1128 | 7027.858 | 7351.791
GSO_161 | br_07_23 | 3 | 7216.0198 | 7207.331 | 7166.9864 | 7301.8819 | 7029.94 | 7392.414 | OK | 7210.751 | 7169.174 | 7029.94 | 7388.204 |  |  |  |  | 7221.2886 | 7166.9864 | 7061.061 | 7392.414
GSO_162 | br_08_23 | 3 | 7215.1432 | 7207.6575 | 7160.6244 | 7285.1353 | 7032.312 | 7354.077 | OK | 7215.4735 | 7160.6244 | 7032.312 | 7348.664 | 7215.8371 | 7161.476 | 7042.811 | 7354.077 | 7214.1189 | 7161.3027 | 7035.953 | 7352.461
GSO_163 | br_09_23 | 3 | 7217.4868 | 7208.479 | 7158.293 | 7296.5459 | 7025.692 | 7350.74 | OK | 7216.7281 | 7158.9996 | 7029.88 | 7349.323 | 7218.3244 | 7159.2007 | 7036.651 | 7344.524 | 7217.4077 | 7158.293 | 7025.692 | 7350.74
GSO_17 | br_024_21 | 3 | 7213.2163 | 7206.991 | 7155.4172 | 7290.7966 | 7020.65 | 7359.735 | OK | 7207.7383 | 7157.2234 | 7032.735 | 7298.912 | 7215.6723 | 7155.4172 | 7020.65 | 7340.337 | 7216.2382 | 7157.0243 | 7035.227 | 7359.735
GSO_18 | br_025_21 | 3 | 7214.2621 | 7207.255 | 7159.347 | 7295.8883 | 7035.527 | 7371.574 | OK | 7218.1791 | 7161.4057 | 7052.055 | 7355.37 | 7206.1489 | 7159.347 | 7035.527 | 7289.948 | 7218.4581 | 7160.459 | 7036.625 | 7371.574
GSO_19 | br_026_21 | 3 | 7217.1733 | 7208.4697 | 7156.5428 | 7294.6037 | 7031.45 | 7357.445 | OK | 7216.7248 | 7157.4247 | 7031.45 | 7357.445 | 7217.6476 | 7157.72 | 7037.628 | 7337.216 | 7217.1475 | 7156.5428 | 7035.338 | 7339.54
GSO_2 | br_02_21 | 3 | 7217.7143 | 7209.0305 | 7154.6143 | 7299.3899 | 7014.129 | 7363.589 | OK | 7217.7415 | 7155.0175 | 7014.129 | 7363.589 | 7218.2129 | 7155.274 | 7032.373 | 7355.642 | 7217.1885 | 7154.6143 | 7020.742 | 7363.238
GSO_20 | br_027_21 | 3 | 7205.7076 | 7200.567 | 7163.416 | 7264.1847 | 7040.882 | 7402.072 | OK | 7205.7076 | 7163.416 | 7040.882 | 7402.072
GSO_21 | br_028_21 | 3 | 7219.2358 | 7209.0887 | 7156.8127 | 7305.799 | 7026.492 | 7381.687 | OK | 7221.1011 | 7161.1557 | 7050.7 | 7381.687 | 7217.251 | 7156.8127 | 7026.492 | 7355.105 | 7219.3554 | 7157.5594 | 7030.65 | 7376.374
GSO_22 | br_029_21 | 3 | 7216.9853 | 7208.496 | 7156.3248 | 7298.5923 | 7028.584 | 7385.958 | OK | 7215.6541 | 7156.3248 | 7028.584 | 7343.157 | 7216.2422 | 7156.6637 | 7031.264 | 7385.958 | 7219.0595 | 7159.4587 | 7042.669 | 7360.393
GSO_23 | br_030_21 | 3 | 7214.3692 | 7207.0337 | 7157.1451 | 7293.317 | 7013.887 | 7392.971 | OK | 7217.5076 | 7160.3787 | 7032.392 | 7384.339 | 7215.7757 | 7158.4472 | 7024.365 | 7368.236 | 7209.8243 | 7157.1451 | 7013.887 | 7392.971
GSO_24 | br_031_21 | 3 | 7209.9378 | 7203.305 | 7168.0318 | 7267.7802 | 7016.239 | 7398.253 | OK | 7208.9368 | 7174.7004 | 7033.155 | 7377.447 | 7212.0685 | 7171.7341 | 7043.772 | 7384.643 | 7208.808 | 7168.0318 | 7016.239 | 7398.253
GSO_25 | br_032_21 | 3 | 7213.2093 | 7206.3355 | 7161.046 | 7285.556 | 7038.822 | 7398.15 | OK | 7215.3822 | 7161.046 | 7050.075 | 7391.01 | 7209.5937 | 7162.9505 | 7038.822 | 7398.15 | 7214.6519 | 7163.2867 | 7041.124 | 7396.496
GSO_26 | br_033_21 | 3 | 7214.6583 | 7207.5343 | 7155.7894 | 7295.49 | 7014.68 | 7361.056 | OK | 7213.9775 | 7159.6718 | 7038.154 | 7333.781 | 7212.5453 | 7156.2635 | 7014.68 | 7337.245 | 7217.4522 | 7155.7894 | 7021.552 | 7361.056
GSO_27 | br_034_21 | 3 | 7217.3987 | 7208.487 | 7158.0667 | 7298.3846 | 7023.281 | 7409.065 | OK | 7217.5732 | 7158.0667 | 7023.281 | 7347.271 | 7215.2699 | 7159.5011 | 7035.279 | 7338.875 | 7219.353 | 7161.7148 | 7033.663 | 7409.065
GSO_28 | br_035_21 | 3 | 7207.1091 | 7202.8208 | 7164.2104 | 7262.7566 | 7029.148 | 7397.887 | OK | 7207.8215 | 7165.3747 | 7048.269 | 7385.741 | 7208.8662 | 7164.2104 | 7029.148 | 7397.887 | 7204.6396 | 7165.0645 | 7038.083 | 7386.067
GSO_29 | br_036_21 | 3 | 7217.2307 | 7208.4595 | 7158.0898 | 7296.5195 | 7026.696 | 7361.989 | OK | 7218.8008 | 7161.3853 | 7026.696 | 7361.989 | 7216.7843 | 7158.0898 | 7034.163 | 7350.564 | 7216.1072 | 7158.3643 | 7044.896 | 7343.326
GSO_3 | br_03_21 | 3 | 7217.7714 | 7208.2625 | 7171.604 | 7286.2557 | 7053.453 | 7383.62 | OK | 7217.7714 | 7171.604 | 7053.453 | 7383.62
GSO_30 | br_037_21 | 3 | 7217.0197 | 7208.4425 | 7156.416 | 7300.6631 | 7033.038 | 7370.04 | OK | 7219.4871 | 7159.5577 | 7040.468 | 7370.04 | 7216.1758 | 7157.2861 | 7034.824 | 7340.439 | 7215.3962 | 7156.416 | 7033.038 | 7357.223
GSO_31 | br_038_21 | 3 | 7205.575 | 7202.019 | 7162.3874 | 7253.6983 | 7007.792 | 7400.844 | OK | 7205.6752 | 7162.9195 | 7007.792 | 7399.343 | 7205.5093 | 7162.492 | 7042.522 | 7400.844 | 7205.5404 | 7162.3874 | 7031.065 | 7394.573
GSO_32 | br_039_21 | 3 | 7218.7084 | 7209.0225 | 7159.3655 | 7300.1693 | 7028.782 | 7384.644 | OK | 7219.6019 | 7160.3207 | 7047.206 | 7384.644 | 7217.9812 | 7161.8561 | 7055.197 | 7353.839 | 7218.5421 | 7159.3655 | 7028.782 | 7367.974
GSO_33 | br_040_21 | 3 | 7212.8077 | 7206.0918 | 7162.3044 | 7283.099 | 7025.724 | 7403.903 | OK | 7210.837 | 7163.6324 | 7034.404 | 7351.762 | 7214.7614 | 7165.1263 | 7045.968 | 7388.206 | 7212.8247 | 7162.3044 | 7025.724 | 7403.903
GSO_34 | br_041_21 | 3 | 7218.4838 | 7208.9707 | 7156.6527 | 7300.8283 | 7015.072 | 7367.529 | OK | 7217.9172 | 7157.6891 | 7028.229 | 7367.529 | 7218.5452 | 7158.2614 | 7018.694 | 7361.218 | 7218.989 | 7156.6527 | 7015.072 | 7362.113
GSO_35 | br_042_21 | 3 | 7216.6833 | 7208.3607 | 7155.425 | 7297.4489 | 7020.614 | 7365.567 | OK | 7216.5678 | 7156.8781 | 7020.614 | 7365.567 | 7215.3526 | 7155.425 | 7025.555 | 7343.82 | 7218.1296 | 7157.0082 | 7027.167 | 7353.833
GSO_36 | br_043_21 | 3 | 7203.9172 | 7201.8702 | 7161.6212 | 7254.6047 | 7030.326 | 7337.693 | OK | 7203.4892 | 7170.5691 | 7061.322 | 7306.786 | 7206.3728 | 7161.8934 | 7053.819 | 7337.693 | 7201.8895 | 7161.6212 | 7030.326 | 7330.966
GSO_37 | br_044_21 | 3 | 7216.4951 | 7208.4568 | 7155.4433 | 7294.393 | 7022.594 | 7364.044 | OK | 7216.4271 | 7156.2827 | 7027.508 | 7333.263 | 7217.1565 | 7155.4433 | 7022.594 | 7364.044 | 7215.9018 | 7157.0619 | 7036.377 | 7353.082
GSO_38 | br_045_21 | 3 | 7215.0596 | 7207.5355 | 7170.1838 | 7276.2219 | 7064.572 | 7342.778 | OK | 7215.0596 | 7170.1838 | 7064.572 | 7342.778
GSO_39 | br_046_21 | 3 | 7215.1734 | 7207.7432 | 7155.6604 | 7289.2733 | 7027.455 | 7357.045 | OK | 7214.3461 | 7156.4961 | 7027.455 | 7347.233 | 7215.8886 | 7156.372 | 7032.851 | 7357.045 | 7215.2854 | 7155.6604 | 7030.602 | 7350.951
GSO_4 | br_04_21 | 3 | 7215.3189 | 7207.9905 | 7153.8733 | 7291.099 | 7020.302 | 7338.272 | OK | 7214.2919 | 7155.628 | 7032.587 | 7336.578 | 7216.5611 | 7156.2722 | 7028.18 | 7338.272 | 7215.1035 | 7153.8733 | 7020.302 | 7334.194
GSO_40 | br_047_21 | 3 | 7215.8568 | 7208.104 | 7157.5942 | 7289.3843 | 7022.226 | 7348.687 | OK | 7215.8721 | 7158.4064 | 7030.971 | 7348.687 | 7215.088 | 7157.5942 | 7022.226 | 7344.815 | 7216.6102 | 7159.8832 | 7038.791 | 7343.286
GSO_41 | br_048_21 | 3 | 7218.0995 | 7208.4733 | 7158.0634 | 7298.8416 | 7026.979 | 7371.369 | OK | 7217.7383 | 7159.4495 | 7026.979 | 7362.056 | 7218.6123 | 7158.0634 | 7038.393 | 7371.369 | 7217.9478 | 7160.848 | 7036.775 | 7358.559
GSO_42 | br_049_21 | 3 | 7218.4544 | 7209.6573 | 7153.5211 | 7303.5955 | 7021.643 | 7364.274 | OK | 7219.4343 | 7154.6007 | 7021.643 | 7364.274 | 7217.4051 | 7153.5211 | 7031.66 | 7348.614 | 7218.5237 | 7154.4451 | 7023.651 | 7355.515
GSO_43 | br_050_21 | 3 | 7216.2435 | 7208.2735 | 7155.4098 | 7291.5136 | 7033.008 | 7346.268 | OK | 7216.6695 | 7156.584 | 7034.626 | 7340.139 | 7216.2767 | 7158.2243 | 7042.783 | 7346.268 | 7215.7842 | 7155.4098 | 7033.008 | 7334.648
GSO_44 | br_051_21 | 3 | 7213.2403 | 7206.3675 | 7163.1437 | 7286.0943 | 7028.315 | 7393.058 | OK |  |  |  |  | 7215.7217 | 7163.1437 | 7028.315 | 7393.058 | 7210.7588 | 7170.8424 | 7037.943 | 7358.573
GSO_45 | br_052_21 | 3 | 7217.0144 | 7208.4208 | 7155.8524 | 7297.333 | 7025.158 | 7348.097 | OK | 7215.9133 | 7157.1122 | 7030.966 | 7329.357 | 7218.619 | 7159.9844 | 7046.351 | 7348.097 | 7216.511 | 7155.8524 | 7025.158 | 7341.13
GSO_46 | br_053_21 | 3 | 7216.6055 | 7208.448 | 7155.0724 | 7294.1416 | 7019.875 | 7356.714 | OK | 7217.5134 | 7157.3281 | 7030.403 | 7350.663 | 7216.3368 | 7155.0724 | 7019.875 | 7356.714 | 7215.9663 | 7155.7057 | 7022.197 | 7335.577
GSO_47 | br_054_21 | 3 | 7208.4652 | 7203.4427 | 7162.8767 | 7281.3782 | 7028.672 | 7383.433 | OK | 7214.5003 | 7162.8767 | 7029.892 | 7366.855 | 7204.873 | 7163.0414 | 7028.672 | 7367.518 | 7206.0224 | 7166.046 | 7042.72 | 7383.433
GSO_48 | br_055_21 | 3 | 7213.2816 | 7205.8092 | 7165.3937 | 7278.9082 | 7037.298 | 7400.607 | OK | 7214.1262 | 7168.9937 | 7040.019 | 7386.898 | 7213.2 | 7166.5917 | 7050.165 | 7396.08 | 7212.5187 | 7165.3937 | 7037.298 | 7400.607
GSO_49 | br_056_21 | 3 | 7212.2652 | 7205.3488 | 7166.8527 | 7280.1449 | 7043.116 | 7392.594 | OK | 7213.7994 | 7167.0694 | 7057.402 | 7392.594 | 7215.1717 | 7169.6101 | 7043.116 | 7379.586 | 7207.8245 | 7166.8527 | 7046.812 | 7380.813
GSO_5 | br_05_21 | 3 | 7213.7876 | 7206.87 | 7158.2647 | 7285.5193 | 7021.195 | 7403.876 | OK | 7215.1929 | 7158.2647 | 7021.195 | 7377.471 | 7213.7879 | 7160.3127 | 7043.416 | 7390.02 | 7212.3819 | 7159.8977 | 7022.957 | 7403.876
GSO_50 | br_057_21 | 3 | 7217.4479 | 7208.345 | 7162.6087 | 7289.8403 | 7048.205 | 7382.127 | OK |  |  |  |  | 7217.4479 | 7162.6087 | 7048.205 | 7382.127
GSO_51 | br_058_21 | 3 | 7212.0441 | 7205.4118 | 7164.7827 | 7274.673 | 7031.074 | 7393.478 | OK | 7212.4391 | 7164.7827 | 7043.323 | 7388.971 | 7210.7764 | 7165.321 | 7031.074 | 7393.478 | 7212.9168 | 7168.6754 | 7032.18 | 7379.251
GSO_52 | br_059_21 | 3 | 7216.349 | 7208.1567 | 7154.95 | 7292.7946 | 7020.362 | 7355.853 | OK | 7217.1545 | 7158.2074 | 7037.862 | 7348.919 | 7216.0559 | 7154.95 | 7020.362 | 7334.09 | 7215.8365 | 7156.0314 | 7022.008 | 7355.853
GSO_53 | br_060_21 | 3 | 7215.8519 | 7207.7742 | 7158.51 | 7299.8983 | 7024.857 | 7371.023 | OK | 7218.6815 | 7158.9707 | 7030.684 | 7354.242 | 7219.8617 | 7162.7831 | 7039.365 | 7371.023 | 7209.0126 | 7158.51 | 7024.857 | 7312.744
GSO_54 | br_061_21 | 3 | 7217.0048 | 7208.6732 | 7155.3215 | 7294.5482 | 7020.097 | 7345.299 | OK | 7217.0266 | 7155.3215 | 7029.599 | 7345.299 | 7216.9324 | 7156.9081 | 7039.188 | 7339.95 | 7217.0555 | 7156.2487 | 7020.097 | 7342.938
GSO_55 | br_062_21 | 3 | 7214.4961 | 7206.7808 | 7161.4228 | 7287.5 | 7035.722 | 7395.43 | OK | 7210.8371 | 7172.5084 | 7035.722 | 7395.43 | 7215.7627 | 7161.4228 | 7043.239 | 7364.353 | 7216.8887 | 7162.8197 | 7044.503 | 7340.372
GSO_56 | br_063_21 | 3 | 7216.9616 | 7208.0357 | 7160.4985 | 7299.8013 | 7029.815 | 7379.176 | OK | 7219.8583 | 7163.0233 | 7043.719 | 7379.13 | 7214.0309 | 7160.8063 | 7034.107 | 7379.176 | 7216.9956 | 7160.4985 | 7029.815 | 7359.505
GSO_57 | br_08_21 | 3 | 7215.7428 | 7207.529 | 7159.9155 | 7299.3301 | 7020.914 | 7366.094 | OK | 7215.334 | 7161.7144 | 7020.914 | 7360.007 | 7219.1604 | 7159.9155 | 7026.914 | 7366.094 | 7212.7341 | 7164.8823 | 7041 | 7362.109
GSO_58 | br_09_21 | 3 | 7216.6127 | 7208.1485 | 7156.4384 | 7293.9913 | 7028.915 | 7340.455 | OK | 7215.8393 | 7156.5744 | 7028.915 | 7340.455 | 7216.443 | 7156.4384 | 7031.447 | 7334.992 | 7217.5558 | 7160.001 | 7037.994 | 7337.18
GSO_59 | br_010_21 | 3 | 7216.5114 | 7208.3147 | 7155.6714 | 7292.9023 | 7029.813 | 7360.041 | OK | 7215.7952 | 7155.6714 | 7030.333 | 7343.653 | 7216.9801 | 7156.827 | 7029.813 | 7360.041 | 7216.759 | 7157.5878 | 7032.205 | 7336.569
GSO_6 | br_06_21 | 3 | 7217.8812 | 7209.1932 | 7155.3929 | 7298.5753 | 7019.858 | 7377.444 | OK | 7217.975 | 7157.262 | 7019.858 | 7360.712 | 7218.6368 | 7158.5274 | 7040.707 | 7377.444 | 7217.0318 | 7155.3929 | 7038.448 | 7368.328
GSO_60 | br_011_21 | 3 | 7216.1349 | 7208.225 | 7156.5718 | 7290.5723 | 7031.344 | 7353.708 | OK | 7216.191 | 7156.5718 | 7031.844 | 7349.984 | 7216.3915 | 7158.6387 | 7037.086 | 7353.708 | 7215.8221 | 7159.2185 | 7031.344 | 7340.735
GSO_61 | br_012_21 | 3 | 7215.4787 | 7208.0417 | 7155.3458 | 7289.509 | 7027.948 | 7346.349 | OK | 7214.9712 | 7155.7443 | 7029.209 | 7333.784 | 7215.7097 | 7155.564 | 7028.811 | 7346.349 | 7215.7552 | 7155.3458 | 7027.948 | 7337.657
GSO_62 | br_013_21 | 3 | 7210.4934 | 7205.6455 | 7155.6228 | 7285.659 | 7024.907 | 7347.292 | OK | 7200.9471 | 7162.9904 | 7050.523 | 7265.269 | 7215.9623 | 7164.2574 | 7057.297 | 7347.292 | 7214.571 | 7155.6228 | 7024.907 | 7342.584
GSO_63 | br_014_21 | 3 | 7215.4477 | 7207.3035 | 7163.6707 | 7288.9791 | 7036.219 | 7389.248 | OK | 7213.9656 | 7170.2834 | 7076.604 | 7389.248 | 7214.9811 | 7163.6707 | 7036.219 | 7367.344 | 7217.3964 | 7165.0408 | 7039.605 | 7374.976
GSO_64 | br_064_21 | 3 | 7216.3105 | 7208.2628 | 7157.4191 | 7292.6235 | 7025.429 | 7366.352 | OK | 7215.9508 | 7157.4191 | 7039.797 | 7364.542 | 7215.9033 | 7159.1644 | 7025.429 | 7366.352 | 7217.0775 | 7157.8661 | 7025.686 | 7349.755
GSO_65 | br_065_21 | 3 | 7207.1599 | 7202.0145 | 7162.1424 | 7269.2626 | 7026.92 | 7399.487 | OK | 7206.1207 | 7163.0298 | 7028.381 | 7393.974 | 7209.0513 | 7162.1424 | 7026.92 | 7395.691 | 7206.3077 | 7163.1053 | 7032.335 | 7399.487
GSO_66 | br_066_21 | 3 | 7216.1698 | 7208.1637 | 7154.9842 | 7295.2833 | 7025.604 | 7359.498 | OK | 7215.1492 | 7154.9842 | 7025.604 | 7345.18 | 7217.6025 | 7156.3804 | 7026.735 | 7359.498 | 7215.7577 | 7157.6622 | 7035.16 | 7342.752
GSO_67 | br_067_21 | 3 | 7218.0193 | 7208.8353 | 7157.8504 | 7296.1246 | 7034.765 | 7375.064 | OK | 7217.8583 | 7158.8614 | 7036.498 | 7375.064 | 7218.7983 | 7160.5464 | 7034.765 | 7362.045 | 7217.4013 | 7157.8504 | 7036.847 | 7346.959
GSO_68 | br_068_21 | 3 | 7217.103 | 7208.4122 | 7156.8834 | 7300.4956 | 7022.938 | 7378.702 | OK | 7216.1525 | 7157.0565 | 7033.7 | 7345.095 | 7219.5354 | 7160.5258 | 7022.938 | 7378.702 | 7215.621 | 7156.8834 | 7024.239 | 7349.637
GSO_69 | br_069_21 | 3 | 7214.1835 | 7207.179 | 7160.1162 | 7282.3762 | 7040.442 | 7404.695 | OK | 7214.1648 | 7160.1162 | 7040.442 | 7404.695 | 7215.0953 | 7163.2573 | 7048.365 | 7380.163 | 7213.2902 | 7160.9632 | 7046.617 | 7370.48
GSO_7 | br_07_21 | 3 | 7200.8526 | 7200.2707 | 7151.5238 | 7265.9657 | 7021.114 | 7394.917 | OK |  |  |  |  | 7205.8972 | 7161.7451 | 7021.114 | 7394.917 | 7195.8081 | 7151.5238 | 7035.899 | 7258.936
GSO_70 | br_070_21 | 3 | 7210.9731 | 7204.7862 | 7164.59 | 7284.615 | 7033.796 | 7397.636 | OK | 7215.6732 | 7164.59 | 7044.224 | 7392.095 | 7209.016 | 7169.5691 | 7075.951 | 7397.636 | 7208.2302 | 7166.832 | 7033.796 | 7381.615
GSO_71 | br_071_21 | 3 | 7215.6696 | 7208.074 | 7154.7971 | 7290.003 | 7025.2 | 7350.03 | OK | 7215.7755 | 7157.0324 | 7031.212 | 7350.03 | 7215.2592 | 7155.167 | 7025.2 | 7338.632 | 7215.9741 | 7154.7971 | 7029.863 | 7346.146
GSO_72 | br_072_21 | 3 | 7214.397 | 7207.3822 | 7157.703 | 7290.686 | 7030.388 | 7365.66 | OK | 7217.0323 | 7159.8799 | 7035.943 | 7365.66 | 7212.2769 | 7157.703 | 7036.086 | 7318.722 | 7213.8818 | 7158.2641 | 7030.388 | 7345.54
GSO_73 | br_073_21 | 3 | 7208.3306 | 7201.901 | 7161.2791 | 7273.6752 | 6987.051 | 7403.747 | OK | 7209.9501 | 7168.1261 | 7039.737 | 7384.712 | 7207.1411 | 7165.0548 | 7041.153 | 7394.523 | 7207.9008 | 7161.2791 | 6987.051 | 7403.747
GSO_74 | br_074_21 | 3 | 7216.604 | 7207.8483 | 7161.1087 | 7294.6044 | 7039.079 | 7405.794 | OK | 7217.9543 | 7163.689 | 7055.504 | 7401.805 | 7215.0811 | 7161.1087 | 7039.079 | 7352.326 | 7216.7767 | 7165.0408 | 7049.876 | 7405.794
GSO_75 | br_075_21 | 3 | 7214.6269 | 7207.1745 | 7160.8418 | 7292.2406 | 7027.191 | 7392.568 | OK | 7212.8538 | 7160.8418 | 7030.621 | 7371.015 | 7217.721 | 7162.0597 | 7027.191 | 7392.568 | 7213.3058 | 7164.9014 | 7027.838 | 7373.57
GSO_76 | br_076_21 | 3 | 7215.5004 | 7207.7875 | 7164.72 | 7281.96 | 7058.493 | 7370.531 | OK | [8 empty] | 7215.5004 | 7164.72 | 7058.493 | 7370.531
GSO_77 | br_077_21 | 3 | 7213.2397 | 7206.9723 | 7155.6683 | 7291.6793 | 7031.704 | 7355.039 | OK | 7216.1447 | 7156.1053 | 7036.922 | 7355.039 | 7216.4596 | 7155.6683 | 7031.704 | 7344.783 | 7207.1148 | 7157.2588 | 7034.795 | 7293.969
GSO_78 | br_078_21 | 3 | 7218.1923 | 7208.7643 | 7158.4231 | 7296.0196 | 7019.933 | 7383.27 | OK | 7218.3944 | 7161.9514 | 7019.933 | 7383.27 | 7217.9901 | 7158.4231 | 7041.958 | 7371.452
GSO_79 | br_079_21 | 3 | 7217.6827 | 7208.2548 | 7158.9527 | 7310.2322 | 7031.057 | 7392.982 | OK | 7221.4765 | 7160.1835 | 7042.092 | 7392.982 | 7215.6318 | 7160.591 | 7042.367 | 7377.536 | 7215.9397 | 7158.9527 | 7031.057 | 7344.135
GSO_8 | br_022_21 | 3 | 7214.2242 | 7206.8805 | 7166.1623 | 7277.7167 | 7023.839 | 7356.725 | OK | [8 empty] | 7214.2242 | 7166.1623 | 7023.839 | 7356.725
GSO_80 | br_080_21 | 3 | 7213.9295 | 7207.3892 | 7156.3121 | 7296.8136 | 7029.388 | 7360.017 | OK | 7206.9182 | 7158.3421 | 7038.262 | 7295.787 | 7216.6189 | 7156.3121 | 7029.388 | 7349.599 | 7218.2514 | 7158.4853 | 7042.835 | 7360.017
GSO_81 | br_081_21 | 3 | 7217.7392 | 7208.4933 | 7158.627 | 7300.9326 | 7028.924 | 7379.533 | OK | 7218.1871 | 7162.2 | 7056.459 | 7376.401 | 7215.0403 | 7158.627 | 7028.924 | 7364.172 | 7219.9903 | 7162.3398 | 7031.609 | 7379.533
GSO_82 | br_082_21 | 3 | 7216.1838 | 7208.2807 | 7155.9567 | 7291.4052 | 7016.762 | 7348.626 | OK | 7216.6384 | 7155.9567 | 7016.762 | 7348.626 | 7216.2977 | 7159.058 | 7018.098 | 7336.403 | 7215.6152 | 7157.9453 | 7043.608 | 7345.808
GSO_83 | br_083_21 | 3 | 7216.4286 | 7208.2788 | 7155.2625 | 7292.5603 | 7023.24 | 7352.078 | OK | 7216.4992 | 7155.936 | 7027.94 | 7343.715 | 7215.7309 | 7155.2625 | 7023.24 | 7339.323 | 7217.0556 | 7156.4478 | 7024.316 | 7352.078
GSO_84 | br_084_21 | 3 | 7216.3921 | 7207.8645 | 7159.738 | 7296.5661 | 7017.501 | 7399.196 | OK | 7218.608 | 7159.738 | 7036.604 | 7369.501 | 7214.7766 | 7167.39 | 7058 | 7399.196 | 7215.7919 | 7165.288 | 7017.501 | 7365.089
GSO_85 | br_085_21 | 3 | 7215.3864 | 7207.4985 | 7161.4787 | 7289.5313 | 7029.753 | 7401.007 | OK | 7216.8278 | 7161.4787 | 7034.763 | 7386.337 | 7215.8186 | 7161.5458 | 7039.173 | 7401.007 | 7213.5127 | 7161.7433 | 7029.753 | 7379.724
GSO_86 | br_086_21 | 3 | 7216.3646 | 7208.1698 | 7157.4523 | 7292.4896 | 7020.439 | 7364.76 | OK | 7214.4339 | 7157.7648 | 7037.464 | 7361.588 | 7217.2619 | 7158.2443 | 7020.439 | 7361.105 | 7217.3979 | 7157.4523 | 7031.181 | 7364.76
GSO_87 | br_087_21 | 3 | 7214.9529 | 7207.6065 | 7157.6638 | 7289.0616 | 7023.684 | 7363.641 | OK | 7213.3463 | 7157.6638 | 7040.907 | 7339.709 | 7216.8372 | 7161.6505 | 7051.221 | 7363.641 | 7214.6752 | 7157.7194 | 7023.684 | 7359.829
GSO_88 | br_088_21 | 3 | 7216.6743 | 7208.0308 | 7157.903 | 7293.8588 | 7024.557 | 7398.63 | OK | 7217.5829 | 7157.903 | 7036.979 | 7355.502 | 7214.7847 | 7160.2295 | 7034.854 | 7398.63 | 7217.6553 | 7162.7731 | 7024.557 | 7386.5
GSO_89 | br_089_21 | 3 | 7204.3218 | 7203.054 | 7155.416 | 7263.6473 | 7028.922 | 7316.769 | OK | 7203.4131 | 7157.0953 | 7043.136 | 7305.109 | 7201.3506 | 7159.0577 | 7037.101 | 7280.262 | 7208.2017 | 7155.416 | 7028.922 | 7316.769
GSO_9 | br_023_21 | 3 | 7211.7125 | 7204.7278 | 7168.3966 | 7274.7069 | 7036.314 | 7398.067 | OK |  |  |  |  | 7213.8407 | 7169.3564 | 7036.314 | 7398.067 | 7209.5842 | 7168.3966 | 7063.268 | 7375.544
GSO_90 | br_090_21 | 3 | 7211.4651 | 7205.1787 | 7161.6914 | 7278.7077 | 7027.269 | 7394.585 | OK | 7211.4057 | 7161.6914 | 7035.345 | 7378.27 | 7213.4059 | 7162.335 | 7046.696 | 7391.01 | 7209.5837 | 7163.7253 | 7027.269 | 7394.585
GSO_91 | br_091_21 | 3 | 7218.0043 | 7208.535 | 7161.9621 | 7293.9873 | 7032.754 | 7381.484 | OK | 7218.63 | 7164.3295 | 7056.984 | 7368.059 | 7217.8125 | 7161.9621 | 7032.754 | 7381.484 | 7217.5705 | 7162.6808 | 7054.194 | 7349.135
GSO_92 | br_092_21 | 3 | 7212.9872 | 7205.9122 | 7160.4825 | 7288.4225 | 7032.834 | 7398.959 | OK | 7216.6166 | 7163.626 | 7044.05 | 7398.959 | 7211.5031 | 7164.3354 | 7032.834 | 7390.946 | 7210.842 | 7160.4825 | 7042.616 | 7371.121
GSO_93 | br_093_21 | 3 | 7214.4987 | 7206.5897 | 7161.8504 | 7288.9437 | 7038.805 | 7413.538 | OK | 7211.8272 | 7164.5423 | 7040.381 | 7413.538 | 7216.6256 | 7161.8504 | 7038.805 | 7377.404 | 7215.0432 | 7167.271 | 7049.811 | 7383.599
GSO_94 | br_094_21 | 3 | 7213.9741 | 7206.6622 | 7162.1317 | 7288.347 | 7018.565 | 7396.239 | OK | 7215.8403 | 7162.1317 | 7024.219 | 7396.239 | 7212.7389 | 7164.207 | 7038.382 | 7396.168 | 7213.343 | 7164.2347 | 7018.565 | 7380.014
GSO_95 | br_095_21 | 3 | 7217.2659 | 7208.5105 | 7156.1458 | 7298.9305 | 7030.294 | 7354.334 | OK | 7215.8261 | 7156.1458 | 7030.294 | 7333.625 | 7217.3642 | 7158.3047 | 7036.175 | 7350.672 | 7218.6072 | 7158.7207 | 7035.639 | 7354.334
GSO_96 | br_096_21 | 3 | 7216.1074 | 7207.7803 | 7156.9344 | 7295.4159 | 7016.661 | 7389.602 | OK | 7215.6623 | 7161.264 | 7016.661 | 7387.063 | 7217.6007 | 7156.9344 | 7025.591 | 7365.089 | 7215.0591 | 7163.269 | 7043.704 | 7389.602
GSO_97 | br_098_21 | 3 | 7215.8654 | 7208.143 | 7154.7981 | 7292.9456 | 7027.295 | 7349.288 | OK | 7216.8698 | 7156.487 | 7035.922 | 7341.841 | 7215.4802 | 7154.7981 | 7027.295 | 7337.104 | 7215.246 | 7157.232 | 7029.951 | 7349.288
GSO_98 | br_099_21 | 3 | 7210.3215 | 7206.2488 | 7155.6829 | 7289.4437 | 7027.973 | 7345.411 | OK | 7215.959 | 7155.6829 | 7030.829 | 7338.381 | 7215.8771 | 7156.3002 | 7027.973 | 7345.411 | 7199.1284 | 7156.447 | 7029.363 | 7238.012
GSO_99 | br_0100_21 | 3 | 7217.6853 | 7208.632 | 7156.4087 | 7298.442 | 7024.329 | 7349.561 | OK | 7218.8637 | 7159.1861 | 7024.329 | 7349.561 | 7217.0449 | 7157.6944 | 7028.516 | 7343.945 | 7217.1472 | 7156.4087 | 7030.285 | 7340.956

## Breaker_Data_Sources
grid_id | DataSourceID | BreakerElementID | DataSourceType | Provider | Metrics | FriendlyID | DataSourcePhases | Direction | ValidRange | HasKWh | HasVoltage | NormalizedPhase
GSO_1 | b1e8c057-fded-4c70-8f86-a33db401b6d1 | br_01_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_01_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_1 | ba6970aa-af7f-428e-9a4f-7826618684b4 | br_01_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_01_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_1 | ea496fcb-6216-4db1-9885-1da5dbf70fa2 | br_01_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_01_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_10 | 396f73e2-6041-46ac-90d5-a9439aef50d8 | br_015_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_015_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_10 | b315ece6-7341-4cdf-a1c9-70a8dbfe93ff | br_015_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_015_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_10 | d140ab36-31a8-40c7-820d-c3a2df82604a | br_015_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_015_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_100 | 3125b67a-cbd0-47b3-94b6-a60b38de7e8b | br_097_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_097_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_100 | 564551fe-ec45-4b6c-a7df-ebfa29a0a242 | br_097_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_097_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_100 | cc6f9a7e-ea1b-4cdb-9c85-6c672b845068 | br_097_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_097_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_101 | 6c559f06-b888-4a9d-ba0f-901b0b19b354 | br_0101_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0101_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_101 | 8f1038a0-f3d5-4f15-bedf-b8f1215601f3 | br_0101_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0101_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_101 | f32aafa6-4f97-40b9-85a1-6516b7a34fb0 | br_0101_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0101_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_102 | 3f11f59f-b6f2-44fe-8a16-f4a87144ca07 | br_0102_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0102_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_102 | 58383f3b-39ee-41c1-9a45-f21c6b309b7c | br_0102_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0102_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_102 | aaef163c-bdc4-464e-9864-b0c0ebdf8662 | br_0102_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0102_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_103 | a3539c00-7186-4684-93db-03123790cf12 | br_0103_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0103_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_103 | d53e58ae-230d-449a-b78d-6b5cfa60f56b | br_0103_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0103_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_103 | d5fd099c-84d4-4965-91b3-bbc0c68d61d1 | br_0103_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0103_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_104 | 0256f17b-1fde-4e5f-aa42-6a293aa27e64 | br_0104_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0104_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_104 | 4922eba1-a72a-4e22-8a37-912d5f9ac46b | br_0104_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0104_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_104 | dbaf906f-b53b-4b15-bd48-42442608214a | br_0104_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0104_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_105 | 11bf4c6d-205c-4caf-b572-7246ab210632 | br_0105_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0105_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_105 | 3943a935-55e7-44b5-a61e-08789763be18 | br_0105_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0105_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_105 | 98dc0614-4560-469e-93e2-97b3c41b5000 | br_0105_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0105_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_106 | 1523bf59-c426-49d7-add2-e9b831978748 | br_0106_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0106_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_106 | e37ebffe-ff65-4277-a7e0-2315cac8c267 | br_0106_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0106_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_106 | f0643cc7-b03a-4328-82d5-2924a650f97f | br_0106_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0106_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_107 | 4113937f-0ce2-415a-9249-ce7327d121f7 | br_0107_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0107_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_107 | 5d59abb9-0bac-4fa7-a891-4e9d4e794c88 | br_0107_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0107_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_107 | b1339292-267a-4146-8873-ecfc9cb1a82e | br_0107_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0107_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_108 | 1886a888-6918-466c-929d-0c8f16370dda | br_0108_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0108_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_108 | c0036365-6459-4cc7-b7b1-ed8933515338 | br_0108_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0108_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_108 | e867a5e4-d5f1-4fdf-98c8-da37424315a6 | br_0108_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0108_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_109 | 0c75d1f1-8237-436b-a2c8-c9b6fdc7a116 | br_0109_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0109_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_109 | e6350d88-56d8-492b-bc1e-dcd90fcca31f | br_0109_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0109_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_109 | ec8ad3c4-a39d-4acb-8788-e7435be58cb7 | br_0109_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0109_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_11 | 469868d0-2f60-42bd-aa67-be26d6eae0eb | br_016_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_016_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_11 | 9cdbec33-569a-438b-ac44-23b272ad169b | br_016_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_016_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_11 | dfea635f-2a86-40f1-9367-d78b6dd6c309 | br_016_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_016_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_110 | 1e111a58-963a-4906-b1f6-e2d03049b19a | br_0110_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0110_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_110 | 8a0dd243-2512-4f92-afd7-db6e79d7496e | br_0110_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0110_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_110 | ca02189c-f89b-417b-a469-ef0366d6da6e | br_0110_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0110_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_111 | 3488e4fc-fa59-4bcf-b967-3b7a890f6c3c | br_0111_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0111_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_111 | e60c92cc-e283-4345-87b0-ba3a9fd78005 | br_0111_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0111_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_111 | f8549391-d242-43a9-9a34-33f872443611 | br_0111_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0111_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_112 | 407ea9ca-a495-4119-a139-1d1233852fdc | br_0112_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0112_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_112 | 99fe4744-38fc-4467-902b-d97556b6d295 | br_0112_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0112_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_112 | e1fd2b67-b072-4575-9f5d-c24af5f52b11 | br_0112_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0112_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_113 | a9bc380c-ca71-4a2b-b314-0f03f9f76581 | br_0113_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0113_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_113 | bdf27366-2b21-4e21-8946-86b299b81d14 | br_0113_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0113_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_113 | f8ddca03-2f28-483b-97fe-a4538d6c4e2b | br_0113_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0113_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_114 | 156d4241-1525-4089-8367-effd61eb4969 | br_0114_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0114_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_114 | 3128527e-a25b-4b2c-9d88-b40eb600580e | br_0114_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0114_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_114 | 34c2c476-7801-4ae6-ba1f-ca1a602925b3 | br_0114_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0114_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_115 | 58786ac1-7ac2-4287-bd8f-add68a4ea208 | br_0115_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0115_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_115 | 820fcd78-48b0-467d-8925-554a0333f605 | br_0115_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0115_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_115 | d3645b59-a71d-4848-9deb-b044c307c52a | br_0115_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0115_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_116 | 2a93f307-f837-4de0-9089-b308bde0f0fd | br_0116_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0116_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_116 | ba9bd088-fa13-4d76-ba16-6dba6a8b45de | br_0116_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0116_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_116 | e9542020-950f-403c-af95-965f8434a9f8 | br_0116_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0116_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_117 | 127d58d0-da5d-47a0-a219-b8c1834a136a | br_0117_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0117_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_117 | 20ca2ff7-1194-405d-9098-d4544944a36d | br_0117_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0117_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_117 | 79b91384-9645-42ed-940d-37fdffcc31a0 | br_0117_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0117_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_118 | 7b9e37f6-9e61-405e-8bc5-9d79097397f4 | br_0118_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0118_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_118 | b2273af8-cb6e-4178-93e7-36fab6dbf2c0 | br_0118_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0118_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_118 | cb23fba1-b5a8-477f-b388-dcbc14cf56b2 | br_0118_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0118_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_119 | 1a46aa48-ac4e-4046-aa43-a61c07c816d6 | br_0119_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0119_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_119 | 3aad3364-ed36-4087-b7d0-6d3b3fa6f823 | br_0119_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0119_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_119 | faec1da7-65b2-4b86-be90-e4357dfde1ce | br_0119_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0119_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_12 | 4c1ed359-972e-4bdd-a0cd-1159d7a32c07 | br_017_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_017_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_12 | e263a729-e360-4716-9561-679bf6b5d16a | br_017_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_017_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_12 | ede6f7c6-f426-4d65-bfe0-7dac24a794c1 | br_017_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_017_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_121 | 0eb7ef08-0441-4661-84d4-63da9255ea41 | br_01_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_01_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_121 | 36cfcc10-f3c4-4989-ae21-5fdd2aa20962 | br_01_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_01_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_121 | 423b0798-4793-4a14-a787-72bb51fb4cef | br_01_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_01_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_122 | 4fa57e43-e6c7-4d4b-a312-3fb0e3337ffc | br_02_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_02_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_122 | abf746be-5de9-44ac-9f69-a717abe29437 | br_02_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_02_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_122 | e63f1c25-1cac-49ae-9929-f96fa015f74e | br_02_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_02_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_123 | 08fe15ea-b154-4270-ad96-7633898d9feb | br_03_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_03_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_123 | 22b46d3c-1104-4a6b-baf0-791554532cbe | br_03_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_03_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_123 | c84967ed-4e26-4447-aaec-39d0dba00695 | br_03_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_03_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_124 | cbbe0d2b-6245-4a4f-bcc2-e456b3e84669 | br_04_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_04_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_124 | e9588dba-e5c4-44a0-a87f-6d585846716c | br_04_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_04_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_124 | f9dd1e2c-0b53-4323-abbd-c79d2b87bf2e | br_04_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_04_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_125 | 16682194-aa4b-49e9-acf2-9c6562595352 | br_05_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_05_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_125 | 99cabfd6-b964-4658-8155-1699ad43459b | br_05_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_05_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_125 | cd7fbbb9-9a6f-4dd9-891c-e37a9557fa12 | br_05_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_05_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_126 | 12d09ac1-fdb6-467e-a1aa-f99f6eed49f6 | br_06_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_06_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_126 | 9006b8b1-eda0-485b-a8d0-426580b8950f | br_06_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_06_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_126 | bc3fda03-9c4b-412b-a5ef-6db07eeba8fc | br_06_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_06_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_127 | 1287cfdf-d61b-4b7d-9c56-4a67e583be03 | br_07_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_07_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_127 | 9962595a-e18a-4855-ab7a-6bcfb11262e4 | br_07_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_07_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_127 | a16d8ea2-fafa-4870-8bff-75e352b48100 | br_07_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_07_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_128 | 3d10e996-315d-4229-9b7c-a9b8e0697db8 | br_08_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_08_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_128 | 692be577-442c-4ab0-b1e1-5785854345e2 | br_08_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_08_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_128 | 6cff9753-e438-465f-8082-4b41468b4f8c | br_08_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_08_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_129 | 066b1670-e5b9-40c9-bd97-907fe78b74e9 | br_09_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_09_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_129 | 686b2171-718b-454f-a63f-7a08af910b78 | br_09_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_09_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_129 | ca9fa130-fc7c-477e-8464-326c962a06af | br_09_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_09_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_13 | 28993f84-c3b9-4382-b199-7eae1602f7b5 | br_018_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_018_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_13 | 538bb977-c069-4a72-a1f5-79ade89be85e | br_018_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_018_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_13 | d4524dc1-a63b-454b-a0d9-1683a9db619b | br_018_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_018_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_130 | 0820aaeb-7057-4894-a6ba-7624e83ee1a7 | br_010_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_010_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_130 | cab2ab50-4b8d-4ecb-98f8-73c155d0b547 | br_010_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_010_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_130 | ec2f67d6-3e29-40e6-b3db-279de5aeb3e1 | br_010_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_010_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_131 | 1a6f96c2-84f7-4c0d-b1a3-ee2364b2f450 | br_011_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_011_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_131 | 434fff6c-2804-492a-a7e9-8c978d0dc8e3 | br_011_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_011_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_131 | 618c145a-b95c-4f8d-9e8d-9389861004d6 | br_011_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_011_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_132 | 0716ea38-77d5-4d34-bc24-820dc14d344a | br_012_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_012_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_132 | 8eae3b99-7252-4faf-9a4e-4abe914bc30e | br_012_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_012_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_132 | 935c3854-ba34-4cf1-b241-c865be78d3bf | br_012_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_012_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_133 | 4d344901-644b-4ea0-b7f1-b381d39a7879 | br_013_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_013_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_133 | c086c5c8-dc85-4746-8b0a-d8e23067358a | br_013_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_013_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_133 | dddfb629-b710-4a70-b13f-4f342bc8fe74 | br_013_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_013_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_134 | 4091c3a2-55c3-4b7e-8d9d-a8e4affed314 | br_014_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_014_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_134 | 57c2fa84-53da-4153-9d01-3c3ac5b2144e | br_014_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_014_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_134 | 7325e088-181d-4e0d-b15b-2dd1fbda83f0 | br_014_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_014_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_135 | 306b628e-5350-43cc-bd44-5524b56eb0e1 | br_015_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_015_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_135 | c3ac0e33-1470-42fd-9a70-99015f289563 | br_015_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_015_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_135 | cb036569-e3a3-4f9a-ab6b-ada0cfc7f7a2 | br_015_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_015_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_136 | 04ce7e89-fb0f-4fb3-9752-836af1c7ab9e | br_016_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_016_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_136 | 1985324e-e67a-4d01-bf4e-cbc1776ba800 | br_016_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_016_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_136 | 66b785ca-af8e-4a6a-8af7-ff9241ec96a5 | br_016_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_016_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_137 | bb261d99-e16f-41bf-90d2-05acc7b4f39c | br_017_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_017_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_137 | cf094241-cd71-4a00-ae80-c341e78225f3 | br_017_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_017_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_137 | d0f42d15-cf63-4976-b310-0a7f21c9a7fc | br_017_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_017_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_138 | 8cf34f38-0fdb-4d44-9870-a7c9c5b5c3b4 | br_018_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_018_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_138 | b91b7108-02a6-4c8f-9294-9075747bf3d2 | br_018_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_018_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_138 | c812a09e-5775-4fbc-93b7-37aa020f3a4a | br_018_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_018_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_139 | 2a67f2a3-ad9e-4413-af20-999870d5694e | br_019_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_019_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_139 | 6ec0fb64-8f9d-48b6-81ae-63048adca78a | br_019_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_019_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_139 | 8781de87-205d-4b90-963f-449d72c41e8c | br_019_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_019_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_14 | 37a8aff5-f4d5-48d1-b094-f7ff7add641f | br_019_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_019_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_14 | 4f0a9de3-7d5d-4d74-841a-ad368a655ddc | br_019_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_019_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_14 | 9df35035-201c-43e2-9c0f-29f5652d20b6 | br_019_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_019_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_140 | 52cf19cb-d2f9-48a0-a5d7-3d345a429c59 | br_020_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_020_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_140 | 7ac282db-535a-4cda-bcc4-f62230cc0be1 | br_020_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_020_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_140 | b6e43aeb-290f-443d-917c-933a0af02698 | br_020_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_020_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_141 | 0b5869b0-b194-4a18-8593-e04336ade6ea | br_021_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_021_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_141 | 78f844cc-a5b4-4d9d-ba33-ef854d68bc8a | br_021_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_021_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_141 | b6f787f7-5117-4b48-81f4-ddbe099f96d7 | br_021_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_021_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_142 | 5c50320a-6541-43e1-a0eb-b3cc85335f92 | br_022_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_022_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_142 | aeed6de5-7aca-4fa3-a5ca-b1f32ee717c2 | br_022_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_022_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_142 | d8586197-7e6c-42e3-af81-89d0f76301f9 | br_022_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_022_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_143 | 15ee4200-f93f-4884-ab81-e52eb3d0b73c | br_023_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_023_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_143 | b2362459-63fa-42c8-b75d-cdff666f2190 | br_023_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_023_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_143 | ef7cab0d-e432-4fb1-aab4-46e5068286b4 | br_023_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_023_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_144 | 82536324-6f01-4e66-a011-7b067544a9ac | br_024_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_024_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_144 | bd7e1df8-2eb1-4167-bee8-930536ce0573 | br_024_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_024_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_144 | cebe0434-4e95-4fd2-8e1e-22573f21abf5 | br_024_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_024_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_145 | 039cb766-152c-4467-9ec0-94180921a657 | br_025_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_025_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_145 | 5042bbb0-cc21-499d-9106-09bd8c86b439 | br_025_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_025_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_145 | e8f52edb-11b6-4a01-8cb4-dde6abb481d7 | br_025_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_025_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_146 | 45141e3c-ee87-445b-a8cd-53eaf3cf8ac6 | br_026_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_026_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_146 | 9c3aa61d-fdd8-4e3a-a859-786b34331466 | br_026_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_026_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_146 | d4d03355-620e-4213-a24e-266e873f3f79 | br_026_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_026_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_147 | 783419bf-1c8f-4783-a364-729c4d25328a | br_027_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_027_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_147 | a6c68db1-932a-455f-9961-2001628d137a | br_027_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_027_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_147 | b05dca4b-f167-46ba-b479-77fc9d306c98 | br_027_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_027_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_148 | 9cb02ef5-7d31-4690-b5cc-1c8ff7465b94 | br_028_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_028_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_148 | e51bd3d2-27db-4e8c-85b3-94bb36fdecb2 | br_028_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_028_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_148 | f209db33-c63a-4eeb-9470-44a070b1f980 | br_028_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_028_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_149 | 22ef08a2-8b87-47bf-912f-a49f8dbe4e0e | br_029_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_029_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_149 | 54f22dd6-dae8-4d6f-8c00-4ee16cc1bce1 | br_029_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_029_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_149 | a7d55959-39f6-4006-8a75-2ac4375060d6 | br_029_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_029_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_15 | 2dfc9022-cd2d-4071-a0ed-f7aa4dbf29b5 | br_020_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_020_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_15 | 34fb9785-294c-4580-94c1-92b57cb0e642 | br_020_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_020_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_15 | dd9e89fb-3f9a-4966-a494-c19ab9432a67 | br_020_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_020_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_150 | 97ae36fa-2e65-4c6d-8a11-b6c4ba921c0d | br_030_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_030_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_150 | 99ca8035-36a9-410b-844c-06c1ddb4c66b | br_030_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_030_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_150 | e18873a3-19e0-4c86-abaf-03f1ea49ef98 | br_030_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_030_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_151 | 051f7584-2010-41f8-9415-9183657a8ae0 | br_031_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_031_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_151 | 0542d836-ab02-49aa-a8b7-a4265443a1c4 | br_031_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_031_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_151 | 5b53a681-1338-4fee-9587-71b3e65506cb | br_031_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_031_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_152 | 3b38bb39-6b77-49e7-b0c7-d3c699da74dc | br_032_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_032_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_152 | 3f75484a-66ad-416b-bdfc-429bf783f99d | br_032_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_032_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_152 | ab723fc3-e0cb-4dbc-8181-5681e5ac3348 | br_032_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_032_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_153 | 07ea0bf7-442d-4e77-b98a-b9e2c8d50114 | br_033_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_033_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_153 | 0d3f8e19-033b-4d8c-a34b-ff04747bd082 | br_033_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_033_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_153 | 5e1ed7ac-1e16-4c51-bb12-e8d8b8c244c4 | br_033_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_033_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_154 | 0840b23d-66b0-48cf-856c-1f62526c7d6e | br_034_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_034_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_154 | 6eba73e4-418d-4cd1-96b6-60b826ae450c | br_034_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_034_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_154 | 70369b74-10d7-4556-af26-c0ccb8f01935 | br_034_22 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_034_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_155 | 033ba35a-0e88-44c7-ae68-9ef721532ab3 | br_01_23 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_01_23.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_155 | d1e45bf7-a00b-40dc-a6ec-c751080a13c9 | br_01_23 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_01_23.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_155 | ecb9c3ef-513f-492a-821c-4bff92c1df9c | br_01_23 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_01_23.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_156 | 12b55d36-db8c-475f-838b-08caf84b6421 | br_02_23 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_02_23.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_156 | 17343a92-f390-4c00-96dd-aa4c8e6f2cf5 | br_02_23 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_02_23.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_156 | 2ec12710-cbb3-4ac0-ae81-f21bc775b59d | br_02_23 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_02_23.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_157 | 962e5ace-7f13-49d9-a1bd-65973f2adfac | br_03_23 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_03_23.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_157 | b96622f9-34da-4d3a-a144-a82c9e2d84a9 | br_03_23 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_03_23.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_157 | d76a1565-b995-4235-9508-12ae427ed548 | br_03_23 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_03_23.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_158 | 5320e9a7-8d71-4f75-b9c9-3a6a37f707db | br_04_23 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_04_23.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_158 | 8e1d3060-4f17-4027-bb48-9326d72d1f5e | br_04_23 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_04_23.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_158 | b84e6ee7-bc4b-467a-884d-e5dac0fbac0b | br_04_23 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_04_23.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_159 | 2e882994-3bef-4961-988c-cd677efd6410 | br_05_23 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_05_23.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_159 | 83f2cd36-180e-4d9a-9105-62a32f68ab85 | br_05_23 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_05_23.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_159 | 96fae847-ae01-4905-9884-47b324a88934 | br_05_23 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_05_23.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_16 | 2b3c0835-4f9e-453c-86b3-35847ab5af94 | br_021_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_021_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_16 | b5d738a6-79bd-43f6-b4e4-0fb4de70abfd | br_021_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_021_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_16 | e4f24c66-81cd-48f4-b9a3-a8aaa9fe8c98 | br_021_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_021_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_160 | 47f0ee8f-4288-4af4-b69a-10cebf43b645 | br_06_23 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_06_23.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_160 | b9360429-edfb-4e59-a900-8a457dc83cba | br_06_23 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_06_23.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_160 | c3e81296-2c1a-4ada-80c1-b847107d5cfb | br_06_23 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_06_23.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_161 | 89a3b24a-887f-4195-8344-51f18a00dbf7 | br_07_23 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_07_23.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_161 | c4eee589-eb1d-4947-bc9b-3f547ec858d4 | br_07_23 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_07_23.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_161 | e61fb2d3-e704-4d3f-bf86-8b04c3724fd7 | br_07_23 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_07_23.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_162 | 4bfd3a0a-1178-4983-b63c-76c387206a99 | br_08_23 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_08_23.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_162 | f4ffa257-f9a9-48e6-8ef7-945f8e687e83 | br_08_23 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_08_23.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_162 | f620b838-2134-4f66-a112-15e5f46318b0 | br_08_23 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_08_23.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_163 | 0d2e0f05-d1e8-46f2-953d-daf9b517d3b5 | br_09_23 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_09_23.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_163 | 9018e821-338d-4aa5-bb0d-3e9aa19f5a3b | br_09_23 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_09_23.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_163 | d90170cc-5eec-43f7-a5d9-cb91dca851cb | br_09_23 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_09_23.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_17 | 3a2af09c-baa8-4dbe-95ab-fb397036b19d | br_024_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_024_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_17 | 883c59a4-ab46-45e2-b36d-e1959b7c89b6 | br_024_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_024_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_17 | f0a67506-31bf-4b47-9614-f559c928646a | br_024_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_024_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_18 | 08eb7b30-b593-4a81-854f-d7a00d46db1e | br_025_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_025_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_18 | 34cac5e4-313a-4454-a92d-abc9047eadc8 | br_025_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_025_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_18 | 90d3f27c-2599-462f-8abb-58371a03ece5 | br_025_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_025_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_19 | a03bc8be-0c7b-4ca4-b625-79f7823155e9 | br_026_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_026_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_19 | cf54e8e6-a9a5-4011-b2be-1226fbdc86cb | br_026_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_026_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_19 | d5920248-7472-436e-b060-c7c2ff9ef29d | br_026_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_026_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_2 | a28c1752-7f45-48c2-b058-b7cdc091e5d6 | br_02_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_02_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_2 | e16fe26a-3331-4e10-bcda-3d5b4cfc42bc | br_02_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_02_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_2 | f5b81547-937f-4c70-92ba-8a0fb6594394 | br_02_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_02_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_20 | 0367f0a8-b7e5-4ca5-94ae-d44fa9d00bfd | br_027_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_027_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_20 | a602edca-8fde-46f7-8d51-40a5f85d6a1d | br_027_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_027_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_20 | c9015052-da74-4877-bbf1-9a6c4275c44d | br_027_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_027_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_21 | 39b0a939-9afe-4c84-bfda-5eec318bc35e | br_028_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_028_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_21 | 6f7a2c02-ca5d-4d73-a76d-82f0fe3158c9 | br_028_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_028_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_21 | a49c303e-bacd-45af-8754-babfb2545a48 | br_028_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_028_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_22 | 60e175bd-dd8d-424f-b541-e6c27675c2ee | br_029_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_029_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_22 | c13495f3-7436-4771-9d8e-028fe398e677 | br_029_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_029_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_22 | f1fcda72-2c9e-4219-9a68-e344865344e1 | br_029_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_029_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_23 | 306a0179-6b1d-4c84-b7ad-c043978706f4 | br_030_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_030_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_23 | 73114768-3396-46b2-8366-027d7f330c2a | br_030_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_030_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_23 | 8896d2cc-f5f3-479a-9806-74f9830d0e65 | br_030_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_030_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_24 | 0e740376-b7d0-46f1-8238-50979ff53b86 | br_031_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_031_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_24 | 3abd341d-8629-4be0-888c-4405cbd18a68 | br_031_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_031_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_24 | 8866ae0d-1645-4e1d-85a9-520a2b057093 | br_031_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_031_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_25 | 6a2617f0-409e-448d-8ce4-c1175edcf36a | br_032_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_032_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_25 | 8c0cf450-9297-450e-b468-8396988be79f | br_032_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_032_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_25 | d4f80b32-222c-49ea-bb38-81080bcb0826 | br_032_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_032_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_26 | 06410d93-c578-4f9d-86d8-8eb333ba28c9 | br_033_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_033_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_26 | 123d2e0f-6c7b-4b17-96d2-32d4328dde67 | br_033_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_033_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_26 | 2ded452d-d964-456f-bc61-891c5e02102b | br_033_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_033_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_27 | 6fdd1896-ad74-48a8-9816-85aa01d652d1 | br_034_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_034_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_27 | 9dbd0f33-80b1-4155-96b0-ea2e0658e691 | br_034_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_034_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_27 | d428eae8-d228-4f79-b9ea-91e3a88bb229 | br_034_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_034_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_28 | 4b1de06e-7ccd-42bd-ba7d-141a0d6eed10 | br_035_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_035_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_28 | 4cc07d73-767d-4a92-aa56-8d6f6139433c | br_035_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_035_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_28 | c3250712-a026-44dc-83b1-ab0b7bd1cef0 | br_035_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_035_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_29 | 37be8bbe-3fc1-42ac-aa14-512831f011d9 | br_036_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_036_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_29 | 53ac9d88-ec7e-422c-9547-7b65d0e1b05c | br_036_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_036_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_29 | bbdb1c8c-b61b-4af3-a00d-d34e99f936e8 | br_036_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_036_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_3 | 262d1506-d23e-42d2-a938-f15cb2f35365 | br_03_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_03_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_3 | 861d3fe8-4f6d-46b5-bb00-6d79ddaf889d | br_03_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_03_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_3 | cabb02b4-86e3-4261-87ef-66f06902bb61 | br_03_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_03_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_30 | 07afe75d-2efa-4a63-8500-f5eed954ebc4 | br_037_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_037_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_30 | 4339844d-f7f4-4af5-a7ce-ff1e206a4bfc | br_037_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_037_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_30 | 80a38063-4b58-4c05-9631-c9f20eaae49f | br_037_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_037_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_31 | c4bbbd0b-e3cc-4312-b11b-48dca067f34f | br_038_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_038_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_31 | dbd51660-93ed-49dc-b484-ac1a2ff93751 | br_038_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_038_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_31 | f5f51af7-9112-4286-adaa-37e4589d054a | br_038_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_038_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_32 | 049d0b94-e086-4825-b104-d454ffd3dc7c | br_039_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_039_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_32 | 81e832b4-cd01-4844-b4d8-6ff81d95dbe4 | br_039_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_039_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_32 | 934aabc4-8b42-44e6-82dc-1b3261dc29d9 | br_039_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_039_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_33 | 2bcc2cc5-82f5-4040-ac32-a00d0d07de51 | br_040_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_040_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_33 | d858a33a-1b66-4073-aed2-4b1a30ad837b | br_040_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_040_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_33 | ee1a565e-ae8b-4984-9f7a-cab15b5447c3 | br_040_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_040_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_34 | 0cbf9200-98b4-43c7-934d-2cc30d8ab63b | br_041_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_041_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_34 | 179024ab-8e49-42be-b943-761705fb5abd | br_041_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_041_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_34 | deb58541-2cca-43d5-86c5-55264c6041d3 | br_041_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_041_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_35 | 6d4ede07-2601-4246-903b-56124df12172 | br_042_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_042_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_35 | d7ccdfd6-6a7d-4338-9666-e79b11f003a9 | br_042_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_042_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_35 | efc37dec-e402-4c7d-81af-aa9cb2729757 | br_042_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_042_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_36 | 1ede274a-9246-4aec-acc0-17642c07af97 | br_043_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_043_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_36 | a492b914-7377-4047-b30b-90aa78dc94d3 | br_043_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_043_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_36 | c95edbeb-bfcc-48be-abeb-7c6ceba7bdae | br_043_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_043_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_37 | 53f8a349-7f61-440d-ad82-54a7f6d15d3a | br_044_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_044_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_37 | 547c5604-b333-47b9-83ad-6f6fa1e88927 | br_044_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_044_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_37 | e72c363a-7373-4a30-a872-329d650d7569 | br_044_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_044_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_38 | 15e8162e-962b-481f-923b-b2fe7c7ce432 | br_045_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_045_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_38 | 31c14863-6ede-40c4-86a5-41eadc729ac2 | br_045_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_045_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_38 | 9c1dc66a-d26b-42ae-9fa5-d4e46c87f492 | br_045_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_045_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_39 | 1ef359a3-1b23-4781-b7f6-73e5a4c4559f | br_046_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_046_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_39 | 77ff5585-562a-45e7-a281-464e98737abb | br_046_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_046_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_39 | 93658bef-4bd5-4300-8424-5c388155968b | br_046_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_046_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_4 | 1da22d5c-e6b3-4228-b327-ddf40f1f21b6 | br_04_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_04_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_4 | 67c44f52-c49c-4993-940f-90408b4b9ae5 | br_04_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_04_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_4 | eda55f14-fedc-4eb6-a389-a51a43231405 | br_04_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_04_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_40 | 58cd6faf-3139-48ff-a9ef-b152b7ebf778 | br_047_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_047_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_40 | 79202d32-8dca-417a-9d59-fc14f3bcaf5f | br_047_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_047_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_40 | ee7aaead-b8fb-40d3-8a03-8ab58a542fdc | br_047_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_047_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_41 | 4f3f10ee-748f-4c21-b9c3-8ac51c8d41f6 | br_048_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_048_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_41 | d7d6e014-1cd2-4cb5-84bb-a00b2cad42e3 | br_048_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_048_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_41 | e1cda877-0a5c-49b1-bd5f-ad8449fb0e0c | br_048_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_048_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_42 | 0b1099db-07b7-4a46-831f-0ab42e837cdd | br_049_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_049_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_42 | 0e80773a-a8cc-45a5-8095-4dc9d8b00215 | br_049_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_049_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_42 | 119ef0a4-9572-4988-9343-96cacd641d11 | br_049_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_049_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_43 | 223df89f-b673-46b7-a74d-953aa3cadd02 | br_050_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_050_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_43 | d260c5dc-0f9a-4ff7-a347-cabc3421f531 | br_050_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_050_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_43 | d8ed1451-4cac-4c54-9238-07312269a3d5 | br_050_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_050_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_44 | 9de5605e-2be3-4478-8321-ec1cfdb77d3e | br_051_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_051_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_44 | ae9708d6-58e3-48d8-b469-2b865749bda5 | br_051_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_051_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_44 | c206a6a0-74a2-4aa0-b700-0397b158b47c | br_051_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_051_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_45 | 0a36e22d-cb96-45c8-8d47-74ede8f433bd | br_052_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_052_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_45 | 87af0485-ac3b-4ef1-bd8e-39742bb1311b | br_052_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_052_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_45 | ac9dddc3-7cae-427c-a129-87d3008b8362 | br_052_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_052_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_46 | 0b8f662d-5bc3-42fe-a24e-070da09bdd80 | br_053_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_053_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_46 | 425e9895-3ec9-4ecf-a2de-00e847c9f5d0 | br_053_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_053_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_46 | e8d1fc00-bcf6-4d05-b6b9-7f38e6915ce5 | br_053_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_053_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_47 | 44d72b2b-4d39-442e-969c-28bfa609a6ca | br_054_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_054_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_47 | 73020989-8b85-4f2f-ae5e-b46034dccc36 | br_054_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_054_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_47 | df231f2b-7e74-4562-8026-e0248f99acb1 | br_054_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_054_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_48 | 2756c12d-de33-427b-a20e-a7524bf8ba2a | br_055_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_055_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_48 | caead5dd-6652-4002-9205-bf1f5d7841a2 | br_055_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_055_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_48 | d501232c-0e9b-4aed-b1c7-0711f51fd12c | br_055_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_055_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_49 | 4e486c1d-6969-466b-bb85-e868d8c69d96 | br_056_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_056_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_49 | 904a534b-b4de-47cc-9111-a909cdd75ff6 | br_056_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_056_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_49 | cf17223b-5ef6-40ff-aa3f-7eaa71fa5ab1 | br_056_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_056_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_5 | 1a7b2ce3-8ce4-43f0-822c-bae88f338574 | br_05_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_05_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_5 | 921b5057-9802-4094-b921-551288ad3d2e | br_05_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_05_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_5 | fdea0e08-11f9-40c1-bd4a-4dfdb8ea2803 | br_05_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_05_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_50 | 02cb60eb-e56b-45c0-871a-7d5da5072e9a | br_057_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_057_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_50 | 4d9bb5e2-1e06-49ed-b322-273c65c7ea12 | br_057_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_057_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_50 | ceeee8fb-13b1-43c7-9caf-4433648f6846 | br_057_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_057_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_51 | 100d5254-7678-4ba2-a678-ffa8ba0ac8ce | br_058_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_058_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_51 | 2dabfa67-e633-42fb-88f8-b99c8c81ce3f | br_058_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_058_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_51 | 40e658e9-710a-4f81-b823-ce3b23d76208 | br_058_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_058_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_52 | 148e241f-8dca-40c2-bc4c-9bba11acb600 | br_059_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_059_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_52 | 54cc7298-372e-4f46-9c94-d78d3e7e3368 | br_059_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_059_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_52 | 740ff96c-6171-4486-bb6a-904851da7f68 | br_059_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_059_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_53 | 3b012ead-fe04-4b66-8c50-59d42334a89c | br_060_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_060_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_53 | 4b800952-fa1b-4668-ba63-4244710bab3c | br_060_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_060_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_53 | 77c08208-993b-4559-b9e2-42c4c772997c | br_060_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_060_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_54 | 0c2d5da7-8b73-4e99-a2ec-e1bd371c44f1 | br_061_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_061_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_54 | b486465e-b5c3-4f46-9979-e961ceb9df52 | br_061_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_061_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_54 | c70624cc-3511-421e-bcd3-4f74ee43c80f | br_061_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_061_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_55 | 0d627f19-7146-43b0-9f7b-bac68e9966db | br_062_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_062_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_55 | 55b291eb-5761-4e7f-8635-63057f856791 | br_062_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_062_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_55 | efb7b851-1f6e-4084-9dd6-5a62049b7654 | br_062_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_062_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_56 | 620a8a0d-bcbd-4f44-be97-24244e308366 | br_063_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_063_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_56 | 748858e9-a0e0-4bc6-a0b7-f4e67d7c9ecd | br_063_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_063_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_56 | d5be6516-e14a-46ab-a02a-0650b74a5159 | br_063_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_063_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_57 | 08dafb35-ef6e-48c6-89ef-1f3412fa5f7e | br_08_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_08_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_57 | 27046833-12e1-4f55-aeb1-743d3fddc9b4 | br_08_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_08_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_57 | e2d61ac2-432e-446d-b560-32b75aebceed | br_08_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_08_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_58 | b8c6df33-b602-4d1c-9dda-e52dfeb41665 | br_09_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_09_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_58 | cd71f269-7897-4746-9a77-c6bc730114fe | br_09_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_09_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_58 | ff232009-b42f-4f71-a769-88a952701609 | br_09_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_09_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_59 | 1231155d-ed13-4563-8801-fa08388d11cd | br_010_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_010_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_59 | 1b822839-e89f-49f2-b2a9-69df27011548 | br_010_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_010_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_59 | 4529fb6d-421e-4f02-9b11-c956a4443f8e | br_010_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_010_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_6 | 120599d7-eee0-4966-bd20-36d9e2e8b089 | br_06_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_06_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_6 | 145f4423-0120-41c0-a961-6f6b453e91a7 | br_06_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_06_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_6 | a5d804f2-bcf0-4e70-ad7f-9ffc889ca71a | br_06_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_06_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_60 | 229fce16-0cb2-401d-957b-9d0d3c2ac1cc | br_011_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_011_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_60 | 52980b4f-3c73-4c68-8631-e69ccc722a34 | br_011_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_011_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_60 | fc187080-4278-4699-8d7f-ded10dc27448 | br_011_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_011_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_61 | 192ef0e0-59f5-4932-a625-7e967573ec09 | br_012_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_012_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_61 | 69c0c6b0-aa07-4cdc-9789-b51b223584c4 | br_012_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_012_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_61 | bdb558af-9d90-4dcd-870e-28a86925b8cc | br_012_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_012_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_62 | 2c8910bb-0c41-4c36-8a5f-d8ffc5e65938 | br_013_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_013_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_62 | 3f59d58a-b780-49d5-86ae-b0b0f01c076d | br_013_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_013_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_62 | decddce1-9f0e-44c6-a3bd-24fdb9cf1a60 | br_013_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_013_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_63 | 167b629e-ae1a-4acd-a435-a9faf6b8f0b1 | br_014_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_014_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_63 | 676b1650-044c-43bf-bea6-3dced2a612c6 | br_014_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_014_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_63 | abbc8c51-7785-4d04-a735-eb965d943d5a | br_014_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_014_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_64 | 8ec9092e-c513-4856-b139-17b0f244b287 | br_064_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_064_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_64 | 96d7ca9d-a8a7-4620-beb4-015993e1495f | br_064_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_064_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_64 | aa668afa-9003-4c02-b068-76a760cba7c4 | br_064_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_064_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_65 | a2d74127-91f7-4d1b-a98b-b3f287f80eec | br_065_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_065_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_65 | a8421f63-1fb7-4386-80d1-558a9049f658 | br_065_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_065_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_65 | c0caf65c-2d30-471b-9a8c-36e1484ba877 | br_065_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_065_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_66 | 0cbf5c43-696f-40b4-ab01-fd3dfd670388 | br_066_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_066_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_66 | 3f826b2c-284b-4880-a9f1-d5554c1e5213 | br_066_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_066_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_66 | aa212fd9-92d5-4c56-9a9e-3014ccc9a7ce | br_066_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_066_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_67 | 4b3c48a3-9a69-47a9-b110-7d0b18cc7f06 | br_067_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_067_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_67 | 5aed073b-49c0-4020-b105-f7e28cfd41ed | br_067_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_067_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_67 | fddc71cc-3766-4601-9ca7-c2caab3c7c4d | br_067_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_067_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_68 | 6abb0433-d7c1-47cb-b500-310c0966ae29 | br_068_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_068_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_68 | b14a51cb-21cb-48f4-91a6-564663c5a923 | br_068_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_068_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_68 | f2986696-35a7-4d1e-a7dd-8b01d8d6756a | br_068_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_068_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_69 | 16e446fe-cce5-4d4b-abd0-d9bf98278835 | br_069_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_069_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_69 | 3f69baec-6464-4c01-91c1-171903c224f7 | br_069_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_069_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_69 | 9255af13-2569-446c-b326-8de2942e3a26 | br_069_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_069_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_7 | 7c4e0a27-0ba8-4589-8efa-9d78e22aeea7 | br_07_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_07_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_7 | 874fce3a-0ddc-405e-8b4d-496bf1208ffa | br_07_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_07_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_7 | b3997dcd-0479-4422-904f-1e86aedb3b49 | br_07_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_07_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_70 | 7a4e8fb6-f007-4d77-bfcb-6a0b0e18561c | br_070_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_070_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_70 | 96d35f0d-746b-4c76-8d6d-a22dac3dcfaa | br_070_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_070_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_70 | ff4d78df-a97d-465a-9270-6b140f05b7ee | br_070_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_070_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_71 | 4ff8b560-0d8d-46ca-aa4f-48e616d84a8c | br_071_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_071_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_71 | 7dec81b6-3b82-498d-bfaa-f44bf5d9581d | br_071_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_071_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_71 | 828a3353-455f-43cc-a9b0-71980deae8fd | br_071_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_071_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_72 | 2f6074d9-3367-424b-9912-3b54ba3842dc | br_072_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_072_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_72 | 5be2e72a-f9e3-4662-bcdd-f6914b127473 | br_072_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_072_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_72 | ceb3c16f-b2c1-4384-83e5-47eb8d9787a9 | br_072_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_072_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_73 | 0a5bd7a0-8dda-4ea9-8140-b43dcad4334a | br_073_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_073_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_73 | dc0e22aa-9b17-4812-81b9-805e6e2fcea4 | br_073_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_073_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_73 | dd7e3ea9-a097-46d9-ba3d-e976877c959f | br_073_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_073_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_74 | 2be1e40d-d971-44eb-9f8e-1f362b00491f | br_074_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_074_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_74 | 4cb9db9e-b9c3-473e-878d-2df2932f4dcf | br_074_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_074_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_74 | b4794b85-7397-40b2-a7b2-50c82c66983d | br_074_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_074_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_75 | 74ba07cb-a526-4618-b499-1a430d0286b7 | br_075_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_075_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_75 | 8cfdaf81-8e59-4486-ba2f-4e450a23c876 | br_075_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_075_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_75 | dc09ae69-e1ee-4c83-9c04-e09da568c6ab | br_075_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_075_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_76 | 89cbe802-faf3-4709-b370-afa1154a5b70 | br_076_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_076_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_76 | a61580ad-490f-42dd-919c-3cfdfb775908 | br_076_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_076_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_76 | fd14c6a3-6658-4039-a0b8-c00ab26e307c | br_076_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_076_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_77 | 04933340-1f7e-4732-a170-31c687c8d71e | br_077_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_077_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_77 | 55611621-48c6-40ab-afb0-d76e41a0d5de | br_077_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_077_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_77 | da253492-f9e5-4572-a892-8cf7206f5562 | br_077_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_077_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_78 | 648e5aaa-f39d-4756-9d09-ca5503bbc225 | br_078_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_078_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_78 | 838a2e79-8d23-4760-9eab-eb6ed2d38b4c | br_078_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_078_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_78 | c0ddba19-fbd3-4341-bb7c-f8d96301d889 | br_078_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_078_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_79 | 02d224d1-8d1b-45bb-98ed-ebc20c74318a | br_079_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_079_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_79 | dfd547e9-e06c-4fe7-8842-913f0b3f7d52 | br_079_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_079_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_79 | f68a1c8a-5406-4783-b8ae-a255bce0e795 | br_079_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_079_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_8 | 14a29c10-6f6b-4045-834c-a8cdccfa7fe8 | br_022_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_022_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_8 | 674756f5-28ec-40f8-8ece-cd6c8a394c18 | br_022_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_022_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_8 | 9e0bf50d-94bd-4e5d-9a43-95a506f4c534 | br_022_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_022_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_80 | 48527915-ef6b-4d16-9525-f6d17fae71ba | br_080_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_080_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_80 | 4fb9d568-cec8-4d2c-b185-503c8441a94f | br_080_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_080_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_80 | e4842198-5ba7-4542-9415-20f0a87511ac | br_080_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_080_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_81 | 27bb62b3-e552-4996-874d-31dcad547987 | br_081_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_081_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_81 | 9a5c0969-f68d-4cea-a13e-ef351a3d3730 | br_081_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_081_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_81 | a8a2fc9d-e642-4554-abad-f2610eb29b51 | br_081_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_081_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_82 | 918cae00-7f70-4556-9d40-35da1f05977d | br_082_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_082_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_82 | 93c33640-e4a0-470f-a164-89c99ae69984 | br_082_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_082_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_82 | a890d29a-0380-4cd2-8cff-f9826e3ff07b | br_082_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_082_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_83 | 48c0048d-65ab-48a8-8cd9-833258bee864 | br_083_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_083_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_83 | 8c265c14-8e0f-4c74-9519-46da2dff7cd1 | br_083_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_083_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_83 | af9148e3-1b4f-4f27-b409-3654c3f953f5 | br_083_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_083_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_84 | 4cc5af87-12cf-4fd1-a89c-0318dc07c068 | br_084_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_084_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_84 | b63c8e73-fffc-4e69-ad08-995c149ebeaa | br_084_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_084_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_84 | d4454767-7751-4c58-9cbd-79e943f45acf | br_084_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_084_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_85 | 4fc59078-b2c4-42d5-b129-faa7a3f54cac | br_085_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_085_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_85 | 6fcd01be-d3d1-4df7-bec8-4f8b1042aac0 | br_085_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_085_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_85 | ac192c64-42ef-423f-814b-c8b837b8f5d2 | br_085_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_085_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_86 | 492c962b-e2b7-4edd-afe9-20606e4114f6 | br_086_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_086_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_86 | 6182a628-fb52-41b9-8b93-90488a51a0fe | br_086_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_086_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_86 | 6927b6e8-4d14-436e-8236-19dc4cdad934 | br_086_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_086_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_87 | 589e4f98-7742-4541-b2c3-6b108b7f9d4d | br_087_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_087_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_87 | d9c84a3d-b565-4642-a7d4-3c9df307b1c8 | br_087_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_087_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_87 | e7689375-373b-4d7a-b001-0fa11239a327 | br_087_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_087_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_88 | 73bea406-8df3-48d6-99e8-780c9ba74d8d | br_088_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_088_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_88 | 93986b58-113b-4798-b153-eda6e8924352 | br_088_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_088_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_88 | b1fd8626-d75b-4f57-95d8-5e0f995f6548 | br_088_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_088_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_89 | a59c7bce-fb93-4255-8dac-4024e2c3a1c9 | br_089_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_089_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_89 | c6e42508-1e1b-4a8d-ad6c-5ed17230666d | br_089_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_089_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_89 | d629f58a-fb37-4300-b174-4dadcd7fdef5 | br_089_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_089_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_9 | 9b89dc0e-e258-4610-b60b-484b1b02a312 | br_023_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_023_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_9 | c7e10126-bd63-4bd3-96ab-07587af29378 | br_023_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_023_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_9 | f631ee12-3be7-417b-ad19-901e9ad68684 | br_023_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_023_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_90 | 59f75e54-a46d-4153-8855-555945d0a888 | br_090_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_090_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_90 | ab8abf18-0128-43c3-8213-8fcc30f583d2 | br_090_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_090_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_90 | f35586be-8010-4ad3-b579-d95b9825cae5 | br_090_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_090_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_91 | 11eec288-b107-4b0d-8513-8e0e8b097ff9 | br_091_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_091_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_91 | 2494a26c-ddcb-40f8-8643-7c936424dfc0 | br_091_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_091_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_91 | 66b6c9ff-fe2f-4708-83aa-26715afe7d27 | br_091_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_091_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_92 | 9e7256be-44ac-40e3-95c4-e604f1b5b6ea | br_092_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_092_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_92 | a984179e-ff24-4a5b-9bff-44fa02582a26 | br_092_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_092_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_92 | fbe573a4-e81d-4315-b9c9-510a65c98be6 | br_092_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_092_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_93 | 531ef22d-48aa-4ee9-88be-bf0b21101c8d | br_093_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_093_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_93 | 75f25960-b76b-4ea6-95b3-22351b5c7fde | br_093_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_093_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_93 | ac7b38f5-50a1-4cc6-bab1-d609ee8f92a4 | br_093_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_093_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_94 | a82b3639-950c-4ba5-8e39-502e435ad83a | br_094_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_094_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_94 | c177967e-e6f6-4644-aa50-326a9ebe3d00 | br_094_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_094_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_94 | f0bd6ef7-dacb-46d2-ad18-589db990b13a | br_094_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_094_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_95 | 859a9ae6-4d75-45f7-af3f-1d1c2c11b96f | br_095_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_095_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_95 | ad766f3b-7d19-4707-8a90-38f818011b97 | br_095_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_095_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_95 | c6b6dfcf-55ed-45e7-9e6a-1ed25774a828 | br_095_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_095_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_96 | 1b5731fb-ced8-4f58-b1ab-d0ee4f8ea875 | br_096_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_096_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_96 | fad28770-b3f6-4478-87a1-3b095d264a87 | br_096_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_096_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_96 | fcbaf392-5711-44ee-86c0-792317753d2f | br_096_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_096_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_97 | 003a8d77-c248-43c2-af2f-1f5f30595e2b | br_098_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_098_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_97 | 3b017716-3815-48f3-bf37-e278bd03cc9d | br_098_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_098_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_97 | b3f7a58f-66bb-4c73-a447-90250ee96029 | br_098_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_098_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_98 | 43272e40-5062-4f3e-9a6d-0899fa207db5 | br_099_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_099_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_98 | 74d4c75b-fdbd-4356-81ba-130cbea2e530 | br_099_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_099_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_98 | e19d273e-4ce0-462d-9501-16552f6df1a5 | br_099_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_099_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_99 | 667e5144-bfb1-4543-a81f-7a88e26190c7 | br_0100_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0100_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_99 | 9d892d7c-e138-4107-8084-bbde890e1cc4 | br_0100_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0100_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_99 | a3c897bb-ba13-4a0b-af16-81acabf20ccd | br_0100_21 | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0100_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A

## Direct_Downstream
grid_id | BreakerElementID | DownstreamElementID | ElementType | ElementCustomerType | Phases | IsProducer | IsConsumer | IsSwitchable | SwitchIsOpen | PowerFlowDirection | UpstreamElementID | Terminal1CN | Terminal2CN | RawRatingA | RawRatingKVA | RawPhaseToPhaseVoltage | RawVoltageLevel | RawPrimaryVoltage | RawSecondaryVoltage
GSO_1 | br_01_21 | recloser_1786_21 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_01_21 | S_nSSEE0_12.47 | S_nSSEE0_12.47_A_S_nCCTT10608 |  |  |  | MV
GSO_102 | br_0102_21 | recloser_1920_21 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_0102_21 | S_nSSEE7_12.47 | S_nSSEE7_12.47_A_S_nCCTT7083 |  |  |  | MV
GSO_106 | br_0106_21 | recloser_1957_21 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_0106_21 | S_nSSEE7_12.47 | S_nSSEE7_12.47_A_S_nCCTT9474 |  |  |  | MV
GSO_107 | br_0107_21 | recloser_1965_21 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_0107_21 | S_nSSEE7_12.47 | S_nSSEE7_12.47_A_S_nCCTT9667 |  |  |  | MV
GSO_113 | br_0113_21 | recloser_1931_21 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_0113_21 | S_nSSEE8_12.47 | S_nSSEE8_12.47_A_S_nCCTT7716 |  |  |  | MV
GSO_119 | br_0119_21 | recloser_1968_21 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_0119_21 | S_nSSEE9_12.47 | S_nSSEE9_12.47_A_S_nCCTT9936 |  |  |  | MV
GSO_122 | br_02_22 | recloser_186_22 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_02_22 | S_nSSEE0_12.47 | S_nSSEE0_12.47_A_S_nCCTT45 |  |  |  | MV
GSO_123 | br_03_22 | recloser_189_22 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_03_22 | S_nSSEE0_12.47 | S_nSSEE0_12.47_A_S_nCCTT521 |  |  |  | MV
GSO_124 | br_04_22 | recloser_198_22 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_04_22 | S_nSSEE0_12.47 | S_nSSEE0_12.47_A_S_nCCTT913 |  |  |  | MV
GSO_126 | br_06_22 | recloser_194_22 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_06_22 | S_nSSEE1_12.47 | S_nSSEE1_12.47_A_S_nCCTT691 |  |  |  | MV
GSO_127 | br_07_22 | recloser_204_22 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_07_22 | S_nSSEE1_12.47 | S_nSSEE1_12.47_A_UCMV43 |  |  |  | MV
GSO_128 | br_08_22 | recloser_205_22 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_08_22 | S_nSSEE1_12.47 | S_nSSEE1_12.47_A_UCMV51 |  |  |  | MV
GSO_129 | br_09_22 | recloser_152_22 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_09_22 | S_nSSEE2_12.47 | S_nSSEE2_12.47_A_S_nCCTT1012 |  |  |  | MV
GSO_131 | br_011_22 | recloser_167_22 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_011_22 | S_nSSEE2_12.47 | S_nSSEE2_12.47_A_S_nCCTT1334 |  |  |  | MV
GSO_132 | br_012_22 | recloser_173_22 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_012_22 | S_nSSEE2_12.47 | S_nSSEE2_12.47_A_S_nCCTT1508 |  |  |  | MV
GSO_136 | br_016_22 | recloser_172_22 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_016_22 | S_nSSEE3_12.47 | S_nCCTT1502 |  |  |  | MV
GSO_137 | br_017_22 | recloser_178_22 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_017_22 | S_nSSEE3_12.47 | S_nSSEE3_12.47_A_S_nCCTT257 |  |  |  | MV
GSO_138 | br_018_22 | recloser_180_22 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_018_22 | S_nSSEE3_12.47 | S_nSSEE3_12.47_A_S_nCCTT288 |  |  |  | MV
GSO_139 | br_019_22 | recloser_190_22 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_019_22 | S_nSSEE3_12.47 | S_nSSEE3_12.47_A_S_nCCTT557 |  |  |  | MV
GSO_141 | br_021_22 | recloser_168_22 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_021_22 | S_nSSEE4_12.47 | S_nSSEE4_12.47_A_S_nCCTT1344 |  |  |  | MV
GSO_144 | br_024_22 | recloser_188_22 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_024_22 | S_nSSEE4_12.47 | S_nSSEE4_12.47_A_S_nCCTT504 |  |  |  | MV
GSO_149 | br_029_22 | recloser_201_22 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_029_22 | S_nSSEE5_12.47 | S_nSSEE5_12.47_A_S_nCCTT988 |  |  |  | MV
GSO_150 | br_030_22 | recloser_170_22 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_030_22 | S_nSSEE6_12.47 | S_nSSEE6_12.47_A_S_nCCTT1419 |  |  |  | MV
GSO_151 | br_031_22 | recloser_179_22 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_031_22 | S_nSSEE6_12.47 | S_nSSEE6_12.47_A_S_nCCTT267 |  |  |  | MV
GSO_152 | br_032_22 | recloser_196_22 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_032_22 | S_nSSEE6_12.47 | S_nSSEE6_12.47_A_S_nCCTT811 |  |  |  | MV
GSO_153 | br_033_22 | recloser_199_22 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_033_22 | S_nSSEE6_12.47 | S_nSSEE6_12.47_A_S_nCCTT972 |  |  |  | MV
GSO_161 | br_07_23 | recloser_469_23 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_07_23 | S_nSSEE1_12.47 | S_nSSEE1_12.47_A_S_nCCTT2630 |  |  |  | MV
GSO_20 | br_027_21 | recloser_1780_21 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_027_21 | S_nSSEE12_12.47 | S_nSSEE12_12.47_A_S_nCCTT10471 |  |  |  | MV
GSO_24 | br_031_21 | recloser_1899_21 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_031_21 | S_nSSEE12_12.47 | S_nSSEE12_12.47_A_S_nCCTT5549 |  |  |  | MV
GSO_28 | br_035_21 | recloser_1840_21 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_035_21 | S_nSSEE13_12.47 | S_nSSEE13_12.47_A_S_nCCTT1498 |  |  |  | MV
GSO_3 | br_03_21 | recloser_1859_21 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_03_21 | S_nSSEE0_12.47 | S_nSSEE0_12.47_A_S_nCCTT2967 |  |  |  | MV
GSO_31 | br_038_21 | recloser_1974_21 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_038_21 | S_nSSEE13_12.47 | S_nSSEE13_12.47_A_UCMV39 |  |  |  | MV
GSO_33 | br_040_21 | recloser_1813_21 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_040_21 | S_nSSEE14_12.47 | S_nSSEE14_12.47_A_S_nCCTT11669 |  |  |  | MV
GSO_38 | br_045_21 | recloser_1787_21 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_045_21 | S_nSSEE15_12.47 | S_nSSEE15_12.47_A_S_nCCTT1062 |  |  |  | MV
GSO_44 | br_051_21 | recloser_1785_21 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_051_21 | S_nSSEE16_12.47 | S_nSSEE16_12.47_A_S_nCCTT10604 |  |  |  | MV
GSO_47 | br_054_21 | recloser_1819_21 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_054_21 | S_nSSEE16_12.47 | S_nSSEE16_12.47_A_S_nCCTT11861 |  |  |  | MV
GSO_49 | br_056_21 | recloser_1832_21 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_056_21 | S_nSSEE16_12.47 | S_nSSEE16_12.47_A_S_nCCTT12332 |  |  |  | MV
GSO_50 | br_057_21 | recloser_1847_21 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_057_21 | S_nSSEE16_12.47 | S_nSSEE16_12.47_A_S_nCCTT2007 |  |  |  | MV
GSO_55 | br_062_21 | recloser_1928_21 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_062_21 | S_nSSEE17_12.47 | S_nSSEE17_12.47_A_S_nCCTT7620 |  |  |  | MV
GSO_70 | br_070_21 | recloser_1963_21 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_070_21 | S_nSSEE2_12.47 | S_nSSEE2_12.47_A_S_nCCTT9608 |  |  |  | MV
GSO_73 | br_073_21 | recloser_1941_21 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_073_21 | S_nSSEE3_12.47 | S_nSSEE3_12.47_A_S_nCCTT8151 |  |  |  | MV
GSO_76 | br_076_21 | recloser_1851_21 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_076_21 | S_nSSEE4_12.47 | S_nSSEE4_12.47_A_S_nCCTT2321 |  |  |  | MV
GSO_78 | br_078_21 | recloser_1871_21 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_078_21 | S_nSSEE4_12.47 | S_nSSEE4_12.47_A_S_nCCTT4102 |  |  |  | MV
GSO_8 | br_022_21 | recloser_1846_21 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_022_21 | S_nSSEE10_12.47 | S_nSSEE10_12.47_A_S_nCCTT1831 |  |  |  | MV
GSO_90 | br_090_21 | recloser_1867_21 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_090_21 | S_nSSEE5_12.47 | S_nSSEE5_12.47_A_S_nCCTT3827 |  |  |  | MV
GSO_93 | br_093_21 | recloser_1874_21 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_093_21 | S_nSSEE5_12.47 | S_nSSEE5_12.47_A_S_nCCTT4180 |  |  |  | MV
GSO_94 | br_094_21 | recloser_1912_21 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_094_21 | S_nSSEE5_12.47 | S_nSSEE5_12.47_A_S_nCCTT6488 |  |  |  | MV

## Direct_Downstream_Summary
grid_id | DirectDownstreamElementCount | DirectDownstreamLineCount | DirectDownstreamTransformerCount | DirectDownstreamSwitchCount
GSO_1 | 1 | 0 | 0 | 1
GSO_102 | 1 | 0 | 0 | 1
GSO_106 | 1 | 0 | 0 | 1
GSO_107 | 1 | 0 | 0 | 1
GSO_113 | 1 | 0 | 0 | 1
GSO_119 | 1 | 0 | 0 | 1
GSO_122 | 1 | 0 | 0 | 1
GSO_123 | 1 | 0 | 0 | 1
GSO_124 | 1 | 0 | 0 | 1
GSO_126 | 1 | 0 | 0 | 1
GSO_127 | 1 | 0 | 0 | 1
GSO_128 | 1 | 0 | 0 | 1
GSO_129 | 1 | 0 | 0 | 1
GSO_131 | 1 | 0 | 0 | 1
GSO_132 | 1 | 0 | 0 | 1
GSO_136 | 1 | 0 | 0 | 1
GSO_137 | 1 | 0 | 0 | 1
GSO_138 | 1 | 0 | 0 | 1
GSO_139 | 1 | 0 | 0 | 1
GSO_141 | 1 | 0 | 0 | 1
GSO_144 | 1 | 0 | 0 | 1
GSO_149 | 1 | 0 | 0 | 1
GSO_150 | 1 | 0 | 0 | 1
GSO_151 | 1 | 0 | 0 | 1
GSO_152 | 1 | 0 | 0 | 1
GSO_153 | 1 | 0 | 0 | 1
GSO_161 | 1 | 0 | 0 | 1
GSO_20 | 1 | 0 | 0 | 1
GSO_24 | 1 | 0 | 0 | 1
GSO_28 | 1 | 0 | 0 | 1
GSO_3 | 1 | 0 | 0 | 1
GSO_31 | 1 | 0 | 0 | 1
GSO_33 | 1 | 0 | 0 | 1
GSO_38 | 1 | 0 | 0 | 1
GSO_44 | 1 | 0 | 0 | 1
GSO_47 | 1 | 0 | 0 | 1
GSO_49 | 1 | 0 | 0 | 1
GSO_50 | 1 | 0 | 0 | 1
GSO_55 | 1 | 0 | 0 | 1
GSO_70 | 1 | 0 | 0 | 1
GSO_73 | 1 | 0 | 0 | 1
GSO_76 | 1 | 0 | 0 | 1
GSO_78 | 1 | 0 | 0 | 1
GSO_8 | 1 | 0 | 0 | 1
GSO_90 | 1 | 0 | 0 | 1
GSO_93 | 1 | 0 | 0 | 1
GSO_94 | 1 | 0 | 0 | 1

## Entrance_Path_Detail
grid_id | BreakerElementID | PathElementID | ElementType | ElementCustomerType | Phases | IsProducer | IsConsumer | IsSwitchable | SwitchIsOpen | PowerFlowDirection | UpstreamElementID | Terminal1CN | Terminal2CN | RawRatingA | RawRatingKVA | RawPhaseToPhaseVoltage | RawVoltageLevel | DepthFromBreaker | IsLine
GSO_1 | br_01_21 | recloser_1786_21 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_01_21 | S_nSSEE0_12.47 | S_nSSEE0_12.47_A_S_nCCTT10608 |  |  |  | MV | 1 | FALSE
GSO_1 | br_01_21 | line_107866_21 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_1786_21 | S_nSSEE0_12.47_A_S_nCCTT10608 | S_nCCTT10608 | 600 |  | 12470 | MV | 2 | TRUE
GSO_102 | br_0102_21 | recloser_1920_21 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_0102_21 | S_nSSEE7_12.47 | S_nSSEE7_12.47_A_S_nCCTT7083 |  |  |  | MV | 1 | FALSE
GSO_102 | br_0102_21 | line_127499_21 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_1920_21 | S_nSSEE7_12.47_A_S_nCCTT7083 | S_nCCTT7083 | 660 |  | 12470 | MV | 2 | TRUE
GSO_106 | br_0106_21 | recloser_1957_21 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_0106_21 | S_nSSEE7_12.47 | S_nSSEE7_12.47_A_S_nCCTT9474 |  |  |  | MV | 1 | FALSE
GSO_106 | br_0106_21 | line_131696_21 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_1957_21 | S_nSSEE7_12.47_A_S_nCCTT9474 | S_nCCTT9474 | 660 |  | 12470 | MV | 2 | TRUE
GSO_107 | br_0107_21 | recloser_1965_21 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_0107_21 | S_nSSEE7_12.47 | S_nSSEE7_12.47_A_S_nCCTT9667 |  |  |  | MV | 1 | FALSE
GSO_107 | br_0107_21 | line_132043_21 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_1965_21 | S_nSSEE7_12.47_A_S_nCCTT9667 | S_nCCTT9667 | 660 |  | 12470 | MV | 2 | TRUE
GSO_113 | br_0113_21 | recloser_1931_21 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_0113_21 | S_nSSEE8_12.47 | S_nSSEE8_12.47_A_S_nCCTT7716 |  |  |  | MV | 1 | FALSE
GSO_113 | br_0113_21 | line_128560_21 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_1931_21 | S_nSSEE8_12.47_A_S_nCCTT7716 | S_nCCTT7716 | 660 |  | 12470 | MV | 2 | TRUE
GSO_119 | br_0119_21 | recloser_1968_21 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_0119_21 | S_nSSEE9_12.47 | S_nSSEE9_12.47_A_S_nCCTT9936 |  |  |  | MV | 1 | FALSE
GSO_119 | br_0119_21 | line_132380_21 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_1968_21 | S_nSSEE9_12.47_A_S_nCCTT9936 | S_nCCTT9936 | 660 |  | 12470 | MV | 2 | TRUE
GSO_122 | br_02_22 | recloser_186_22 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_02_22 | S_nSSEE0_12.47 | S_nSSEE0_12.47_A_S_nCCTT45 |  |  |  | MV | 1 | FALSE
GSO_122 | br_02_22 | line_5852_22 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_186_22 | S_nSSEE0_12.47_A_S_nCCTT45 | S_nCCTT45 | 660 |  | 12470 | MV | 2 | TRUE
GSO_123 | br_03_22 | recloser_189_22 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_03_22 | S_nSSEE0_12.47 | S_nSSEE0_12.47_A_S_nCCTT521 |  |  |  | MV | 1 | FALSE
GSO_123 | br_03_22 | line_6019_22 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_189_22 | S_nSSEE0_12.47_A_S_nCCTT521 | S_nCCTT521 | 660 |  | 12470 | MV | 2 | TRUE
GSO_124 | br_04_22 | recloser_198_22 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_04_22 | S_nSSEE0_12.47 | S_nSSEE0_12.47_A_S_nCCTT913 |  |  |  | MV | 1 | FALSE
GSO_124 | br_04_22 | line_6716_22 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_198_22 | S_nSSEE0_12.47_A_S_nCCTT913 | S_nCCTT913 | 660 |  | 12470 | MV | 2 | TRUE
GSO_126 | br_06_22 | recloser_194_22 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_06_22 | S_nSSEE1_12.47 | S_nSSEE1_12.47_A_S_nCCTT691 |  |  |  | MV | 1 | FALSE
GSO_126 | br_06_22 | line_6387_22 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_194_22 | S_nSSEE1_12.47_A_S_nCCTT691 | S_nCCTT691 | 660 |  | 12470 | MV | 2 | TRUE
GSO_127 | br_07_22 | recloser_204_22 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_07_22 | S_nSSEE1_12.47 | S_nSSEE1_12.47_A_UCMV43 |  |  |  | MV | 1 | FALSE
GSO_127 | br_07_22 | line_6871_22 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_204_22 | S_nSSEE1_12.47_A_UCMV43 | UCMV43 | 660 |  | 12470 | MV | 2 | TRUE
GSO_128 | br_08_22 | recloser_205_22 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_08_22 | S_nSSEE1_12.47 | S_nSSEE1_12.47_A_UCMV51 |  |  |  | MV | 1 | FALSE
GSO_128 | br_08_22 | line_6872_22 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_205_22 | S_nSSEE1_12.47_A_UCMV51 | UCMV51 | 660 |  | 12470 | MV | 2 | TRUE
GSO_129 | br_09_22 | recloser_152_22 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_09_22 | S_nSSEE2_12.47 | S_nSSEE2_12.47_A_S_nCCTT1012 |  |  |  | MV | 1 | FALSE
GSO_129 | br_09_22 | line_3574_22 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_152_22 | S_nSSEE2_12.47_A_S_nCCTT1012 | S_nCCTT1012 | 660 |  | 12470 | MV | 2 | TRUE
GSO_131 | br_011_22 | recloser_167_22 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_011_22 | S_nSSEE2_12.47 | S_nSSEE2_12.47_A_S_nCCTT1334 |  |  |  | MV | 1 | FALSE
GSO_131 | br_011_22 | line_4538_22 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_167_22 | S_nSSEE2_12.47_A_S_nCCTT1334 | S_nCCTT1334 | 660 |  | 12470 | MV | 2 | TRUE
GSO_132 | br_012_22 | recloser_173_22 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_012_22 | S_nSSEE2_12.47 | S_nSSEE2_12.47_A_S_nCCTT1508 |  |  |  | MV | 1 | FALSE
GSO_132 | br_012_22 | line_4993_22 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_173_22 | S_nSSEE2_12.47_A_S_nCCTT1508 | S_nCCTT1508 | 660 |  | 12470 | MV | 2 | TRUE
GSO_136 | br_016_22 | recloser_172_22 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_016_22 | S_nSSEE3_12.47 | S_nCCTT1502 |  |  |  | MV | 1 | FALSE
GSO_136 | br_016_22 | fuse_88_22 | Fuse | switchable_element-Fuse | C | FALSE | FALSE | TRUE | FALSE | 1to2 | recloser_172_22 | S_nCCTT1502 | S_nCCTT1502_A_S_nCCTT1524 |  |  |  | MV | 2 | FALSE
GSO_136 | br_016_22 | line_4976_22 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_172_22 | S_nCCTT1502 | S_nCCTT1546 | 660 |  | 12470 | MV | 2 | TRUE
GSO_136 | br_016_22 | tr_562_22 | Transformer | transformer | A | FALSE | FALSE | FALSE |  | 1to2 | recloser_172_22 | S_nCCTT1502 | S_nCCTT1502_BT |  | 25.0 |  | MV/LV | 2 | FALSE
GSO_136 | br_016_22 | line_2222_22 | ACLineSegment | line_segment | A | FALSE | FALSE | FALSE |  | 1to2 | tr_562_22 | S_nCCTT1502_BT | S_Dummy2657 | 350 |  | 240 | LV | 3 | TRUE
GSO_136 | br_016_22 | line_4975_22 | ACLineSegment | line_segment | C | FALSE | FALSE | FALSE |  | 1to2 | fuse_88_22 | S_nCCTT1502_A_S_nCCTT1524 | S_nCCTT1524 | 240 |  | 7200 | MV | 3 | TRUE
GSO_136 | br_016_22 | line_4978_22 | ACLineSegment | line_segment | A | FALSE | FALSE | FALSE |  | 1to2 | tr_562_22 | S_nCCTT1502_BT | UCLV9920 | 265 |  | 240 | LV | 3 | TRUE
GSO_137 | br_017_22 | recloser_178_22 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_017_22 | S_nSSEE3_12.47 | S_nSSEE3_12.47_A_S_nCCTT257 |  |  |  | MV | 1 | FALSE
GSO_137 | br_017_22 | line_5445_22 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_178_22 | S_nSSEE3_12.47_A_S_nCCTT257 | S_nCCTT257 | 660 |  | 12470 | MV | 2 | TRUE
GSO_138 | br_018_22 | recloser_180_22 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_018_22 | S_nSSEE3_12.47 | S_nSSEE3_12.47_A_S_nCCTT288 |  |  |  | MV | 1 | FALSE
GSO_138 | br_018_22 | line_5493_22 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_180_22 | S_nSSEE3_12.47_A_S_nCCTT288 | S_nCCTT288 | 660 |  | 12470 | MV | 2 | TRUE
GSO_139 | br_019_22 | recloser_190_22 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_019_22 | S_nSSEE3_12.47 | S_nSSEE3_12.47_A_S_nCCTT557 |  |  |  | MV | 1 | FALSE
GSO_139 | br_019_22 | line_6094_22 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_190_22 | S_nSSEE3_12.47_A_S_nCCTT557 | S_nCCTT557 | 660 |  | 12470 | MV | 2 | TRUE
GSO_141 | br_021_22 | recloser_168_22 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_021_22 | S_nSSEE4_12.47 | S_nSSEE4_12.47_A_S_nCCTT1344 |  |  |  | MV | 1 | FALSE
GSO_141 | br_021_22 | line_4565_22 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_168_22 | S_nSSEE4_12.47_A_S_nCCTT1344 | S_nCCTT1344 | 660 |  | 12470 | MV | 2 | TRUE
GSO_144 | br_024_22 | recloser_188_22 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_024_22 | S_nSSEE4_12.47 | S_nSSEE4_12.47_A_S_nCCTT504 |  |  |  | MV | 1 | FALSE
GSO_144 | br_024_22 | line_5978_22 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_188_22 | S_nSSEE4_12.47_A_S_nCCTT504 | S_nCCTT504 | 600 |  | 12470 | MV | 2 | TRUE
GSO_149 | br_029_22 | recloser_201_22 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_029_22 | S_nSSEE5_12.47 | S_nSSEE5_12.47_A_S_nCCTT988 |  |  |  | MV | 1 | FALSE
GSO_149 | br_029_22 | line_6853_22 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_201_22 | S_nSSEE5_12.47_A_S_nCCTT988 | S_nCCTT988 | 660 |  | 12470 | MV | 2 | TRUE
GSO_150 | br_030_22 | recloser_170_22 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_030_22 | S_nSSEE6_12.47 | S_nSSEE6_12.47_A_S_nCCTT1419 |  |  |  | MV | 1 | FALSE
GSO_150 | br_030_22 | line_4767_22 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_170_22 | S_nSSEE6_12.47_A_S_nCCTT1419 | S_nCCTT1419 | 660 |  | 12470 | MV | 2 | TRUE
GSO_151 | br_031_22 | recloser_179_22 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_031_22 | S_nSSEE6_12.47 | S_nSSEE6_12.47_A_S_nCCTT267 |  |  |  | MV | 1 | FALSE
GSO_151 | br_031_22 | line_5462_22 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_179_22 | S_nSSEE6_12.47_A_S_nCCTT267 | S_nCCTT267 | 660 |  | 12470 | MV | 2 | TRUE
GSO_152 | br_032_22 | recloser_196_22 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_032_22 | S_nSSEE6_12.47 | S_nSSEE6_12.47_A_S_nCCTT811 |  |  |  | MV | 1 | FALSE
GSO_152 | br_032_22 | line_6573_22 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_196_22 | S_nSSEE6_12.47_A_S_nCCTT811 | S_nCCTT811 | 660 |  | 12470 | MV | 2 | TRUE
GSO_153 | br_033_22 | recloser_199_22 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_033_22 | S_nSSEE6_12.47 | S_nSSEE6_12.47_A_S_nCCTT972 |  |  |  | MV | 1 | FALSE
GSO_153 | br_033_22 | line_6823_22 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_199_22 | S_nSSEE6_12.47_A_S_nCCTT972 | S_nCCTT972 | 660 |  | 12470 | MV | 2 | TRUE
GSO_161 | br_07_23 | recloser_469_23 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_07_23 | S_nSSEE1_12.47 | S_nSSEE1_12.47_A_S_nCCTT2630 |  |  |  | MV | 1 | FALSE
GSO_161 | br_07_23 | line_12976_23 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_469_23 | S_nSSEE1_12.47_A_S_nCCTT2630 | S_nCCTT2630 | 660 |  | 12470 | MV | 2 | TRUE
GSO_20 | br_027_21 | recloser_1780_21 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_027_21 | S_nSSEE12_12.47 | S_nSSEE12_12.47_A_S_nCCTT10471 |  |  |  | MV | 1 | FALSE
GSO_20 | br_027_21 | line_107423_21 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_1780_21 | S_nSSEE12_12.47_A_S_nCCTT10471 | S_nCCTT10471 | 660 |  | 12470 | MV | 2 | TRUE
GSO_24 | br_031_21 | recloser_1899_21 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_031_21 | S_nSSEE12_12.47 | S_nSSEE12_12.47_A_S_nCCTT5549 |  |  |  | MV | 1 | FALSE
GSO_24 | br_031_21 | line_124522_21 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_1899_21 | S_nSSEE12_12.47_A_S_nCCTT5549 | S_nCCTT5549 | 660 |  | 12470 | MV | 2 | TRUE
GSO_28 | br_035_21 | recloser_1840_21 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_035_21 | S_nSSEE13_12.47 | S_nSSEE13_12.47_A_S_nCCTT1498 |  |  |  | MV | 1 | FALSE
GSO_28 | br_035_21 | line_114507_21 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_1840_21 | S_nSSEE13_12.47_A_S_nCCTT1498 | S_nCCTT1498 | 660 |  | 12470 | MV | 2 | TRUE
GSO_3 | br_03_21 | recloser_1859_21 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_03_21 | S_nSSEE0_12.47 | S_nSSEE0_12.47_A_S_nCCTT2967 |  |  |  | MV | 1 | FALSE
GSO_3 | br_03_21 | line_118795_21 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_1859_21 | S_nSSEE0_12.47_A_S_nCCTT2967 | S_nCCTT2967 | 600 |  | 12470 | MV | 2 | TRUE
GSO_31 | br_038_21 | recloser_1974_21 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_038_21 | S_nSSEE13_12.47 | S_nSSEE13_12.47_A_UCMV39 |  |  |  | MV | 1 | FALSE
GSO_31 | br_038_21 | line_132463_21 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_1974_21 | S_nSSEE13_12.47_A_UCMV39 | UCMV39 | 660 |  | 12470 | MV | 2 | TRUE
GSO_33 | br_040_21 | recloser_1813_21 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_040_21 | S_nSSEE14_12.47 | S_nSSEE14_12.47_A_S_nCCTT11669 |  |  |  | MV | 1 | FALSE
GSO_33 | br_040_21 | line_111181_21 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_1813_21 | S_nSSEE14_12.47_A_S_nCCTT11669 | S_nCCTT11669 | 660 |  | 12470 | MV | 2 | TRUE
GSO_38 | br_045_21 | recloser_1787_21 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_045_21 | S_nSSEE15_12.47 | S_nSSEE15_12.47_A_S_nCCTT1062 |  |  |  | MV | 1 | FALSE
GSO_38 | br_045_21 | line_107900_21 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_1787_21 | S_nSSEE15_12.47_A_S_nCCTT1062 | S_nCCTT1062 | 660 |  | 12470 | MV | 2 | TRUE
GSO_44 | br_051_21 | recloser_1785_21 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_051_21 | S_nSSEE16_12.47 | S_nSSEE16_12.47_A_S_nCCTT10604 |  |  |  | MV | 1 | FALSE
GSO_44 | br_051_21 | line_107855_21 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_1785_21 | S_nSSEE16_12.47_A_S_nCCTT10604 | S_nCCTT10604 | 600 |  | 12470 | MV | 2 | TRUE
GSO_47 | br_054_21 | recloser_1819_21 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_054_21 | S_nSSEE16_12.47 | S_nSSEE16_12.47_A_S_nCCTT11861 |  |  |  | MV | 1 | FALSE
GSO_47 | br_054_21 | line_111700_21 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_1819_21 | S_nSSEE16_12.47_A_S_nCCTT11861 | S_nCCTT11861 | 660 |  | 12470 | MV | 2 | TRUE
GSO_49 | br_056_21 | recloser_1832_21 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_056_21 | S_nSSEE16_12.47 | S_nSSEE16_12.47_A_S_nCCTT12332 |  |  |  | MV | 1 | FALSE
GSO_49 | br_056_21 | line_112897_21 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_1832_21 | S_nSSEE16_12.47_A_S_nCCTT12332 | S_nCCTT12332 | 660 |  | 12470 | MV | 2 | TRUE
GSO_50 | br_057_21 | recloser_1847_21 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_057_21 | S_nSSEE16_12.47 | S_nSSEE16_12.47_A_S_nCCTT2007 |  |  |  | MV | 1 | FALSE
GSO_50 | br_057_21 | line_116016_21 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_1847_21 | S_nSSEE16_12.47_A_S_nCCTT2007 | S_nCCTT2007 | 600 |  | 12470 | MV | 2 | TRUE
GSO_55 | br_062_21 | recloser_1928_21 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_062_21 | S_nSSEE17_12.47 | S_nSSEE17_12.47_A_S_nCCTT7620 |  |  |  | MV | 1 | FALSE
GSO_55 | br_062_21 | line_128388_21 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_1928_21 | S_nSSEE17_12.47_A_S_nCCTT7620 | S_nCCTT7620 | 600 |  | 12470 | MV | 2 | TRUE
GSO_70 | br_070_21 | recloser_1963_21 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_070_21 | S_nSSEE2_12.47 | S_nSSEE2_12.47_A_S_nCCTT9608 |  |  |  | MV | 1 | FALSE
GSO_70 | br_070_21 | line_131920_21 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_1963_21 | S_nSSEE2_12.47_A_S_nCCTT9608 | S_nCCTT9608 | 660 |  | 12470 | MV | 2 | TRUE
GSO_73 | br_073_21 | recloser_1941_21 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_073_21 | S_nSSEE3_12.47 | S_nSSEE3_12.47_A_S_nCCTT8151 |  |  |  | MV | 1 | FALSE
GSO_73 | br_073_21 | line_129349_21 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_1941_21 | S_nSSEE3_12.47_A_S_nCCTT8151 | S_nCCTT8151 | 600 |  | 12470 | MV | 2 | TRUE
GSO_76 | br_076_21 | recloser_1851_21 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_076_21 | S_nSSEE4_12.47 | S_nSSEE4_12.47_A_S_nCCTT2321 |  |  |  | MV | 1 | FALSE
GSO_76 | br_076_21 | line_116886_21 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_1851_21 | S_nSSEE4_12.47_A_S_nCCTT2321 | S_nCCTT2321 | 600 |  | 12470 | MV | 2 | TRUE
GSO_78 | br_078_21 | recloser_1871_21 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_078_21 | S_nSSEE4_12.47 | S_nSSEE4_12.47_A_S_nCCTT4102 |  |  |  | MV | 1 | FALSE
GSO_78 | br_078_21 | line_121156_21 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_1871_21 | S_nSSEE4_12.47_A_S_nCCTT4102 | S_nCCTT4102 | 600 |  | 12470 | MV | 2 | TRUE
GSO_8 | br_022_21 | recloser_1846_21 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_022_21 | S_nSSEE10_12.47 | S_nSSEE10_12.47_A_S_nCCTT1831 |  |  |  | MV | 1 | FALSE
GSO_8 | br_022_21 | line_115508_21 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_1846_21 | S_nSSEE10_12.47_A_S_nCCTT1831 | S_nCCTT1831 | 660 |  | 12470 | MV | 2 | TRUE
GSO_90 | br_090_21 | recloser_1867_21 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_090_21 | S_nSSEE5_12.47 | S_nSSEE5_12.47_A_S_nCCTT3827 |  |  |  | MV | 1 | FALSE
GSO_90 | br_090_21 | line_120694_21 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_1867_21 | S_nSSEE5_12.47_A_S_nCCTT3827 | S_nCCTT3827 | 660 |  | 12470 | MV | 2 | TRUE
GSO_93 | br_093_21 | recloser_1874_21 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_093_21 | S_nSSEE5_12.47 | S_nSSEE5_12.47_A_S_nCCTT4180 |  |  |  | MV | 1 | FALSE
GSO_93 | br_093_21 | line_121299_21 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_1874_21 | S_nSSEE5_12.47_A_S_nCCTT4180 | S_nCCTT4180 | 660 |  | 12470 | MV | 2 | TRUE
GSO_94 | br_094_21 | recloser_1912_21 | Switch | switchable_element-Recloser | ABC | FALSE | FALSE | TRUE | FALSE | 1to2 | br_094_21 | S_nSSEE5_12.47 | S_nSSEE5_12.47_A_S_nCCTT6488 |  |  |  | MV | 1 | FALSE
GSO_94 | br_094_21 | line_126351_21 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_1912_21 | S_nSSEE5_12.47_A_S_nCCTT6488 | S_nCCTT6488 | 600 |  | 12470 | MV | 2 | TRUE

## Entrance_Lines
grid_id | BreakerElementID | PathElementID | ElementType | ElementCustomerType | Phases | IsProducer | IsConsumer | IsSwitchable | SwitchIsOpen | PowerFlowDirection | UpstreamElementID | Terminal1CN | Terminal2CN | RawRatingA | RawRatingKVA | RawPhaseToPhaseVoltage | RawVoltageLevel | DepthFromBreaker | IsLine | LineRatingA | PhaseToPhaseVoltageRaw | VoltageLevelRaw | LineVoltageKV | LineVoltageInterpretation | CalculatedLineKVA | CalculatedLineMVA | CalculatedLineMW
GSO_1 | br_01_21 | line_107866_21 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_1786_21 | S_nSSEE0_12.47_A_S_nCCTT10608 | S_nCCTT10608 | 600 |  | 12470 | MV | 2 | TRUE | 600 | 12470 |  | 12.47 | Raw value interpreted as volts | 12959.2041 | 12.9592 | 12.3112
GSO_102 | br_0102_21 | line_127499_21 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_1920_21 | S_nSSEE7_12.47_A_S_nCCTT7083 | S_nCCTT7083 | 660 |  | 12470 | MV | 2 | TRUE | 660 | 12470 |  | 12.47 | Raw value interpreted as volts | 14255.1246 | 14.2551 | 13.5424
GSO_106 | br_0106_21 | line_131696_21 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_1957_21 | S_nSSEE7_12.47_A_S_nCCTT9474 | S_nCCTT9474 | 660 |  | 12470 | MV | 2 | TRUE | 660 | 12470 |  | 12.47 | Raw value interpreted as volts | 14255.1246 | 14.2551 | 13.5424
GSO_107 | br_0107_21 | line_132043_21 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_1965_21 | S_nSSEE7_12.47_A_S_nCCTT9667 | S_nCCTT9667 | 660 |  | 12470 | MV | 2 | TRUE | 660 | 12470 |  | 12.47 | Raw value interpreted as volts | 14255.1246 | 14.2551 | 13.5424
GSO_113 | br_0113_21 | line_128560_21 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_1931_21 | S_nSSEE8_12.47_A_S_nCCTT7716 | S_nCCTT7716 | 660 |  | 12470 | MV | 2 | TRUE | 660 | 12470 |  | 12.47 | Raw value interpreted as volts | 14255.1246 | 14.2551 | 13.5424
GSO_119 | br_0119_21 | line_132380_21 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_1968_21 | S_nSSEE9_12.47_A_S_nCCTT9936 | S_nCCTT9936 | 660 |  | 12470 | MV | 2 | TRUE | 660 | 12470 |  | 12.47 | Raw value interpreted as volts | 14255.1246 | 14.2551 | 13.5424
GSO_122 | br_02_22 | line_5852_22 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_186_22 | S_nSSEE0_12.47_A_S_nCCTT45 | S_nCCTT45 | 660 |  | 12470 | MV | 2 | TRUE | 660 | 12470 |  | 12.47 | Raw value interpreted as volts | 14255.1246 | 14.2551 | 13.5424
GSO_123 | br_03_22 | line_6019_22 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_189_22 | S_nSSEE0_12.47_A_S_nCCTT521 | S_nCCTT521 | 660 |  | 12470 | MV | 2 | TRUE | 660 | 12470 |  | 12.47 | Raw value interpreted as volts | 14255.1246 | 14.2551 | 13.5424
GSO_124 | br_04_22 | line_6716_22 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_198_22 | S_nSSEE0_12.47_A_S_nCCTT913 | S_nCCTT913 | 660 |  | 12470 | MV | 2 | TRUE | 660 | 12470 |  | 12.47 | Raw value interpreted as volts | 14255.1246 | 14.2551 | 13.5424
GSO_126 | br_06_22 | line_6387_22 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_194_22 | S_nSSEE1_12.47_A_S_nCCTT691 | S_nCCTT691 | 660 |  | 12470 | MV | 2 | TRUE | 660 | 12470 |  | 12.47 | Raw value interpreted as volts | 14255.1246 | 14.2551 | 13.5424
GSO_127 | br_07_22 | line_6871_22 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_204_22 | S_nSSEE1_12.47_A_UCMV43 | UCMV43 | 660 |  | 12470 | MV | 2 | TRUE | 660 | 12470 |  | 12.47 | Raw value interpreted as volts | 14255.1246 | 14.2551 | 13.5424
GSO_128 | br_08_22 | line_6872_22 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_205_22 | S_nSSEE1_12.47_A_UCMV51 | UCMV51 | 660 |  | 12470 | MV | 2 | TRUE | 660 | 12470 |  | 12.47 | Raw value interpreted as volts | 14255.1246 | 14.2551 | 13.5424
GSO_129 | br_09_22 | line_3574_22 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_152_22 | S_nSSEE2_12.47_A_S_nCCTT1012 | S_nCCTT1012 | 660 |  | 12470 | MV | 2 | TRUE | 660 | 12470 |  | 12.47 | Raw value interpreted as volts | 14255.1246 | 14.2551 | 13.5424
GSO_131 | br_011_22 | line_4538_22 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_167_22 | S_nSSEE2_12.47_A_S_nCCTT1334 | S_nCCTT1334 | 660 |  | 12470 | MV | 2 | TRUE | 660 | 12470 |  | 12.47 | Raw value interpreted as volts | 14255.1246 | 14.2551 | 13.5424
GSO_132 | br_012_22 | line_4993_22 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_173_22 | S_nSSEE2_12.47_A_S_nCCTT1508 | S_nCCTT1508 | 660 |  | 12470 | MV | 2 | TRUE | 660 | 12470 |  | 12.47 | Raw value interpreted as volts | 14255.1246 | 14.2551 | 13.5424
GSO_136 | br_016_22 | line_4976_22 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_172_22 | S_nCCTT1502 | S_nCCTT1546 | 660 |  | 12470 | MV | 2 | TRUE | 660 | 12470 |  | 12.47 | Raw value interpreted as volts | 14255.1246 | 14.2551 | 13.5424
GSO_137 | br_017_22 | line_5445_22 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_178_22 | S_nSSEE3_12.47_A_S_nCCTT257 | S_nCCTT257 | 660 |  | 12470 | MV | 2 | TRUE | 660 | 12470 |  | 12.47 | Raw value interpreted as volts | 14255.1246 | 14.2551 | 13.5424
GSO_138 | br_018_22 | line_5493_22 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_180_22 | S_nSSEE3_12.47_A_S_nCCTT288 | S_nCCTT288 | 660 |  | 12470 | MV | 2 | TRUE | 660 | 12470 |  | 12.47 | Raw value interpreted as volts | 14255.1246 | 14.2551 | 13.5424
GSO_139 | br_019_22 | line_6094_22 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_190_22 | S_nSSEE3_12.47_A_S_nCCTT557 | S_nCCTT557 | 660 |  | 12470 | MV | 2 | TRUE | 660 | 12470 |  | 12.47 | Raw value interpreted as volts | 14255.1246 | 14.2551 | 13.5424
GSO_141 | br_021_22 | line_4565_22 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_168_22 | S_nSSEE4_12.47_A_S_nCCTT1344 | S_nCCTT1344 | 660 |  | 12470 | MV | 2 | TRUE | 660 | 12470 |  | 12.47 | Raw value interpreted as volts | 14255.1246 | 14.2551 | 13.5424
GSO_144 | br_024_22 | line_5978_22 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_188_22 | S_nSSEE4_12.47_A_S_nCCTT504 | S_nCCTT504 | 600 |  | 12470 | MV | 2 | TRUE | 600 | 12470 |  | 12.47 | Raw value interpreted as volts | 12959.2041 | 12.9592 | 12.3112
GSO_149 | br_029_22 | line_6853_22 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_201_22 | S_nSSEE5_12.47_A_S_nCCTT988 | S_nCCTT988 | 660 |  | 12470 | MV | 2 | TRUE | 660 | 12470 |  | 12.47 | Raw value interpreted as volts | 14255.1246 | 14.2551 | 13.5424
GSO_150 | br_030_22 | line_4767_22 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_170_22 | S_nSSEE6_12.47_A_S_nCCTT1419 | S_nCCTT1419 | 660 |  | 12470 | MV | 2 | TRUE | 660 | 12470 |  | 12.47 | Raw value interpreted as volts | 14255.1246 | 14.2551 | 13.5424
GSO_151 | br_031_22 | line_5462_22 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_179_22 | S_nSSEE6_12.47_A_S_nCCTT267 | S_nCCTT267 | 660 |  | 12470 | MV | 2 | TRUE | 660 | 12470 |  | 12.47 | Raw value interpreted as volts | 14255.1246 | 14.2551 | 13.5424
GSO_152 | br_032_22 | line_6573_22 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_196_22 | S_nSSEE6_12.47_A_S_nCCTT811 | S_nCCTT811 | 660 |  | 12470 | MV | 2 | TRUE | 660 | 12470 |  | 12.47 | Raw value interpreted as volts | 14255.1246 | 14.2551 | 13.5424
GSO_153 | br_033_22 | line_6823_22 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_199_22 | S_nSSEE6_12.47_A_S_nCCTT972 | S_nCCTT972 | 660 |  | 12470 | MV | 2 | TRUE | 660 | 12470 |  | 12.47 | Raw value interpreted as volts | 14255.1246 | 14.2551 | 13.5424
GSO_161 | br_07_23 | line_12976_23 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_469_23 | S_nSSEE1_12.47_A_S_nCCTT2630 | S_nCCTT2630 | 660 |  | 12470 | MV | 2 | TRUE | 660 | 12470 |  | 12.47 | Raw value interpreted as volts | 14255.1246 | 14.2551 | 13.5424
GSO_20 | br_027_21 | line_107423_21 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_1780_21 | S_nSSEE12_12.47_A_S_nCCTT10471 | S_nCCTT10471 | 660 |  | 12470 | MV | 2 | TRUE | 660 | 12470 |  | 12.47 | Raw value interpreted as volts | 14255.1246 | 14.2551 | 13.5424
GSO_24 | br_031_21 | line_124522_21 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_1899_21 | S_nSSEE12_12.47_A_S_nCCTT5549 | S_nCCTT5549 | 660 |  | 12470 | MV | 2 | TRUE | 660 | 12470 |  | 12.47 | Raw value interpreted as volts | 14255.1246 | 14.2551 | 13.5424
GSO_28 | br_035_21 | line_114507_21 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_1840_21 | S_nSSEE13_12.47_A_S_nCCTT1498 | S_nCCTT1498 | 660 |  | 12470 | MV | 2 | TRUE | 660 | 12470 |  | 12.47 | Raw value interpreted as volts | 14255.1246 | 14.2551 | 13.5424
GSO_3 | br_03_21 | line_118795_21 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_1859_21 | S_nSSEE0_12.47_A_S_nCCTT2967 | S_nCCTT2967 | 600 |  | 12470 | MV | 2 | TRUE | 600 | 12470 |  | 12.47 | Raw value interpreted as volts | 12959.2041 | 12.9592 | 12.3112
GSO_31 | br_038_21 | line_132463_21 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_1974_21 | S_nSSEE13_12.47_A_UCMV39 | UCMV39 | 660 |  | 12470 | MV | 2 | TRUE | 660 | 12470 |  | 12.47 | Raw value interpreted as volts | 14255.1246 | 14.2551 | 13.5424
GSO_33 | br_040_21 | line_111181_21 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_1813_21 | S_nSSEE14_12.47_A_S_nCCTT11669 | S_nCCTT11669 | 660 |  | 12470 | MV | 2 | TRUE | 660 | 12470 |  | 12.47 | Raw value interpreted as volts | 14255.1246 | 14.2551 | 13.5424
GSO_38 | br_045_21 | line_107900_21 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_1787_21 | S_nSSEE15_12.47_A_S_nCCTT1062 | S_nCCTT1062 | 660 |  | 12470 | MV | 2 | TRUE | 660 | 12470 |  | 12.47 | Raw value interpreted as volts | 14255.1246 | 14.2551 | 13.5424
GSO_44 | br_051_21 | line_107855_21 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_1785_21 | S_nSSEE16_12.47_A_S_nCCTT10604 | S_nCCTT10604 | 600 |  | 12470 | MV | 2 | TRUE | 600 | 12470 |  | 12.47 | Raw value interpreted as volts | 12959.2041 | 12.9592 | 12.3112
GSO_47 | br_054_21 | line_111700_21 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_1819_21 | S_nSSEE16_12.47_A_S_nCCTT11861 | S_nCCTT11861 | 660 |  | 12470 | MV | 2 | TRUE | 660 | 12470 |  | 12.47 | Raw value interpreted as volts | 14255.1246 | 14.2551 | 13.5424
GSO_49 | br_056_21 | line_112897_21 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_1832_21 | S_nSSEE16_12.47_A_S_nCCTT12332 | S_nCCTT12332 | 660 |  | 12470 | MV | 2 | TRUE | 660 | 12470 |  | 12.47 | Raw value interpreted as volts | 14255.1246 | 14.2551 | 13.5424
GSO_50 | br_057_21 | line_116016_21 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_1847_21 | S_nSSEE16_12.47_A_S_nCCTT2007 | S_nCCTT2007 | 600 |  | 12470 | MV | 2 | TRUE | 600 | 12470 |  | 12.47 | Raw value interpreted as volts | 12959.2041 | 12.9592 | 12.3112
GSO_55 | br_062_21 | line_128388_21 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_1928_21 | S_nSSEE17_12.47_A_S_nCCTT7620 | S_nCCTT7620 | 600 |  | 12470 | MV | 2 | TRUE | 600 | 12470 |  | 12.47 | Raw value interpreted as volts | 12959.2041 | 12.9592 | 12.3112
GSO_70 | br_070_21 | line_131920_21 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_1963_21 | S_nSSEE2_12.47_A_S_nCCTT9608 | S_nCCTT9608 | 660 |  | 12470 | MV | 2 | TRUE | 660 | 12470 |  | 12.47 | Raw value interpreted as volts | 14255.1246 | 14.2551 | 13.5424
GSO_73 | br_073_21 | line_129349_21 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_1941_21 | S_nSSEE3_12.47_A_S_nCCTT8151 | S_nCCTT8151 | 600 |  | 12470 | MV | 2 | TRUE | 600 | 12470 |  | 12.47 | Raw value interpreted as volts | 12959.2041 | 12.9592 | 12.3112
GSO_76 | br_076_21 | line_116886_21 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_1851_21 | S_nSSEE4_12.47_A_S_nCCTT2321 | S_nCCTT2321 | 600 |  | 12470 | MV | 2 | TRUE | 600 | 12470 |  | 12.47 | Raw value interpreted as volts | 12959.2041 | 12.9592 | 12.3112
GSO_78 | br_078_21 | line_121156_21 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_1871_21 | S_nSSEE4_12.47_A_S_nCCTT4102 | S_nCCTT4102 | 600 |  | 12470 | MV | 2 | TRUE | 600 | 12470 |  | 12.47 | Raw value interpreted as volts | 12959.2041 | 12.9592 | 12.3112
GSO_8 | br_022_21 | line_115508_21 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_1846_21 | S_nSSEE10_12.47_A_S_nCCTT1831 | S_nCCTT1831 | 660 |  | 12470 | MV | 2 | TRUE | 660 | 12470 |  | 12.47 | Raw value interpreted as volts | 14255.1246 | 14.2551 | 13.5424
GSO_90 | br_090_21 | line_120694_21 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_1867_21 | S_nSSEE5_12.47_A_S_nCCTT3827 | S_nCCTT3827 | 660 |  | 12470 | MV | 2 | TRUE | 660 | 12470 |  | 12.47 | Raw value interpreted as volts | 14255.1246 | 14.2551 | 13.5424
GSO_93 | br_093_21 | line_121299_21 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_1874_21 | S_nSSEE5_12.47_A_S_nCCTT4180 | S_nCCTT4180 | 660 |  | 12470 | MV | 2 | TRUE | 660 | 12470 |  | 12.47 | Raw value interpreted as volts | 14255.1246 | 14.2551 | 13.5424
GSO_94 | br_094_21 | line_126351_21 | ACLineSegment | line_segment | ABC | FALSE | FALSE | FALSE |  | 1to2 | recloser_1912_21 | S_nSSEE5_12.47_A_S_nCCTT6488 | S_nCCTT6488 | 600 |  | 12470 | MV | 2 | TRUE | 600 | 12470 |  | 12.47 | Raw value interpreted as volts | 12959.2041 | 12.9592 | 12.3112

## Entrance_Line_Summary
grid_id | EntranceLineCount | EntranceLineIDs | EntranceLineSearchDepth | EntranceLinesWithUsableCapacity | MinimumEntranceLineMVA | MaximumEntranceLineMVA | SumEntranceLineMVA | MinimumEntranceLineMW | MaximumEntranceLineMW | SumEntranceLineMW | PrimaryEntranceLineID | PrimaryEntranceLineRatingA | PrimaryEntranceLineVoltageKV | PrimaryEntranceLineMVA | PrimaryEntranceLineMW
GSO_1 | 1 | line_107866_21 | 2 | 1 | 12.9592 | 12.9592 | 12.9592 | 12.3112 | 12.3112 | 12.3112 | line_107866_21 | 600 | 12.47 | 12.9592 | 12.3112
GSO_102 | 1 | line_127499_21 | 2 | 1 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | line_127499_21 | 660 | 12.47 | 14.2551 | 13.5424
GSO_106 | 1 | line_131696_21 | 2 | 1 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | line_131696_21 | 660 | 12.47 | 14.2551 | 13.5424
GSO_107 | 1 | line_132043_21 | 2 | 1 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | line_132043_21 | 660 | 12.47 | 14.2551 | 13.5424
GSO_113 | 1 | line_128560_21 | 2 | 1 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | line_128560_21 | 660 | 12.47 | 14.2551 | 13.5424
GSO_119 | 1 | line_132380_21 | 2 | 1 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | line_132380_21 | 660 | 12.47 | 14.2551 | 13.5424
GSO_122 | 1 | line_5852_22 | 2 | 1 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | line_5852_22 | 660 | 12.47 | 14.2551 | 13.5424
GSO_123 | 1 | line_6019_22 | 2 | 1 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | line_6019_22 | 660 | 12.47 | 14.2551 | 13.5424
GSO_124 | 1 | line_6716_22 | 2 | 1 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | line_6716_22 | 660 | 12.47 | 14.2551 | 13.5424
GSO_126 | 1 | line_6387_22 | 2 | 1 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | line_6387_22 | 660 | 12.47 | 14.2551 | 13.5424
GSO_127 | 1 | line_6871_22 | 2 | 1 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | line_6871_22 | 660 | 12.47 | 14.2551 | 13.5424
GSO_128 | 1 | line_6872_22 | 2 | 1 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | line_6872_22 | 660 | 12.47 | 14.2551 | 13.5424
GSO_129 | 1 | line_3574_22 | 2 | 1 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | line_3574_22 | 660 | 12.47 | 14.2551 | 13.5424
GSO_131 | 1 | line_4538_22 | 2 | 1 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | line_4538_22 | 660 | 12.47 | 14.2551 | 13.5424
GSO_132 | 1 | line_4993_22 | 2 | 1 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | line_4993_22 | 660 | 12.47 | 14.2551 | 13.5424
GSO_136 | 1 | line_4976_22 | 2 | 1 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | line_4976_22 | 660 | 12.47 | 14.2551 | 13.5424
GSO_137 | 1 | line_5445_22 | 2 | 1 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | line_5445_22 | 660 | 12.47 | 14.2551 | 13.5424
GSO_138 | 1 | line_5493_22 | 2 | 1 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | line_5493_22 | 660 | 12.47 | 14.2551 | 13.5424
GSO_139 | 1 | line_6094_22 | 2 | 1 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | line_6094_22 | 660 | 12.47 | 14.2551 | 13.5424
GSO_141 | 1 | line_4565_22 | 2 | 1 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | line_4565_22 | 660 | 12.47 | 14.2551 | 13.5424
GSO_144 | 1 | line_5978_22 | 2 | 1 | 12.9592 | 12.9592 | 12.9592 | 12.3112 | 12.3112 | 12.3112 | line_5978_22 | 600 | 12.47 | 12.9592 | 12.3112
GSO_149 | 1 | line_6853_22 | 2 | 1 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | line_6853_22 | 660 | 12.47 | 14.2551 | 13.5424
GSO_150 | 1 | line_4767_22 | 2 | 1 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | line_4767_22 | 660 | 12.47 | 14.2551 | 13.5424
GSO_151 | 1 | line_5462_22 | 2 | 1 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | line_5462_22 | 660 | 12.47 | 14.2551 | 13.5424
GSO_152 | 1 | line_6573_22 | 2 | 1 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | line_6573_22 | 660 | 12.47 | 14.2551 | 13.5424
GSO_153 | 1 | line_6823_22 | 2 | 1 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | line_6823_22 | 660 | 12.47 | 14.2551 | 13.5424
GSO_161 | 1 | line_12976_23 | 2 | 1 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | line_12976_23 | 660 | 12.47 | 14.2551 | 13.5424
GSO_20 | 1 | line_107423_21 | 2 | 1 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | line_107423_21 | 660 | 12.47 | 14.2551 | 13.5424
GSO_24 | 1 | line_124522_21 | 2 | 1 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | line_124522_21 | 660 | 12.47 | 14.2551 | 13.5424
GSO_28 | 1 | line_114507_21 | 2 | 1 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | line_114507_21 | 660 | 12.47 | 14.2551 | 13.5424
GSO_3 | 1 | line_118795_21 | 2 | 1 | 12.9592 | 12.9592 | 12.9592 | 12.3112 | 12.3112 | 12.3112 | line_118795_21 | 600 | 12.47 | 12.9592 | 12.3112
GSO_31 | 1 | line_132463_21 | 2 | 1 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | line_132463_21 | 660 | 12.47 | 14.2551 | 13.5424
GSO_33 | 1 | line_111181_21 | 2 | 1 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | line_111181_21 | 660 | 12.47 | 14.2551 | 13.5424
GSO_38 | 1 | line_107900_21 | 2 | 1 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | line_107900_21 | 660 | 12.47 | 14.2551 | 13.5424
GSO_44 | 1 | line_107855_21 | 2 | 1 | 12.9592 | 12.9592 | 12.9592 | 12.3112 | 12.3112 | 12.3112 | line_107855_21 | 600 | 12.47 | 12.9592 | 12.3112
GSO_47 | 1 | line_111700_21 | 2 | 1 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | line_111700_21 | 660 | 12.47 | 14.2551 | 13.5424
GSO_49 | 1 | line_112897_21 | 2 | 1 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | line_112897_21 | 660 | 12.47 | 14.2551 | 13.5424
GSO_50 | 1 | line_116016_21 | 2 | 1 | 12.9592 | 12.9592 | 12.9592 | 12.3112 | 12.3112 | 12.3112 | line_116016_21 | 600 | 12.47 | 12.9592 | 12.3112
GSO_55 | 1 | line_128388_21 | 2 | 1 | 12.9592 | 12.9592 | 12.9592 | 12.3112 | 12.3112 | 12.3112 | line_128388_21 | 600 | 12.47 | 12.9592 | 12.3112
GSO_70 | 1 | line_131920_21 | 2 | 1 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | line_131920_21 | 660 | 12.47 | 14.2551 | 13.5424
GSO_73 | 1 | line_129349_21 | 2 | 1 | 12.9592 | 12.9592 | 12.9592 | 12.3112 | 12.3112 | 12.3112 | line_129349_21 | 600 | 12.47 | 12.9592 | 12.3112
GSO_76 | 1 | line_116886_21 | 2 | 1 | 12.9592 | 12.9592 | 12.9592 | 12.3112 | 12.3112 | 12.3112 | line_116886_21 | 600 | 12.47 | 12.9592 | 12.3112
GSO_78 | 1 | line_121156_21 | 2 | 1 | 12.9592 | 12.9592 | 12.9592 | 12.3112 | 12.3112 | 12.3112 | line_121156_21 | 600 | 12.47 | 12.9592 | 12.3112
GSO_8 | 1 | line_115508_21 | 2 | 1 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | line_115508_21 | 660 | 12.47 | 14.2551 | 13.5424
GSO_90 | 1 | line_120694_21 | 2 | 1 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | line_120694_21 | 660 | 12.47 | 14.2551 | 13.5424
GSO_93 | 1 | line_121299_21 | 2 | 1 | 14.2551 | 14.2551 | 14.2551 | 13.5424 | 13.5424 | 13.5424 | line_121299_21 | 660 | 12.47 | 14.2551 | 13.5424
GSO_94 | 1 | line_126351_21 | 2 | 1 | 12.9592 | 12.9592 | 12.9592 | 12.3112 | 12.3112 | 12.3112 | line_126351_21 | 600 | 12.47 | 12.9592 | 12.3112

## Methodology
Item | Explanation
Purpose | Validate the electrical entrance of each Greensboro feeder after the breaker/source audit showed that breaker rating_a and voltage_level are not populated.
Feeder breaker | The breaker remains the feeder root and feeder-level SCADA measurement point. Stored breaker rating_kva is retained as the root apparent-power rating candidate.
Entrance topology | The script follows downstream upstream_grid_element_id relationships from the breaker until it reaches the first line element(s) on each branch.
Line capacity | For each first downstream line, apparent-power capacity is calculated as sqrt(3) × nominal line-to-line kV × rating_a.
Voltage source | ph_ph_voltage is preferred. voltage_level is used only as a fallback when ph_ph_voltage is unavailable.
Voltage units | Nominal line voltages >=1000 are interpreted as volts and divided by 1000; values 100–999 are interpreted as low-voltage volts; values <=100 are interpreted as kV.
SCADA load | Full-year breaker kWh from 2024-01-01 00:00:00+00 through 2025-01-01 00:00:00+00 is converted to MW using observed interval duration.
SCADA voltage | The same breaker SCADA sources are queried for V by phase. Average, median, P05, P95, minimum, and maximum voltage are summarized.
SCADA voltage validation | Measured breaker voltage is compared with both line-to-line and phase-to-neutral interpretations of the first downstream line nominal voltage. The closest interpretation is reported.
Breaker/line check | A first downstream line or collection of entrance lines is considered plausibly supportive when the breaker MVA is no more than approximately 10.0% above available entrance-line capacity.
Provisional capacity | Breaker and line MVA are converted to screening MW with assumed power factor 0.95. Provisional results are retained even when full validation is unavailable.
Validated capacity | ValidatedEntranceCapacityMW and ValidatedEntranceHeadroomMW are populated only for feeders with High or Medium entrance-capacity confidence.
Multiple entrance lines | SumEntranceLineMVA is used only as a feeder-root screening check when multiple first lines exist. It is not assumed to be the capacity of any one downstream site/path.
Critical limitation | This remains a feeder-entrance screen. It is not final data-center hosting capacity. A specific proposed connection point must still be evaluated against every line, transformer, voltage, and load constraint on its electrical path.
Next phase | Use the validated shortlist first, then the provisional shortlist if necessary, for detailed path-specific topology reconstruction and incremental data-center load testing.