## Candidate_Summary
CandidateKey | GridID | SubstationID | CandidateLineID | CandidateNode | CandidateNodeMethod | RootNode | BaseFirmHostingMW | FeederPeakMW | FeederCycleRank | FeederIsRadial | BasePathPhysicalElementCount | BasePathLineCount | BasePathTransformerCount | BasePathSwitchingDeviceCount | SinglePointFailureCount | PathContingenciesSurvived | PathContingencySurvivalPct | MinimumTopologicalEdgeCut | EdgeDisjointPathCount | WorstSurvivingStaticBottleneckMW | WorstSurvivingConservativeScreeningMW | InternalN1ScreeningMW | InternalContingencyStatus | AllPathOutagesStructurallySurvivable | AllSurvivingAlternatePathsThermallyScreened | SourceBreakerContingencyIncluded | CrossFeederReroutingIncluded | ReliabilityRankingDataReady | HardMILPContingencyCapacityReady | MILPInterpretation | InternalReliabilityRank
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | S_nCCTT45 | CandidateNodeField | S_nSSEE0_12.47 | 13.5096 | 0.03276 | 0 | TRUE | 2 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | ALL_PATH_ELEMENT_OUTAGES_ISOLATE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Use structural contingency metrics for reliability comparison. Do not claim full utility N-1 or source-loss survivability. | 1
GSO_124¦line_6716_22 | GSO_124 | hvmv_1_22 | line_6716_22 | S_nCCTT913 | CandidateNodeField | S_nSSEE0_12.47 | 13.4085 | 0.13387 | 0 | TRUE | 2 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | ALL_PATH_ELEMENT_OUTAGES_ISOLATE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Use structural contingency metrics for reliability comparison. Do not claim full utility N-1 or source-loss survivability. | 2
GSO_123¦line_6019_22 | GSO_123 | hvmv_1_22 | line_6019_22 | S_nCCTT521 | CandidateNodeField | S_nSSEE0_12.47 | 13.1777 | 0.36464 | 0 | TRUE | 2 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | ALL_PATH_ELEMENT_OUTAGES_ISOLATE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Use structural contingency metrics for reliability comparison. Do not claim full utility N-1 or source-loss survivability. | 3
GSO_121¦line_3530_22 | GSO_121 | hvmv_1_22 | line_3530_22 | S_nCCTT0 | CandidateNodeField | S_nSSEE0_12.47 | 13.1607 | 0.38162 | 1 | FALSE | 2 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | ALL_PATH_ELEMENT_OUTAGES_ISOLATE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Use structural contingency metrics for reliability comparison. Do not claim full utility N-1 or source-loss survivability. | 4
GSO_144¦line_5978_22 | GSO_144 | hvmv_5_22 | line_5978_22 | S_nCCTT504 | CandidateNodeField | S_nSSEE4_12.47 | 11.2671 | 0.13286 | 0 | TRUE | 2 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | ALL_PATH_ELEMENT_OUTAGES_ISOLATE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Use structural contingency metrics for reliability comparison. Do not claim full utility N-1 or source-loss survivability. | 5
GSO_141¦line_4565_22 | GSO_141 | hvmv_5_22 | line_4565_22 | S_nCCTT1344 | CandidateNodeField | S_nSSEE4_12.47 | 11.02 | 0.37996 | 0 | TRUE | 2 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | ALL_PATH_ELEMENT_OUTAGES_ISOLATE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Use structural contingency metrics for reliability comparison. Do not claim full utility N-1 or source-loss survivability. | 6
GSO_145¦line_6170_22 | GSO_145 | hvmv_5_22 | line_6170_22 | S_nCCTT59 | CandidateNodeField | S_nSSEE4_12.47 | 10.6656 | 0.73442 | 1 | FALSE | 2 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | ALL_PATH_ELEMENT_OUTAGES_ISOLATE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Use structural contingency metrics for reliability comparison. Do not claim full utility N-1 or source-loss survivability. | 7
GSO_142¦line_5429_22 | GSO_142 | hvmv_5_22 | line_5429_22 | S_nCCTT245 | CandidateNodeField | S_nSSEE4_12.47 | 10.6074 | 0.79259 | 2 | FALSE | 2 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | ALL_PATH_ELEMENT_OUTAGES_ISOLATE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Use structural contingency metrics for reliability comparison. Do not claim full utility N-1 or source-loss survivability. | 8
GSO_18¦line_108323_21 | GSO_18 | hvmv_4_21 | line_108323_21 | S_nCCTT10746 | CandidateNodeField | S_nSSEE11_12.47 | 10.3769 | 2.2897 | 2 | FALSE | 2 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | ALL_PATH_ELEMENT_OUTAGES_ISOLATE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Use structural contingency metrics for reliability comparison. Do not claim full utility N-1 or source-loss survivability. | 9
GSO_127¦line_6871_22 | GSO_127 | hvmv_2_22 | line_6871_22 | UCMV43 | CandidateNodeField | S_nSSEE1_12.47 | 9.4748 | 0.025212 | 0 | TRUE | 2 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | ALL_PATH_ELEMENT_OUTAGES_ISOLATE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | Use structural contingency metrics for reliability comparison. Do not claim full utility N-1 or source-loss survivability. | 10

## Contingency_Detail
CandidateKey | GridID | SubstationID | CandidateLineID | FailedElementID | FailedElementType | FailedElementClass | FailedElementCapacityMW | PathPairIndex | ParallelPhysicalElementsOnPair | FailureIsolatesCandidate | SurvivingInternalPath | SurvivingPathNodes | StaticAlternatePathBottleneckMW | ConservativeContingencyScreeningMW | ThermalScreeningResolved | MissingRatedAlternatePathElements | Interpretation
GSO_121¦line_3530_22 | GSO_121 | hvmv_1_22 | line_3530_22 | recloser_151_22 | Switch | Switch |  | 0 | 1 | TRUE | FALSE |  | 0 | 0 | TRUE |  | Single physical element outage isolates the candidate from the modeled feeder root.
GSO_121¦line_3530_22 | GSO_121 | hvmv_1_22 | line_3530_22 | line_3530_22 | ACLineSegment | Line | 13.5424 | 1 | 1 | TRUE | FALSE |  | 0 | 0 | TRUE |  | Single physical element outage isolates the candidate from the modeled feeder root.
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | recloser_186_22 | Switch | Switch |  | 0 | 1 | TRUE | FALSE |  | 0 | 0 | TRUE |  | Single physical element outage isolates the candidate from the modeled feeder root.
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | line_5852_22 | ACLineSegment | Line | 13.5424 | 1 | 1 | TRUE | FALSE |  | 0 | 0 | TRUE |  | Single physical element outage isolates the candidate from the modeled feeder root.
GSO_123¦line_6019_22 | GSO_123 | hvmv_1_22 | line_6019_22 | recloser_189_22 | Switch | Switch |  | 0 | 1 | TRUE | FALSE |  | 0 | 0 | TRUE |  | Single physical element outage isolates the candidate from the modeled feeder root.
GSO_123¦line_6019_22 | GSO_123 | hvmv_1_22 | line_6019_22 | line_6019_22 | ACLineSegment | Line | 13.5424 | 1 | 1 | TRUE | FALSE |  | 0 | 0 | TRUE |  | Single physical element outage isolates the candidate from the modeled feeder root.
GSO_124¦line_6716_22 | GSO_124 | hvmv_1_22 | line_6716_22 | recloser_198_22 | Switch | Switch |  | 0 | 1 | TRUE | FALSE |  | 0 | 0 | TRUE |  | Single physical element outage isolates the candidate from the modeled feeder root.
GSO_124¦line_6716_22 | GSO_124 | hvmv_1_22 | line_6716_22 | line_6716_22 | ACLineSegment | Line | 13.5424 | 1 | 1 | TRUE | FALSE |  | 0 | 0 | TRUE |  | Single physical element outage isolates the candidate from the modeled feeder root.
GSO_127¦line_6871_22 | GSO_127 | hvmv_2_22 | line_6871_22 | recloser_204_22 | Switch | Switch |  | 0 | 1 | TRUE | FALSE |  | 0 | 0 | TRUE |  | Single physical element outage isolates the candidate from the modeled feeder root.
GSO_127¦line_6871_22 | GSO_127 | hvmv_2_22 | line_6871_22 | line_6871_22 | ACLineSegment | Line | 13.5424 | 1 | 1 | TRUE | FALSE |  | 0 | 0 | TRUE |  | Single physical element outage isolates the candidate from the modeled feeder root.
GSO_141¦line_4565_22 | GSO_141 | hvmv_5_22 | line_4565_22 | recloser_168_22 | Switch | Switch |  | 0 | 1 | TRUE | FALSE |  | 0 | 0 | TRUE |  | Single physical element outage isolates the candidate from the modeled feeder root.
GSO_141¦line_4565_22 | GSO_141 | hvmv_5_22 | line_4565_22 | line_4565_22 | ACLineSegment | Line | 13.5424 | 1 | 1 | TRUE | FALSE |  | 0 | 0 | TRUE |  | Single physical element outage isolates the candidate from the modeled feeder root.
GSO_142¦line_5429_22 | GSO_142 | hvmv_5_22 | line_5429_22 | recloser_177_22 | Switch | Switch |  | 0 | 1 | TRUE | FALSE |  | 0 | 0 | TRUE |  | Single physical element outage isolates the candidate from the modeled feeder root.
GSO_142¦line_5429_22 | GSO_142 | hvmv_5_22 | line_5429_22 | line_5429_22 | ACLineSegment | Line | 13.5424 | 1 | 1 | TRUE | FALSE |  | 0 | 0 | TRUE |  | Single physical element outage isolates the candidate from the modeled feeder root.
GSO_144¦line_5978_22 | GSO_144 | hvmv_5_22 | line_5978_22 | recloser_188_22 | Switch | Switch |  | 0 | 1 | TRUE | FALSE |  | 0 | 0 | TRUE |  | Single physical element outage isolates the candidate from the modeled feeder root.
GSO_144¦line_5978_22 | GSO_144 | hvmv_5_22 | line_5978_22 | line_5978_22 | ACLineSegment | Line | 12.3112 | 1 | 1 | TRUE | FALSE |  | 0 | 0 | TRUE |  | Single physical element outage isolates the candidate from the modeled feeder root.
GSO_145¦line_6170_22 | GSO_145 | hvmv_5_22 | line_6170_22 | recloser_192_22 | Switch | Switch |  | 0 | 1 | TRUE | FALSE |  | 0 | 0 | TRUE |  | Single physical element outage isolates the candidate from the modeled feeder root.
GSO_145¦line_6170_22 | GSO_145 | hvmv_5_22 | line_6170_22 | line_6170_22 | ACLineSegment | Line | 13.5424 | 1 | 1 | TRUE | FALSE |  | 0 | 0 | TRUE |  | Single physical element outage isolates the candidate from the modeled feeder root.
GSO_18¦line_108323_21 | GSO_18 | hvmv_4_21 | line_108323_21 | recloser_1790_21 | Switch | Switch |  | 0 | 1 | TRUE | FALSE |  | 0 | 0 | TRUE |  | Single physical element outage isolates the candidate from the modeled feeder root.
GSO_18¦line_108323_21 | GSO_18 | hvmv_4_21 | line_108323_21 | line_108323_21 | ACLineSegment | Line | 13.5424 | 1 | 1 | TRUE | FALSE |  | 0 | 0 | TRUE |  | Single physical element outage isolates the candidate from the modeled feeder root.

## Normal_Path_Elements
CandidateKey | GridID | SubstationID | CandidateLineID | PathPairIndex | FromNode | ToNode | ElementID | ElementType | ElementClass | CapacityMW | RatingA | VoltageKV | RatingKVA | CapacityMethod | ParallelPhysicalElementsOnPair | AllPhysicalElementIDsOnPair | FailureIsolatesCandidate
GSO_121¦line_3530_22 | GSO_121 | hvmv_1_22 | line_3530_22 | 0 | S_nSSEE0_12.47 | S_nSSEE0_12.47_A_S_nCCTT0 | recloser_151_22 | Switch | Switch |  |  |  |  | ConnectivityOnly | 1 | recloser_151_22 | TRUE
GSO_121¦line_3530_22 | GSO_121 | hvmv_1_22 | line_3530_22 | 1 | S_nSSEE0_12.47_A_S_nCCTT0 | S_nCCTT0 | line_3530_22 | ACLineSegment | Line | 13.5424 | 660 | 12.47 |  | Line_CurrentVoltagePF | 1 | line_3530_22 | TRUE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 0 | S_nSSEE0_12.47 | S_nSSEE0_12.47_A_S_nCCTT45 | recloser_186_22 | Switch | Switch |  |  |  |  | ConnectivityOnly | 1 | recloser_186_22 | TRUE
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 1 | S_nSSEE0_12.47_A_S_nCCTT45 | S_nCCTT45 | line_5852_22 | ACLineSegment | Line | 13.5424 | 660 | 12.47 |  | Line_CurrentVoltagePF | 1 | line_5852_22 | TRUE
GSO_123¦line_6019_22 | GSO_123 | hvmv_1_22 | line_6019_22 | 0 | S_nSSEE0_12.47 | S_nSSEE0_12.47_A_S_nCCTT521 | recloser_189_22 | Switch | Switch |  |  |  |  | ConnectivityOnly | 1 | recloser_189_22 | TRUE
GSO_123¦line_6019_22 | GSO_123 | hvmv_1_22 | line_6019_22 | 1 | S_nSSEE0_12.47_A_S_nCCTT521 | S_nCCTT521 | line_6019_22 | ACLineSegment | Line | 13.5424 | 660 | 12.47 |  | Line_CurrentVoltagePF | 1 | line_6019_22 | TRUE
GSO_124¦line_6716_22 | GSO_124 | hvmv_1_22 | line_6716_22 | 0 | S_nSSEE0_12.47 | S_nSSEE0_12.47_A_S_nCCTT913 | recloser_198_22 | Switch | Switch |  |  |  |  | ConnectivityOnly | 1 | recloser_198_22 | TRUE
GSO_124¦line_6716_22 | GSO_124 | hvmv_1_22 | line_6716_22 | 1 | S_nSSEE0_12.47_A_S_nCCTT913 | S_nCCTT913 | line_6716_22 | ACLineSegment | Line | 13.5424 | 660 | 12.47 |  | Line_CurrentVoltagePF | 1 | line_6716_22 | TRUE
GSO_127¦line_6871_22 | GSO_127 | hvmv_2_22 | line_6871_22 | 0 | S_nSSEE1_12.47 | S_nSSEE1_12.47_A_UCMV43 | recloser_204_22 | Switch | Switch |  |  |  |  | ConnectivityOnly | 1 | recloser_204_22 | TRUE
GSO_127¦line_6871_22 | GSO_127 | hvmv_2_22 | line_6871_22 | 1 | S_nSSEE1_12.47_A_UCMV43 | UCMV43 | line_6871_22 | ACLineSegment | Line | 13.5424 | 660 | 12.47 |  | Line_CurrentVoltagePF | 1 | line_6871_22 | TRUE
GSO_141¦line_4565_22 | GSO_141 | hvmv_5_22 | line_4565_22 | 0 | S_nSSEE4_12.47 | S_nSSEE4_12.47_A_S_nCCTT1344 | recloser_168_22 | Switch | Switch |  |  |  |  | ConnectivityOnly | 1 | recloser_168_22 | TRUE
GSO_141¦line_4565_22 | GSO_141 | hvmv_5_22 | line_4565_22 | 1 | S_nSSEE4_12.47_A_S_nCCTT1344 | S_nCCTT1344 | line_4565_22 | ACLineSegment | Line | 13.5424 | 660 | 12.47 |  | Line_CurrentVoltagePF | 1 | line_4565_22 | TRUE
GSO_142¦line_5429_22 | GSO_142 | hvmv_5_22 | line_5429_22 | 0 | S_nSSEE4_12.47 | S_nSSEE4_12.47_A_S_nCCTT245 | recloser_177_22 | Switch | Switch |  |  |  |  | ConnectivityOnly | 1 | recloser_177_22 | TRUE
GSO_142¦line_5429_22 | GSO_142 | hvmv_5_22 | line_5429_22 | 1 | S_nSSEE4_12.47_A_S_nCCTT245 | S_nCCTT245 | line_5429_22 | ACLineSegment | Line | 13.5424 | 660 | 12.47 |  | Line_CurrentVoltagePF | 1 | line_5429_22 | TRUE
GSO_144¦line_5978_22 | GSO_144 | hvmv_5_22 | line_5978_22 | 0 | S_nSSEE4_12.47 | S_nSSEE4_12.47_A_S_nCCTT504 | recloser_188_22 | Switch | Switch |  |  |  |  | ConnectivityOnly | 1 | recloser_188_22 | TRUE
GSO_144¦line_5978_22 | GSO_144 | hvmv_5_22 | line_5978_22 | 1 | S_nSSEE4_12.47_A_S_nCCTT504 | S_nCCTT504 | line_5978_22 | ACLineSegment | Line | 12.3112 | 600 | 12.47 |  | Line_CurrentVoltagePF | 1 | line_5978_22 | TRUE
GSO_145¦line_6170_22 | GSO_145 | hvmv_5_22 | line_6170_22 | 0 | S_nSSEE4_12.47 | S_nSSEE4_12.47_A_S_nCCTT59 | recloser_192_22 | Switch | Switch |  |  |  |  | ConnectivityOnly | 1 | recloser_192_22 | TRUE
GSO_145¦line_6170_22 | GSO_145 | hvmv_5_22 | line_6170_22 | 1 | S_nSSEE4_12.47_A_S_nCCTT59 | S_nCCTT59 | line_6170_22 | ACLineSegment | Line | 13.5424 | 660 | 12.47 |  | Line_CurrentVoltagePF | 1 | line_6170_22 | TRUE
GSO_18¦line_108323_21 | GSO_18 | hvmv_4_21 | line_108323_21 | 0 | S_nSSEE11_12.47 | S_nSSEE11_12.47_A_S_nCCTT10746 | recloser_1790_21 | Switch | Switch |  |  |  |  | ConnectivityOnly | 1 | recloser_1790_21 | TRUE
GSO_18¦line_108323_21 | GSO_18 | hvmv_4_21 | line_108323_21 | 1 | S_nSSEE11_12.47_A_S_nCCTT10746 | S_nCCTT10746 | line_108323_21 | ACLineSegment | Line | 13.5424 | 660 | 12.47 |  | Line_CurrentVoltagePF | 1 | line_108323_21 | TRUE

## Feeder_Diagnostics
GridID | BreakerID | RootNode | ActivePhysicalElements | ActiveTopologyNodes | ActiveTopologyNodePairs | CycleRank | IsRadial | SkippedOpenSwitches | SkippedMissingTerminalElements | SourceBreakerExcludedFromInternalAudit | BreakerTerminalComponentSizes
GSO_121 | br_01_22 | S_nSSEE0_12.47 | 280 | 280 | 280 | 1 | FALSE | 0 | 0 | TRUE | {'S_nSSEE0': 0, 'S_nSSEE0_12.47': 280}
GSO_122 | br_02_22 | S_nSSEE0_12.47 | 10 | 11 | 10 | 0 | TRUE | 0 | 0 | TRUE | {'S_nSSEE0': 0, 'S_nSSEE0_12.47': 11}
GSO_123 | br_03_22 | S_nSSEE0_12.47 | 182 | 183 | 182 | 0 | TRUE | 0 | 0 | TRUE | {'S_nSSEE0': 0, 'S_nSSEE0_12.47': 183}
GSO_124 | br_04_22 | S_nSSEE0_12.47 | 57 | 58 | 57 | 0 | TRUE | 0 | 0 | TRUE | {'S_nSSEE0': 0, 'S_nSSEE0_12.47': 58}
GSO_127 | br_07_22 | S_nSSEE1_12.47 | 2 | 3 | 2 | 0 | TRUE | 0 | 0 | TRUE | {'S_nSSEE1': 0, 'S_nSSEE1_12.47': 3}
GSO_141 | br_021_22 | S_nSSEE4_12.47 | 239 | 240 | 239 | 0 | TRUE | 0 | 0 | TRUE | {'S_nSSEE4': 0, 'S_nSSEE4_12.47': 240}
GSO_142 | br_022_22 | S_nSSEE4_12.47 | 564 | 563 | 564 | 2 | FALSE | 0 | 0 | TRUE | {'S_nSSEE4': 0, 'S_nSSEE4_12.47': 563}
GSO_144 | br_024_22 | S_nSSEE4_12.47 | 79 | 80 | 79 | 0 | TRUE | 0 | 0 | TRUE | {'S_nSSEE4': 0, 'S_nSSEE4_12.47': 80}
GSO_145 | br_025_22 | S_nSSEE4_12.47 | 495 | 455 | 455 | 1 | FALSE | 0 | 0 | TRUE | {'S_nSSEE4': 0, 'S_nSSEE4_12.47': 455}
GSO_18 | br_025_21 | S_nSSEE11_12.47 | 1417 | 1416 | 1417 | 2 | FALSE | 0 | 0 | TRUE | {'S_nSSEE11': 0, 'S_nSSEE11_12.47': 1416}

## Assumptions
Item | Assumption
Scope | This audit tests internal active-feeder topology between the downstream side of the source breaker and the candidate location.
Source breaker / feeder-source outage | Excluded. Surviving a feeder-source or source-breaker outage requires validated cross-feeder or alternate-source transfer, which the separate rerouting audit could not establish.
Contingencies tested | Each physical line, transformer, switch, recloser, fuse, or regulator on the normal source-to-candidate path is removed one at a time.
Open switches | Elements explicitly marked switch_is_open=True are excluded from the active topology. This audit does not assume an open device can automatically close unless it is already represented as part of the active alternate route.
Parallel elements | Physical parallel elements are retained separately for outage connectivity. Their ratings are never summed; when multiple rated elements remain on the same node pair, the lowest surviving rating is used conservatively.
Structural survival | A contingency survives structurally only when the candidate remains connected to the modeled feeder root after the failed physical element is removed.
Static alternate-path bottleneck | For a surviving route, the static bottleneck is the minimum PF-adjusted line/transformer rating on the selected widest surviving path. Connectivity-only switching devices do not create a thermal rating.
Conservative screening hosting | ConservativeContingencyScreeningMW = max(static surviving path bottleneck - full annual feeder breaker peak, 0). Subtracting the entire feeder peak from every path element is intentionally conservative.
Not AC contingency power flow | The screening MW does not model impedance-driven load redistribution, voltage, reactive power, losses, fault current, protection coordination, or switching time.
Internal N-1 screening | InternalN1ScreeningMW is zero if any tested normal-path element outage isolates the candidate. It is a feeder-topology screening floor, not a claim of utility N-1 service.
MILP use | Structural metrics are ready for site-reliability comparison. InternalN1ScreeningMW should not become a hard capacity constraint until its conservative treatment is reviewed against the audit results.
Power factor | Line and transformer ratings are converted to MW at PF=0.95, matching the thermal hosting base case.