## Scenario_Summary
CandidateKey | GridID | BaseDCMW | OutageDurationHours | PVCapacityMW | PVCapacityRatioToDC | InstalledBatteryPowerMW | InstalledBatteryMWh | Simulations | SuccessCount | FailureCount | SuccessRate | FailureRate | MeanUnservedEnergyMWh | P95UnservedEnergyMWh | P99UnservedEnergyMWh | MaximumUnservedEnergyMWh | P05MinimumSOCFraction | P50MinimumSOCFraction | BatteryMinimumSOCHitRate | PCSConstraintEncounterRate | EnergyConstraintEncounterRate | MeanEnduranceHours | P05EnduranceHours | MeanPVDirectMWh | MeanPVChargeToBatteryACMWh | MeanPVCurtailedMWh | MeanBatteryDeliveredMWh | EnergySOCFailureCount | PCSPowerFailureCount | EnergyAndPCSFailureCount | OtherFailureCount | BatteryOnlySuccessRate | BatteryOnlyMeanUnservedEnergyMWh | BatteryOnlyP99UnservedEnergyMWh | BatteryOnlyMeanEnduranceHours | SuccessRateImprovementFromPV | MeanUnservedEnergyReductionFromPVMWh | P99UnservedEnergyReductionFromPVMWh | MeanEnduranceImprovementFromPVHours
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 4 | 0 | 0 | 13.5096 | 71.1032 | 10000 | 0 | 10000 | 0% | 100% | 5.1257 | 10.3385 | 12.1842 | 14.5098 | 10% | 10% | 91.63% | 100% | 91.63% | 0 | 0 | 0 | 0 | 0 | 48.9128 | 0 | 837 | 9163 | 0 | 0% | 5.1257 | 12.1842 | 0 | 0 | 0 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 4 | 6.7548 | 0.5 | 13.5096 | 71.1032 | 10000 | 2976 | 7024 | 29.76% | 70.24% | 2.767 | 9.0675 | 11.3836 | 14.1522 | 10% | 10% | 54.97% | 69.47% | 54.97% | 1.5538 | 0 | 5.6911 | 0 | 0 | 45.5804 | 77 | 1527 | 5420 | 0 | 0% | 5.1257 | 12.1842 | 0 | 0.2976 | 2.3587 | 0.80057 | 1.5538
GSO_122¦line_5852_22 | GSO_122 | 13.5096 | 4 | 13.5096 | 1 | 13.5096 | 71.1032 | 10000 | 3271 | 6729 | 32.71% | 67.29% | 2.4532 | 8.9997 | 11.3655 | 14.0644 | 10% | 11.28% | 46.65% | 67.29% | 46.65% | 1.6411 | 0 | 11.5774 | 0.0045379 | 0 | 40.0079 | 0 | 2064 | 4665 | 0 | 0% | 5.1257 | 12.1842 | 0 | 0.3271 | 2.6725 | 0.8187 | 1.6411

## Failure_Drivers
OutageDurationHours | PVCapacityMW | FailureDriver | SimulationCount | ScenarioSimulationCount | FractionOfScenario
4 | 0 | ENERGY_AND_PCS | 9163 | 10000 | 91.63%
4 | 0 | PCS_POWER | 837 | 10000 | 8.37%
4 | 6.7548 | ENERGY_AND_PCS | 5420 | 10000 | 54.2%
4 | 6.7548 | ENERGY_SOC | 77 | 10000 | 0.77%
4 | 6.7548 | PCS_POWER | 1527 | 10000 | 15.27%
4 | 6.7548 | SUCCESS | 2976 | 10000 | 29.76%
4 | 13.5096 | ENERGY_AND_PCS | 4665 | 10000 | 46.65%
4 | 13.5096 | PCS_POWER | 2064 | 10000 | 20.64%
4 | 13.5096 | SUCCESS | 3271 | 10000 | 32.71%

## Deterministic_Design
CandidateKey | GridID | SubstationID | CandidateLineID | BaseDCMW | BatteryPowerMW | BatteryInstalledMWh
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 13.5096 | 71.1032

## Assumptions
Item | Value
Purpose | Fixed-design Monte Carlo validation. The battery is never resized inside the simulation.
Selected site | GSO_122 ¦ line_5852_22 ¦ hvmv_1_22
Fixed DC load | 13.509608 MW
Fixed BESS | 13.509608 MW / 71.103202 MWh
Design source | 100% service ¦ 4h ¦ 0.000 MW PV
Simulations per scenario | 10000
Random seed | 2026
Outage start sampling | Uniform with replacement from all complete historical 2024 starts in the PV profile.
PV treatment | Real contiguous historical PV blocks. PV serves load first, excess PV charges battery, remainder is curtailed.
Start SOC triangular | (0.75, 0.9, 0.95)
Capacity derate triangular | (0.9, 0.97, 1.0)
Charge efficiency triangular | (0.9, 0.95, 0.97)
Discharge efficiency triangular | (0.9, 0.95, 0.97)
PCS availability triangular | (0.95, 1.0, 1.0)
Critical-load factor triangular | (1.0, 1.0, 1.0)
PV-output multiplier triangular | (1.0, 1.0, 1.0)
Interpretation | Triangular ranges are scenario assumptions unless supported by measured data; they are not claimed empirical probability distributions.
Not randomized | Unresolved station capacity, feeder ties, AC voltage/reactive limits, and protection limits remain unresolved rather than being invented.