## Substation_Summary
SubstationID | ExpectedFeederCount | LoadedFeederCount | AllExpectedFeedersLoaded | CompleteIntervals | ExpectedIntervals | ProfileCoveragePct | SubstationProfileStatus | AverageMW | P95MW | P99MW | CoincidentPeakMW | PeakTimestampUTC | MinimumNetMW | PeakAbsoluteMW | AnnualEnergyMWh | LoadFactor | SumIndividualFeederPeaksMW | CoincidenceFactor | DiversityFactor | CurrentMILPCandidateFeederCount | CurrentCandidateFirmHostingSumMW_UpperBound
hvmv_13_21 | 10 | 10 | TRUE | 105348 | 105408 | 99.9431 | READY | 10.286 | 14.9733 | 17.0939 | 19.5567 | 2024-01-21 04:00 | 6.9347 | 19.5567 | 90300.8406 | 0.52596 | 19.7846 | 0.98848 | 1.0117 | 0 | 0
hvmv_2_21 | 7 | 7 | TRUE | 105348 | 105408 | 99.9431 | READY | 8.4767 | 12.9367 | 14.9719 | 17.3574 | 2024-01-21 04:00 | 5.2299 | 17.3574 | 74416.9573 | 0.48836 | 17.4341 | 0.9956 | 1.0044 | 0 | 0
hvmv_3_21 | 9 | 9 | TRUE | 105348 | 105408 | 99.9431 | READY | 8.8082 | 12.8257 | 14.656 | 16.9458 | 2024-01-21 04:00 | 5.7133 | 16.9458 | 77326.9737 | 0.51978 | 16.9729 | 0.99841 | 1.0016 | 0 | 0
hvmv_9_21 | 11 | 11 | TRUE | 105348 | 105408 | 99.9431 | READY | 8.5816 | 12.5224 | 14.3489 | 16.4919 | 2024-01-21 04:00 | 5.7352 | 16.4919 | 75338.1964 | 0.52035 | 16.7075 | 0.9871 | 1.0131 | 0 | 0
hvmv_14_21 | 11 | 11 | TRUE | 105348 | 105408 | 99.9431 | READY | 8.8538 | 11.9539 | 13.3262 | 15.0565 | 2024-01-21 04:00 | 6.6325 | 15.0565 | 77727.6052 | 0.58804 | 15.5104 | 0.97074 | 1.0301 | 0 | 0
hvmv_15_21 | 4 | 4 | TRUE | 105348 | 105408 | 99.9431 | READY | 7.3044 | 10.9602 | 12.6165 | 14.7045 | 2024-01-21 04:00 | 4.6585 | 14.7045 | 64125.2795 | 0.49674 | 14.7401 | 0.99759 | 1.0024 | 0 | 0
hvmv_7_21 | 6 | 6 | TRUE | 105348 | 105408 | 99.9431 | READY | 7.1736 | 10.3552 | 11.7978 | 13.3872 | 2024-01-18 04:00 | 4.84 | 13.3872 | 62976.9549 | 0.53585 | 13.612 | 0.98348 | 1.0168 | 0 | 0
hvmv_16_21 | 7 | 7 | TRUE | 105348 | 105408 | 99.9431 | READY | 6.5449 | 9.8309 | 11.2366 | 13.06 | 2024-01-21 04:00 | 4.1466 | 13.06 | 57458.1153 | 0.50115 | 13.0929 | 0.99749 | 1.0025 | 0 | 0
hvmv_17_21 | 7 | 7 | TRUE | 105348 | 105408 | 99.9431 | READY | 6.5755 | 9.5733 | 10.9091 | 12.4749 | 2024-01-21 04:00 | 4.4462 | 12.4749 | 57725.913 | 0.52709 | 12.6552 | 0.98575 | 1.0145 | 0 | 0
hvmv_11_21 | 7 | 7 | TRUE | 105348 | 105408 | 99.9431 | READY | 6.1902 | 8.7689 | 9.9044 | 11.5184 | 2024-01-21 04:00 | 4.337 | 11.5184 | 54343.429 | 0.53742 | 11.5205 | 0.99982 | 1.0002 | 0 | 0
hvmv_4_21 | 3 | 3 | TRUE | 105348 | 105408 | 99.9431 | READY | 5.5174 | 8.2443 | 9.463 | 10.9621 | 2024-01-18 04:00 | 3.6182 | 10.9621 | 48437.1363 | 0.50332 | 10.9889 | 0.99756 | 1.0024 | 1 | 10.3769
hvmv_8_21 | 5 | 5 | TRUE | 105348 | 105408 | 99.9431 | READY | 5.0893 | 7.7092 | 8.9189 | 10.3636 | 2024-01-21 04:00 | 3.1666 | 10.3636 | 44679.0884 | 0.49108 | 10.426 | 0.99401 | 1.006 | 0 | 0
hvmv_1_21 | 7 | 7 | TRUE | 105348 | 105408 | 99.9431 | READY | 5.3534 | 7.7049 | 8.7742 | 9.961 | 2024-01-21 04:00 | 3.6062 | 9.961 | 46997.4762 | 0.53744 | 10.1424 | 0.98211 | 1.0182 | 0 | 0
hvmv_1_23 | 4 | 4 | TRUE | 105348 | 105408 | 99.9431 | READY | 5.0485 | 7.4839 | 8.5729 | 9.8808 | 2024-01-21 04:00 | 3.2194 | 9.8808 | 44320.5321 | 0.51094 | 9.9382 | 0.99422 | 1.0058 | 0 | 0
hvmv_5_21 | 8 | 8 | TRUE | 105348 | 105408 | 99.9431 | READY | 5.2548 | 7.2995 | 8.2148 | 9.4955 | 2024-01-21 04:00 | 3.8305 | 9.4955 | 46131.9243 | 0.5534 | 9.5737 | 0.99182 | 1.0082 | 0 | 0
hvmv_12_21 | 5 | 5 | TRUE | 105348 | 105408 | 99.9431 | READY | 4.926 | 7.0139 | 7.9455 | 9.0553 | 2024-01-18 04:00 | 3.456 | 9.0553 | 43245.5894 | 0.54399 | 9.2034 | 0.98391 | 1.0164 | 0 | 0
hvmv_18_21 | 5 | 5 | TRUE | 105348 | 105408 | 99.9431 | READY | 4.7357 | 6.7366 | 7.6047 | 8.6543 | 2024-01-21 04:00 | 3.2542 | 8.6543 | 41575.0672 | 0.54721 | 8.7875 | 0.98485 | 1.0154 | 0 | 0
hvmv_2_23 | 3 | 3 | TRUE | 105348 | 105408 | 99.9431 | READY | 4.0917 | 6.0663 | 6.99 | 8.1793 | 2024-01-21 04:00 | 2.6338 | 8.1793 | 35920.8471 | 0.50025 | 8.1838 | 0.99945 | 1.0006 | 0 | 0
hvmv_10_21 | 3 | 3 | TRUE | 105348 | 105408 | 99.9431 | READY | 3.0835 | 4.6008 | 5.2788 | 6.1336 | 2024-01-21 04:00 | 2.0159 | 6.1336 | 27069.7429 | 0.50272 | 6.1575 | 0.99612 | 1.0039 | 0 | 0
hvmv_5_22 | 5 | 5 | TRUE | 105348 | 105408 | 99.9431 | READY | 2.5068 | 3.4495 | 3.8779 | 4.4648 | 2024-01-21 04:00 | 1.7795 | 4.4648 | 22007.454 | 0.56146 | 4.5806 | 0.97473 | 1.0259 | 4 | 43.5602
hvmv_3_23 | 2 | 2 | TRUE | 105348 | 105408 | 99.9431 | READY | 2.1126 | 3.1271 | 3.5791 | 4.1269 | 2024-01-18 04:00 | 1.3771 | 4.1269 | 18546.8392 | 0.51191 | 4.1765 | 0.98813 | 1.012 | 0 | 0
hvmv_6_21 | 4 | 4 | TRUE | 105348 | 105408 | 99.9431 | READY | 2.0831 | 2.9824 | 3.3695 | 3.8358 | 2024-01-21 04:00 | 1.4463 | 3.8358 | 18287.4188 | 0.54306 | 3.9485 | 0.97145 | 1.0294 | 0 | 0
hvmv_3_22 | 7 | 7 | TRUE | 105348 | 105408 | 99.9431 | READY | 1.7883 | 2.0878 | 2.2393 | 2.5225 | 2024-01-22 04:00 | 1.3788 | 2.5225 | 15699.5667 | 0.70893 | 2.6464 | 0.9532 | 1.0491 | 0 | 0
hvmv_7_22 | 5 | 5 | TRUE | 105348 | 105408 | 99.9431 | READY | 1.3279 | 1.6091 | 1.7367 | 1.9938 | 2024-01-21 04:00 | 1.0709 | 1.9938 | 11657.9606 | 0.66605 | 2.0786 | 0.95919 | 1.0425 | 0 | 0
hvmv_4_22 | 5 | 5 | TRUE | 105348 | 105408 | 99.9431 | READY | 1.1722 | 1.4087 | 1.5224 | 1.7871 | 2024-01-21 04:00 | 0.85938 | 1.7871 | 10290.8063 | 0.65592 | 1.8489 | 0.96657 | 1.0346 | 0 | 0
hvmv_6_22 | 4 | 4 | TRUE | 105348 | 105408 | 99.9431 | READY | 1.0566 | 1.3869 | 1.5285 | 1.7832 | 2024-01-21 04:00 | 0.79354 | 1.7832 | 9275.9908 | 0.59254 | 1.8561 | 0.96071 | 1.0409 | 0 | 0
hvmv_1_22 | 4 | 4 | TRUE | 105348 | 105408 | 99.9431 | READY | 0.59032 | 0.70412 | 0.75547 | 0.87823 | 2024-01-22 04:00 | 0.47406 | 0.87823 | 5182.3912 | 0.67216 | 0.9129 | 0.96202 | 1.0395 | 4 | 53.2566
hvmv_2_22 | 4 | 4 | TRUE | 105348 | 105408 | 99.9431 | READY | 0.47306 | 0.56262 | 0.60639 | 0.69532 | 2024-01-20 15:00 | 0.38132 | 0.69532 | 4152.9531 | 0.68035 | 0.74162 | 0.93756 | 1.0666 | 1 | 9.4748

## Current_Candidate_Subs
SubstationID | ExpectedFeederCount | LoadedFeederCount | AllExpectedFeedersLoaded | CompleteIntervals | ExpectedIntervals | ProfileCoveragePct | SubstationProfileStatus | AverageMW | P95MW | P99MW | CoincidentPeakMW | PeakTimestampUTC | MinimumNetMW | PeakAbsoluteMW | AnnualEnergyMWh | LoadFactor | SumIndividualFeederPeaksMW | CoincidenceFactor | DiversityFactor | CurrentMILPCandidateFeederCount | CurrentCandidateFirmHostingSumMW_UpperBound
hvmv_1_22 | 4 | 4 | TRUE | 105348 | 105408 | 99.9431 | READY | 0.59032 | 0.70412 | 0.75547 | 0.87823 | 2024-01-22 04:00 | 0.47406 | 0.87823 | 5182.3912 | 0.67216 | 0.9129 | 0.96202 | 1.0395 | 4 | 53.2566
hvmv_5_22 | 5 | 5 | TRUE | 105348 | 105408 | 99.9431 | READY | 2.5068 | 3.4495 | 3.8779 | 4.4648 | 2024-01-21 04:00 | 1.7795 | 4.4648 | 22007.454 | 0.56146 | 4.5806 | 0.97473 | 1.0259 | 4 | 43.5602
hvmv_4_21 | 3 | 3 | TRUE | 105348 | 105408 | 99.9431 | READY | 5.5174 | 8.2443 | 9.463 | 10.9621 | 2024-01-18 04:00 | 3.6182 | 10.9621 | 48437.1363 | 0.50332 | 10.9889 | 0.99756 | 1.0024 | 1 | 10.3769
hvmv_2_22 | 4 | 4 | TRUE | 105348 | 105408 | 99.9431 | READY | 0.47306 | 0.56262 | 0.60639 | 0.69532 | 2024-01-20 15:00 | 0.38132 | 0.69532 | 4152.9531 | 0.68035 | 0.74162 | 0.93756 | 1.0666 | 1 | 9.4748

## Substation_Feeder_Map
GridID | BreakerID | SubstationID | SubstationEntityFound | BreakerKWhSourceCount | FirmHostingMW | IsCurrentMILPCandidate
GSO_54 | br_061_21 | hvmv_10_21 | TRUE | 3 |  | FALSE
GSO_55 | br_062_21 | hvmv_10_21 | TRUE | 3 |  | FALSE
GSO_56 | br_063_21 | hvmv_10_21 | TRUE | 3 |  | FALSE
GSO_64 | br_064_21 | hvmv_11_21 | TRUE | 3 |  | FALSE
GSO_65 | br_065_21 | hvmv_11_21 | TRUE | 3 |  | FALSE
GSO_66 | br_066_21 | hvmv_11_21 | TRUE | 3 |  | FALSE
GSO_67 | br_067_21 | hvmv_11_21 | TRUE | 3 |  | FALSE
GSO_68 | br_068_21 | hvmv_11_21 | TRUE | 3 |  | FALSE
GSO_69 | br_069_21 | hvmv_11_21 | TRUE | 3 |  | FALSE
GSO_70 | br_070_21 | hvmv_11_21 | TRUE | 3 |  | FALSE
GSO_1 | br_01_21 | hvmv_1_21 | TRUE | 3 |  | FALSE
GSO_2 | br_02_21 | hvmv_1_21 | TRUE | 3 |  | FALSE
GSO_3 | br_03_21 | hvmv_1_21 | TRUE | 3 |  | FALSE
GSO_4 | br_04_21 | hvmv_1_21 | TRUE | 3 |  | FALSE
GSO_5 | br_05_21 | hvmv_1_21 | TRUE | 3 |  | FALSE
GSO_6 | br_06_21 | hvmv_1_21 | TRUE | 3 |  | FALSE
GSO_7 | br_07_21 | hvmv_1_21 | TRUE | 3 |  | FALSE
GSO_121 | br_01_22 | hvmv_1_22 | TRUE | 3 | 13.1607 | TRUE
GSO_122 | br_02_22 | hvmv_1_22 | TRUE | 3 | 13.5096 | TRUE
GSO_123 | br_03_22 | hvmv_1_22 | TRUE | 3 | 13.1777 | TRUE
GSO_124 | br_04_22 | hvmv_1_22 | TRUE | 3 | 13.4085 | TRUE
GSO_71 | br_071_21 | hvmv_12_21 | TRUE | 3 |  | FALSE
GSO_72 | br_072_21 | hvmv_12_21 | TRUE | 3 |  | FALSE
GSO_73 | br_073_21 | hvmv_12_21 | TRUE | 3 |  | FALSE
GSO_74 | br_074_21 | hvmv_12_21 | TRUE | 3 |  | FALSE
GSO_75 | br_075_21 | hvmv_12_21 | TRUE | 3 |  | FALSE
GSO_155 | br_01_23 | hvmv_1_23 | TRUE | 3 |  | FALSE
GSO_156 | br_02_23 | hvmv_1_23 | TRUE | 3 |  | FALSE
GSO_157 | br_03_23 | hvmv_1_23 | TRUE | 3 |  | FALSE
GSO_158 | br_04_23 | hvmv_1_23 | TRUE | 3 |  | FALSE
GSO_76 | br_076_21 | hvmv_13_21 | TRUE | 3 |  | FALSE
GSO_77 | br_077_21 | hvmv_13_21 | TRUE | 3 |  | FALSE
GSO_78 | br_078_21 | hvmv_13_21 | TRUE | 3 |  | FALSE
GSO_79 | br_079_21 | hvmv_13_21 | TRUE | 3 |  | FALSE
GSO_80 | br_080_21 | hvmv_13_21 | TRUE | 3 |  | FALSE
GSO_81 | br_081_21 | hvmv_13_21 | TRUE | 3 |  | FALSE
GSO_82 | br_082_21 | hvmv_13_21 | TRUE | 3 |  | FALSE
GSO_83 | br_083_21 | hvmv_13_21 | TRUE | 3 |  | FALSE
GSO_84 | br_084_21 | hvmv_13_21 | TRUE | 3 |  | FALSE
GSO_85 | br_085_21 | hvmv_13_21 | TRUE | 3 |  | FALSE
GSO_86 | br_086_21 | hvmv_14_21 | TRUE | 3 |  | FALSE
GSO_87 | br_087_21 | hvmv_14_21 | TRUE | 3 |  | FALSE
GSO_88 | br_088_21 | hvmv_14_21 | TRUE | 3 |  | FALSE
GSO_89 | br_089_21 | hvmv_14_21 | TRUE | 3 |  | FALSE
GSO_90 | br_090_21 | hvmv_14_21 | TRUE | 3 |  | FALSE
GSO_91 | br_091_21 | hvmv_14_21 | TRUE | 3 |  | FALSE
GSO_92 | br_092_21 | hvmv_14_21 | TRUE | 3 |  | FALSE
GSO_93 | br_093_21 | hvmv_14_21 | TRUE | 3 |  | FALSE
GSO_94 | br_094_21 | hvmv_14_21 | TRUE | 3 |  | FALSE
GSO_95 | br_095_21 | hvmv_14_21 | TRUE | 3 |  | FALSE
GSO_96 | br_096_21 | hvmv_14_21 | TRUE | 3 |  | FALSE
GSO_100 | br_097_21 | hvmv_15_21 | TRUE | 3 |  | FALSE
GSO_97 | br_098_21 | hvmv_15_21 | TRUE | 3 |  | FALSE
GSO_98 | br_099_21 | hvmv_15_21 | TRUE | 3 |  | FALSE
GSO_99 | br_0100_21 | hvmv_15_21 | TRUE | 3 |  | FALSE
GSO_101 | br_0101_21 | hvmv_16_21 | TRUE | 3 |  | FALSE
GSO_102 | br_0102_21 | hvmv_16_21 | TRUE | 3 |  | FALSE
GSO_103 | br_0103_21 | hvmv_16_21 | TRUE | 3 |  | FALSE
GSO_104 | br_0104_21 | hvmv_16_21 | TRUE | 3 |  | FALSE
GSO_105 | br_0105_21 | hvmv_16_21 | TRUE | 3 |  | FALSE
GSO_106 | br_0106_21 | hvmv_16_21 | TRUE | 3 |  | FALSE
GSO_107 | br_0107_21 | hvmv_16_21 | TRUE | 3 |  | FALSE
GSO_108 | br_0108_21 | hvmv_17_21 | TRUE | 3 |  | FALSE
GSO_109 | br_0109_21 | hvmv_17_21 | TRUE | 3 |  | FALSE
GSO_110 | br_0110_21 | hvmv_17_21 | TRUE | 3 |  | FALSE
GSO_111 | br_0111_21 | hvmv_17_21 | TRUE | 3 |  | FALSE
GSO_112 | br_0112_21 | hvmv_17_21 | TRUE | 3 |  | FALSE
GSO_113 | br_0113_21 | hvmv_17_21 | TRUE | 3 |  | FALSE
GSO_114 | br_0114_21 | hvmv_17_21 | TRUE | 3 |  | FALSE
GSO_115 | br_0115_21 | hvmv_18_21 | TRUE | 3 |  | FALSE
GSO_116 | br_0116_21 | hvmv_18_21 | TRUE | 3 |  | FALSE
GSO_117 | br_0117_21 | hvmv_18_21 | TRUE | 3 |  | FALSE
GSO_118 | br_0118_21 | hvmv_18_21 | TRUE | 3 |  | FALSE
GSO_119 | br_0119_21 | hvmv_18_21 | TRUE | 3 |  | FALSE
GSO_57 | br_08_21 | hvmv_2_21 | TRUE | 3 |  | FALSE
GSO_58 | br_09_21 | hvmv_2_21 | TRUE | 3 |  | FALSE
GSO_59 | br_010_21 | hvmv_2_21 | TRUE | 3 |  | FALSE
GSO_60 | br_011_21 | hvmv_2_21 | TRUE | 3 |  | FALSE
GSO_61 | br_012_21 | hvmv_2_21 | TRUE | 3 |  | FALSE
GSO_62 | br_013_21 | hvmv_2_21 | TRUE | 3 |  | FALSE
GSO_63 | br_014_21 | hvmv_2_21 | TRUE | 3 |  | FALSE
GSO_125 | br_05_22 | hvmv_2_22 | TRUE | 3 |  | FALSE
GSO_126 | br_06_22 | hvmv_2_22 | TRUE | 3 |  | FALSE
GSO_127 | br_07_22 | hvmv_2_22 | TRUE | 3 | 9.4748 | TRUE
GSO_128 | br_08_22 | hvmv_2_22 | TRUE | 3 |  | FALSE
GSO_159 | br_05_23 | hvmv_2_23 | TRUE | 3 |  | FALSE
GSO_160 | br_06_23 | hvmv_2_23 | TRUE | 3 |  | FALSE
GSO_161 | br_07_23 | hvmv_2_23 | TRUE | 3 |  | FALSE
GSO_10 | br_015_21 | hvmv_3_21 | TRUE | 3 |  | FALSE
GSO_11 | br_016_21 | hvmv_3_21 | TRUE | 3 |  | FALSE
GSO_12 | br_017_21 | hvmv_3_21 | TRUE | 3 |  | FALSE
GSO_13 | br_018_21 | hvmv_3_21 | TRUE | 3 |  | FALSE
GSO_14 | br_019_21 | hvmv_3_21 | TRUE | 3 |  | FALSE
GSO_15 | br_020_21 | hvmv_3_21 | TRUE | 3 |  | FALSE
GSO_16 | br_021_21 | hvmv_3_21 | TRUE | 3 |  | FALSE
GSO_8 | br_022_21 | hvmv_3_21 | TRUE | 3 |  | FALSE
GSO_9 | br_023_21 | hvmv_3_21 | TRUE | 3 |  | FALSE
GSO_129 | br_09_22 | hvmv_3_22 | TRUE | 3 |  | FALSE
GSO_130 | br_010_22 | hvmv_3_22 | TRUE | 3 |  | FALSE
GSO_131 | br_011_22 | hvmv_3_22 | TRUE | 3 |  | FALSE
GSO_132 | br_012_22 | hvmv_3_22 | TRUE | 3 |  | FALSE
GSO_133 | br_013_22 | hvmv_3_22 | TRUE | 3 |  | FALSE
GSO_134 | br_014_22 | hvmv_3_22 | TRUE | 3 |  | FALSE
GSO_135 | br_015_22 | hvmv_3_22 | TRUE | 3 |  | FALSE
GSO_162 | br_08_23 | hvmv_3_23 | TRUE | 3 |  | FALSE
GSO_163 | br_09_23 | hvmv_3_23 | TRUE | 3 |  | FALSE
GSO_17 | br_024_21 | hvmv_4_21 | TRUE | 3 |  | FALSE
GSO_18 | br_025_21 | hvmv_4_21 | TRUE | 3 | 10.3769 | TRUE
GSO_19 | br_026_21 | hvmv_4_21 | TRUE | 3 |  | FALSE
GSO_136 | br_016_22 | hvmv_4_22 | TRUE | 3 |  | FALSE
GSO_137 | br_017_22 | hvmv_4_22 | TRUE | 3 |  | FALSE
GSO_138 | br_018_22 | hvmv_4_22 | TRUE | 3 |  | FALSE
GSO_139 | br_019_22 | hvmv_4_22 | TRUE | 3 |  | FALSE
GSO_140 | br_020_22 | hvmv_4_22 | TRUE | 3 |  | FALSE
GSO_20 | br_027_21 | hvmv_5_21 | TRUE | 3 |  | FALSE
GSO_21 | br_028_21 | hvmv_5_21 | TRUE | 3 |  | FALSE
GSO_22 | br_029_21 | hvmv_5_21 | TRUE | 3 |  | FALSE
GSO_23 | br_030_21 | hvmv_5_21 | TRUE | 3 |  | FALSE
GSO_24 | br_031_21 | hvmv_5_21 | TRUE | 3 |  | FALSE
GSO_25 | br_032_21 | hvmv_5_21 | TRUE | 3 |  | FALSE
GSO_26 | br_033_21 | hvmv_5_21 | TRUE | 3 |  | FALSE
GSO_27 | br_034_21 | hvmv_5_21 | TRUE | 3 |  | FALSE
GSO_141 | br_021_22 | hvmv_5_22 | TRUE | 3 | 11.02 | TRUE
GSO_142 | br_022_22 | hvmv_5_22 | TRUE | 3 | 10.6074 | TRUE
GSO_143 | br_023_22 | hvmv_5_22 | TRUE | 3 |  | FALSE
GSO_144 | br_024_22 | hvmv_5_22 | TRUE | 3 | 11.2671 | TRUE
GSO_145 | br_025_22 | hvmv_5_22 | TRUE | 3 | 10.6656 | TRUE
GSO_28 | br_035_21 | hvmv_6_21 | TRUE | 3 |  | FALSE
GSO_29 | br_036_21 | hvmv_6_21 | TRUE | 3 |  | FALSE
GSO_30 | br_037_21 | hvmv_6_21 | TRUE | 3 |  | FALSE
GSO_31 | br_038_21 | hvmv_6_21 | TRUE | 3 |  | FALSE
GSO_146 | br_026_22 | hvmv_6_22 | TRUE | 3 |  | FALSE
GSO_147 | br_027_22 | hvmv_6_22 | TRUE | 3 |  | FALSE
GSO_148 | br_028_22 | hvmv_6_22 | TRUE | 3 |  | FALSE
GSO_149 | br_029_22 | hvmv_6_22 | TRUE | 3 |  | FALSE
GSO_32 | br_039_21 | hvmv_7_21 | TRUE | 3 |  | FALSE
GSO_33 | br_040_21 | hvmv_7_21 | TRUE | 3 |  | FALSE
GSO_34 | br_041_21 | hvmv_7_21 | TRUE | 3 |  | FALSE
GSO_35 | br_042_21 | hvmv_7_21 | TRUE | 3 |  | FALSE
GSO_36 | br_043_21 | hvmv_7_21 | TRUE | 3 |  | FALSE
GSO_37 | br_044_21 | hvmv_7_21 | TRUE | 3 |  | FALSE
GSO_150 | br_030_22 | hvmv_7_22 | TRUE | 3 |  | FALSE
GSO_151 | br_031_22 | hvmv_7_22 | TRUE | 3 |  | FALSE
GSO_152 | br_032_22 | hvmv_7_22 | TRUE | 3 |  | FALSE
GSO_153 | br_033_22 | hvmv_7_22 | TRUE | 3 |  | FALSE
GSO_154 | br_034_22 | hvmv_7_22 | TRUE | 3 |  | FALSE
GSO_38 | br_045_21 | hvmv_8_21 | TRUE | 3 |  | FALSE
GSO_39 | br_046_21 | hvmv_8_21 | TRUE | 3 |  | FALSE
GSO_40 | br_047_21 | hvmv_8_21 | TRUE | 3 |  | FALSE
GSO_41 | br_048_21 | hvmv_8_21 | TRUE | 3 |  | FALSE
GSO_42 | br_049_21 | hvmv_8_21 | TRUE | 3 |  | FALSE
GSO_43 | br_050_21 | hvmv_9_21 | TRUE | 3 |  | FALSE
GSO_44 | br_051_21 | hvmv_9_21 | TRUE | 3 |  | FALSE
GSO_45 | br_052_21 | hvmv_9_21 | TRUE | 3 |  | FALSE
GSO_46 | br_053_21 | hvmv_9_21 | TRUE | 3 |  | FALSE
GSO_47 | br_054_21 | hvmv_9_21 | TRUE | 3 |  | FALSE
GSO_48 | br_055_21 | hvmv_9_21 | TRUE | 3 |  | FALSE
GSO_49 | br_056_21 | hvmv_9_21 | TRUE | 3 |  | FALSE
GSO_50 | br_057_21 | hvmv_9_21 | TRUE | 3 |  | FALSE
GSO_51 | br_058_21 | hvmv_9_21 | TRUE | 3 |  | FALSE
GSO_52 | br_059_21 | hvmv_9_21 | TRUE | 3 |  | FALSE
GSO_53 | br_060_21 | hvmv_9_21 | TRUE | 3 |  | FALSE

## Feeder_Profile_Quality
GridID | BreakerID | SourceCount | ExpectedIntervals | RawCompleteIntervals | AcceptedIntervals | CoveragePct | PeakMW | P95MW | AverageMW | AnnualEnergyMWh | FirstAcceptedTimestampUTC | LastAcceptedTimestampUTC | ProfileStatus | Error | SubstationID | SubstationEntityFound | IsCurrentMILPCandidate
GSO_54 | br_061_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 5.0799 | 3.7884 | 2.5084 | 22020.8537 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_10_21 | TRUE | FALSE
GSO_55 | br_062_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 0.26848 | 0.19112 | 0.12347 | 1083.9367 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_10_21 | TRUE | FALSE
GSO_56 | br_063_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 0.80917 | 0.62017 | 0.45164 | 3964.9525 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_10_21 | TRUE | FALSE
GSO_64 | br_064_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 2.3845 | 1.8163 | 1.2676 | 11128.008 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_11_21 | TRUE | FALSE
GSO_65 | br_065_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 0.21571 | 0.16918 | 0.14171 | 1244.0666 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_11_21 | TRUE | FALSE
GSO_66 | br_066_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 2.6972 | 2.0344 | 1.3628 | 11963.9205 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_11_21 | TRUE | FALSE
GSO_67 | br_067_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 2.8646 | 2.1371 | 1.4901 | 13081.7237 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_11_21 | TRUE | FALSE
GSO_68 | br_068_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 2.3491 | 1.8094 | 1.2841 | 11273.5455 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_11_21 | TRUE | FALSE
GSO_69 | br_069_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 0.49324 | 0.38227 | 0.29078 | 2552.8011 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_11_21 | TRUE | FALSE
GSO_70 | br_070_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 0.51608 | 0.42007 | 0.35304 | 3099.3635 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_11_21 | TRUE | FALSE
GSO_71 | br_071_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 5.5004 | 4.1681 | 2.7774 | 24382.6835 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_12_21 | TRUE | FALSE
GSO_72 | br_072_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 1.741 | 1.3238 | 0.95133 | 8351.7618 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_12_21 | TRUE | FALSE
GSO_73 | br_073_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 0.097896 | 0.06612 | 0.053536 | 469.9947 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_12_21 | TRUE | FALSE
GSO_74 | br_074_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 1.0535 | 0.87569 | 0.71292 | 6258.6866 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_12_21 | TRUE | FALSE
GSO_75 | br_075_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 0.81054 | 0.58537 | 0.43085 | 3782.4628 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_12_21 | TRUE | FALSE
GSO_76 | br_076_21 | 1 | 105408 | 105348 | 105348 | 99.9431 | 0.052824 | 0.036908 | 0.02376 | 208.5879 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_13_21 | TRUE | FALSE
GSO_77 | br_077_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 5.1594 | 3.9175 | 2.6294 | 23083.1265 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_13_21 | TRUE | FALSE
GSO_78 | br_078_21 | 2 | 105408 | 105348 | 105348 | 99.9431 | 0.32894 | 0.24664 | 0.16943 | 1487.4536 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_13_21 | TRUE | FALSE
GSO_79 | br_079_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 1.4952 | 1.1479 | 0.85586 | 7513.6012 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_13_21 | TRUE | FALSE
GSO_80 | br_080_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 1.9457 | 1.4855 | 1.0636 | 9336.9778 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_13_21 | TRUE | FALSE
GSO_81 | br_081_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 2.07 | 1.5889 | 1.1689 | 10262.0004 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_13_21 | TRUE | FALSE
GSO_82 | br_082_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 3.3849 | 2.5113 | 1.6447 | 14439.1133 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_13_21 | TRUE | FALSE
GSO_83 | br_083_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 4.2004 | 3.158 | 2.0902 | 18350.1449 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_13_21 | TRUE | FALSE
GSO_84 | br_084_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 0.36289 | 0.26237 | 0.1731 | 1519.6427 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_13_21 | TRUE | FALSE
GSO_85 | br_085_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 0.78437 | 0.6065 | 0.46705 | 4100.1925 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_13_21 | TRUE | FALSE
GSO_86 | br_086_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 1.9608 | 1.5183 | 1.0764 | 9449.6617 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_14_21 | TRUE | FALSE
GSO_87 | br_087_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 1.8016 | 1.4151 | 1.0482 | 9201.916 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_14_21 | TRUE | FALSE
GSO_88 | br_088_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 1.3613 | 1.0329 | 0.76138 | 6684.1726 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_14_21 | TRUE | FALSE
GSO_89 | br_089_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 1.3116 | 1.013 | 0.76922 | 6752.9916 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_14_21 | TRUE | FALSE
GSO_90 | br_090_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 0.63064 | 0.50003 | 0.41465 | 3640.1743 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_14_21 | TRUE | FALSE
GSO_91 | br_091_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 1.6821 | 1.2713 | 0.96936 | 8510.0331 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_14_21 | TRUE | FALSE
GSO_92 | br_092_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 0.76915 | 0.61804 | 0.50669 | 4448.1954 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_14_21 | TRUE | FALSE
GSO_93 | br_093_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 0.70237 | 0.55536 | 0.45692 | 4011.309 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_14_21 | TRUE | FALSE
GSO_94 | br_094_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 0.50374 | 0.40645 | 0.33065 | 2902.7893 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_14_21 | TRUE | FALSE
GSO_95 | br_095_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 3.4292 | 2.5471 | 1.708 | 14994.4069 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_14_21 | TRUE | FALSE
GSO_96 | br_096_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 1.358 | 1.0681 | 0.81239 | 7131.9553 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_14_21 | TRUE | FALSE
GSO_100 | br_097_21 | 2 | 105408 | 105348 | 105348 | 99.9431 | 0.37085 | 0.26832 | 0.17463 | 1533.1188 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_15_21 | TRUE | FALSE
GSO_97 | br_098_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 4.1702 | 3.1628 | 2.111 | 18532.8783 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_15_21 | TRUE | FALSE
GSO_98 | br_099_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 5.674 | 4.1417 | 2.6962 | 23669.701 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_15_21 | TRUE | FALSE
GSO_99 | br_0100_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 4.525 | 3.3894 | 2.3225 | 20389.5814 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_15_21 | TRUE | FALSE
GSO_101 | br_0101_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 1.1216 | 0.87754 | 0.66936 | 5876.2851 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_16_21 | TRUE | FALSE
GSO_102 | br_0102_21 | 2 | 105408 | 105348 | 105348 | 99.9431 | 0.05448 | 0.0333 | 0.021543 | 189.1283 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_16_21 | TRUE | FALSE
GSO_103 | br_0103_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 4.187 | 3.1027 | 2.0181 | 17716.5921 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_16_21 | TRUE | FALSE
GSO_104 | br_0104_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 3.8614 | 2.8894 | 1.917 | 16829.0801 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_16_21 | TRUE | FALSE
GSO_105 | br_0105_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 3.66 | 2.7735 | 1.8088 | 15879.5491 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_16_21 | TRUE | FALSE
GSO_106 | br_0106_21 | 2 | 105408 | 105348 | 105348 | 99.9431 | 0.09288 | 0.064536 | 0.041269 | 362.2967 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_16_21 | TRUE | FALSE
GSO_107 | br_0107_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 0.11552 | 0.08376 | 0.068935 | 605.184 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_16_21 | TRUE | FALSE
GSO_108 | br_0108_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 2.4922 | 1.9144 | 1.2795 | 11232.7272 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_17_21 | TRUE | FALSE
GSO_109 | br_0109_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 2.2226 | 1.6922 | 1.16 | 10184.0053 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_17_21 | TRUE | FALSE
GSO_110 | br_0110_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 4.5154 | 3.3579 | 2.1945 | 19265.0797 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_17_21 | TRUE | FALSE
GSO_111 | br_0111_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 1.156 | 0.90895 | 0.65645 | 5762.9999 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_17_21 | TRUE | FALSE
GSO_112 | br_0112_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 0.77134 | 0.58066 | 0.47836 | 4199.5049 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_17_21 | TRUE | FALSE
GSO_113 | br_0113_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 0.091248 | 0.065088 | 0.053802 | 472.3268 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_17_21 | TRUE | FALSE
GSO_114 | br_0114_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 1.4064 | 1.0582 | 0.75285 | 6609.2691 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_17_21 | TRUE | FALSE
GSO_115 | br_0115_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 2.2713 | 1.7258 | 1.1974 | 10512.3001 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_18_21 | TRUE | FALSE
GSO_116 | br_0116_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 1.0806 | 0.8443 | 0.64103 | 5627.566 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_18_21 | TRUE | FALSE
GSO_117 | br_0117_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 3.528 | 2.682 | 1.821 | 15986.5852 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_18_21 | TRUE | FALSE
GSO_118 | br_0118_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 1.5724 | 1.2453 | 0.92656 | 8134.311 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_18_21 | TRUE | FALSE
GSO_119 | br_0119_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 0.33516 | 0.23111 | 0.14971 | 1314.305 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_18_21 | TRUE | FALSE
GSO_1 | br_01_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 0.83644 | 0.69786 | 0.57147 | 5016.9081 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_1_21 | TRUE | FALSE
GSO_2 | br_02_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 2.2932 | 1.7331 | 1.2027 | 10558.7858 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_1_21 | TRUE | FALSE
GSO_3 | br_03_21 | 1 | 105408 | 105348 | 105348 | 99.9431 | 0.038244 | 0.021876 | 0.014119 | 123.9485 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_1_21 | TRUE | FALSE
GSO_4 | br_04_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 5.0234 | 3.721 | 2.4126 | 21180.5008 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_1_21 | TRUE | FALSE
GSO_5 | br_05_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 1.0512 | 0.83893 | 0.6801 | 5970.6108 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_1_21 | TRUE | FALSE
GSO_6 | br_06_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 0.82657 | 0.637 | 0.44327 | 3891.4392 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_1_21 | TRUE | FALSE
GSO_7 | br_07_21 | 2 | 105408 | 105348 | 105348 | 99.9431 | 0.073416 | 0.0468 | 0.029079 | 255.2829 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_1_21 | TRUE | FALSE
GSO_121 | br_01_22 | 3 | 105408 | 105348 | 105348 | 99.9431 | 0.38162 | 0.30456 | 0.24467 | 2147.9335 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_1_22 | TRUE | TRUE
GSO_122 | br_02_22 | 3 | 105408 | 105348 | 105348 | 99.9431 | 0.03276 | 0.024036 | 0.019727 | 173.1856 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_1_22 | TRUE | TRUE
GSO_123 | br_03_22 | 3 | 105408 | 105348 | 105348 | 99.9431 | 0.36464 | 0.28877 | 0.24819 | 2178.9009 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_1_22 | TRUE | TRUE
GSO_124 | br_04_22 | 3 | 105408 | 105348 | 105348 | 99.9431 | 0.13387 | 0.0957 | 0.077728 | 682.3711 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_1_22 | TRUE | TRUE
GSO_155 | br_01_23 | 3 | 105408 | 105348 | 105348 | 99.9431 | 1.2782 | 0.94631 | 0.64645 | 5675.1525 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_1_23 | TRUE | FALSE
GSO_156 | br_02_23 | 3 | 105408 | 105348 | 105348 | 99.9431 | 3.0797 | 2.3544 | 1.5909 | 13966.2051 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_1_23 | TRUE | FALSE
GSO_157 | br_03_23 | 3 | 105408 | 105348 | 105348 | 99.9431 | 2.889 | 2.1269 | 1.4377 | 12621.1549 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_1_23 | TRUE | FALSE
GSO_158 | br_04_23 | 3 | 105408 | 105348 | 105348 | 99.9431 | 2.6914 | 2.0512 | 1.3735 | 12058.0196 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_1_23 | TRUE | FALSE
GSO_57 | br_08_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 1.0327 | 0.75041 | 0.53196 | 4670.0379 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_2_21 | TRUE | FALSE
GSO_58 | br_09_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 4.1658 | 3.0619 | 2.002 | 17575.2141 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_2_21 | TRUE | FALSE
GSO_59 | br_010_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 3.1957 | 2.377 | 1.5447 | 13561.1414 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_2_21 | TRUE | FALSE
GSO_60 | br_011_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 2.859 | 2.0963 | 1.3871 | 12177.6215 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_2_21 | TRUE | FALSE
GSO_61 | br_012_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 5.2018 | 3.922 | 2.5424 | 22319.8014 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_2_21 | TRUE | FALSE
GSO_62 | br_013_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 0.85519 | 0.62888 | 0.40929 | 3593.1998 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_2_21 | TRUE | FALSE
GSO_63 | br_014_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 0.12385 | 0.090528 | 0.059226 | 519.9413 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_2_21 | TRUE | FALSE
GSO_125 | br_05_22 | 3 | 105408 | 105348 | 105348 | 99.9431 | 0.3241 | 0.25126 | 0.20672 | 1814.7555 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_2_22 | TRUE | FALSE
GSO_126 | br_06_22 | 3 | 105408 | 105348 | 105348 | 99.9431 | 0.24218 | 0.18904 | 0.15702 | 1378.4941 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_2_22 | TRUE | FALSE
GSO_127 | br_07_22 | 3 | 105408 | 105348 | 105348 | 99.9431 | 0.025212 | 0.016656 | 0.012603 | 110.6401 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_2_22 | TRUE | TRUE
GSO_128 | br_08_22 | 3 | 105408 | 105348 | 105348 | 99.9431 | 0.15013 | 0.11608 | 0.096715 | 849.0634 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_2_22 | TRUE | FALSE
GSO_159 | br_05_23 | 3 | 105408 | 105348 | 105348 | 99.9431 | 3.469 | 2.5527 | 1.722 | 15117.8344 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_2_23 | TRUE | FALSE
GSO_160 | br_06_23 | 3 | 105408 | 105348 | 105348 | 99.9431 | 4.6476 | 3.4652 | 2.3408 | 20549.5022 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_2_23 | TRUE | FALSE
GSO_161 | br_07_23 | 2 | 105408 | 105348 | 105348 | 99.9431 | 0.06714 | 0.044532 | 0.028877 | 253.5105 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_2_23 | TRUE | FALSE
GSO_10 | br_015_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 1.894 | 1.3981 | 0.9939 | 8725.484 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_3_21 | TRUE | FALSE
GSO_11 | br_016_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 2.1962 | 1.7004 | 1.2134 | 10652.59 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_3_21 | TRUE | FALSE
GSO_12 | br_017_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 2.4984 | 1.896 | 1.2344 | 10836.446 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_3_21 | TRUE | FALSE
GSO_13 | br_018_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 2.5309 | 1.9149 | 1.3096 | 11496.5861 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_3_21 | TRUE | FALSE
GSO_14 | br_019_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 2.6885 | 2.0384 | 1.403 | 12316.509 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_3_21 | TRUE | FALSE
GSO_15 | br_020_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 3.3588 | 2.5284 | 1.6994 | 14918.8008 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_3_21 | TRUE | FALSE
GSO_16 | br_021_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 1.7095 | 1.2917 | 0.91765 | 8056.0089 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_3_21 | TRUE | FALSE
GSO_8 | br_022_21 | 1 | 105408 | 105348 | 105348 | 99.9431 | 0.058212 | 0.034476 | 0.022721 | 199.4709 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_3_21 | TRUE | FALSE
GSO_9 | br_023_21 | 2 | 105408 | 105348 | 105348 | 99.9431 | 0.038448 | 0.022788 | 0.014247 | 125.078 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_3_21 | TRUE | FALSE
GSO_129 | br_09_22 | 3 | 105408 | 105348 | 105348 | 99.9431 | 0.26306 | 0.20905 | 0.17276 | 1516.6756 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_3_22 | TRUE | FALSE
GSO_130 | br_010_22 | 3 | 105408 | 105348 | 105348 | 99.9431 | 0.31823 | 0.24804 | 0.21103 | 1852.6126 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_3_22 | TRUE | FALSE
GSO_131 | br_011_22 | 3 | 105408 | 105348 | 105348 | 99.9431 | 0.073452 | 0.053576 | 0.04523 | 397.0711 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_3_22 | TRUE | FALSE
GSO_132 | br_012_22 | 3 | 105408 | 105348 | 105348 | 99.9431 | 0.45876 | 0.37998 | 0.32331 | 2838.319 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_3_22 | TRUE | FALSE
GSO_133 | br_013_22 | 3 | 105408 | 105348 | 105348 | 99.9431 | 0.6777 | 0.52895 | 0.44721 | 3926.0723 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_3_22 | TRUE | FALSE
GSO_134 | br_014_22 | 3 | 105408 | 105348 | 105348 | 99.9431 | 0.32862 | 0.26444 | 0.22056 | 1936.3004 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_3_22 | TRUE | FALSE
GSO_135 | br_015_22 | 3 | 105408 | 105348 | 105348 | 99.9431 | 0.52656 | 0.42978 | 0.36821 | 3232.5157 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_3_22 | TRUE | FALSE
GSO_162 | br_08_23 | 3 | 105408 | 105348 | 105348 | 99.9431 | 1.0057 | 0.75386 | 0.50804 | 4460.0406 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_3_23 | TRUE | FALSE
GSO_163 | br_09_23 | 3 | 105408 | 105348 | 105348 | 99.9431 | 3.1708 | 2.3743 | 1.6046 | 14086.7986 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_3_23 | TRUE | FALSE
GSO_17 | br_024_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 3.5366 | 2.6953 | 1.8182 | 15962.399 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_4_21 | TRUE | FALSE
GSO_18 | br_025_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 2.2897 | 1.713 | 1.1891 | 10438.9644 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_4_21 | TRUE | TRUE
GSO_19 | br_026_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 5.1626 | 3.8361 | 2.5101 | 22035.7729 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_4_21 | TRUE | FALSE
GSO_136 | br_016_22 | 3 | 105408 | 105348 | 105348 | 99.9431 | 0.34441 | 0.26099 | 0.22044 | 1935.2701 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_4_22 | TRUE | FALSE
GSO_137 | br_017_22 | 3 | 105408 | 105348 | 105348 | 99.9431 | 0.30721 | 0.25138 | 0.21405 | 1879.141 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_4_22 | TRUE | FALSE
GSO_138 | br_018_22 | 3 | 105408 | 105348 | 105348 | 99.9431 | 0.38712 | 0.29495 | 0.22654 | 1988.759 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_4_22 | TRUE | FALSE
GSO_139 | br_019_22 | 3 | 105408 | 105348 | 105348 | 99.9431 | 0.50093 | 0.3653 | 0.30302 | 2660.205 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_4_22 | TRUE | FALSE
GSO_140 | br_020_22 | 3 | 105408 | 105348 | 105348 | 99.9431 | 0.30924 | 0.2472 | 0.20816 | 1827.4312 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_4_22 | TRUE | FALSE
GSO_20 | br_027_21 | 1 | 105408 | 105348 | 105348 | 99.9431 | 0.007668 | 0.004752 | 0.0032747 | 28.7485 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_5_21 | TRUE | FALSE
GSO_21 | br_028_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 1.6817 | 1.2838 | 0.9294 | 8159.177 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_5_21 | TRUE | FALSE
GSO_22 | br_029_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 1.7494 | 1.3475 | 0.94167 | 8266.9408 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_5_21 | TRUE | FALSE
GSO_23 | br_030_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 1.1484 | 0.87494 | 0.63701 | 5592.2698 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_5_21 | TRUE | FALSE
GSO_24 | br_031_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 0.067452 | 0.050748 | 0.042273 | 371.118 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_5_21 | TRUE | FALSE
GSO_25 | br_032_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 0.62447 | 0.49246 | 0.406 | 3564.2564 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_5_21 | TRUE | FALSE
GSO_26 | br_033_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 1.89 | 1.4436 | 1.0473 | 9194.3042 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_5_21 | TRUE | FALSE
GSO_27 | br_034_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 2.4046 | 1.7988 | 1.2479 | 10955.1095 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_5_21 | TRUE | FALSE
GSO_141 | br_021_22 | 3 | 105408 | 105348 | 105348 | 99.9431 | 0.37996 | 0.29074 | 0.23482 | 2061.47 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_5_22 | TRUE | TRUE
GSO_142 | br_022_22 | 3 | 105408 | 105348 | 105348 | 99.9431 | 0.79259 | 0.62478 | 0.52512 | 4610.0614 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_5_22 | TRUE | TRUE
GSO_143 | br_023_22 | 3 | 105408 | 105348 | 105348 | 99.9431 | 2.5408 | 1.8959 | 1.249 | 10964.718 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_5_22 | TRUE | FALSE
GSO_144 | br_024_22 | 2 | 105408 | 105348 | 105348 | 99.9431 | 0.13286 | 0.090084 | 0.057412 | 504.0176 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_5_22 | TRUE | TRUE
GSO_145 | br_025_22 | 3 | 105408 | 105348 | 105348 | 99.9431 | 0.73442 | 0.56032 | 0.4405 | 3867.187 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_5_22 | TRUE | TRUE
GSO_28 | br_035_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 0.11803 | 0.079944 | 0.062273 | 546.6914 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_6_21 | TRUE | FALSE
GSO_29 | br_036_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 1.9875 | 1.5256 | 1.0643 | 9343.425 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_6_21 | TRUE | FALSE
GSO_30 | br_037_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 1.8068 | 1.3691 | 0.94227 | 8272.1682 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_6_21 | TRUE | FALSE
GSO_31 | br_038_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 0.036228 | 0.022212 | 0.014254 | 125.1343 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_6_21 | TRUE | FALSE
GSO_146 | br_026_22 | 3 | 105408 | 105348 | 105348 | 99.9431 | 0.97618 | 0.72908 | 0.5382 | 4724.901 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_6_22 | TRUE | FALSE
GSO_147 | br_027_22 | 3 | 105408 | 105348 | 105348 | 99.9431 | 0.29234 | 0.21618 | 0.16253 | 1426.8288 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_6_22 | TRUE | FALSE
GSO_148 | br_028_22 | 3 | 105408 | 105348 | 105348 | 99.9431 | 0.49594 | 0.37366 | 0.29922 | 2626.861 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_6_22 | TRUE | FALSE
GSO_149 | br_029_22 | 3 | 105408 | 105348 | 105348 | 99.9431 | 0.091644 | 0.069716 | 0.056658 | 497.4 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_6_22 | TRUE | FALSE
GSO_32 | br_039_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 1.2177 | 0.94806 | 0.70222 | 6164.793 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_7_21 | TRUE | FALSE
GSO_33 | br_040_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 0.88399 | 0.70153 | 0.5803 | 5094.4382 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_7_21 | TRUE | FALSE
GSO_34 | br_041_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 2.2167 | 1.6717 | 1.1591 | 10175.3536 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_7_21 | TRUE | FALSE
GSO_35 | br_042_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 3.5443 | 2.6524 | 1.7539 | 15397.5107 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_7_21 | TRUE | FALSE
GSO_36 | br_043_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 0.4952 | 0.40406 | 0.34312 | 3012.2093 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_7_21 | TRUE | FALSE
GSO_37 | br_044_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 5.2542 | 3.9761 | 2.635 | 23132.6502 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_7_21 | TRUE | FALSE
GSO_150 | br_030_22 | 3 | 105408 | 105348 | 105348 | 99.9431 | 0.22006 | 0.15808 | 0.13007 | 1141.878 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_7_22 | TRUE | FALSE
GSO_151 | br_031_22 | 3 | 105408 | 105348 | 105348 | 99.9431 | 0.73038 | 0.54888 | 0.42541 | 3734.6714 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_7_22 | TRUE | FALSE
GSO_152 | br_032_22 | 3 | 105408 | 105348 | 105348 | 99.9431 | 0.0261 | 0.01728 | 0.012 | 105.3465 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_7_22 | TRUE | FALSE
GSO_153 | br_033_22 | 3 | 105408 | 105348 | 105348 | 99.9431 | 0.84121 | 0.69708 | 0.59934 | 5261.5984 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_7_22 | TRUE | FALSE
GSO_154 | br_034_22 | 3 | 105408 | 105348 | 105348 | 99.9431 | 0.26084 | 0.19657 | 0.16112 | 1414.4663 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_7_22 | TRUE | FALSE
GSO_38 | br_045_21 | 1 | 105408 | 105348 | 105348 | 99.9431 | 0.042336 | 0.024204 | 0.015622 | 137.1452 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_8_21 | TRUE | FALSE
GSO_39 | br_046_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 2.3656 | 1.7841 | 1.194 | 10481.8026 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_8_21 | TRUE | FALSE
GSO_40 | br_047_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 2.0837 | 1.5401 | 1.0344 | 9081.3549 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_8_21 | TRUE | FALSE
GSO_41 | br_048_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 1.859 | 1.3503 | 0.89469 | 7854.4609 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_8_21 | TRUE | FALSE
GSO_42 | br_049_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 4.0752 | 3.0111 | 1.9506 | 17124.3248 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_8_21 | TRUE | FALSE
GSO_43 | br_050_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 4.3723 | 3.2839 | 2.2069 | 19374.1517 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_9_21 | TRUE | FALSE
GSO_44 | br_051_21 | 2 | 105408 | 105348 | 105348 | 99.9431 | 0.065292 | 0.04086 | 0.026956 | 236.651 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_9_21 | TRUE | FALSE
GSO_45 | br_052_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 3.3731 | 2.498 | 1.6229 | 14247.6176 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_9_21 | TRUE | FALSE
GSO_46 | br_053_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 2.9347 | 2.2132 | 1.4964 | 13136.8862 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_9_21 | TRUE | FALSE
GSO_47 | br_054_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 0.35389 | 0.27116 | 0.21699 | 1904.9135 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_9_21 | TRUE | FALSE
GSO_48 | br_055_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 0.50413 | 0.40578 | 0.34809 | 3055.9175 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_9_21 | TRUE | FALSE
GSO_49 | br_056_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 0.19782 | 0.15506 | 0.12927 | 1134.8355 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_9_21 | TRUE | FALSE
GSO_50 | br_057_21 | 1 | 105408 | 105348 | 105348 | 99.9431 | 0.06354 | 0.042684 | 0.027447 | 240.9607 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_9_21 | TRUE | FALSE
GSO_51 | br_058_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 0.35236 | 0.2792 | 0.24078 | 2113.7732 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_9_21 | TRUE | FALSE
GSO_52 | br_059_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 3.1697 | 2.3443 | 1.5455 | 13567.8171 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_9_21 | TRUE | FALSE
GSO_53 | br_060_21 | 3 | 105408 | 105348 | 105348 | 99.9431 | 1.3206 | 0.99739 | 0.72043 | 6324.6724 | 2024-01-01 05:00 | 2024-12-31 23:55 | READY |  | hvmv_9_21 | TRUE | FALSE

## Coincidence_Analysis
SubstationID | CoincidentPeakMW | SumIndividualFeederPeaksMW | PeakReductionFromCoincidenceMW | CoincidenceFactor | DiversityFactor | PeakTimestampUTC | ProfileCoveragePct | ProfileStatus
hvmv_13_21 | 19.5567 | 19.7846 | 0.22786 | 0.98848 | 1.0117 | 2024-01-21 04:00 | 99.9431 | READY
hvmv_2_21 | 17.3574 | 17.4341 | 0.076728 | 0.9956 | 1.0044 | 2024-01-21 04:00 | 99.9431 | READY
hvmv_3_21 | 16.9458 | 16.9729 | 0.02706 | 0.99841 | 1.0016 | 2024-01-21 04:00 | 99.9431 | READY
hvmv_9_21 | 16.4919 | 16.7075 | 0.21554 | 0.9871 | 1.0131 | 2024-01-21 04:00 | 99.9431 | READY
hvmv_14_21 | 15.0565 | 15.5104 | 0.45386 | 0.97074 | 1.0301 | 2024-01-21 04:00 | 99.9431 | READY
hvmv_15_21 | 14.7045 | 14.7401 | 0.035556 | 0.99759 | 1.0024 | 2024-01-21 04:00 | 99.9431 | READY
hvmv_7_21 | 13.3872 | 13.612 | 0.22483 | 0.98348 | 1.0168 | 2024-01-18 04:00 | 99.9431 | READY
hvmv_16_21 | 13.06 | 13.0929 | 0.032916 | 0.99749 | 1.0025 | 2024-01-21 04:00 | 99.9431 | READY
hvmv_17_21 | 12.4749 | 12.6552 | 0.18031 | 0.98575 | 1.0145 | 2024-01-21 04:00 | 99.9431 | READY
hvmv_11_21 | 11.5184 | 11.5205 | 0.002112 | 0.99982 | 1.0002 | 2024-01-21 04:00 | 99.9431 | READY
hvmv_4_21 | 10.9621 | 10.9889 | 0.026844 | 0.99756 | 1.0024 | 2024-01-18 04:00 | 99.9431 | READY
hvmv_8_21 | 10.3636 | 10.426 | 0.062412 | 0.99401 | 1.006 | 2024-01-21 04:00 | 99.9431 | READY
hvmv_1_21 | 9.961 | 10.1424 | 0.18143 | 0.98211 | 1.0182 | 2024-01-21 04:00 | 99.9431 | READY
hvmv_1_23 | 9.8808 | 9.9382 | 0.057396 | 0.99422 | 1.0058 | 2024-01-21 04:00 | 99.9431 | READY
hvmv_5_21 | 9.4955 | 9.5737 | 0.078276 | 0.99182 | 1.0082 | 2024-01-21 04:00 | 99.9431 | READY
hvmv_12_21 | 9.0553 | 9.2034 | 0.1481 | 0.98391 | 1.0164 | 2024-01-18 04:00 | 99.9431 | READY
hvmv_18_21 | 8.6543 | 8.7875 | 0.13313 | 0.98485 | 1.0154 | 2024-01-21 04:00 | 99.9431 | READY
hvmv_2_23 | 8.1793 | 8.1838 | 0.0045 | 0.99945 | 1.0006 | 2024-01-21 04:00 | 99.9431 | READY
hvmv_10_21 | 6.1336 | 6.1575 | 0.023904 | 0.99612 | 1.0039 | 2024-01-21 04:00 | 99.9431 | READY
hvmv_5_22 | 4.4648 | 4.5806 | 0.11576 | 0.97473 | 1.0259 | 2024-01-21 04:00 | 99.9431 | READY
hvmv_3_23 | 4.1269 | 4.1765 | 0.049584 | 0.98813 | 1.012 | 2024-01-18 04:00 | 99.9431 | READY
hvmv_6_21 | 3.8358 | 3.9485 | 0.11273 | 0.97145 | 1.0294 | 2024-01-21 04:00 | 99.9431 | READY
hvmv_3_22 | 2.5225 | 2.6464 | 0.12385 | 0.9532 | 1.0491 | 2024-01-22 04:00 | 99.9431 | READY
hvmv_7_22 | 1.9938 | 2.0786 | 0.084828 | 0.95919 | 1.0425 | 2024-01-21 04:00 | 99.9431 | READY
hvmv_4_22 | 1.7871 | 1.8489 | 0.0618 | 0.96657 | 1.0346 | 2024-01-21 04:00 | 99.9431 | READY
hvmv_6_22 | 1.7832 | 1.8561 | 0.072924 | 0.96071 | 1.0409 | 2024-01-21 04:00 | 99.9431 | READY
hvmv_1_22 | 0.87823 | 0.9129 | 0.034668 | 0.96202 | 1.0395 | 2024-01-22 04:00 | 99.9431 | READY
hvmv_2_22 | 0.69532 | 0.74162 | 0.046308 | 0.93756 | 1.0666 | 2024-01-20 15:00 | 99.9431 | READY

## MILP_Capacity_Input
SubstationID | TotalCapacityMW | ExistingCoincidentPeakMW | AvailableAdditionalCapacityMW | HeadroomAt80PctMW | HeadroomAt90PctMW | HeadroomAt100PctMW | CapacitySource | SubstationProfileStatus | ProfileCoveragePct | ExpectedFeederCount | LoadedFeederCount | Notes
hvmv_10_21 |  | 6.1336 |  |  |  |  | Review | READY | 99.9431 | 3 | 3
hvmv_11_21 |  | 11.5184 |  |  |  |  | Review | READY | 99.9431 | 7 | 7
hvmv_12_21 |  | 9.0553 |  |  |  |  | Review | READY | 99.9431 | 5 | 5
hvmv_13_21 |  | 19.5567 |  |  |  |  | Review | READY | 99.9431 | 10 | 10
hvmv_14_21 |  | 15.0565 |  |  |  |  | Review | READY | 99.9431 | 11 | 11
hvmv_15_21 |  | 14.7045 |  |  |  |  | Review | READY | 99.9431 | 4 | 4
hvmv_16_21 |  | 13.06 |  |  |  |  | Review | READY | 99.9431 | 7 | 7
hvmv_17_21 |  | 12.4749 |  |  |  |  | Review | READY | 99.9431 | 7 | 7
hvmv_18_21 |  | 8.6543 |  |  |  |  | Review | READY | 99.9431 | 5 | 5
hvmv_1_21 |  | 9.961 |  |  |  |  | Review | READY | 99.9431 | 7 | 7
hvmv_1_22 |  | 0.87823 |  |  |  |  | Review | READY | 99.9431 | 4 | 4 | Populate either AvailableAdditionalCapacityMW directly, or TotalCapacityMW and ExistingCoincidentPeakMW.
hvmv_1_23 |  | 9.8808 |  |  |  |  | Review | READY | 99.9431 | 4 | 4
hvmv_2_21 |  | 17.3574 |  |  |  |  | Review | READY | 99.9431 | 7 | 7
hvmv_2_22 |  | 0.69532 |  |  |  |  | Review | READY | 99.9431 | 4 | 4 | Populate either AvailableAdditionalCapacityMW directly, or TotalCapacityMW and ExistingCoincidentPeakMW.
hvmv_2_23 |  | 8.1793 |  |  |  |  | Review | READY | 99.9431 | 3 | 3
hvmv_3_21 |  | 16.9458 |  |  |  |  | Review | READY | 99.9431 | 9 | 9
hvmv_3_22 |  | 2.5225 |  |  |  |  | Review | READY | 99.9431 | 7 | 7
hvmv_3_23 |  | 4.1269 |  |  |  |  | Review | READY | 99.9431 | 2 | 2
hvmv_4_21 |  | 10.9621 |  |  |  |  | Review | READY | 99.9431 | 3 | 3 | Populate either AvailableAdditionalCapacityMW directly, or TotalCapacityMW and ExistingCoincidentPeakMW.
hvmv_4_22 |  | 1.7871 |  |  |  |  | Review | READY | 99.9431 | 5 | 5
hvmv_5_21 |  | 9.4955 |  |  |  |  | Review | READY | 99.9431 | 8 | 8
hvmv_5_22 |  | 4.4648 |  |  |  |  | Review | READY | 99.9431 | 5 | 5 | Populate either AvailableAdditionalCapacityMW directly, or TotalCapacityMW and ExistingCoincidentPeakMW.
hvmv_6_21 |  | 3.8358 |  |  |  |  | Review | READY | 99.9431 | 4 | 4
hvmv_6_22 |  | 1.7832 |  |  |  |  | Review | READY | 99.9431 | 4 | 4
hvmv_7_21 |  | 13.3872 |  |  |  |  | Review | READY | 99.9431 | 6 | 6
hvmv_7_22 |  | 1.9938 |  |  |  |  | Review | READY | 99.9431 | 5 | 5
hvmv_8_21 |  | 10.3636 |  |  |  |  | Review | READY | 99.9431 | 5 | 5
hvmv_9_21 |  | 16.4919 |  |  |  |  | Review | READY | 99.9431 | 11 | 11

## Assumptions
Item | Assumption
Substation relationship | CircuitBreaker.meta['enclosure_id'] identifies the modeled substation shared by Greensboro feeder breakers.
Population | All mapped GSO feeder breakers are included in each substation load profile, not only current data-center candidate feeders.
Time resolution | Breaker kWh is aggregated to five-minute intervals and converted to average interval MW.
Phase/source handling | All breaker kWh sources are aligned. A feeder interval is accepted only when every breaker kWh source is present after limited internal-gap interpolation.
Interpolation | Only internal gaps up to 12 five-minute intervals are interpolated. Boundary gaps and longer gaps remain missing.
Missing feeder data | Missing feeder load is never treated as zero. A substation interval is complete only when every expected mapped feeder has a usable value.
Coincident peak | ExistingCoincidentPeakMW is the maximum timestamp-aligned sum of all mapped feeder breaker MW for the substation, not the sum of independent feeder annual peaks.
Coincidence factor | CoincidenceFactor = coincident substation peak / sum of individual feeder peaks.
Diversity factor | DiversityFactor = sum of individual feeder peaks / coincident substation peak.
Load factor | LoadFactor = average complete-interval substation MW / coincident peak MW.
MILP admission | ExistingCoincidentPeakMW is populated into the MILP capacity input only when every mapped feeder is loaded and complete substation profile coverage is at least 99.0%.
Capacity | The script does not infer or sum breaker ratings to create substation capacity. TotalCapacityMW remains an explicit external input.
Planning views | When TotalCapacityMW is supplied, the script reports headroom at 80%, 90%, and 100% of stated capacity. The base MILP uses its configured capacity rule separately.
Direction | Substation load is the signed sum of feeder real-power estimates. CoincidentPeakMW uses the maximum positive net load because the modeled data-center load is an added positive load.
Interpretation | These are modeled existing substation load profiles. They do not establish a substation thermal capacity without an explicit capacity value.