## Headline_Recommendation
CandidateKey | GridID | SubstationID | CandidateLineID | FixedDCMW | OutageDurationHours | ServiceTarget | ReliabilityTarget | PVCapacityMW | RecommendedBatteryPowerMW | RecommendedBatteryInstalledMWh | SimulatedSuccessRate | PowerIncreaseVsDeterministicMW | PowerIncreaseVsDeterministicPct | EnergyIncreaseVsDeterministicMWh | EnergyIncreaseVsDeterministicPct | RecommendationPolicy
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 4 | 1 | 0.99 | 0 | 14.1851 | 92.4342 | 99.11% | 0.67548 | 0.05 | 21.331 | 0.3 | MIN_MAX_RELATIVE_OVERSIZE

## Recommendations
OutageDurationHours | PVCapacityMW | PVCapacityRatioToDC | ReliabilityTarget | PassingDesignFound | RecommendedBatteryPowerMW | RecommendedBatteryInstalledMWh | PowerMultiplier | EnergyMultiplier | SimulatedSuccessRate | MeanUnservedEnergyMWh | P99UnservedEnergyMWh | P05MinimumSOCFraction | PCSConstraintEncounterRate | EnergyConstraintEncounterRate
4 | 0 | 0 | 0.95 | TRUE | 14.1851 | 88.879 | 1.05 | 1.25 | 96.25% | 0.045179 | 1.7206 | 10.74% | 0.2% | 3.55%
4 | 0 | 0 | 0.99 | TRUE | 14.1851 | 92.4342 | 1.05 | 1.3 | 99.11% | 0.0055399 | 0 | 13.4% | 0.2% | 0.69%
4 | 0 | 0 | 0.999 | TRUE | 14.5228 | 95.9893 | 1.075 | 1.35 | 99.98% | 0.00010203 | 0 | 15.85% | 0% | 0.02%
4 | 6.7548 | 0.5 | 0.95 | TRUE | 14.1851 | 88.879 | 1.05 | 1.25 | 98.18% | 0.021838 | 0.91294 | 12.68% | 0.15% | 1.67%
4 | 6.7548 | 0.5 | 0.99 | TRUE | 14.1851 | 92.4342 | 1.05 | 1.3 | 99.52% | 0.0029617 | 0 | 15.27% | 0.15% | 0.33%
4 | 6.7548 | 0.5 | 0.999 | TRUE | 14.5228 | 95.9893 | 1.075 | 1.35 | 99.98% | 0.00010203 | 0 | 17.71% | 0% | 0.02%
4 | 13.5096 | 1 | 0.95 | TRUE | 14.5228 | 85.3238 | 1.075 | 1.2 | 95.06% | 0.084191 | 2.9086 | 10.07% | 0% | 4.94%
4 | 13.5096 | 1 | 0.99 | TRUE | 14.1851 | 92.4342 | 1.05 | 1.3 | 99.54% | 0.0027878 | 0 | 15.49% | 0.15% | 0.31%
4 | 13.5096 | 1 | 0.999 | TRUE | 14.5228 | 95.9893 | 1.075 | 1.35 | 99.98% | 0.00010203 | 0 | 17.93% | 0% | 0.02%

## Design_Grid
OutageDurationHours | PVCapacityMW | PVCapacityRatioToDC | PowerMultiplier | EnergyMultiplier | BatteryPowerMW | BatteryInstalledMWh | MaxRelativeOversize | SuccessRate | FailureRate | MeanUnservedEnergyMWh | P95UnservedEnergyMWh | P99UnservedEnergyMWh | MaximumUnservedEnergyMWh | P95PeakUnservedPowerMW | P99PeakUnservedPowerMW | P05MinimumSOCFraction | P50MinimumSOCFraction | MinimumSOCHitRate | PCSConstraintEncounterRate | EnergyConstraintEncounterRate | MeanEnduranceHours | P05EnduranceHours | MeanPVDirectMWh | MeanPVChargeToBatteryACMWh | MeanBatteryDeliveredMWh | Meets_95_0pct | Meets_99_0pct | Meets_99_9pct | ParetoEfficient
4 | 0 | 0 | 1 | 1 | 13.5096 | 71.1032 | 1 | 0% | 100% | 5.1257 | 10.3385 | 12.1842 | 14.5098 | 13.5096 | 13.5096 | 10% | 10% | 91.63% | 100% | 91.63% | 0 | 0 | 0 | 0 | 48.9128 | FALSE | FALSE | FALSE | TRUE
4 | 0 | 0 | 1 | 1.05 | 13.5096 | 74.6584 | 1.05 | 0% | 100% | 3.1934 | 8.1535 | 10.0915 | 12.5334 | 13.5096 | 13.5096 | 10% | 10% | 67.24% | 100% | 67.24% | 0 | 0 | 0 | 0 | 50.8451 | FALSE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1 | 1.1 | 13.5096 | 78.2135 | 1.1 | 0% | 100% | 1.9563 | 5.9685 | 7.9987 | 10.5569 | 13.5096 | 13.5096 | 10% | 11.39% | 39.45% | 100% | 39.45% | 0 | 0 | 0 | 0 | 52.0821 | FALSE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1 | 1.15 | 13.5096 | 81.7687 | 1.15 | 0% | 100% | 1.3044 | 3.7835 | 5.906 | 8.5805 | 13.5096 | 13.5096 | 10% | 14.71% | 19.61% | 100% | 19.61% | 0 | 0 | 0 | 0 | 52.7341 | FALSE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1 | 1.2 | 13.5096 | 85.3238 | 1.2 | 0% | 100% | 1.0163 | 2.3294 | 3.8133 | 6.6041 | 8.8598 | 13.5096 | 10% | 17.73% | 7.67% | 100% | 7.67% | 0 | 0 | 0 | 0 | 53.0222 | FALSE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1 | 1.25 | 13.5096 | 88.879 | 1.25 | 0% | 100% | 0.92254 | 2.125 | 2.4892 | 4.6276 | 0.55783 | 12.2883 | 11.86% | 20.52% | 2.18% | 100% | 2.18% | 0 | 0 | 0 | 0 | 53.1159 | FALSE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1 | 1.3 | 13.5096 | 92.4342 | 1.3 | 0% | 100% | 0.90104 | 2.0887 | 2.421 | 2.6661 | 0.52534 | 0.61544 | 14.46% | 23.09% | 0.29% | 100% | 0.29% | 0 | 0 | 0 | 0 | 53.1374 | FALSE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1 | 1.35 | 13.5096 | 95.9893 | 1.35 | 0% | 100% | 0.89927 | 2.0874 | 2.4183 | 2.6661 | 0.52186 | 0.60457 | 16.89% | 25.45% | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 53.1392 | FALSE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1 | 1.4 | 13.5096 | 99.5445 | 1.4 | 0% | 100% | 0.89927 | 2.0874 | 2.4183 | 2.6661 | 0.52186 | 0.60457 | 19.12% | 27.67% | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 53.1392 | FALSE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1 | 1.45 | 13.5096 | 103.0996 | 1.45 | 0% | 100% | 0.89927 | 2.0874 | 2.4183 | 2.6661 | 0.52186 | 0.60457 | 21.2% | 29.73% | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 53.1392 | FALSE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1 | 1.5 | 13.5096 | 106.6548 | 1.5 | 0% | 100% | 0.89927 | 2.0874 | 2.4183 | 2.6661 | 0.52186 | 0.60457 | 23.13% | 31.66% | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 53.1392 | FALSE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1 | 1.55 | 13.5096 | 110.21 | 1.55 | 0% | 100% | 0.89927 | 2.0874 | 2.4183 | 2.6661 | 0.52186 | 0.60457 | 24.95% | 33.45% | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 53.1392 | FALSE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1 | 1.6 | 13.5096 | 113.7651 | 1.6 | 0% | 100% | 0.89927 | 2.0874 | 2.4183 | 2.6661 | 0.52186 | 0.60457 | 26.65% | 35.15% | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 53.1392 | FALSE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1 | 1.65 | 13.5096 | 117.3203 | 1.65 | 0% | 100% | 0.89927 | 2.0874 | 2.4183 | 2.6661 | 0.52186 | 0.60457 | 28.27% | 36.73% | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 53.1392 | FALSE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1 | 1.7 | 13.5096 | 120.8754 | 1.7 | 0% | 100% | 0.89927 | 2.0874 | 2.4183 | 2.6661 | 0.52186 | 0.60457 | 29.77% | 38.21% | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 53.1392 | FALSE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1 | 1.75 | 13.5096 | 124.4306 | 1.75 | 0% | 100% | 0.89927 | 2.0874 | 2.4183 | 2.6661 | 0.52186 | 0.60457 | 31.18% | 39.63% | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 53.1392 | FALSE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1 | 1.8 | 13.5096 | 127.9858 | 1.8 | 0% | 100% | 0.89927 | 2.0874 | 2.4183 | 2.6661 | 0.52186 | 0.60457 | 32.52% | 40.95% | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 53.1392 | FALSE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1.025 | 1 | 13.8473 | 71.1032 | 1.025 | 2.24% | 97.76% | 5.0711 | 10.3385 | 12.1842 | 14.5098 | 13.5096 | 13.5096 | 10% | 10% | 96.27% | 26.34% | 96.27% | 2.6399 | 0 | 0 | 0 | 48.9673 | FALSE | FALSE | FALSE | TRUE
4 | 0 | 0 | 1.025 | 1.05 | 13.8473 | 74.6584 | 1.05 | 16.62% | 83.38% | 2.9545 | 8.1535 | 10.0915 | 12.5334 | 13.5096 | 13.5096 | 10% | 10% | 76.15% | 26.34% | 76.15% | 2.7625 | 0 | 0 | 0 | 51.0839 | FALSE | FALSE | FALSE | TRUE
4 | 0 | 0 | 1.025 | 1.1 | 13.8473 | 78.2135 | 1.1 | 37.85% | 62.15% | 1.4986 | 5.9685 | 7.9987 | 10.5569 | 13.5096 | 13.5096 | 10% | 10.33% | 47.44% | 26.34% | 47.44% | 2.8526 | 0 | 0 | 0 | 52.5399 | FALSE | FALSE | FALSE | TRUE
4 | 0 | 0 | 1.025 | 1.15 | 13.8473 | 81.7687 | 1.15 | 54.44% | 45.56% | 0.68704 | 3.7835 | 5.906 | 8.5805 | 13.5096 | 13.5096 | 10% | 13.66% | 24.95% | 26.34% | 24.95% | 2.9053 | 0 | 0 | 0 | 53.3514 | FALSE | FALSE | FALSE | TRUE
4 | 0 | 0 | 1.025 | 1.2 | 13.8473 | 85.3238 | 1.2 | 65.16% | 34.84% | 0.30433 | 1.5985 | 3.8133 | 6.6041 | 13.5096 | 13.5096 | 10% | 16.73% | 10.89% | 26.34% | 10.89% | 2.9319 | 0 | 0 | 0 | 53.7341 | FALSE | FALSE | FALSE | TRUE
4 | 0 | 0 | 1.025 | 1.25 | 13.8473 | 88.879 | 1.25 | 70.94% | 29.06% | 0.16403 | 0.92667 | 1.7206 | 4.6276 | 0.26411 | 13.5096 | 10.88% | 19.56% | 3.33% | 26.34% | 3.33% | 2.9426 | 0 | 0 | 0 | 53.8744 | FALSE | FALSE | FALSE | TRUE
4 | 0 | 0 | 1.025 | 1.3 | 13.8473 | 92.4342 | 1.3 | 73.14% | 26.86% | 0.12696 | 0.79759 | 1.163 | 2.6512 | 0.2066 | 0.31396 | 13.53% | 22.16% | 0.66% | 26.34% | 0.66% | 2.9459 | 0 | 0 | 0 | 53.9115 | FALSE | FALSE | FALSE | TRUE
4 | 0 | 0 | 1.025 | 1.35 | 13.8473 | 95.9893 | 1.35 | 73.64% | 26.36% | 0.12224 | 0.78865 | 1.1278 | 1.3818 | 0.1975 | 0.28269 | 15.98% | 24.58% | 0.02% | 26.34% | 0.02% | 2.9464 | 0 | 0 | 0 | 53.9162 | FALSE | FALSE | FALSE | TRUE
4 | 0 | 0 | 1.025 | 1.4 | 13.8473 | 99.5445 | 1.4 | 73.66% | 26.34% | 0.12214 | 0.78865 | 1.1278 | 1.3818 | 0.19716 | 0.28194 | 18.26% | 26.82% | 0% | 26.34% | 0% | 2.9464 | 0 | 0 | 0 | 53.9163 | FALSE | FALSE | FALSE | TRUE
4 | 0 | 0 | 1.025 | 1.45 | 13.8473 | 103.0996 | 1.45 | 73.66% | 26.34% | 0.12214 | 0.78865 | 1.1278 | 1.3818 | 0.19716 | 0.28194 | 20.36% | 28.91% | 0% | 26.34% | 0% | 2.9464 | 0 | 0 | 0 | 53.9163 | FALSE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1.025 | 1.5 | 13.8473 | 106.6548 | 1.5 | 73.66% | 26.34% | 0.12214 | 0.78865 | 1.1278 | 1.3818 | 0.19716 | 0.28194 | 22.33% | 30.86% | 0% | 26.34% | 0% | 2.9464 | 0 | 0 | 0 | 53.9163 | FALSE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1.025 | 1.55 | 13.8473 | 110.21 | 1.55 | 73.66% | 26.34% | 0.12214 | 0.78865 | 1.1278 | 1.3818 | 0.19716 | 0.28194 | 24.19% | 32.68% | 0% | 26.34% | 0% | 2.9464 | 0 | 0 | 0 | 53.9163 | FALSE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1.025 | 1.6 | 13.8473 | 113.7651 | 1.6 | 73.66% | 26.34% | 0.12214 | 0.78865 | 1.1278 | 1.3818 | 0.19716 | 0.28194 | 25.93% | 34.38% | 0% | 26.34% | 0% | 2.9464 | 0 | 0 | 0 | 53.9163 | FALSE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1.025 | 1.65 | 13.8473 | 117.3203 | 1.65 | 73.66% | 26.34% | 0.12214 | 0.78865 | 1.1278 | 1.3818 | 0.19716 | 0.28194 | 27.56% | 35.99% | 0% | 26.34% | 0% | 2.9464 | 0 | 0 | 0 | 53.9163 | FALSE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1.025 | 1.7 | 13.8473 | 120.8754 | 1.7 | 73.66% | 26.34% | 0.12214 | 0.78865 | 1.1278 | 1.3818 | 0.19716 | 0.28194 | 29.08% | 37.49% | 0% | 26.34% | 0% | 2.9464 | 0 | 0 | 0 | 53.9163 | FALSE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1.025 | 1.75 | 13.8473 | 124.4306 | 1.75 | 73.66% | 26.34% | 0.12214 | 0.78865 | 1.1278 | 1.3818 | 0.19716 | 0.28194 | 30.52% | 38.91% | 0% | 26.34% | 0% | 2.9464 | 0 | 0 | 0 | 53.9163 | FALSE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1.025 | 1.8 | 13.8473 | 127.9858 | 1.8 | 73.66% | 26.34% | 0.12214 | 0.78865 | 1.1278 | 1.3818 | 0.19716 | 0.28194 | 31.87% | 40.25% | 0% | 26.34% | 0% | 2.9464 | 0 | 0 | 0 | 53.9163 | FALSE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1.05 | 1 | 14.1851 | 71.1032 | 1.05 | 3.19% | 96.81% | 5.0646 | 10.3385 | 12.1842 | 14.5098 | 13.5096 | 13.5096 | 10% | 10% | 96.81% | 0.2% | 96.81% | 3.5772 | 3.1667 | 0 | 0 | 48.9738 | FALSE | FALSE | FALSE | TRUE
4 | 0 | 0 | 1.05 | 1.05 | 14.1851 | 74.6584 | 1.05 | 22.62% | 77.38% | 2.9217 | 8.1535 | 10.0915 | 12.5334 | 13.5096 | 13.5096 | 10% | 10% | 77.34% | 0.2% | 77.34% | 3.743 | 3.3333 | 0 | 0 | 51.1168 | FALSE | FALSE | FALSE | TRUE
4 | 0 | 0 | 1.05 | 1.1 | 14.1851 | 78.2135 | 1.1 | 51.16% | 48.84% | 1.4325 | 5.9685 | 7.9987 | 10.5569 | 13.5096 | 13.5096 | 10% | 10.15% | 48.74% | 0.2% | 48.74% | 3.865 | 3.5 | 0 | 0 | 52.6059 | FALSE | FALSE | FALSE | TRUE
4 | 0 | 0 | 1.05 | 1.15 | 14.1851 | 81.7687 | 1.15 | 73.91% | 26.09% | 0.59376 | 3.7835 | 5.906 | 8.5805 | 13.5096 | 13.5096 | 10% | 13.51% | 25.96% | 0.2% | 25.96% | 3.9368 | 3.6667 | 0 | 0 | 53.4447 | FALSE | FALSE | FALSE | TRUE
4 | 0 | 0 | 1.05 | 1.2 | 14.1851 | 85.3238 | 1.2 | 88.42% | 11.58% | 0.19352 | 1.5985 | 3.8133 | 6.6041 | 13.5096 | 13.5096 | 10% | 16.59% | 11.4% | 0.2% | 11.4% | 3.9726 | 3.8333 | 0 | 0 | 53.8449 | FALSE | FALSE | FALSE | TRUE
4 | 0 | 0 | 1.05 | 1.25 | 14.1851 | 88.879 | 1.25 | 96.25% | 3.75% | 0.045179 | 0 | 1.7206 | 4.6276 | 0 | 13.5096 | 10.74% | 19.42% | 3.55% | 0.2% | 3.55% | 3.987 | 4 | 0 | 0 | 53.9933 | TRUE | FALSE | FALSE | TRUE
4 | 0 | 0 | 1.05 | 1.3 | 14.1851 | 92.4342 | 1.3 | 99.11% | 0.89% | 0.0055399 | 0 | 0 | 2.6512 | 0 | 0 | 13.4% | 22.04% | 0.69% | 0.2% | 0.69% | 3.9912 | 4 | 0 | 0 | 54.0329 | TRUE | TRUE | FALSE | TRUE
4 | 0 | 0 | 1.05 | 1.35 | 14.1851 | 95.9893 | 1.35 | 99.78% | 0.22% | 0.00018231 | 0 | 0 | 0.67476 | 0 | 0 | 15.85% | 24.45% | 0.02% | 0.2% | 0.02% | 3.992 | 4 | 0 | 0 | 54.0383 | TRUE | TRUE | FALSE | TRUE
4 | 0 | 0 | 1.05 | 1.4 | 14.1851 | 99.5445 | 1.4 | 99.8% | 0.2% | 8.0281e-05 | 0 | 0 | 0.097512 | 0 | 0 | 18.13% | 26.7% | 0% | 0.2% | 0% | 3.992 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | FALSE | TRUE
4 | 0 | 0 | 1.05 | 1.45 | 14.1851 | 103.0996 | 1.45 | 99.8% | 0.2% | 8.0281e-05 | 0 | 0 | 0.097512 | 0 | 0 | 20.25% | 28.79% | 0% | 0.2% | 0% | 3.992 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | FALSE | FALSE
4 | 0 | 0 | 1.05 | 1.5 | 14.1851 | 106.6548 | 1.5 | 99.8% | 0.2% | 8.0281e-05 | 0 | 0 | 0.097512 | 0 | 0 | 22.22% | 30.75% | 0% | 0.2% | 0% | 3.992 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | FALSE | FALSE
4 | 0 | 0 | 1.05 | 1.55 | 14.1851 | 110.21 | 1.55 | 99.8% | 0.2% | 8.0281e-05 | 0 | 0 | 0.097512 | 0 | 0 | 24.07% | 32.57% | 0% | 0.2% | 0% | 3.992 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | FALSE | FALSE
4 | 0 | 0 | 1.05 | 1.6 | 14.1851 | 113.7651 | 1.6 | 99.8% | 0.2% | 8.0281e-05 | 0 | 0 | 0.097512 | 0 | 0 | 25.81% | 34.29% | 0% | 0.2% | 0% | 3.992 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | FALSE | FALSE
4 | 0 | 0 | 1.05 | 1.65 | 14.1851 | 117.3203 | 1.65 | 99.8% | 0.2% | 8.0281e-05 | 0 | 0 | 0.097512 | 0 | 0 | 27.44% | 35.88% | 0% | 0.2% | 0% | 3.992 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | FALSE | FALSE
4 | 0 | 0 | 1.05 | 1.7 | 14.1851 | 120.8754 | 1.7 | 99.8% | 0.2% | 8.0281e-05 | 0 | 0 | 0.097512 | 0 | 0 | 28.98% | 37.38% | 0% | 0.2% | 0% | 3.992 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | FALSE | FALSE
4 | 0 | 0 | 1.05 | 1.75 | 14.1851 | 124.4306 | 1.75 | 99.8% | 0.2% | 8.0281e-05 | 0 | 0 | 0.097512 | 0 | 0 | 30.42% | 38.82% | 0% | 0.2% | 0% | 3.992 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | FALSE | FALSE
4 | 0 | 0 | 1.05 | 1.8 | 14.1851 | 127.9858 | 1.8 | 99.8% | 0.2% | 8.0281e-05 | 0 | 0 | 0.097512 | 0 | 0 | 31.8% | 40.16% | 0% | 0.2% | 0% | 3.992 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | FALSE | FALSE
4 | 0 | 0 | 1.075 | 1 | 14.5228 | 71.1032 | 1.075 | 3.19% | 96.81% | 5.0646 | 10.3385 | 12.1842 | 14.5098 | 13.5096 | 13.5096 | 10% | 10% | 96.81% | 0% | 96.81% | 3.5843 | 3.1667 | 0 | 0 | 48.9738 | FALSE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1.075 | 1.05 | 14.5228 | 74.6584 | 1.075 | 22.66% | 77.34% | 2.9217 | 8.1535 | 10.0915 | 12.5334 | 13.5096 | 13.5096 | 10% | 10% | 77.34% | 0% | 77.34% | 3.7505 | 3.3333 | 0 | 0 | 51.1168 | FALSE | FALSE | FALSE | TRUE
4 | 0 | 0 | 1.075 | 1.1 | 14.5228 | 78.2135 | 1.1 | 51.26% | 48.74% | 1.4325 | 5.9685 | 7.9987 | 10.5569 | 13.5096 | 13.5096 | 10% | 10.15% | 48.74% | 0% | 48.74% | 3.8727 | 3.5 | 0 | 0 | 52.6059 | FALSE | FALSE | FALSE | TRUE
4 | 0 | 0 | 1.075 | 1.15 | 14.5228 | 81.7687 | 1.15 | 74.04% | 25.96% | 0.5937 | 3.7835 | 5.906 | 8.5805 | 13.5096 | 13.5096 | 10% | 13.51% | 25.96% | 0% | 25.96% | 3.9447 | 3.6667 | 0 | 0 | 53.4447 | FALSE | FALSE | FALSE | TRUE
4 | 0 | 0 | 1.075 | 1.2 | 14.5228 | 85.3238 | 1.2 | 88.6% | 11.4% | 0.19344 | 1.5985 | 3.8133 | 6.6041 | 13.5096 | 13.5096 | 10% | 16.59% | 11.4% | 0% | 11.4% | 3.9805 | 3.8333 | 0 | 0 | 53.845 | FALSE | FALSE | FALSE | TRUE
4 | 0 | 0 | 1.075 | 1.25 | 14.5228 | 88.879 | 1.25 | 96.45% | 3.55% | 0.045098 | 0 | 1.7206 | 4.6276 | 0 | 13.5096 | 10.74% | 19.42% | 3.55% | 0% | 3.55% | 3.995 | 4 | 0 | 0 | 53.9933 | TRUE | FALSE | FALSE | TRUE
4 | 0 | 0 | 1.075 | 1.3 | 14.5228 | 92.4342 | 1.3 | 99.31% | 0.69% | 0.0054596 | 0 | 0 | 2.6512 | 0 | 0 | 13.4% | 22.04% | 0.69% | 0% | 0.69% | 3.9992 | 4 | 0 | 0 | 54.033 | TRUE | TRUE | FALSE | TRUE
4 | 0 | 0 | 1.075 | 1.35 | 14.5228 | 95.9893 | 1.35 | 99.98% | 0.02% | 0.00010203 | 0 | 0 | 0.67476 | 0 | 0 | 15.85% | 24.45% | 0.02% | 0% | 0.02% | 4 | 4 | 0 | 0 | 54.0383 | TRUE | TRUE | TRUE | TRUE
4 | 0 | 0 | 1.075 | 1.4 | 14.5228 | 99.5445 | 1.4 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 18.13% | 26.7% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | TRUE
4 | 0 | 0 | 1.075 | 1.45 | 14.5228 | 103.0996 | 1.45 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 20.25% | 28.79% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.075 | 1.5 | 14.5228 | 106.6548 | 1.5 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 22.22% | 30.75% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.075 | 1.55 | 14.5228 | 110.21 | 1.55 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 24.07% | 32.57% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.075 | 1.6 | 14.5228 | 113.7651 | 1.6 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 25.81% | 34.29% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.075 | 1.65 | 14.5228 | 117.3203 | 1.65 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 27.44% | 35.88% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.075 | 1.7 | 14.5228 | 120.8754 | 1.7 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 28.98% | 37.38% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.075 | 1.75 | 14.5228 | 124.4306 | 1.75 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 30.42% | 38.82% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.075 | 1.8 | 14.5228 | 127.9858 | 1.8 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 31.8% | 40.16% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.1 | 1 | 14.8606 | 71.1032 | 1.1 | 3.19% | 96.81% | 5.0646 | 10.3385 | 12.1842 | 14.5098 | 13.5096 | 13.5096 | 10% | 10% | 96.81% | 0% | 96.81% | 3.5843 | 3.1667 | 0 | 0 | 48.9738 | FALSE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1.1 | 1.05 | 14.8606 | 74.6584 | 1.1 | 22.66% | 77.34% | 2.9217 | 8.1535 | 10.0915 | 12.5334 | 13.5096 | 13.5096 | 10% | 10% | 77.34% | 0% | 77.34% | 3.7505 | 3.3333 | 0 | 0 | 51.1168 | FALSE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1.1 | 1.1 | 14.8606 | 78.2135 | 1.1 | 51.26% | 48.74% | 1.4325 | 5.9685 | 7.9987 | 10.5569 | 13.5096 | 13.5096 | 10% | 10.15% | 48.74% | 0% | 48.74% | 3.8727 | 3.5 | 0 | 0 | 52.6059 | FALSE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1.1 | 1.15 | 14.8606 | 81.7687 | 1.15 | 74.04% | 25.96% | 0.5937 | 3.7835 | 5.906 | 8.5805 | 13.5096 | 13.5096 | 10% | 13.51% | 25.96% | 0% | 25.96% | 3.9447 | 3.6667 | 0 | 0 | 53.4447 | FALSE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1.1 | 1.2 | 14.8606 | 85.3238 | 1.2 | 88.6% | 11.4% | 0.19344 | 1.5985 | 3.8133 | 6.6041 | 13.5096 | 13.5096 | 10% | 16.59% | 11.4% | 0% | 11.4% | 3.9805 | 3.8333 | 0 | 0 | 53.845 | FALSE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1.1 | 1.25 | 14.8606 | 88.879 | 1.25 | 96.45% | 3.55% | 0.045098 | 0 | 1.7206 | 4.6276 | 0 | 13.5096 | 10.74% | 19.42% | 3.55% | 0% | 3.55% | 3.995 | 4 | 0 | 0 | 53.9933 | TRUE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1.1 | 1.3 | 14.8606 | 92.4342 | 1.3 | 99.31% | 0.69% | 0.0054596 | 0 | 0 | 2.6512 | 0 | 0 | 13.4% | 22.04% | 0.69% | 0% | 0.69% | 3.9992 | 4 | 0 | 0 | 54.033 | TRUE | TRUE | FALSE | FALSE
4 | 0 | 0 | 1.1 | 1.35 | 14.8606 | 95.9893 | 1.35 | 99.98% | 0.02% | 0.00010203 | 0 | 0 | 0.67476 | 0 | 0 | 15.85% | 24.45% | 0.02% | 0% | 0.02% | 4 | 4 | 0 | 0 | 54.0383 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.1 | 1.4 | 14.8606 | 99.5445 | 1.4 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 18.13% | 26.7% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.1 | 1.45 | 14.8606 | 103.0996 | 1.45 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 20.25% | 28.79% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.1 | 1.5 | 14.8606 | 106.6548 | 1.5 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 22.22% | 30.75% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.1 | 1.55 | 14.8606 | 110.21 | 1.55 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 24.07% | 32.57% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.1 | 1.6 | 14.8606 | 113.7651 | 1.6 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 25.81% | 34.29% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.1 | 1.65 | 14.8606 | 117.3203 | 1.65 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 27.44% | 35.88% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.1 | 1.7 | 14.8606 | 120.8754 | 1.7 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 28.98% | 37.38% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.1 | 1.75 | 14.8606 | 124.4306 | 1.75 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 30.42% | 38.82% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.1 | 1.8 | 14.8606 | 127.9858 | 1.8 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 31.8% | 40.16% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.125 | 1 | 15.1983 | 71.1032 | 1.125 | 3.19% | 96.81% | 5.0646 | 10.3385 | 12.1842 | 14.5098 | 13.5096 | 13.5096 | 10% | 10% | 96.81% | 0% | 96.81% | 3.5843 | 3.1667 | 0 | 0 | 48.9738 | FALSE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1.125 | 1.05 | 15.1983 | 74.6584 | 1.125 | 22.66% | 77.34% | 2.9217 | 8.1535 | 10.0915 | 12.5334 | 13.5096 | 13.5096 | 10% | 10% | 77.34% | 0% | 77.34% | 3.7505 | 3.3333 | 0 | 0 | 51.1168 | FALSE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1.125 | 1.1 | 15.1983 | 78.2135 | 1.125 | 51.26% | 48.74% | 1.4325 | 5.9685 | 7.9987 | 10.5569 | 13.5096 | 13.5096 | 10% | 10.15% | 48.74% | 0% | 48.74% | 3.8727 | 3.5 | 0 | 0 | 52.6059 | FALSE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1.125 | 1.15 | 15.1983 | 81.7687 | 1.15 | 74.04% | 25.96% | 0.5937 | 3.7835 | 5.906 | 8.5805 | 13.5096 | 13.5096 | 10% | 13.51% | 25.96% | 0% | 25.96% | 3.9447 | 3.6667 | 0 | 0 | 53.4447 | FALSE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1.125 | 1.2 | 15.1983 | 85.3238 | 1.2 | 88.6% | 11.4% | 0.19344 | 1.5985 | 3.8133 | 6.6041 | 13.5096 | 13.5096 | 10% | 16.59% | 11.4% | 0% | 11.4% | 3.9805 | 3.8333 | 0 | 0 | 53.845 | FALSE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1.125 | 1.25 | 15.1983 | 88.879 | 1.25 | 96.45% | 3.55% | 0.045098 | 0 | 1.7206 | 4.6276 | 0 | 13.5096 | 10.74% | 19.42% | 3.55% | 0% | 3.55% | 3.995 | 4 | 0 | 0 | 53.9933 | TRUE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1.125 | 1.3 | 15.1983 | 92.4342 | 1.3 | 99.31% | 0.69% | 0.0054596 | 0 | 0 | 2.6512 | 0 | 0 | 13.4% | 22.04% | 0.69% | 0% | 0.69% | 3.9992 | 4 | 0 | 0 | 54.033 | TRUE | TRUE | FALSE | FALSE
4 | 0 | 0 | 1.125 | 1.35 | 15.1983 | 95.9893 | 1.35 | 99.98% | 0.02% | 0.00010203 | 0 | 0 | 0.67476 | 0 | 0 | 15.85% | 24.45% | 0.02% | 0% | 0.02% | 4 | 4 | 0 | 0 | 54.0383 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.125 | 1.4 | 15.1983 | 99.5445 | 1.4 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 18.13% | 26.7% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.125 | 1.45 | 15.1983 | 103.0996 | 1.45 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 20.25% | 28.79% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.125 | 1.5 | 15.1983 | 106.6548 | 1.5 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 22.22% | 30.75% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.125 | 1.55 | 15.1983 | 110.21 | 1.55 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 24.07% | 32.57% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.125 | 1.6 | 15.1983 | 113.7651 | 1.6 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 25.81% | 34.29% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.125 | 1.65 | 15.1983 | 117.3203 | 1.65 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 27.44% | 35.88% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.125 | 1.7 | 15.1983 | 120.8754 | 1.7 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 28.98% | 37.38% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.125 | 1.75 | 15.1983 | 124.4306 | 1.75 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 30.42% | 38.82% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.125 | 1.8 | 15.1983 | 127.9858 | 1.8 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 31.8% | 40.16% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.15 | 1 | 15.536 | 71.1032 | 1.15 | 3.19% | 96.81% | 5.0646 | 10.3385 | 12.1842 | 14.5098 | 13.5096 | 13.5096 | 10% | 10% | 96.81% | 0% | 96.81% | 3.5843 | 3.1667 | 0 | 0 | 48.9738 | FALSE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1.15 | 1.05 | 15.536 | 74.6584 | 1.15 | 22.66% | 77.34% | 2.9217 | 8.1535 | 10.0915 | 12.5334 | 13.5096 | 13.5096 | 10% | 10% | 77.34% | 0% | 77.34% | 3.7505 | 3.3333 | 0 | 0 | 51.1168 | FALSE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1.15 | 1.1 | 15.536 | 78.2135 | 1.15 | 51.26% | 48.74% | 1.4325 | 5.9685 | 7.9987 | 10.5569 | 13.5096 | 13.5096 | 10% | 10.15% | 48.74% | 0% | 48.74% | 3.8727 | 3.5 | 0 | 0 | 52.6059 | FALSE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1.15 | 1.15 | 15.536 | 81.7687 | 1.15 | 74.04% | 25.96% | 0.5937 | 3.7835 | 5.906 | 8.5805 | 13.5096 | 13.5096 | 10% | 13.51% | 25.96% | 0% | 25.96% | 3.9447 | 3.6667 | 0 | 0 | 53.4447 | FALSE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1.15 | 1.2 | 15.536 | 85.3238 | 1.2 | 88.6% | 11.4% | 0.19344 | 1.5985 | 3.8133 | 6.6041 | 13.5096 | 13.5096 | 10% | 16.59% | 11.4% | 0% | 11.4% | 3.9805 | 3.8333 | 0 | 0 | 53.845 | FALSE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1.15 | 1.25 | 15.536 | 88.879 | 1.25 | 96.45% | 3.55% | 0.045098 | 0 | 1.7206 | 4.6276 | 0 | 13.5096 | 10.74% | 19.42% | 3.55% | 0% | 3.55% | 3.995 | 4 | 0 | 0 | 53.9933 | TRUE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1.15 | 1.3 | 15.536 | 92.4342 | 1.3 | 99.31% | 0.69% | 0.0054596 | 0 | 0 | 2.6512 | 0 | 0 | 13.4% | 22.04% | 0.69% | 0% | 0.69% | 3.9992 | 4 | 0 | 0 | 54.033 | TRUE | TRUE | FALSE | FALSE
4 | 0 | 0 | 1.15 | 1.35 | 15.536 | 95.9893 | 1.35 | 99.98% | 0.02% | 0.00010203 | 0 | 0 | 0.67476 | 0 | 0 | 15.85% | 24.45% | 0.02% | 0% | 0.02% | 4 | 4 | 0 | 0 | 54.0383 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.15 | 1.4 | 15.536 | 99.5445 | 1.4 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 18.13% | 26.7% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.15 | 1.45 | 15.536 | 103.0996 | 1.45 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 20.25% | 28.79% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.15 | 1.5 | 15.536 | 106.6548 | 1.5 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 22.22% | 30.75% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.15 | 1.55 | 15.536 | 110.21 | 1.55 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 24.07% | 32.57% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.15 | 1.6 | 15.536 | 113.7651 | 1.6 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 25.81% | 34.29% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.15 | 1.65 | 15.536 | 117.3203 | 1.65 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 27.44% | 35.88% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.15 | 1.7 | 15.536 | 120.8754 | 1.7 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 28.98% | 37.38% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.15 | 1.75 | 15.536 | 124.4306 | 1.75 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 30.42% | 38.82% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.15 | 1.8 | 15.536 | 127.9858 | 1.8 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 31.8% | 40.16% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.175 | 1 | 15.8738 | 71.1032 | 1.175 | 3.19% | 96.81% | 5.0646 | 10.3385 | 12.1842 | 14.5098 | 13.5096 | 13.5096 | 10% | 10% | 96.81% | 0% | 96.81% | 3.5843 | 3.1667 | 0 | 0 | 48.9738 | FALSE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1.175 | 1.05 | 15.8738 | 74.6584 | 1.175 | 22.66% | 77.34% | 2.9217 | 8.1535 | 10.0915 | 12.5334 | 13.5096 | 13.5096 | 10% | 10% | 77.34% | 0% | 77.34% | 3.7505 | 3.3333 | 0 | 0 | 51.1168 | FALSE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1.175 | 1.1 | 15.8738 | 78.2135 | 1.175 | 51.26% | 48.74% | 1.4325 | 5.9685 | 7.9987 | 10.5569 | 13.5096 | 13.5096 | 10% | 10.15% | 48.74% | 0% | 48.74% | 3.8727 | 3.5 | 0 | 0 | 52.6059 | FALSE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1.175 | 1.15 | 15.8738 | 81.7687 | 1.175 | 74.04% | 25.96% | 0.5937 | 3.7835 | 5.906 | 8.5805 | 13.5096 | 13.5096 | 10% | 13.51% | 25.96% | 0% | 25.96% | 3.9447 | 3.6667 | 0 | 0 | 53.4447 | FALSE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1.175 | 1.2 | 15.8738 | 85.3238 | 1.2 | 88.6% | 11.4% | 0.19344 | 1.5985 | 3.8133 | 6.6041 | 13.5096 | 13.5096 | 10% | 16.59% | 11.4% | 0% | 11.4% | 3.9805 | 3.8333 | 0 | 0 | 53.845 | FALSE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1.175 | 1.25 | 15.8738 | 88.879 | 1.25 | 96.45% | 3.55% | 0.045098 | 0 | 1.7206 | 4.6276 | 0 | 13.5096 | 10.74% | 19.42% | 3.55% | 0% | 3.55% | 3.995 | 4 | 0 | 0 | 53.9933 | TRUE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1.175 | 1.3 | 15.8738 | 92.4342 | 1.3 | 99.31% | 0.69% | 0.0054596 | 0 | 0 | 2.6512 | 0 | 0 | 13.4% | 22.04% | 0.69% | 0% | 0.69% | 3.9992 | 4 | 0 | 0 | 54.033 | TRUE | TRUE | FALSE | FALSE
4 | 0 | 0 | 1.175 | 1.35 | 15.8738 | 95.9893 | 1.35 | 99.98% | 0.02% | 0.00010203 | 0 | 0 | 0.67476 | 0 | 0 | 15.85% | 24.45% | 0.02% | 0% | 0.02% | 4 | 4 | 0 | 0 | 54.0383 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.175 | 1.4 | 15.8738 | 99.5445 | 1.4 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 18.13% | 26.7% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.175 | 1.45 | 15.8738 | 103.0996 | 1.45 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 20.25% | 28.79% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.175 | 1.5 | 15.8738 | 106.6548 | 1.5 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 22.22% | 30.75% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.175 | 1.55 | 15.8738 | 110.21 | 1.55 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 24.07% | 32.57% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.175 | 1.6 | 15.8738 | 113.7651 | 1.6 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 25.81% | 34.29% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.175 | 1.65 | 15.8738 | 117.3203 | 1.65 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 27.44% | 35.88% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.175 | 1.7 | 15.8738 | 120.8754 | 1.7 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 28.98% | 37.38% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.175 | 1.75 | 15.8738 | 124.4306 | 1.75 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 30.42% | 38.82% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.175 | 1.8 | 15.8738 | 127.9858 | 1.8 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 31.8% | 40.16% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.2 | 1 | 16.2115 | 71.1032 | 1.2 | 3.19% | 96.81% | 5.0646 | 10.3385 | 12.1842 | 14.5098 | 13.5096 | 13.5096 | 10% | 10% | 96.81% | 0% | 96.81% | 3.5843 | 3.1667 | 0 | 0 | 48.9738 | FALSE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1.2 | 1.05 | 16.2115 | 74.6584 | 1.2 | 22.66% | 77.34% | 2.9217 | 8.1535 | 10.0915 | 12.5334 | 13.5096 | 13.5096 | 10% | 10% | 77.34% | 0% | 77.34% | 3.7505 | 3.3333 | 0 | 0 | 51.1168 | FALSE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1.2 | 1.1 | 16.2115 | 78.2135 | 1.2 | 51.26% | 48.74% | 1.4325 | 5.9685 | 7.9987 | 10.5569 | 13.5096 | 13.5096 | 10% | 10.15% | 48.74% | 0% | 48.74% | 3.8727 | 3.5 | 0 | 0 | 52.6059 | FALSE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1.2 | 1.15 | 16.2115 | 81.7687 | 1.2 | 74.04% | 25.96% | 0.5937 | 3.7835 | 5.906 | 8.5805 | 13.5096 | 13.5096 | 10% | 13.51% | 25.96% | 0% | 25.96% | 3.9447 | 3.6667 | 0 | 0 | 53.4447 | FALSE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1.2 | 1.2 | 16.2115 | 85.3238 | 1.2 | 88.6% | 11.4% | 0.19344 | 1.5985 | 3.8133 | 6.6041 | 13.5096 | 13.5096 | 10% | 16.59% | 11.4% | 0% | 11.4% | 3.9805 | 3.8333 | 0 | 0 | 53.845 | FALSE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1.2 | 1.25 | 16.2115 | 88.879 | 1.25 | 96.45% | 3.55% | 0.045098 | 0 | 1.7206 | 4.6276 | 0 | 13.5096 | 10.74% | 19.42% | 3.55% | 0% | 3.55% | 3.995 | 4 | 0 | 0 | 53.9933 | TRUE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1.2 | 1.3 | 16.2115 | 92.4342 | 1.3 | 99.31% | 0.69% | 0.0054596 | 0 | 0 | 2.6512 | 0 | 0 | 13.4% | 22.04% | 0.69% | 0% | 0.69% | 3.9992 | 4 | 0 | 0 | 54.033 | TRUE | TRUE | FALSE | FALSE
4 | 0 | 0 | 1.2 | 1.35 | 16.2115 | 95.9893 | 1.35 | 99.98% | 0.02% | 0.00010203 | 0 | 0 | 0.67476 | 0 | 0 | 15.85% | 24.45% | 0.02% | 0% | 0.02% | 4 | 4 | 0 | 0 | 54.0383 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.2 | 1.4 | 16.2115 | 99.5445 | 1.4 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 18.13% | 26.7% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.2 | 1.45 | 16.2115 | 103.0996 | 1.45 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 20.25% | 28.79% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.2 | 1.5 | 16.2115 | 106.6548 | 1.5 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 22.22% | 30.75% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.2 | 1.55 | 16.2115 | 110.21 | 1.55 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 24.07% | 32.57% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.2 | 1.6 | 16.2115 | 113.7651 | 1.6 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 25.81% | 34.29% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.2 | 1.65 | 16.2115 | 117.3203 | 1.65 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 27.44% | 35.88% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.2 | 1.7 | 16.2115 | 120.8754 | 1.7 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 28.98% | 37.38% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.2 | 1.75 | 16.2115 | 124.4306 | 1.75 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 30.42% | 38.82% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.2 | 1.8 | 16.2115 | 127.9858 | 1.8 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 31.8% | 40.16% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.225 | 1 | 16.5493 | 71.1032 | 1.225 | 3.19% | 96.81% | 5.0646 | 10.3385 | 12.1842 | 14.5098 | 13.5096 | 13.5096 | 10% | 10% | 96.81% | 0% | 96.81% | 3.5843 | 3.1667 | 0 | 0 | 48.9738 | FALSE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1.225 | 1.05 | 16.5493 | 74.6584 | 1.225 | 22.66% | 77.34% | 2.9217 | 8.1535 | 10.0915 | 12.5334 | 13.5096 | 13.5096 | 10% | 10% | 77.34% | 0% | 77.34% | 3.7505 | 3.3333 | 0 | 0 | 51.1168 | FALSE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1.225 | 1.1 | 16.5493 | 78.2135 | 1.225 | 51.26% | 48.74% | 1.4325 | 5.9685 | 7.9987 | 10.5569 | 13.5096 | 13.5096 | 10% | 10.15% | 48.74% | 0% | 48.74% | 3.8727 | 3.5 | 0 | 0 | 52.6059 | FALSE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1.225 | 1.15 | 16.5493 | 81.7687 | 1.225 | 74.04% | 25.96% | 0.5937 | 3.7835 | 5.906 | 8.5805 | 13.5096 | 13.5096 | 10% | 13.51% | 25.96% | 0% | 25.96% | 3.9447 | 3.6667 | 0 | 0 | 53.4447 | FALSE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1.225 | 1.2 | 16.5493 | 85.3238 | 1.225 | 88.6% | 11.4% | 0.19344 | 1.5985 | 3.8133 | 6.6041 | 13.5096 | 13.5096 | 10% | 16.59% | 11.4% | 0% | 11.4% | 3.9805 | 3.8333 | 0 | 0 | 53.845 | FALSE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1.225 | 1.25 | 16.5493 | 88.879 | 1.25 | 96.45% | 3.55% | 0.045098 | 0 | 1.7206 | 4.6276 | 0 | 13.5096 | 10.74% | 19.42% | 3.55% | 0% | 3.55% | 3.995 | 4 | 0 | 0 | 53.9933 | TRUE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1.225 | 1.3 | 16.5493 | 92.4342 | 1.3 | 99.31% | 0.69% | 0.0054596 | 0 | 0 | 2.6512 | 0 | 0 | 13.4% | 22.04% | 0.69% | 0% | 0.69% | 3.9992 | 4 | 0 | 0 | 54.033 | TRUE | TRUE | FALSE | FALSE
4 | 0 | 0 | 1.225 | 1.35 | 16.5493 | 95.9893 | 1.35 | 99.98% | 0.02% | 0.00010203 | 0 | 0 | 0.67476 | 0 | 0 | 15.85% | 24.45% | 0.02% | 0% | 0.02% | 4 | 4 | 0 | 0 | 54.0383 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.225 | 1.4 | 16.5493 | 99.5445 | 1.4 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 18.13% | 26.7% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.225 | 1.45 | 16.5493 | 103.0996 | 1.45 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 20.25% | 28.79% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.225 | 1.5 | 16.5493 | 106.6548 | 1.5 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 22.22% | 30.75% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.225 | 1.55 | 16.5493 | 110.21 | 1.55 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 24.07% | 32.57% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.225 | 1.6 | 16.5493 | 113.7651 | 1.6 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 25.81% | 34.29% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.225 | 1.65 | 16.5493 | 117.3203 | 1.65 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 27.44% | 35.88% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.225 | 1.7 | 16.5493 | 120.8754 | 1.7 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 28.98% | 37.38% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.225 | 1.75 | 16.5493 | 124.4306 | 1.75 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 30.42% | 38.82% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.225 | 1.8 | 16.5493 | 127.9858 | 1.8 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 31.8% | 40.16% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.25 | 1 | 16.887 | 71.1032 | 1.25 | 3.19% | 96.81% | 5.0646 | 10.3385 | 12.1842 | 14.5098 | 13.5096 | 13.5096 | 10% | 10% | 96.81% | 0% | 96.81% | 3.5843 | 3.1667 | 0 | 0 | 48.9738 | FALSE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1.25 | 1.05 | 16.887 | 74.6584 | 1.25 | 22.66% | 77.34% | 2.9217 | 8.1535 | 10.0915 | 12.5334 | 13.5096 | 13.5096 | 10% | 10% | 77.34% | 0% | 77.34% | 3.7505 | 3.3333 | 0 | 0 | 51.1168 | FALSE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1.25 | 1.1 | 16.887 | 78.2135 | 1.25 | 51.26% | 48.74% | 1.4325 | 5.9685 | 7.9987 | 10.5569 | 13.5096 | 13.5096 | 10% | 10.15% | 48.74% | 0% | 48.74% | 3.8727 | 3.5 | 0 | 0 | 52.6059 | FALSE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1.25 | 1.15 | 16.887 | 81.7687 | 1.25 | 74.04% | 25.96% | 0.5937 | 3.7835 | 5.906 | 8.5805 | 13.5096 | 13.5096 | 10% | 13.51% | 25.96% | 0% | 25.96% | 3.9447 | 3.6667 | 0 | 0 | 53.4447 | FALSE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1.25 | 1.2 | 16.887 | 85.3238 | 1.25 | 88.6% | 11.4% | 0.19344 | 1.5985 | 3.8133 | 6.6041 | 13.5096 | 13.5096 | 10% | 16.59% | 11.4% | 0% | 11.4% | 3.9805 | 3.8333 | 0 | 0 | 53.845 | FALSE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1.25 | 1.25 | 16.887 | 88.879 | 1.25 | 96.45% | 3.55% | 0.045098 | 0 | 1.7206 | 4.6276 | 0 | 13.5096 | 10.74% | 19.42% | 3.55% | 0% | 3.55% | 3.995 | 4 | 0 | 0 | 53.9933 | TRUE | FALSE | FALSE | FALSE
4 | 0 | 0 | 1.25 | 1.3 | 16.887 | 92.4342 | 1.3 | 99.31% | 0.69% | 0.0054596 | 0 | 0 | 2.6512 | 0 | 0 | 13.4% | 22.04% | 0.69% | 0% | 0.69% | 3.9992 | 4 | 0 | 0 | 54.033 | TRUE | TRUE | FALSE | FALSE
4 | 0 | 0 | 1.25 | 1.35 | 16.887 | 95.9893 | 1.35 | 99.98% | 0.02% | 0.00010203 | 0 | 0 | 0.67476 | 0 | 0 | 15.85% | 24.45% | 0.02% | 0% | 0.02% | 4 | 4 | 0 | 0 | 54.0383 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.25 | 1.4 | 16.887 | 99.5445 | 1.4 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 18.13% | 26.7% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.25 | 1.45 | 16.887 | 103.0996 | 1.45 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 20.25% | 28.79% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.25 | 1.5 | 16.887 | 106.6548 | 1.5 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 22.22% | 30.75% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.25 | 1.55 | 16.887 | 110.21 | 1.55 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 24.07% | 32.57% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.25 | 1.6 | 16.887 | 113.7651 | 1.6 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 25.81% | 34.29% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.25 | 1.65 | 16.887 | 117.3203 | 1.65 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 27.44% | 35.88% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.25 | 1.7 | 16.887 | 120.8754 | 1.7 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 28.98% | 37.38% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.25 | 1.75 | 16.887 | 124.4306 | 1.75 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 30.42% | 38.82% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 0 | 0 | 1.25 | 1.8 | 16.887 | 127.9858 | 1.8 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 31.8% | 40.16% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1 | 1 | 13.5096 | 71.1032 | 1 | 30.4% | 69.6% | 2.7623 | 9.0815 | 11.5056 | 14.5098 | 13.5096 | 13.5096 | 10% | 10% | 54.65% | 68.9% | 54.65% | 1.5676 | 0 | 5.7131 | 0 | 45.563 | FALSE | FALSE | FALSE | TRUE
4 | 6.7548 | 0.5 | 1 | 1.05 | 13.5096 | 74.6584 | 1.05 | 30.95% | 69.05% | 1.6612 | 6.839 | 9.4017 | 12.5334 | 13.5096 | 13.5096 | 10% | 12.7% | 37.12% | 68.9% | 37.12% | 1.5686 | 0 | 5.7131 | 0 | 46.6641 | FALSE | FALSE | FALSE | TRUE
4 | 6.7548 | 0.5 | 1 | 1.1 | 13.5096 | 78.2135 | 1.1 | 31.09% | 68.91% | 0.9969 | 4.5962 | 7.2761 | 10.5569 | 13.5096 | 13.5096 | 10% | 16.16% | 20.77% | 68.9% | 20.77% | 1.5688 | 0 | 5.7131 | 0 | 47.3284 | FALSE | FALSE | FALSE | TRUE
4 | 6.7548 | 0.5 | 1 | 1.15 | 13.5096 | 81.7687 | 1.15 | 31.1% | 68.9% | 0.65981 | 2.472 | 5.1506 | 8.5805 | 13.5096 | 13.5096 | 10% | 19.31% | 9.91% | 68.9% | 9.91% | 1.5688 | 0 | 5.7131 | 0 | 47.6655 | FALSE | FALSE | FALSE | TRUE
4 | 6.7548 | 0.5 | 1 | 1.2 | 13.5096 | 85.3238 | 1.2 | 31.1% | 68.9% | 0.51944 | 1.9159 | 3.0276 | 6.6041 | 0.57884 | 13.5096 | 10.83% | 22.21% | 3.68% | 68.9% | 3.68% | 1.5688 | 0 | 5.7131 | 0 | 47.8058 | FALSE | FALSE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1 | 1.25 | 13.5096 | 88.879 | 1.25 | 31.1% | 68.9% | 0.47466 | 1.7573 | 2.2949 | 4.6276 | 0.50617 | 1.0206 | 13.61% | 24.87% | 1.07% | 68.9% | 1.07% | 1.5688 | 0 | 5.7131 | 0 | 47.8506 | FALSE | FALSE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1 | 1.3 | 13.5096 | 92.4342 | 1.3 | 31.1% | 68.9% | 0.4636 | 1.7344 | 2.2462 | 2.6661 | 0.48723 | 0.59768 | 16.19% | 27.33% | 0.14% | 68.9% | 0.14% | 1.5688 | 0 | 5.7131 | 0 | 47.8617 | FALSE | FALSE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1 | 1.35 | 13.5096 | 95.9893 | 1.35 | 31.1% | 68.9% | 0.46246 | 1.7281 | 2.2444 | 2.6661 | 0.48454 | 0.59229 | 18.61% | 29.59% | 0% | 68.9% | 0% | 1.5688 | 0 | 5.7131 | 0 | 47.8628 | FALSE | FALSE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1 | 1.4 | 13.5096 | 99.5445 | 1.4 | 31.1% | 68.9% | 0.46246 | 1.7281 | 2.2444 | 2.6661 | 0.48454 | 0.59229 | 20.82% | 31.72% | 0% | 68.9% | 0% | 1.5688 | 0 | 5.7131 | 0 | 47.8628 | FALSE | FALSE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1 | 1.45 | 13.5096 | 103.0996 | 1.45 | 31.1% | 68.9% | 0.46246 | 1.7281 | 2.2444 | 2.6661 | 0.48454 | 0.59229 | 22.9% | 33.68% | 0% | 68.9% | 0% | 1.5688 | 0 | 5.7131 | 0 | 47.8628 | FALSE | FALSE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1 | 1.5 | 13.5096 | 106.6548 | 1.5 | 31.1% | 68.9% | 0.46246 | 1.7281 | 2.2444 | 2.6661 | 0.48454 | 0.59229 | 24.83% | 35.5% | 0% | 68.9% | 0% | 1.5688 | 0 | 5.7131 | 0 | 47.8628 | FALSE | FALSE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1 | 1.55 | 13.5096 | 110.21 | 1.55 | 31.1% | 68.9% | 0.46246 | 1.7281 | 2.2444 | 2.6661 | 0.48454 | 0.59229 | 26.62% | 37.22% | 0% | 68.9% | 0% | 1.5688 | 0 | 5.7131 | 0 | 47.8628 | FALSE | FALSE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1 | 1.6 | 13.5096 | 113.7651 | 1.6 | 31.1% | 68.9% | 0.46246 | 1.7281 | 2.2444 | 2.6661 | 0.48454 | 0.59229 | 28.29% | 38.81% | 0% | 68.9% | 0% | 1.5688 | 0 | 5.7131 | 0 | 47.8628 | FALSE | FALSE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1 | 1.65 | 13.5096 | 117.3203 | 1.65 | 31.1% | 68.9% | 0.46246 | 1.7281 | 2.2444 | 2.6661 | 0.48454 | 0.59229 | 29.88% | 40.33% | 0% | 68.9% | 0% | 1.5688 | 0 | 5.7131 | 0 | 47.8628 | FALSE | FALSE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1 | 1.7 | 13.5096 | 120.8754 | 1.7 | 31.1% | 68.9% | 0.46246 | 1.7281 | 2.2444 | 2.6661 | 0.48454 | 0.59229 | 31.37% | 41.76% | 0% | 68.9% | 0% | 1.5688 | 0 | 5.7131 | 0 | 47.8628 | FALSE | FALSE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1 | 1.75 | 13.5096 | 124.4306 | 1.75 | 31.1% | 68.9% | 0.46246 | 1.7281 | 2.2444 | 2.6661 | 0.48454 | 0.59229 | 32.78% | 43.09% | 0% | 68.9% | 0% | 1.5688 | 0 | 5.7131 | 0 | 47.8628 | FALSE | FALSE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1 | 1.8 | 13.5096 | 127.9858 | 1.8 | 31.1% | 68.9% | 0.46246 | 1.7281 | 2.2444 | 2.6661 | 0.48454 | 0.59229 | 34.1% | 44.35% | 0% | 68.9% | 0% | 1.5688 | 0 | 5.7131 | 0 | 47.8628 | FALSE | FALSE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1.025 | 1 | 13.8473 | 71.1032 | 1.025 | 39.21% | 60.79% | 2.7171 | 9.0815 | 11.5056 | 14.5098 | 13.5096 | 13.5096 | 10% | 10% | 57.46% | 17.84% | 57.46% | 3.2094 | 0 | 5.7131 | 0 | 45.6082 | FALSE | FALSE | FALSE | TRUE
4 | 6.7548 | 0.5 | 1.025 | 1.05 | 13.8473 | 74.6584 | 1.05 | 50.92% | 49.08% | 1.5174 | 6.839 | 9.4017 | 12.5334 | 13.5096 | 13.5096 | 10% | 11.81% | 41.44% | 17.84% | 41.44% | 3.2824 | 0 | 5.7131 | 0 | 46.8079 | FALSE | FALSE | FALSE | TRUE
4 | 6.7548 | 0.5 | 1.025 | 1.1 | 13.8473 | 78.2135 | 1.1 | 63.46% | 36.54% | 0.74497 | 4.5962 | 7.2761 | 10.5569 | 13.5096 | 13.5096 | 10% | 15.33% | 24.71% | 17.84% | 24.71% | 3.3315 | 0 | 5.7131 | 0 | 47.5803 | FALSE | FALSE | FALSE | TRUE
4 | 6.7548 | 0.5 | 1.025 | 1.15 | 13.8473 | 81.7687 | 1.15 | 72.71% | 27.29% | 0.33319 | 2.362 | 5.1506 | 8.5805 | 13.5096 | 13.5096 | 10% | 18.52% | 12.47% | 17.84% | 12.47% | 3.359 | 0 | 5.7131 | 0 | 47.9921 | FALSE | FALSE | FALSE | TRUE
4 | 6.7548 | 0.5 | 1.025 | 1.2 | 13.8473 | 85.3238 | 1.2 | 78.24% | 21.76% | 0.14691 | 0.85068 | 3.0276 | 6.6041 | 0.35297 | 13.5096 | 10% | 21.47% | 5.09% | 17.84% | 5.09% | 3.3721 | 0 | 5.7131 | 0 | 48.1784 | FALSE | FALSE | FALSE | TRUE
4 | 6.7548 | 0.5 | 1.025 | 1.25 | 13.8473 | 88.879 | 1.25 | 80.86% | 19.14% | 0.08165 | 0.56053 | 1.1998 | 4.6276 | 0.19517 | 10.0913 | 12.79% | 24.17% | 1.54% | 17.84% | 1.54% | 3.377 | 0 | 5.7131 | 0 | 48.2436 | FALSE | FALSE | FALSE | TRUE
4 | 6.7548 | 0.5 | 1.025 | 1.3 | 13.8473 | 92.4342 | 1.3 | 81.91% | 18.09% | 0.063761 | 0.48725 | 0.98409 | 2.6512 | 0.16581 | 0.28194 | 15.42% | 26.66% | 0.31% | 17.84% | 0.31% | 3.3786 | 0 | 5.7131 | 0 | 48.2615 | FALSE | FALSE | FALSE | TRUE
4 | 6.7548 | 0.5 | 1.025 | 1.35 | 13.8473 | 95.9893 | 1.35 | 82.14% | 17.86% | 0.061284 | 0.47347 | 0.95681 | 1.3818 | 0.15934 | 0.26942 | 17.84% | 28.94% | 0.02% | 17.84% | 0.02% | 3.3789 | 0 | 5.7131 | 0 | 48.264 | FALSE | FALSE | FALSE | TRUE
4 | 6.7548 | 0.5 | 1.025 | 1.4 | 13.8473 | 99.5445 | 1.4 | 82.16% | 17.84% | 0.061182 | 0.47302 | 0.95681 | 1.3818 | 0.15916 | 0.26936 | 20.08% | 31.08% | 0% | 17.84% | 0% | 3.3789 | 0 | 5.7131 | 0 | 48.2641 | FALSE | FALSE | FALSE | TRUE
4 | 6.7548 | 0.5 | 1.025 | 1.45 | 13.8473 | 103.0996 | 1.45 | 82.16% | 17.84% | 0.061182 | 0.47302 | 0.95681 | 1.3818 | 0.15916 | 0.26936 | 22.15% | 33.08% | 0% | 17.84% | 0% | 3.3789 | 0 | 5.7131 | 0 | 48.2641 | FALSE | FALSE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1.025 | 1.5 | 13.8473 | 106.6548 | 1.5 | 82.16% | 17.84% | 0.061182 | 0.47302 | 0.95681 | 1.3818 | 0.15916 | 0.26936 | 24.1% | 34.94% | 0% | 17.84% | 0% | 3.3789 | 0 | 5.7131 | 0 | 48.2641 | FALSE | FALSE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1.025 | 1.55 | 13.8473 | 110.21 | 1.55 | 82.16% | 17.84% | 0.061182 | 0.47302 | 0.95681 | 1.3818 | 0.15916 | 0.26936 | 25.92% | 36.68% | 0% | 17.84% | 0% | 3.3789 | 0 | 5.7131 | 0 | 48.2641 | FALSE | FALSE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1.025 | 1.6 | 13.8473 | 113.7651 | 1.6 | 82.16% | 17.84% | 0.061182 | 0.47302 | 0.95681 | 1.3818 | 0.15916 | 0.26936 | 27.61% | 38.28% | 0% | 17.84% | 0% | 3.3789 | 0 | 5.7131 | 0 | 48.2641 | FALSE | FALSE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1.025 | 1.65 | 13.8473 | 117.3203 | 1.65 | 82.16% | 17.84% | 0.061182 | 0.47302 | 0.95681 | 1.3818 | 0.15916 | 0.26936 | 29.21% | 39.81% | 0% | 17.84% | 0% | 3.3789 | 0 | 5.7131 | 0 | 48.2641 | FALSE | FALSE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1.025 | 1.7 | 13.8473 | 120.8754 | 1.7 | 82.16% | 17.84% | 0.061182 | 0.47302 | 0.95681 | 1.3818 | 0.15916 | 0.26936 | 30.73% | 41.25% | 0% | 17.84% | 0% | 3.3789 | 0 | 5.7131 | 0 | 48.2641 | FALSE | FALSE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1.025 | 1.75 | 13.8473 | 124.4306 | 1.75 | 82.16% | 17.84% | 0.061182 | 0.47302 | 0.95681 | 1.3818 | 0.15916 | 0.26936 | 32.12% | 42.6% | 0% | 17.84% | 0% | 3.3789 | 0 | 5.7131 | 0 | 48.2641 | FALSE | FALSE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1.025 | 1.8 | 13.8473 | 127.9858 | 1.8 | 82.16% | 17.84% | 0.061182 | 0.47302 | 0.95681 | 1.3818 | 0.15916 | 0.26936 | 33.46% | 43.88% | 0% | 17.84% | 0% | 3.3789 | 0 | 5.7131 | 0 | 48.2641 | FALSE | FALSE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1.05 | 1 | 14.1851 | 71.1032 | 1.05 | 42.13% | 57.87% | 2.7115 | 9.0815 | 11.5056 | 14.5098 | 13.5096 | 13.5096 | 10% | 10% | 57.85% | 0.15% | 57.85% | 3.7659 | 3.25 | 5.7131 | 0 | 45.6138 | FALSE | FALSE | FALSE | TRUE
4 | 6.7548 | 0.5 | 1.05 | 1.05 | 14.1851 | 74.6584 | 1.05 | 57.86% | 42.14% | 1.4976 | 6.839 | 9.4017 | 12.5334 | 13.5096 | 13.5096 | 10% | 11.69% | 42.1% | 0.15% | 42.1% | 3.864 | 3.4167 | 5.7131 | 0 | 46.8277 | FALSE | FALSE | FALSE | TRUE
4 | 6.7548 | 0.5 | 1.05 | 1.1 | 14.1851 | 78.2135 | 1.1 | 74.57% | 25.43% | 0.71006 | 4.5962 | 7.2761 | 10.5569 | 13.5096 | 13.5096 | 10% | 15.21% | 25.34% | 0.15% | 25.34% | 3.9303 | 3.5833 | 5.7131 | 0 | 47.6152 | FALSE | FALSE | FALSE | TRUE
4 | 6.7548 | 0.5 | 1.05 | 1.15 | 14.1851 | 81.7687 | 1.15 | 86.93% | 13.07% | 0.28585 | 2.362 | 5.1506 | 8.5805 | 13.5096 | 13.5096 | 10% | 18.44% | 12.96% | 0.15% | 12.96% | 3.9675 | 3.75 | 5.7131 | 0 | 48.0394 | FALSE | FALSE | FALSE | TRUE
4 | 6.7548 | 0.5 | 1.05 | 1.2 | 14.1851 | 85.3238 | 1.2 | 94.52% | 5.48% | 0.091108 | 0.12812 | 3.0276 | 6.6041 | 1.5374 | 13.5096 | 10% | 21.38% | 5.34% | 0.15% | 5.34% | 3.9854 | 3.9167 | 5.7131 | 0 | 48.2342 | FALSE | FALSE | FALSE | TRUE
4 | 6.7548 | 0.5 | 1.05 | 1.25 | 14.1851 | 88.879 | 1.25 | 98.18% | 1.82% | 0.021838 | 0 | 0.91294 | 4.6276 | 0 | 10.9552 | 12.68% | 24.08% | 1.67% | 0.15% | 1.67% | 3.9921 | 4 | 5.7131 | 0 | 48.3035 | TRUE | FALSE | FALSE | TRUE
4 | 6.7548 | 0.5 | 1.05 | 1.3 | 14.1851 | 92.4342 | 1.3 | 99.52% | 0.48% | 0.0029617 | 0 | 0 | 2.6512 | 0 | 0 | 15.27% | 26.55% | 0.33% | 0.15% | 0.33% | 3.9942 | 4 | 5.7131 | 0 | 48.3223 | TRUE | TRUE | FALSE | TRUE
4 | 6.7548 | 0.5 | 1.05 | 1.35 | 14.1851 | 95.9893 | 1.35 | 99.83% | 0.17% | 0.00014487 | 0 | 0 | 0.67476 | 0 | 0 | 17.71% | 28.86% | 0.02% | 0.15% | 0.02% | 3.9945 | 4 | 5.7131 | 0 | 48.3251 | TRUE | TRUE | FALSE | TRUE
4 | 6.7548 | 0.5 | 1.05 | 1.4 | 14.1851 | 99.5445 | 1.4 | 99.85% | 0.15% | 4.2843e-05 | 0 | 0 | 0.097512 | 0 | 0 | 19.93% | 31% | 0% | 0.15% | 0% | 3.9946 | 4 | 5.7131 | 0 | 48.3252 | TRUE | TRUE | FALSE | TRUE
4 | 6.7548 | 0.5 | 1.05 | 1.45 | 14.1851 | 103.0996 | 1.45 | 99.85% | 0.15% | 4.2843e-05 | 0 | 0 | 0.097512 | 0 | 0 | 22.03% | 32.99% | 0% | 0.15% | 0% | 3.9946 | 4 | 5.7131 | 0 | 48.3252 | TRUE | TRUE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1.05 | 1.5 | 14.1851 | 106.6548 | 1.5 | 99.85% | 0.15% | 4.2843e-05 | 0 | 0 | 0.097512 | 0 | 0 | 23.99% | 34.85% | 0% | 0.15% | 0% | 3.9946 | 4 | 5.7131 | 0 | 48.3252 | TRUE | TRUE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1.05 | 1.55 | 14.1851 | 110.21 | 1.55 | 99.85% | 0.15% | 4.2843e-05 | 0 | 0 | 0.097512 | 0 | 0 | 25.81% | 36.58% | 0% | 0.15% | 0% | 3.9946 | 4 | 5.7131 | 0 | 48.3252 | TRUE | TRUE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1.05 | 1.6 | 14.1851 | 113.7651 | 1.6 | 99.85% | 0.15% | 4.2843e-05 | 0 | 0 | 0.097512 | 0 | 0 | 27.5% | 38.21% | 0% | 0.15% | 0% | 3.9946 | 4 | 5.7131 | 0 | 48.3252 | TRUE | TRUE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1.05 | 1.65 | 14.1851 | 117.3203 | 1.65 | 99.85% | 0.15% | 4.2843e-05 | 0 | 0 | 0.097512 | 0 | 0 | 29.09% | 39.74% | 0% | 0.15% | 0% | 3.9946 | 4 | 5.7131 | 0 | 48.3252 | TRUE | TRUE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1.05 | 1.7 | 14.1851 | 120.8754 | 1.7 | 99.85% | 0.15% | 4.2843e-05 | 0 | 0 | 0.097512 | 0 | 0 | 30.58% | 41.17% | 0% | 0.15% | 0% | 3.9946 | 4 | 5.7131 | 0 | 48.3252 | TRUE | TRUE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1.05 | 1.75 | 14.1851 | 124.4306 | 1.75 | 99.85% | 0.15% | 4.2843e-05 | 0 | 0 | 0.097512 | 0 | 0 | 32.03% | 42.52% | 0% | 0.15% | 0% | 3.9946 | 4 | 5.7131 | 0 | 48.3252 | TRUE | TRUE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1.05 | 1.8 | 14.1851 | 127.9858 | 1.8 | 99.85% | 0.15% | 4.2843e-05 | 0 | 0 | 0.097512 | 0 | 0 | 33.38% | 43.82% | 0% | 0.15% | 0% | 3.9946 | 4 | 5.7131 | 0 | 48.3252 | TRUE | TRUE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1.075 | 1 | 14.5228 | 71.1032 | 1.075 | 42.15% | 57.85% | 2.7115 | 9.0815 | 11.5056 | 14.5098 | 13.5096 | 13.5096 | 10% | 10% | 57.85% | 0% | 57.85% | 3.7708 | 3.25 | 5.7131 | 0 | 45.6138 | FALSE | FALSE | FALSE | TRUE
4 | 6.7548 | 0.5 | 1.075 | 1.05 | 14.5228 | 74.6584 | 1.075 | 57.9% | 42.1% | 1.4976 | 6.839 | 9.4017 | 12.5334 | 13.5096 | 13.5096 | 10% | 11.69% | 42.1% | 0% | 42.1% | 3.8691 | 3.4167 | 5.7131 | 0 | 46.8277 | FALSE | FALSE | FALSE | TRUE
4 | 6.7548 | 0.5 | 1.075 | 1.1 | 14.5228 | 78.2135 | 1.1 | 74.66% | 25.34% | 0.71003 | 4.5962 | 7.2761 | 10.5569 | 13.5096 | 13.5096 | 10% | 15.21% | 25.34% | 0% | 25.34% | 3.9356 | 3.5833 | 5.7131 | 0 | 47.6153 | FALSE | FALSE | FALSE | TRUE
4 | 6.7548 | 0.5 | 1.075 | 1.15 | 14.5228 | 81.7687 | 1.15 | 87.04% | 12.96% | 0.28582 | 2.362 | 5.1506 | 8.5805 | 13.5096 | 13.5096 | 10% | 18.44% | 12.96% | 0% | 12.96% | 3.9729 | 3.75 | 5.7131 | 0 | 48.0395 | FALSE | FALSE | FALSE | TRUE
4 | 6.7548 | 0.5 | 1.075 | 1.2 | 14.5228 | 85.3238 | 1.2 | 94.66% | 5.34% | 0.09107 | 0.12812 | 3.0276 | 6.6041 | 1.5374 | 13.5096 | 10% | 21.38% | 5.34% | 0% | 5.34% | 3.9908 | 3.9167 | 5.7131 | 0 | 48.2342 | FALSE | FALSE | FALSE | TRUE
4 | 6.7548 | 0.5 | 1.075 | 1.25 | 14.5228 | 88.879 | 1.25 | 98.33% | 1.67% | 0.021795 | 0 | 0.91294 | 4.6276 | 0 | 10.9552 | 12.68% | 24.08% | 1.67% | 0% | 1.67% | 3.9976 | 4 | 5.7131 | 0 | 48.3035 | TRUE | FALSE | FALSE | TRUE
4 | 6.7548 | 0.5 | 1.075 | 1.3 | 14.5228 | 92.4342 | 1.3 | 99.67% | 0.33% | 0.0029188 | 0 | 0 | 2.6512 | 0 | 0 | 15.27% | 26.55% | 0.33% | 0% | 0.33% | 3.9996 | 4 | 5.7131 | 0 | 48.3224 | TRUE | TRUE | FALSE | TRUE
4 | 6.7548 | 0.5 | 1.075 | 1.35 | 14.5228 | 95.9893 | 1.35 | 99.98% | 0.02% | 0.00010203 | 0 | 0 | 0.67476 | 0 | 0 | 17.71% | 28.86% | 0.02% | 0% | 0.02% | 4 | 4 | 5.7131 | 0 | 48.3252 | TRUE | TRUE | TRUE | TRUE
4 | 6.7548 | 0.5 | 1.075 | 1.4 | 14.5228 | 99.5445 | 1.4 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 19.93% | 31% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | TRUE
4 | 6.7548 | 0.5 | 1.075 | 1.45 | 14.5228 | 103.0996 | 1.45 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 22.03% | 32.99% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.075 | 1.5 | 14.5228 | 106.6548 | 1.5 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 23.99% | 34.85% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.075 | 1.55 | 14.5228 | 110.21 | 1.55 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 25.81% | 36.58% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.075 | 1.6 | 14.5228 | 113.7651 | 1.6 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 27.5% | 38.21% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.075 | 1.65 | 14.5228 | 117.3203 | 1.65 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 29.09% | 39.74% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.075 | 1.7 | 14.5228 | 120.8754 | 1.7 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 30.58% | 41.17% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.075 | 1.75 | 14.5228 | 124.4306 | 1.75 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 32.03% | 42.52% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.075 | 1.8 | 14.5228 | 127.9858 | 1.8 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 33.38% | 43.82% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.1 | 1 | 14.8606 | 71.1032 | 1.1 | 42.15% | 57.85% | 2.7115 | 9.0815 | 11.5056 | 14.5098 | 13.5096 | 13.5096 | 10% | 10% | 57.85% | 0% | 57.85% | 3.7708 | 3.25 | 5.7131 | 0 | 45.6138 | FALSE | FALSE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1.1 | 1.05 | 14.8606 | 74.6584 | 1.1 | 57.9% | 42.1% | 1.4976 | 6.839 | 9.4017 | 12.5334 | 13.5096 | 13.5096 | 10% | 11.69% | 42.1% | 0% | 42.1% | 3.8691 | 3.4167 | 5.7131 | 0 | 46.8277 | FALSE | FALSE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1.1 | 1.1 | 14.8606 | 78.2135 | 1.1 | 74.66% | 25.34% | 0.71003 | 4.5962 | 7.2761 | 10.5569 | 13.5096 | 13.5096 | 10% | 15.21% | 25.34% | 0% | 25.34% | 3.9356 | 3.5833 | 5.7131 | 0 | 47.6153 | FALSE | FALSE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1.1 | 1.15 | 14.8606 | 81.7687 | 1.15 | 87.04% | 12.96% | 0.28582 | 2.362 | 5.1506 | 8.5805 | 13.5096 | 13.5096 | 10% | 18.44% | 12.96% | 0% | 12.96% | 3.9729 | 3.75 | 5.7131 | 0 | 48.0395 | FALSE | FALSE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1.1 | 1.2 | 14.8606 | 85.3238 | 1.2 | 94.66% | 5.34% | 0.09107 | 0.12812 | 3.0276 | 6.6041 | 1.5374 | 13.5096 | 10% | 21.38% | 5.34% | 0% | 5.34% | 3.9908 | 3.9167 | 5.7131 | 0 | 48.2342 | FALSE | FALSE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1.1 | 1.25 | 14.8606 | 88.879 | 1.25 | 98.33% | 1.67% | 0.021795 | 0 | 0.91294 | 4.6276 | 0 | 10.9552 | 12.68% | 24.08% | 1.67% | 0% | 1.67% | 3.9976 | 4 | 5.7131 | 0 | 48.3035 | TRUE | FALSE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1.1 | 1.3 | 14.8606 | 92.4342 | 1.3 | 99.67% | 0.33% | 0.0029188 | 0 | 0 | 2.6512 | 0 | 0 | 15.27% | 26.55% | 0.33% | 0% | 0.33% | 3.9996 | 4 | 5.7131 | 0 | 48.3224 | TRUE | TRUE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1.1 | 1.35 | 14.8606 | 95.9893 | 1.35 | 99.98% | 0.02% | 0.00010203 | 0 | 0 | 0.67476 | 0 | 0 | 17.71% | 28.86% | 0.02% | 0% | 0.02% | 4 | 4 | 5.7131 | 0 | 48.3252 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.1 | 1.4 | 14.8606 | 99.5445 | 1.4 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 19.93% | 31% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.1 | 1.45 | 14.8606 | 103.0996 | 1.45 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 22.03% | 32.99% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.1 | 1.5 | 14.8606 | 106.6548 | 1.5 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 23.99% | 34.85% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.1 | 1.55 | 14.8606 | 110.21 | 1.55 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 25.81% | 36.58% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.1 | 1.6 | 14.8606 | 113.7651 | 1.6 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 27.5% | 38.21% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.1 | 1.65 | 14.8606 | 117.3203 | 1.65 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 29.09% | 39.74% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.1 | 1.7 | 14.8606 | 120.8754 | 1.7 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 30.58% | 41.17% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.1 | 1.75 | 14.8606 | 124.4306 | 1.75 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 32.03% | 42.52% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.1 | 1.8 | 14.8606 | 127.9858 | 1.8 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 33.38% | 43.82% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.125 | 1 | 15.1983 | 71.1032 | 1.125 | 42.15% | 57.85% | 2.7115 | 9.0815 | 11.5056 | 14.5098 | 13.5096 | 13.5096 | 10% | 10% | 57.85% | 0% | 57.85% | 3.7708 | 3.25 | 5.7131 | 0 | 45.6138 | FALSE | FALSE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1.125 | 1.05 | 15.1983 | 74.6584 | 1.125 | 57.9% | 42.1% | 1.4976 | 6.839 | 9.4017 | 12.5334 | 13.5096 | 13.5096 | 10% | 11.69% | 42.1% | 0% | 42.1% | 3.8691 | 3.4167 | 5.7131 | 0 | 46.8277 | FALSE | FALSE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1.125 | 1.1 | 15.1983 | 78.2135 | 1.125 | 74.66% | 25.34% | 0.71003 | 4.5962 | 7.2761 | 10.5569 | 13.5096 | 13.5096 | 10% | 15.21% | 25.34% | 0% | 25.34% | 3.9356 | 3.5833 | 5.7131 | 0 | 47.6153 | FALSE | FALSE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1.125 | 1.15 | 15.1983 | 81.7687 | 1.15 | 87.04% | 12.96% | 0.28582 | 2.362 | 5.1506 | 8.5805 | 13.5096 | 13.5096 | 10% | 18.44% | 12.96% | 0% | 12.96% | 3.9729 | 3.75 | 5.7131 | 0 | 48.0395 | FALSE | FALSE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1.125 | 1.2 | 15.1983 | 85.3238 | 1.2 | 94.66% | 5.34% | 0.09107 | 0.12812 | 3.0276 | 6.6041 | 1.5374 | 13.5096 | 10% | 21.38% | 5.34% | 0% | 5.34% | 3.9908 | 3.9167 | 5.7131 | 0 | 48.2342 | FALSE | FALSE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1.125 | 1.25 | 15.1983 | 88.879 | 1.25 | 98.33% | 1.67% | 0.021795 | 0 | 0.91294 | 4.6276 | 0 | 10.9552 | 12.68% | 24.08% | 1.67% | 0% | 1.67% | 3.9976 | 4 | 5.7131 | 0 | 48.3035 | TRUE | FALSE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1.125 | 1.3 | 15.1983 | 92.4342 | 1.3 | 99.67% | 0.33% | 0.0029188 | 0 | 0 | 2.6512 | 0 | 0 | 15.27% | 26.55% | 0.33% | 0% | 0.33% | 3.9996 | 4 | 5.7131 | 0 | 48.3224 | TRUE | TRUE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1.125 | 1.35 | 15.1983 | 95.9893 | 1.35 | 99.98% | 0.02% | 0.00010203 | 0 | 0 | 0.67476 | 0 | 0 | 17.71% | 28.86% | 0.02% | 0% | 0.02% | 4 | 4 | 5.7131 | 0 | 48.3252 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.125 | 1.4 | 15.1983 | 99.5445 | 1.4 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 19.93% | 31% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.125 | 1.45 | 15.1983 | 103.0996 | 1.45 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 22.03% | 32.99% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.125 | 1.5 | 15.1983 | 106.6548 | 1.5 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 23.99% | 34.85% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.125 | 1.55 | 15.1983 | 110.21 | 1.55 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 25.81% | 36.58% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.125 | 1.6 | 15.1983 | 113.7651 | 1.6 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 27.5% | 38.21% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.125 | 1.65 | 15.1983 | 117.3203 | 1.65 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 29.09% | 39.74% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.125 | 1.7 | 15.1983 | 120.8754 | 1.7 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 30.58% | 41.17% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.125 | 1.75 | 15.1983 | 124.4306 | 1.75 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 32.03% | 42.52% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.125 | 1.8 | 15.1983 | 127.9858 | 1.8 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 33.38% | 43.82% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.15 | 1 | 15.536 | 71.1032 | 1.15 | 42.15% | 57.85% | 2.7115 | 9.0815 | 11.5056 | 14.5098 | 13.5096 | 13.5096 | 10% | 10% | 57.85% | 0% | 57.85% | 3.7708 | 3.25 | 5.7131 | 0 | 45.6138 | FALSE | FALSE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1.15 | 1.05 | 15.536 | 74.6584 | 1.15 | 57.9% | 42.1% | 1.4976 | 6.839 | 9.4017 | 12.5334 | 13.5096 | 13.5096 | 10% | 11.69% | 42.1% | 0% | 42.1% | 3.8691 | 3.4167 | 5.7131 | 0 | 46.8277 | FALSE | FALSE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1.15 | 1.1 | 15.536 | 78.2135 | 1.15 | 74.66% | 25.34% | 0.71003 | 4.5962 | 7.2761 | 10.5569 | 13.5096 | 13.5096 | 10% | 15.21% | 25.34% | 0% | 25.34% | 3.9356 | 3.5833 | 5.7131 | 0 | 47.6153 | FALSE | FALSE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1.15 | 1.15 | 15.536 | 81.7687 | 1.15 | 87.04% | 12.96% | 0.28582 | 2.362 | 5.1506 | 8.5805 | 13.5096 | 13.5096 | 10% | 18.44% | 12.96% | 0% | 12.96% | 3.9729 | 3.75 | 5.7131 | 0 | 48.0395 | FALSE | FALSE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1.15 | 1.2 | 15.536 | 85.3238 | 1.2 | 94.66% | 5.34% | 0.09107 | 0.12812 | 3.0276 | 6.6041 | 1.5374 | 13.5096 | 10% | 21.38% | 5.34% | 0% | 5.34% | 3.9908 | 3.9167 | 5.7131 | 0 | 48.2342 | FALSE | FALSE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1.15 | 1.25 | 15.536 | 88.879 | 1.25 | 98.33% | 1.67% | 0.021795 | 0 | 0.91294 | 4.6276 | 0 | 10.9552 | 12.68% | 24.08% | 1.67% | 0% | 1.67% | 3.9976 | 4 | 5.7131 | 0 | 48.3035 | TRUE | FALSE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1.15 | 1.3 | 15.536 | 92.4342 | 1.3 | 99.67% | 0.33% | 0.0029188 | 0 | 0 | 2.6512 | 0 | 0 | 15.27% | 26.55% | 0.33% | 0% | 0.33% | 3.9996 | 4 | 5.7131 | 0 | 48.3224 | TRUE | TRUE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1.15 | 1.35 | 15.536 | 95.9893 | 1.35 | 99.98% | 0.02% | 0.00010203 | 0 | 0 | 0.67476 | 0 | 0 | 17.71% | 28.86% | 0.02% | 0% | 0.02% | 4 | 4 | 5.7131 | 0 | 48.3252 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.15 | 1.4 | 15.536 | 99.5445 | 1.4 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 19.93% | 31% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.15 | 1.45 | 15.536 | 103.0996 | 1.45 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 22.03% | 32.99% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.15 | 1.5 | 15.536 | 106.6548 | 1.5 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 23.99% | 34.85% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.15 | 1.55 | 15.536 | 110.21 | 1.55 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 25.81% | 36.58% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.15 | 1.6 | 15.536 | 113.7651 | 1.6 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 27.5% | 38.21% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.15 | 1.65 | 15.536 | 117.3203 | 1.65 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 29.09% | 39.74% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.15 | 1.7 | 15.536 | 120.8754 | 1.7 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 30.58% | 41.17% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.15 | 1.75 | 15.536 | 124.4306 | 1.75 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 32.03% | 42.52% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.15 | 1.8 | 15.536 | 127.9858 | 1.8 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 33.38% | 43.82% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.175 | 1 | 15.8738 | 71.1032 | 1.175 | 42.15% | 57.85% | 2.7115 | 9.0815 | 11.5056 | 14.5098 | 13.5096 | 13.5096 | 10% | 10% | 57.85% | 0% | 57.85% | 3.7708 | 3.25 | 5.7131 | 0 | 45.6138 | FALSE | FALSE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1.175 | 1.05 | 15.8738 | 74.6584 | 1.175 | 57.9% | 42.1% | 1.4976 | 6.839 | 9.4017 | 12.5334 | 13.5096 | 13.5096 | 10% | 11.69% | 42.1% | 0% | 42.1% | 3.8691 | 3.4167 | 5.7131 | 0 | 46.8277 | FALSE | FALSE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1.175 | 1.1 | 15.8738 | 78.2135 | 1.175 | 74.66% | 25.34% | 0.71003 | 4.5962 | 7.2761 | 10.5569 | 13.5096 | 13.5096 | 10% | 15.21% | 25.34% | 0% | 25.34% | 3.9356 | 3.5833 | 5.7131 | 0 | 47.6153 | FALSE | FALSE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1.175 | 1.15 | 15.8738 | 81.7687 | 1.175 | 87.04% | 12.96% | 0.28582 | 2.362 | 5.1506 | 8.5805 | 13.5096 | 13.5096 | 10% | 18.44% | 12.96% | 0% | 12.96% | 3.9729 | 3.75 | 5.7131 | 0 | 48.0395 | FALSE | FALSE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1.175 | 1.2 | 15.8738 | 85.3238 | 1.2 | 94.66% | 5.34% | 0.09107 | 0.12812 | 3.0276 | 6.6041 | 1.5374 | 13.5096 | 10% | 21.38% | 5.34% | 0% | 5.34% | 3.9908 | 3.9167 | 5.7131 | 0 | 48.2342 | FALSE | FALSE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1.175 | 1.25 | 15.8738 | 88.879 | 1.25 | 98.33% | 1.67% | 0.021795 | 0 | 0.91294 | 4.6276 | 0 | 10.9552 | 12.68% | 24.08% | 1.67% | 0% | 1.67% | 3.9976 | 4 | 5.7131 | 0 | 48.3035 | TRUE | FALSE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1.175 | 1.3 | 15.8738 | 92.4342 | 1.3 | 99.67% | 0.33% | 0.0029188 | 0 | 0 | 2.6512 | 0 | 0 | 15.27% | 26.55% | 0.33% | 0% | 0.33% | 3.9996 | 4 | 5.7131 | 0 | 48.3224 | TRUE | TRUE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1.175 | 1.35 | 15.8738 | 95.9893 | 1.35 | 99.98% | 0.02% | 0.00010203 | 0 | 0 | 0.67476 | 0 | 0 | 17.71% | 28.86% | 0.02% | 0% | 0.02% | 4 | 4 | 5.7131 | 0 | 48.3252 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.175 | 1.4 | 15.8738 | 99.5445 | 1.4 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 19.93% | 31% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.175 | 1.45 | 15.8738 | 103.0996 | 1.45 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 22.03% | 32.99% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.175 | 1.5 | 15.8738 | 106.6548 | 1.5 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 23.99% | 34.85% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.175 | 1.55 | 15.8738 | 110.21 | 1.55 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 25.81% | 36.58% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.175 | 1.6 | 15.8738 | 113.7651 | 1.6 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 27.5% | 38.21% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.175 | 1.65 | 15.8738 | 117.3203 | 1.65 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 29.09% | 39.74% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.175 | 1.7 | 15.8738 | 120.8754 | 1.7 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 30.58% | 41.17% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.175 | 1.75 | 15.8738 | 124.4306 | 1.75 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 32.03% | 42.52% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.175 | 1.8 | 15.8738 | 127.9858 | 1.8 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 33.38% | 43.82% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.2 | 1 | 16.2115 | 71.1032 | 1.2 | 42.15% | 57.85% | 2.7115 | 9.0815 | 11.5056 | 14.5098 | 13.5096 | 13.5096 | 10% | 10% | 57.85% | 0% | 57.85% | 3.7708 | 3.25 | 5.7131 | 0 | 45.6138 | FALSE | FALSE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1.2 | 1.05 | 16.2115 | 74.6584 | 1.2 | 57.9% | 42.1% | 1.4976 | 6.839 | 9.4017 | 12.5334 | 13.5096 | 13.5096 | 10% | 11.69% | 42.1% | 0% | 42.1% | 3.8691 | 3.4167 | 5.7131 | 0 | 46.8277 | FALSE | FALSE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1.2 | 1.1 | 16.2115 | 78.2135 | 1.2 | 74.66% | 25.34% | 0.71003 | 4.5962 | 7.2761 | 10.5569 | 13.5096 | 13.5096 | 10% | 15.21% | 25.34% | 0% | 25.34% | 3.9356 | 3.5833 | 5.7131 | 0 | 47.6153 | FALSE | FALSE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1.2 | 1.15 | 16.2115 | 81.7687 | 1.2 | 87.04% | 12.96% | 0.28582 | 2.362 | 5.1506 | 8.5805 | 13.5096 | 13.5096 | 10% | 18.44% | 12.96% | 0% | 12.96% | 3.9729 | 3.75 | 5.7131 | 0 | 48.0395 | FALSE | FALSE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1.2 | 1.2 | 16.2115 | 85.3238 | 1.2 | 94.66% | 5.34% | 0.09107 | 0.12812 | 3.0276 | 6.6041 | 1.5374 | 13.5096 | 10% | 21.38% | 5.34% | 0% | 5.34% | 3.9908 | 3.9167 | 5.7131 | 0 | 48.2342 | FALSE | FALSE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1.2 | 1.25 | 16.2115 | 88.879 | 1.25 | 98.33% | 1.67% | 0.021795 | 0 | 0.91294 | 4.6276 | 0 | 10.9552 | 12.68% | 24.08% | 1.67% | 0% | 1.67% | 3.9976 | 4 | 5.7131 | 0 | 48.3035 | TRUE | FALSE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1.2 | 1.3 | 16.2115 | 92.4342 | 1.3 | 99.67% | 0.33% | 0.0029188 | 0 | 0 | 2.6512 | 0 | 0 | 15.27% | 26.55% | 0.33% | 0% | 0.33% | 3.9996 | 4 | 5.7131 | 0 | 48.3224 | TRUE | TRUE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1.2 | 1.35 | 16.2115 | 95.9893 | 1.35 | 99.98% | 0.02% | 0.00010203 | 0 | 0 | 0.67476 | 0 | 0 | 17.71% | 28.86% | 0.02% | 0% | 0.02% | 4 | 4 | 5.7131 | 0 | 48.3252 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.2 | 1.4 | 16.2115 | 99.5445 | 1.4 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 19.93% | 31% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.2 | 1.45 | 16.2115 | 103.0996 | 1.45 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 22.03% | 32.99% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.2 | 1.5 | 16.2115 | 106.6548 | 1.5 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 23.99% | 34.85% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.2 | 1.55 | 16.2115 | 110.21 | 1.55 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 25.81% | 36.58% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.2 | 1.6 | 16.2115 | 113.7651 | 1.6 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 27.5% | 38.21% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.2 | 1.65 | 16.2115 | 117.3203 | 1.65 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 29.09% | 39.74% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.2 | 1.7 | 16.2115 | 120.8754 | 1.7 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 30.58% | 41.17% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.2 | 1.75 | 16.2115 | 124.4306 | 1.75 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 32.03% | 42.52% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.2 | 1.8 | 16.2115 | 127.9858 | 1.8 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 33.38% | 43.82% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.225 | 1 | 16.5493 | 71.1032 | 1.225 | 42.15% | 57.85% | 2.7115 | 9.0815 | 11.5056 | 14.5098 | 13.5096 | 13.5096 | 10% | 10% | 57.85% | 0% | 57.85% | 3.7708 | 3.25 | 5.7131 | 0 | 45.6138 | FALSE | FALSE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1.225 | 1.05 | 16.5493 | 74.6584 | 1.225 | 57.9% | 42.1% | 1.4976 | 6.839 | 9.4017 | 12.5334 | 13.5096 | 13.5096 | 10% | 11.69% | 42.1% | 0% | 42.1% | 3.8691 | 3.4167 | 5.7131 | 0 | 46.8277 | FALSE | FALSE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1.225 | 1.1 | 16.5493 | 78.2135 | 1.225 | 74.66% | 25.34% | 0.71003 | 4.5962 | 7.2761 | 10.5569 | 13.5096 | 13.5096 | 10% | 15.21% | 25.34% | 0% | 25.34% | 3.9356 | 3.5833 | 5.7131 | 0 | 47.6153 | FALSE | FALSE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1.225 | 1.15 | 16.5493 | 81.7687 | 1.225 | 87.04% | 12.96% | 0.28582 | 2.362 | 5.1506 | 8.5805 | 13.5096 | 13.5096 | 10% | 18.44% | 12.96% | 0% | 12.96% | 3.9729 | 3.75 | 5.7131 | 0 | 48.0395 | FALSE | FALSE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1.225 | 1.2 | 16.5493 | 85.3238 | 1.225 | 94.66% | 5.34% | 0.09107 | 0.12812 | 3.0276 | 6.6041 | 1.5374 | 13.5096 | 10% | 21.38% | 5.34% | 0% | 5.34% | 3.9908 | 3.9167 | 5.7131 | 0 | 48.2342 | FALSE | FALSE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1.225 | 1.25 | 16.5493 | 88.879 | 1.25 | 98.33% | 1.67% | 0.021795 | 0 | 0.91294 | 4.6276 | 0 | 10.9552 | 12.68% | 24.08% | 1.67% | 0% | 1.67% | 3.9976 | 4 | 5.7131 | 0 | 48.3035 | TRUE | FALSE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1.225 | 1.3 | 16.5493 | 92.4342 | 1.3 | 99.67% | 0.33% | 0.0029188 | 0 | 0 | 2.6512 | 0 | 0 | 15.27% | 26.55% | 0.33% | 0% | 0.33% | 3.9996 | 4 | 5.7131 | 0 | 48.3224 | TRUE | TRUE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1.225 | 1.35 | 16.5493 | 95.9893 | 1.35 | 99.98% | 0.02% | 0.00010203 | 0 | 0 | 0.67476 | 0 | 0 | 17.71% | 28.86% | 0.02% | 0% | 0.02% | 4 | 4 | 5.7131 | 0 | 48.3252 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.225 | 1.4 | 16.5493 | 99.5445 | 1.4 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 19.93% | 31% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.225 | 1.45 | 16.5493 | 103.0996 | 1.45 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 22.03% | 32.99% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.225 | 1.5 | 16.5493 | 106.6548 | 1.5 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 23.99% | 34.85% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.225 | 1.55 | 16.5493 | 110.21 | 1.55 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 25.81% | 36.58% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.225 | 1.6 | 16.5493 | 113.7651 | 1.6 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 27.5% | 38.21% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.225 | 1.65 | 16.5493 | 117.3203 | 1.65 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 29.09% | 39.74% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.225 | 1.7 | 16.5493 | 120.8754 | 1.7 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 30.58% | 41.17% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.225 | 1.75 | 16.5493 | 124.4306 | 1.75 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 32.03% | 42.52% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.225 | 1.8 | 16.5493 | 127.9858 | 1.8 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 33.38% | 43.82% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.25 | 1 | 16.887 | 71.1032 | 1.25 | 42.15% | 57.85% | 2.7115 | 9.0815 | 11.5056 | 14.5098 | 13.5096 | 13.5096 | 10% | 10% | 57.85% | 0% | 57.85% | 3.7708 | 3.25 | 5.7131 | 0 | 45.6138 | FALSE | FALSE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1.25 | 1.05 | 16.887 | 74.6584 | 1.25 | 57.9% | 42.1% | 1.4976 | 6.839 | 9.4017 | 12.5334 | 13.5096 | 13.5096 | 10% | 11.69% | 42.1% | 0% | 42.1% | 3.8691 | 3.4167 | 5.7131 | 0 | 46.8277 | FALSE | FALSE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1.25 | 1.1 | 16.887 | 78.2135 | 1.25 | 74.66% | 25.34% | 0.71003 | 4.5962 | 7.2761 | 10.5569 | 13.5096 | 13.5096 | 10% | 15.21% | 25.34% | 0% | 25.34% | 3.9356 | 3.5833 | 5.7131 | 0 | 47.6153 | FALSE | FALSE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1.25 | 1.15 | 16.887 | 81.7687 | 1.25 | 87.04% | 12.96% | 0.28582 | 2.362 | 5.1506 | 8.5805 | 13.5096 | 13.5096 | 10% | 18.44% | 12.96% | 0% | 12.96% | 3.9729 | 3.75 | 5.7131 | 0 | 48.0395 | FALSE | FALSE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1.25 | 1.2 | 16.887 | 85.3238 | 1.25 | 94.66% | 5.34% | 0.09107 | 0.12812 | 3.0276 | 6.6041 | 1.5374 | 13.5096 | 10% | 21.38% | 5.34% | 0% | 5.34% | 3.9908 | 3.9167 | 5.7131 | 0 | 48.2342 | FALSE | FALSE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1.25 | 1.25 | 16.887 | 88.879 | 1.25 | 98.33% | 1.67% | 0.021795 | 0 | 0.91294 | 4.6276 | 0 | 10.9552 | 12.68% | 24.08% | 1.67% | 0% | 1.67% | 3.9976 | 4 | 5.7131 | 0 | 48.3035 | TRUE | FALSE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1.25 | 1.3 | 16.887 | 92.4342 | 1.3 | 99.67% | 0.33% | 0.0029188 | 0 | 0 | 2.6512 | 0 | 0 | 15.27% | 26.55% | 0.33% | 0% | 0.33% | 3.9996 | 4 | 5.7131 | 0 | 48.3224 | TRUE | TRUE | FALSE | FALSE
4 | 6.7548 | 0.5 | 1.25 | 1.35 | 16.887 | 95.9893 | 1.35 | 99.98% | 0.02% | 0.00010203 | 0 | 0 | 0.67476 | 0 | 0 | 17.71% | 28.86% | 0.02% | 0% | 0.02% | 4 | 4 | 5.7131 | 0 | 48.3252 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.25 | 1.4 | 16.887 | 99.5445 | 1.4 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 19.93% | 31% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.25 | 1.45 | 16.887 | 103.0996 | 1.45 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 22.03% | 32.99% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.25 | 1.5 | 16.887 | 106.6548 | 1.5 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 23.99% | 34.85% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.25 | 1.55 | 16.887 | 110.21 | 1.55 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 25.81% | 36.58% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.25 | 1.6 | 16.887 | 113.7651 | 1.6 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 27.5% | 38.21% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.25 | 1.65 | 16.887 | 117.3203 | 1.65 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 29.09% | 39.74% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.25 | 1.7 | 16.887 | 120.8754 | 1.7 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 30.58% | 41.17% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.25 | 1.75 | 16.887 | 124.4306 | 1.75 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 32.03% | 42.52% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 6.7548 | 0.5 | 1.25 | 1.8 | 16.887 | 127.9858 | 1.8 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 33.38% | 43.82% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1 | 1 | 13.5096 | 71.1032 | 1 | 32.33% | 67.67% | 2.4843 | 8.9091 | 11.3949 | 14.5098 | 13.5096 | 13.5096 | 10% | 11.04% | 47.26% | 67.67% | 47.26% | 1.6207 | 0 | 11.4225 | 0.003816 | 40.1317 | FALSE | FALSE | FALSE | TRUE
4 | 13.5096 | 1 | 1 | 1.05 | 13.5096 | 74.6584 | 1.05 | 32.33% | 67.67% | 1.5199 | 6.6654 | 9.274 | 12.5334 | 13.5096 | 13.5096 | 10% | 14.81% | 32.93% | 67.67% | 32.93% | 1.6207 | 0 | 11.4225 | 0.003816 | 41.096 | FALSE | FALSE | FALSE | FALSE
4 | 13.5096 | 1 | 1 | 1.1 | 13.5096 | 78.2135 | 1.1 | 32.33% | 67.67% | 0.9328 | 4.4345 | 7.1591 | 10.5569 | 13.5096 | 13.5096 | 10% | 18.19% | 18.22% | 67.67% | 18.22% | 1.6207 | 0 | 11.4225 | 0.003816 | 41.6832 | FALSE | FALSE | FALSE | FALSE
4 | 13.5096 | 1 | 1 | 1.15 | 13.5096 | 81.7687 | 1.15 | 32.33% | 67.67% | 0.63257 | 2.3793 | 5.0391 | 8.5805 | 13.5096 | 13.5096 | 10% | 21.28% | 8.95% | 67.67% | 8.95% | 1.6207 | 0 | 11.4225 | 0.003816 | 41.9834 | FALSE | FALSE | FALSE | FALSE
4 | 13.5096 | 1 | 1 | 1.2 | 13.5096 | 85.3238 | 1.2 | 32.33% | 67.67% | 0.50561 | 1.8798 | 2.9086 | 6.6041 | 0.56739 | 13.5096 | 11.1% | 24.13% | 3.37% | 67.67% | 3.37% | 1.6207 | 0 | 11.4225 | 0.003816 | 42.1103 | FALSE | FALSE | FALSE | FALSE
4 | 13.5096 | 1 | 1 | 1.25 | 13.5096 | 88.879 | 1.25 | 32.33% | 67.67% | 0.46453 | 1.7485 | 2.2812 | 4.6276 | 0.50501 | 0.65758 | 13.9% | 26.78% | 1% | 67.67% | 1% | 1.6207 | 0 | 11.4225 | 0.003816 | 42.1514 | FALSE | FALSE | FALSE | FALSE
4 | 13.5096 | 1 | 1 | 1.3 | 13.5096 | 92.4342 | 1.3 | 32.33% | 67.67% | 0.45448 | 1.7152 | 2.242 | 2.6661 | 0.48577 | 0.59593 | 16.48% | 29.21% | 0.13% | 67.67% | 0.13% | 1.6207 | 0 | 11.4225 | 0.003816 | 42.1615 | FALSE | FALSE | FALSE | FALSE
4 | 13.5096 | 1 | 1 | 1.35 | 13.5096 | 95.9893 | 1.35 | 32.33% | 67.67% | 0.45341 | 1.7098 | 2.2342 | 2.6661 | 0.48365 | 0.59225 | 18.87% | 31.44% | 0% | 67.67% | 0% | 1.6207 | 0 | 11.4225 | 0.003816 | 42.1625 | FALSE | FALSE | FALSE | FALSE
4 | 13.5096 | 1 | 1 | 1.4 | 13.5096 | 99.5445 | 1.4 | 32.33% | 67.67% | 0.45341 | 1.7098 | 2.2342 | 2.6661 | 0.48365 | 0.59225 | 21.1% | 33.51% | 0% | 67.67% | 0% | 1.6207 | 0 | 11.4225 | 0.003816 | 42.1625 | FALSE | FALSE | FALSE | FALSE
4 | 13.5096 | 1 | 1 | 1.45 | 13.5096 | 103.0996 | 1.45 | 32.33% | 67.67% | 0.45341 | 1.7098 | 2.2342 | 2.6661 | 0.48365 | 0.59225 | 23.18% | 35.44% | 0% | 67.67% | 0% | 1.6207 | 0 | 11.4225 | 0.003816 | 42.1625 | FALSE | FALSE | FALSE | FALSE
4 | 13.5096 | 1 | 1 | 1.5 | 13.5096 | 106.6548 | 1.5 | 32.33% | 67.67% | 0.45341 | 1.7098 | 2.2342 | 2.6661 | 0.48365 | 0.59225 | 25.11% | 37.25% | 0% | 67.67% | 0% | 1.6207 | 0 | 11.4225 | 0.003816 | 42.1625 | FALSE | FALSE | FALSE | FALSE
4 | 13.5096 | 1 | 1 | 1.55 | 13.5096 | 110.21 | 1.55 | 32.33% | 67.67% | 0.45341 | 1.7098 | 2.2342 | 2.6661 | 0.48365 | 0.59225 | 26.9% | 38.96% | 0% | 67.67% | 0% | 1.6207 | 0 | 11.4225 | 0.003816 | 42.1625 | FALSE | FALSE | FALSE | FALSE
4 | 13.5096 | 1 | 1 | 1.6 | 13.5096 | 113.7651 | 1.6 | 32.33% | 67.67% | 0.45341 | 1.7098 | 2.2342 | 2.6661 | 0.48365 | 0.59225 | 28.6% | 40.54% | 0% | 67.67% | 0% | 1.6207 | 0 | 11.4225 | 0.003816 | 42.1625 | FALSE | FALSE | FALSE | FALSE
4 | 13.5096 | 1 | 1 | 1.65 | 13.5096 | 117.3203 | 1.65 | 32.33% | 67.67% | 0.45341 | 1.7098 | 2.2342 | 2.6661 | 0.48365 | 0.59225 | 30.16% | 42.05% | 0% | 67.67% | 0% | 1.6207 | 0 | 11.4225 | 0.003816 | 42.1625 | FALSE | FALSE | FALSE | FALSE
4 | 13.5096 | 1 | 1 | 1.7 | 13.5096 | 120.8754 | 1.7 | 32.33% | 67.67% | 0.45341 | 1.7098 | 2.2342 | 2.6661 | 0.48365 | 0.59225 | 31.64% | 43.41% | 0% | 67.67% | 0% | 1.6207 | 0 | 11.4225 | 0.003816 | 42.1625 | FALSE | FALSE | FALSE | FALSE
4 | 13.5096 | 1 | 1 | 1.75 | 13.5096 | 124.4306 | 1.75 | 32.33% | 67.67% | 0.45341 | 1.7098 | 2.2342 | 2.6661 | 0.48365 | 0.59225 | 33% | 44.74% | 0% | 67.67% | 0% | 1.6207 | 0 | 11.4225 | 0.003816 | 42.1625 | FALSE | FALSE | FALSE | FALSE
4 | 13.5096 | 1 | 1 | 1.8 | 13.5096 | 127.9858 | 1.8 | 32.33% | 67.67% | 0.45341 | 1.7098 | 2.2342 | 2.6661 | 0.48365 | 0.59225 | 34.34% | 45.99% | 0% | 67.67% | 0% | 1.6207 | 0 | 11.4225 | 0.003816 | 42.1625 | FALSE | FALSE | FALSE | FALSE
4 | 13.5096 | 1 | 1.025 | 1 | 13.8473 | 71.1032 | 1.025 | 45.14% | 54.86% | 2.4249 | 8.9091 | 11.3949 | 14.5098 | 13.5096 | 13.5096 | 10% | 10.07% | 49.86% | 17.62% | 49.86% | 3.2384 | 0 | 11.4225 | 0.003816 | 40.1911 | FALSE | FALSE | FALSE | TRUE
4 | 13.5096 | 1 | 1.025 | 1.05 | 13.8473 | 74.6584 | 1.05 | 54.37% | 45.63% | 1.369 | 6.6654 | 9.274 | 12.5334 | 13.5096 | 13.5096 | 10% | 13.85% | 37.15% | 17.62% | 37.15% | 3.3023 | 0 | 11.4225 | 0.003816 | 41.247 | FALSE | FALSE | FALSE | TRUE
4 | 13.5096 | 1 | 1.025 | 1.1 | 13.8473 | 78.2135 | 1.1 | 65.84% | 34.16% | 0.67883 | 4.4345 | 7.1591 | 10.5569 | 13.5096 | 13.5096 | 10% | 17.3% | 21.91% | 17.62% | 21.91% | 3.3464 | 0 | 11.4225 | 0.003816 | 41.9371 | FALSE | FALSE | FALSE | TRUE
4 | 13.5096 | 1 | 1.025 | 1.15 | 13.8473 | 81.7687 | 1.15 | 73.74% | 26.26% | 0.30891 | 2.1959 | 5.0391 | 8.5805 | 13.5096 | 13.5096 | 10% | 20.46% | 11.37% | 17.62% | 11.37% | 3.3709 | 0 | 11.4225 | 0.003816 | 42.307 | FALSE | FALSE | FALSE | TRUE
4 | 13.5096 | 1 | 1.025 | 1.2 | 13.8473 | 85.3238 | 1.2 | 78.73% | 21.27% | 0.13958 | 0.81254 | 2.9086 | 6.6041 | 0.3023 | 13.5096 | 10.26% | 23.35% | 4.7% | 17.62% | 4.7% | 3.3828 | 0 | 11.4225 | 0.003816 | 42.4764 | FALSE | FALSE | FALSE | TRUE
4 | 13.5096 | 1 | 1.025 | 1.25 | 13.8473 | 88.879 | 1.25 | 81.21% | 18.79% | 0.079393 | 0.55326 | 1.171 | 4.6276 | 0.19123 | 8.964 | 13.06% | 26% | 1.4% | 17.62% | 1.4% | 3.3875 | 0 | 11.4225 | 0.003816 | 42.5366 | FALSE | FALSE | FALSE | TRUE
4 | 13.5096 | 1 | 1.025 | 1.3 | 13.8473 | 92.4342 | 1.3 | 82.14% | 17.86% | 0.062843 | 0.47814 | 0.9831 | 2.6512 | 0.16314 | 0.28062 | 15.69% | 28.47% | 0.29% | 17.62% | 0.29% | 3.3889 | 0 | 11.4225 | 0.003816 | 42.5531 | FALSE | FALSE | FALSE | TRUE
4 | 13.5096 | 1 | 1.025 | 1.35 | 13.8473 | 95.9893 | 1.35 | 82.36% | 17.64% | 0.060528 | 0.46442 | 0.94985 | 1.3818 | 0.15857 | 0.26938 | 18.07% | 30.75% | 0.02% | 17.62% | 0.02% | 3.3891 | 0 | 11.4225 | 0.003816 | 42.5554 | FALSE | FALSE | FALSE | TRUE
4 | 13.5096 | 1 | 1.025 | 1.4 | 13.8473 | 99.5445 | 1.4 | 82.38% | 17.62% | 0.060426 | 0.46424 | 0.94985 | 1.3818 | 0.158 | 0.26931 | 20.33% | 32.84% | 0% | 17.62% | 0% | 3.3892 | 0 | 11.4225 | 0.003816 | 42.5555 | FALSE | FALSE | FALSE | TRUE
4 | 13.5096 | 1 | 1.025 | 1.45 | 13.8473 | 103.0996 | 1.45 | 82.38% | 17.62% | 0.060426 | 0.46424 | 0.94985 | 1.3818 | 0.158 | 0.26931 | 22.41% | 34.78% | 0% | 17.62% | 0% | 3.3892 | 0 | 11.4225 | 0.003816 | 42.5555 | FALSE | FALSE | FALSE | FALSE
4 | 13.5096 | 1 | 1.025 | 1.5 | 13.8473 | 106.6548 | 1.5 | 82.38% | 17.62% | 0.060426 | 0.46424 | 0.94985 | 1.3818 | 0.158 | 0.26931 | 24.35% | 36.62% | 0% | 17.62% | 0% | 3.3892 | 0 | 11.4225 | 0.003816 | 42.5555 | FALSE | FALSE | FALSE | FALSE
4 | 13.5096 | 1 | 1.025 | 1.55 | 13.8473 | 110.21 | 1.55 | 82.38% | 17.62% | 0.060426 | 0.46424 | 0.94985 | 1.3818 | 0.158 | 0.26931 | 26.16% | 38.34% | 0% | 17.62% | 0% | 3.3892 | 0 | 11.4225 | 0.003816 | 42.5555 | FALSE | FALSE | FALSE | FALSE
4 | 13.5096 | 1 | 1.025 | 1.6 | 13.8473 | 113.7651 | 1.6 | 82.38% | 17.62% | 0.060426 | 0.46424 | 0.94985 | 1.3818 | 0.158 | 0.26931 | 27.88% | 39.96% | 0% | 17.62% | 0% | 3.3892 | 0 | 11.4225 | 0.003816 | 42.5555 | FALSE | FALSE | FALSE | FALSE
4 | 13.5096 | 1 | 1.025 | 1.65 | 13.8473 | 117.3203 | 1.65 | 82.38% | 17.62% | 0.060426 | 0.46424 | 0.94985 | 1.3818 | 0.158 | 0.26931 | 29.49% | 41.48% | 0% | 17.62% | 0% | 3.3892 | 0 | 11.4225 | 0.003816 | 42.5555 | FALSE | FALSE | FALSE | FALSE
4 | 13.5096 | 1 | 1.025 | 1.7 | 13.8473 | 120.8754 | 1.7 | 82.38% | 17.62% | 0.060426 | 0.46424 | 0.94985 | 1.3818 | 0.158 | 0.26931 | 30.99% | 42.92% | 0% | 17.62% | 0% | 3.3892 | 0 | 11.4225 | 0.003816 | 42.5555 | FALSE | FALSE | FALSE | FALSE
4 | 13.5096 | 1 | 1.025 | 1.75 | 13.8473 | 124.4306 | 1.75 | 82.38% | 17.62% | 0.060426 | 0.46424 | 0.94985 | 1.3818 | 0.158 | 0.26931 | 32.4% | 44.23% | 0% | 17.62% | 0% | 3.3892 | 0 | 11.4225 | 0.003816 | 42.5555 | FALSE | FALSE | FALSE | FALSE
4 | 13.5096 | 1 | 1.025 | 1.8 | 13.8473 | 127.9858 | 1.8 | 82.38% | 17.62% | 0.060426 | 0.46424 | 0.94985 | 1.3818 | 0.158 | 0.26931 | 33.74% | 45.49% | 0% | 17.62% | 0% | 3.3892 | 0 | 11.4225 | 0.003816 | 42.5555 | FALSE | FALSE | FALSE | FALSE
4 | 13.5096 | 1 | 1.05 | 1 | 14.1851 | 71.1032 | 1.05 | 49.69% | 50.31% | 2.4166 | 8.9091 | 11.3949 | 14.5098 | 13.5096 | 13.5096 | 10% | 10% | 50.27% | 0.15% | 50.27% | 3.791 | 3.25 | 11.4225 | 0.003816 | 40.1994 | FALSE | FALSE | FALSE | TRUE
4 | 13.5096 | 1 | 1.05 | 1.05 | 14.1851 | 74.6584 | 1.05 | 62.18% | 37.82% | 1.3478 | 6.6654 | 9.274 | 12.5334 | 13.5096 | 13.5096 | 10% | 13.69% | 37.77% | 0.15% | 37.77% | 3.8769 | 3.4167 | 11.4225 | 0.003816 | 41.2682 | FALSE | FALSE | FALSE | TRUE
4 | 13.5096 | 1 | 1.05 | 1.1 | 14.1851 | 78.2135 | 1.1 | 77.36% | 22.64% | 0.6433 | 4.4345 | 7.1591 | 10.5569 | 13.5096 | 13.5096 | 10% | 17.14% | 22.54% | 0.15% | 22.54% | 3.9365 | 3.5833 | 11.4225 | 0.003816 | 41.9727 | FALSE | FALSE | FALSE | TRUE
4 | 13.5096 | 1 | 1.05 | 1.15 | 14.1851 | 81.7687 | 1.15 | 88.05% | 11.95% | 0.2615 | 2.1959 | 5.0391 | 8.5805 | 13.5096 | 13.5096 | 10% | 20.33% | 11.83% | 0.15% | 11.83% | 3.9697 | 3.75 | 11.4225 | 0.003816 | 42.3545 | FALSE | FALSE | FALSE | TRUE
4 | 13.5096 | 1 | 1.05 | 1.2 | 14.1851 | 85.3238 | 1.2 | 94.92% | 5.08% | 0.08423 | 0.0065002 | 2.9086 | 6.6041 | 0.012122 | 13.5096 | 10.07% | 23.2% | 4.94% | 0.15% | 4.94% | 3.9861 | 3.9167 | 11.4225 | 0.003816 | 42.5317 | FALSE | FALSE | FALSE | TRUE
4 | 13.5096 | 1 | 1.05 | 1.25 | 14.1851 | 88.879 | 1.25 | 98.34% | 1.66% | 0.020265 | 0 | 0.79196 | 4.6276 | 0 | 9.5035 | 12.89% | 25.88% | 1.51% | 0.15% | 1.51% | 3.9924 | 4 | 11.4225 | 0.003816 | 42.5957 | TRUE | FALSE | FALSE | TRUE
4 | 13.5096 | 1 | 1.05 | 1.3 | 14.1851 | 92.4342 | 1.3 | 99.54% | 0.46% | 0.0027878 | 0 | 0 | 2.6512 | 0 | 0 | 15.49% | 28.32% | 0.31% | 0.15% | 0.31% | 3.9942 | 4 | 11.4225 | 0.003816 | 42.6132 | TRUE | TRUE | FALSE | TRUE
4 | 13.5096 | 1 | 1.05 | 1.35 | 14.1851 | 95.9893 | 1.35 | 99.83% | 0.17% | 0.00014487 | 0 | 0 | 0.67476 | 0 | 0 | 17.93% | 30.63% | 0.02% | 0.15% | 0.02% | 3.9945 | 4 | 11.4225 | 0.003816 | 42.6158 | TRUE | TRUE | FALSE | TRUE
4 | 13.5096 | 1 | 1.05 | 1.4 | 14.1851 | 99.5445 | 1.4 | 99.85% | 0.15% | 4.2843e-05 | 0 | 0 | 0.097512 | 0 | 0 | 20.2% | 32.74% | 0% | 0.15% | 0% | 3.9946 | 4 | 11.4225 | 0.003816 | 42.6159 | TRUE | TRUE | FALSE | TRUE
4 | 13.5096 | 1 | 1.05 | 1.45 | 14.1851 | 103.0996 | 1.45 | 99.85% | 0.15% | 4.2843e-05 | 0 | 0 | 0.097512 | 0 | 0 | 22.29% | 34.69% | 0% | 0.15% | 0% | 3.9946 | 4 | 11.4225 | 0.003816 | 42.6159 | TRUE | TRUE | FALSE | FALSE
4 | 13.5096 | 1 | 1.05 | 1.5 | 14.1851 | 106.6548 | 1.5 | 99.85% | 0.15% | 4.2843e-05 | 0 | 0 | 0.097512 | 0 | 0 | 24.22% | 36.51% | 0% | 0.15% | 0% | 3.9946 | 4 | 11.4225 | 0.003816 | 42.6159 | TRUE | TRUE | FALSE | FALSE
4 | 13.5096 | 1 | 1.05 | 1.55 | 14.1851 | 110.21 | 1.55 | 99.85% | 0.15% | 4.2843e-05 | 0 | 0 | 0.097512 | 0 | 0 | 26.05% | 38.22% | 0% | 0.15% | 0% | 3.9946 | 4 | 11.4225 | 0.003816 | 42.6159 | TRUE | TRUE | FALSE | FALSE
4 | 13.5096 | 1 | 1.05 | 1.6 | 14.1851 | 113.7651 | 1.6 | 99.85% | 0.15% | 4.2843e-05 | 0 | 0 | 0.097512 | 0 | 0 | 27.77% | 39.84% | 0% | 0.15% | 0% | 3.9946 | 4 | 11.4225 | 0.003816 | 42.6159 | TRUE | TRUE | FALSE | FALSE
4 | 13.5096 | 1 | 1.05 | 1.65 | 14.1851 | 117.3203 | 1.65 | 99.85% | 0.15% | 4.2843e-05 | 0 | 0 | 0.097512 | 0 | 0 | 29.38% | 41.38% | 0% | 0.15% | 0% | 3.9946 | 4 | 11.4225 | 0.003816 | 42.6159 | TRUE | TRUE | FALSE | FALSE
4 | 13.5096 | 1 | 1.05 | 1.7 | 14.1851 | 120.8754 | 1.7 | 99.85% | 0.15% | 4.2843e-05 | 0 | 0 | 0.097512 | 0 | 0 | 30.91% | 42.8% | 0% | 0.15% | 0% | 3.9946 | 4 | 11.4225 | 0.003816 | 42.6159 | TRUE | TRUE | FALSE | FALSE
4 | 13.5096 | 1 | 1.05 | 1.75 | 14.1851 | 124.4306 | 1.75 | 99.85% | 0.15% | 4.2843e-05 | 0 | 0 | 0.097512 | 0 | 0 | 32.33% | 44.15% | 0% | 0.15% | 0% | 3.9946 | 4 | 11.4225 | 0.003816 | 42.6159 | TRUE | TRUE | FALSE | FALSE
4 | 13.5096 | 1 | 1.05 | 1.8 | 14.1851 | 127.9858 | 1.8 | 99.85% | 0.15% | 4.2843e-05 | 0 | 0 | 0.097512 | 0 | 0 | 33.66% | 45.41% | 0% | 0.15% | 0% | 3.9946 | 4 | 11.4225 | 0.003816 | 42.6159 | TRUE | TRUE | FALSE | FALSE
4 | 13.5096 | 1 | 1.075 | 1 | 14.5228 | 71.1032 | 1.075 | 49.73% | 50.27% | 2.4166 | 8.9091 | 11.3949 | 14.5098 | 13.5096 | 13.5096 | 10% | 10% | 50.27% | 0% | 50.27% | 3.796 | 3.25 | 11.4225 | 0.003816 | 40.1994 | FALSE | FALSE | FALSE | TRUE
4 | 13.5096 | 1 | 1.075 | 1.05 | 14.5228 | 74.6584 | 1.075 | 62.23% | 37.77% | 1.3478 | 6.6654 | 9.274 | 12.5334 | 13.5096 | 13.5096 | 10% | 13.69% | 37.77% | 0% | 37.77% | 3.8821 | 3.4167 | 11.4225 | 0.003816 | 41.2682 | FALSE | FALSE | FALSE | TRUE
4 | 13.5096 | 1 | 1.075 | 1.1 | 14.5228 | 78.2135 | 1.1 | 77.46% | 22.54% | 0.64327 | 4.4345 | 7.1591 | 10.5569 | 13.5096 | 13.5096 | 10% | 17.14% | 22.54% | 0% | 22.54% | 3.9418 | 3.5833 | 11.4225 | 0.003816 | 41.9727 | FALSE | FALSE | FALSE | TRUE
4 | 13.5096 | 1 | 1.075 | 1.15 | 14.5228 | 81.7687 | 1.15 | 88.17% | 11.83% | 0.26146 | 2.1959 | 5.0391 | 8.5805 | 13.5096 | 13.5096 | 10% | 20.33% | 11.83% | 0% | 11.83% | 3.9751 | 3.8333 | 11.4225 | 0.003816 | 42.3545 | FALSE | FALSE | FALSE | TRUE
4 | 13.5096 | 1 | 1.075 | 1.2 | 14.5228 | 85.3238 | 1.2 | 95.06% | 4.94% | 0.084191 | 0 | 2.9086 | 6.6041 | 0 | 13.5096 | 10.07% | 23.2% | 4.94% | 0% | 4.94% | 3.9915 | 4 | 11.4225 | 0.003816 | 42.5318 | TRUE | FALSE | FALSE | TRUE
4 | 13.5096 | 1 | 1.075 | 1.25 | 14.5228 | 88.879 | 1.25 | 98.49% | 1.51% | 0.020222 | 0 | 0.79196 | 4.6276 | 0 | 9.5035 | 12.89% | 25.88% | 1.51% | 0% | 1.51% | 3.9978 | 4 | 11.4225 | 0.003816 | 42.5957 | TRUE | FALSE | FALSE | TRUE
4 | 13.5096 | 1 | 1.075 | 1.3 | 14.5228 | 92.4342 | 1.3 | 99.69% | 0.31% | 0.002745 | 0 | 0 | 2.6512 | 0 | 0 | 15.49% | 28.32% | 0.31% | 0% | 0.31% | 3.9996 | 4 | 11.4225 | 0.003816 | 42.6132 | TRUE | TRUE | FALSE | TRUE
4 | 13.5096 | 1 | 1.075 | 1.35 | 14.5228 | 95.9893 | 1.35 | 99.98% | 0.02% | 0.00010203 | 0 | 0 | 0.67476 | 0 | 0 | 17.93% | 30.63% | 0.02% | 0% | 0.02% | 4 | 4 | 11.4225 | 0.003816 | 42.6159 | TRUE | TRUE | TRUE | TRUE
4 | 13.5096 | 1 | 1.075 | 1.4 | 14.5228 | 99.5445 | 1.4 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 20.2% | 32.74% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | TRUE
4 | 13.5096 | 1 | 1.075 | 1.45 | 14.5228 | 103.0996 | 1.45 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 22.29% | 34.69% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.075 | 1.5 | 14.5228 | 106.6548 | 1.5 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 24.22% | 36.51% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.075 | 1.55 | 14.5228 | 110.21 | 1.55 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 26.05% | 38.22% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.075 | 1.6 | 14.5228 | 113.7651 | 1.6 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 27.77% | 39.84% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.075 | 1.65 | 14.5228 | 117.3203 | 1.65 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 29.38% | 41.38% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.075 | 1.7 | 14.5228 | 120.8754 | 1.7 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 30.91% | 42.8% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.075 | 1.75 | 14.5228 | 124.4306 | 1.75 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 32.33% | 44.15% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.075 | 1.8 | 14.5228 | 127.9858 | 1.8 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 33.66% | 45.41% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.1 | 1 | 14.8606 | 71.1032 | 1.1 | 49.73% | 50.27% | 2.4166 | 8.9091 | 11.3949 | 14.5098 | 13.5096 | 13.5096 | 10% | 10% | 50.27% | 0% | 50.27% | 3.796 | 3.25 | 11.4225 | 0.003816 | 40.1994 | FALSE | FALSE | FALSE | FALSE
4 | 13.5096 | 1 | 1.1 | 1.05 | 14.8606 | 74.6584 | 1.1 | 62.23% | 37.77% | 1.3478 | 6.6654 | 9.274 | 12.5334 | 13.5096 | 13.5096 | 10% | 13.69% | 37.77% | 0% | 37.77% | 3.8821 | 3.4167 | 11.4225 | 0.003816 | 41.2682 | FALSE | FALSE | FALSE | FALSE
4 | 13.5096 | 1 | 1.1 | 1.1 | 14.8606 | 78.2135 | 1.1 | 77.46% | 22.54% | 0.64327 | 4.4345 | 7.1591 | 10.5569 | 13.5096 | 13.5096 | 10% | 17.14% | 22.54% | 0% | 22.54% | 3.9418 | 3.5833 | 11.4225 | 0.003816 | 41.9727 | FALSE | FALSE | FALSE | FALSE
4 | 13.5096 | 1 | 1.1 | 1.15 | 14.8606 | 81.7687 | 1.15 | 88.17% | 11.83% | 0.26146 | 2.1959 | 5.0391 | 8.5805 | 13.5096 | 13.5096 | 10% | 20.33% | 11.83% | 0% | 11.83% | 3.9751 | 3.8333 | 11.4225 | 0.003816 | 42.3545 | FALSE | FALSE | FALSE | FALSE
4 | 13.5096 | 1 | 1.1 | 1.2 | 14.8606 | 85.3238 | 1.2 | 95.06% | 4.94% | 0.084191 | 0 | 2.9086 | 6.6041 | 0 | 13.5096 | 10.07% | 23.2% | 4.94% | 0% | 4.94% | 3.9915 | 4 | 11.4225 | 0.003816 | 42.5318 | TRUE | FALSE | FALSE | FALSE
4 | 13.5096 | 1 | 1.1 | 1.25 | 14.8606 | 88.879 | 1.25 | 98.49% | 1.51% | 0.020222 | 0 | 0.79196 | 4.6276 | 0 | 9.5035 | 12.89% | 25.88% | 1.51% | 0% | 1.51% | 3.9978 | 4 | 11.4225 | 0.003816 | 42.5957 | TRUE | FALSE | FALSE | FALSE
4 | 13.5096 | 1 | 1.1 | 1.3 | 14.8606 | 92.4342 | 1.3 | 99.69% | 0.31% | 0.002745 | 0 | 0 | 2.6512 | 0 | 0 | 15.49% | 28.32% | 0.31% | 0% | 0.31% | 3.9996 | 4 | 11.4225 | 0.003816 | 42.6132 | TRUE | TRUE | FALSE | FALSE
4 | 13.5096 | 1 | 1.1 | 1.35 | 14.8606 | 95.9893 | 1.35 | 99.98% | 0.02% | 0.00010203 | 0 | 0 | 0.67476 | 0 | 0 | 17.93% | 30.63% | 0.02% | 0% | 0.02% | 4 | 4 | 11.4225 | 0.003816 | 42.6159 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.1 | 1.4 | 14.8606 | 99.5445 | 1.4 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 20.2% | 32.74% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.1 | 1.45 | 14.8606 | 103.0996 | 1.45 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 22.29% | 34.69% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.1 | 1.5 | 14.8606 | 106.6548 | 1.5 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 24.22% | 36.51% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.1 | 1.55 | 14.8606 | 110.21 | 1.55 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 26.05% | 38.22% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.1 | 1.6 | 14.8606 | 113.7651 | 1.6 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 27.77% | 39.84% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.1 | 1.65 | 14.8606 | 117.3203 | 1.65 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 29.38% | 41.38% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.1 | 1.7 | 14.8606 | 120.8754 | 1.7 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 30.91% | 42.8% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.1 | 1.75 | 14.8606 | 124.4306 | 1.75 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 32.33% | 44.15% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.1 | 1.8 | 14.8606 | 127.9858 | 1.8 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 33.66% | 45.41% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.125 | 1 | 15.1983 | 71.1032 | 1.125 | 49.73% | 50.27% | 2.4166 | 8.9091 | 11.3949 | 14.5098 | 13.5096 | 13.5096 | 10% | 10% | 50.27% | 0% | 50.27% | 3.796 | 3.25 | 11.4225 | 0.003816 | 40.1994 | FALSE | FALSE | FALSE | FALSE
4 | 13.5096 | 1 | 1.125 | 1.05 | 15.1983 | 74.6584 | 1.125 | 62.23% | 37.77% | 1.3478 | 6.6654 | 9.274 | 12.5334 | 13.5096 | 13.5096 | 10% | 13.69% | 37.77% | 0% | 37.77% | 3.8821 | 3.4167 | 11.4225 | 0.003816 | 41.2682 | FALSE | FALSE | FALSE | FALSE
4 | 13.5096 | 1 | 1.125 | 1.1 | 15.1983 | 78.2135 | 1.125 | 77.46% | 22.54% | 0.64327 | 4.4345 | 7.1591 | 10.5569 | 13.5096 | 13.5096 | 10% | 17.14% | 22.54% | 0% | 22.54% | 3.9418 | 3.5833 | 11.4225 | 0.003816 | 41.9727 | FALSE | FALSE | FALSE | FALSE
4 | 13.5096 | 1 | 1.125 | 1.15 | 15.1983 | 81.7687 | 1.15 | 88.17% | 11.83% | 0.26146 | 2.1959 | 5.0391 | 8.5805 | 13.5096 | 13.5096 | 10% | 20.33% | 11.83% | 0% | 11.83% | 3.9751 | 3.8333 | 11.4225 | 0.003816 | 42.3545 | FALSE | FALSE | FALSE | FALSE
4 | 13.5096 | 1 | 1.125 | 1.2 | 15.1983 | 85.3238 | 1.2 | 95.06% | 4.94% | 0.084191 | 0 | 2.9086 | 6.6041 | 0 | 13.5096 | 10.07% | 23.2% | 4.94% | 0% | 4.94% | 3.9915 | 4 | 11.4225 | 0.003816 | 42.5318 | TRUE | FALSE | FALSE | FALSE
4 | 13.5096 | 1 | 1.125 | 1.25 | 15.1983 | 88.879 | 1.25 | 98.49% | 1.51% | 0.020222 | 0 | 0.79196 | 4.6276 | 0 | 9.5035 | 12.89% | 25.88% | 1.51% | 0% | 1.51% | 3.9978 | 4 | 11.4225 | 0.003816 | 42.5957 | TRUE | FALSE | FALSE | FALSE
4 | 13.5096 | 1 | 1.125 | 1.3 | 15.1983 | 92.4342 | 1.3 | 99.69% | 0.31% | 0.002745 | 0 | 0 | 2.6512 | 0 | 0 | 15.49% | 28.32% | 0.31% | 0% | 0.31% | 3.9996 | 4 | 11.4225 | 0.003816 | 42.6132 | TRUE | TRUE | FALSE | FALSE
4 | 13.5096 | 1 | 1.125 | 1.35 | 15.1983 | 95.9893 | 1.35 | 99.98% | 0.02% | 0.00010203 | 0 | 0 | 0.67476 | 0 | 0 | 17.93% | 30.63% | 0.02% | 0% | 0.02% | 4 | 4 | 11.4225 | 0.003816 | 42.6159 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.125 | 1.4 | 15.1983 | 99.5445 | 1.4 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 20.2% | 32.74% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.125 | 1.45 | 15.1983 | 103.0996 | 1.45 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 22.29% | 34.69% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.125 | 1.5 | 15.1983 | 106.6548 | 1.5 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 24.22% | 36.51% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.125 | 1.55 | 15.1983 | 110.21 | 1.55 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 26.05% | 38.22% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.125 | 1.6 | 15.1983 | 113.7651 | 1.6 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 27.77% | 39.84% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.125 | 1.65 | 15.1983 | 117.3203 | 1.65 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 29.38% | 41.38% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.125 | 1.7 | 15.1983 | 120.8754 | 1.7 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 30.91% | 42.8% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.125 | 1.75 | 15.1983 | 124.4306 | 1.75 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 32.33% | 44.15% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.125 | 1.8 | 15.1983 | 127.9858 | 1.8 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 33.66% | 45.41% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.15 | 1 | 15.536 | 71.1032 | 1.15 | 49.73% | 50.27% | 2.4166 | 8.9091 | 11.3949 | 14.5098 | 13.5096 | 13.5096 | 10% | 10% | 50.27% | 0% | 50.27% | 3.796 | 3.25 | 11.4225 | 0.003816 | 40.1994 | FALSE | FALSE | FALSE | FALSE
4 | 13.5096 | 1 | 1.15 | 1.05 | 15.536 | 74.6584 | 1.15 | 62.23% | 37.77% | 1.3478 | 6.6654 | 9.274 | 12.5334 | 13.5096 | 13.5096 | 10% | 13.69% | 37.77% | 0% | 37.77% | 3.8821 | 3.4167 | 11.4225 | 0.003816 | 41.2682 | FALSE | FALSE | FALSE | FALSE
4 | 13.5096 | 1 | 1.15 | 1.1 | 15.536 | 78.2135 | 1.15 | 77.46% | 22.54% | 0.64327 | 4.4345 | 7.1591 | 10.5569 | 13.5096 | 13.5096 | 10% | 17.14% | 22.54% | 0% | 22.54% | 3.9418 | 3.5833 | 11.4225 | 0.003816 | 41.9727 | FALSE | FALSE | FALSE | FALSE
4 | 13.5096 | 1 | 1.15 | 1.15 | 15.536 | 81.7687 | 1.15 | 88.17% | 11.83% | 0.26146 | 2.1959 | 5.0391 | 8.5805 | 13.5096 | 13.5096 | 10% | 20.33% | 11.83% | 0% | 11.83% | 3.9751 | 3.8333 | 11.4225 | 0.003816 | 42.3545 | FALSE | FALSE | FALSE | FALSE
4 | 13.5096 | 1 | 1.15 | 1.2 | 15.536 | 85.3238 | 1.2 | 95.06% | 4.94% | 0.084191 | 0 | 2.9086 | 6.6041 | 0 | 13.5096 | 10.07% | 23.2% | 4.94% | 0% | 4.94% | 3.9915 | 4 | 11.4225 | 0.003816 | 42.5318 | TRUE | FALSE | FALSE | FALSE
4 | 13.5096 | 1 | 1.15 | 1.25 | 15.536 | 88.879 | 1.25 | 98.49% | 1.51% | 0.020222 | 0 | 0.79196 | 4.6276 | 0 | 9.5035 | 12.89% | 25.88% | 1.51% | 0% | 1.51% | 3.9978 | 4 | 11.4225 | 0.003816 | 42.5957 | TRUE | FALSE | FALSE | FALSE
4 | 13.5096 | 1 | 1.15 | 1.3 | 15.536 | 92.4342 | 1.3 | 99.69% | 0.31% | 0.002745 | 0 | 0 | 2.6512 | 0 | 0 | 15.49% | 28.32% | 0.31% | 0% | 0.31% | 3.9996 | 4 | 11.4225 | 0.003816 | 42.6132 | TRUE | TRUE | FALSE | FALSE
4 | 13.5096 | 1 | 1.15 | 1.35 | 15.536 | 95.9893 | 1.35 | 99.98% | 0.02% | 0.00010203 | 0 | 0 | 0.67476 | 0 | 0 | 17.93% | 30.63% | 0.02% | 0% | 0.02% | 4 | 4 | 11.4225 | 0.003816 | 42.6159 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.15 | 1.4 | 15.536 | 99.5445 | 1.4 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 20.2% | 32.74% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.15 | 1.45 | 15.536 | 103.0996 | 1.45 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 22.29% | 34.69% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.15 | 1.5 | 15.536 | 106.6548 | 1.5 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 24.22% | 36.51% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.15 | 1.55 | 15.536 | 110.21 | 1.55 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 26.05% | 38.22% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.15 | 1.6 | 15.536 | 113.7651 | 1.6 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 27.77% | 39.84% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.15 | 1.65 | 15.536 | 117.3203 | 1.65 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 29.38% | 41.38% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.15 | 1.7 | 15.536 | 120.8754 | 1.7 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 30.91% | 42.8% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.15 | 1.75 | 15.536 | 124.4306 | 1.75 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 32.33% | 44.15% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.15 | 1.8 | 15.536 | 127.9858 | 1.8 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 33.66% | 45.41% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.175 | 1 | 15.8738 | 71.1032 | 1.175 | 49.73% | 50.27% | 2.4166 | 8.9091 | 11.3949 | 14.5098 | 13.5096 | 13.5096 | 10% | 10% | 50.27% | 0% | 50.27% | 3.796 | 3.25 | 11.4225 | 0.003816 | 40.1994 | FALSE | FALSE | FALSE | FALSE
4 | 13.5096 | 1 | 1.175 | 1.05 | 15.8738 | 74.6584 | 1.175 | 62.23% | 37.77% | 1.3478 | 6.6654 | 9.274 | 12.5334 | 13.5096 | 13.5096 | 10% | 13.69% | 37.77% | 0% | 37.77% | 3.8821 | 3.4167 | 11.4225 | 0.003816 | 41.2682 | FALSE | FALSE | FALSE | FALSE
4 | 13.5096 | 1 | 1.175 | 1.1 | 15.8738 | 78.2135 | 1.175 | 77.46% | 22.54% | 0.64327 | 4.4345 | 7.1591 | 10.5569 | 13.5096 | 13.5096 | 10% | 17.14% | 22.54% | 0% | 22.54% | 3.9418 | 3.5833 | 11.4225 | 0.003816 | 41.9727 | FALSE | FALSE | FALSE | FALSE
4 | 13.5096 | 1 | 1.175 | 1.15 | 15.8738 | 81.7687 | 1.175 | 88.17% | 11.83% | 0.26146 | 2.1959 | 5.0391 | 8.5805 | 13.5096 | 13.5096 | 10% | 20.33% | 11.83% | 0% | 11.83% | 3.9751 | 3.8333 | 11.4225 | 0.003816 | 42.3545 | FALSE | FALSE | FALSE | FALSE
4 | 13.5096 | 1 | 1.175 | 1.2 | 15.8738 | 85.3238 | 1.2 | 95.06% | 4.94% | 0.084191 | 0 | 2.9086 | 6.6041 | 0 | 13.5096 | 10.07% | 23.2% | 4.94% | 0% | 4.94% | 3.9915 | 4 | 11.4225 | 0.003816 | 42.5318 | TRUE | FALSE | FALSE | FALSE
4 | 13.5096 | 1 | 1.175 | 1.25 | 15.8738 | 88.879 | 1.25 | 98.49% | 1.51% | 0.020222 | 0 | 0.79196 | 4.6276 | 0 | 9.5035 | 12.89% | 25.88% | 1.51% | 0% | 1.51% | 3.9978 | 4 | 11.4225 | 0.003816 | 42.5957 | TRUE | FALSE | FALSE | FALSE
4 | 13.5096 | 1 | 1.175 | 1.3 | 15.8738 | 92.4342 | 1.3 | 99.69% | 0.31% | 0.002745 | 0 | 0 | 2.6512 | 0 | 0 | 15.49% | 28.32% | 0.31% | 0% | 0.31% | 3.9996 | 4 | 11.4225 | 0.003816 | 42.6132 | TRUE | TRUE | FALSE | FALSE
4 | 13.5096 | 1 | 1.175 | 1.35 | 15.8738 | 95.9893 | 1.35 | 99.98% | 0.02% | 0.00010203 | 0 | 0 | 0.67476 | 0 | 0 | 17.93% | 30.63% | 0.02% | 0% | 0.02% | 4 | 4 | 11.4225 | 0.003816 | 42.6159 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.175 | 1.4 | 15.8738 | 99.5445 | 1.4 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 20.2% | 32.74% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.175 | 1.45 | 15.8738 | 103.0996 | 1.45 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 22.29% | 34.69% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.175 | 1.5 | 15.8738 | 106.6548 | 1.5 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 24.22% | 36.51% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.175 | 1.55 | 15.8738 | 110.21 | 1.55 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 26.05% | 38.22% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.175 | 1.6 | 15.8738 | 113.7651 | 1.6 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 27.77% | 39.84% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.175 | 1.65 | 15.8738 | 117.3203 | 1.65 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 29.38% | 41.38% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.175 | 1.7 | 15.8738 | 120.8754 | 1.7 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 30.91% | 42.8% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.175 | 1.75 | 15.8738 | 124.4306 | 1.75 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 32.33% | 44.15% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.175 | 1.8 | 15.8738 | 127.9858 | 1.8 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 33.66% | 45.41% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.2 | 1 | 16.2115 | 71.1032 | 1.2 | 49.73% | 50.27% | 2.4166 | 8.9091 | 11.3949 | 14.5098 | 13.5096 | 13.5096 | 10% | 10% | 50.27% | 0% | 50.27% | 3.796 | 3.25 | 11.4225 | 0.003816 | 40.1994 | FALSE | FALSE | FALSE | FALSE
4 | 13.5096 | 1 | 1.2 | 1.05 | 16.2115 | 74.6584 | 1.2 | 62.23% | 37.77% | 1.3478 | 6.6654 | 9.274 | 12.5334 | 13.5096 | 13.5096 | 10% | 13.69% | 37.77% | 0% | 37.77% | 3.8821 | 3.4167 | 11.4225 | 0.003816 | 41.2682 | FALSE | FALSE | FALSE | FALSE
4 | 13.5096 | 1 | 1.2 | 1.1 | 16.2115 | 78.2135 | 1.2 | 77.46% | 22.54% | 0.64327 | 4.4345 | 7.1591 | 10.5569 | 13.5096 | 13.5096 | 10% | 17.14% | 22.54% | 0% | 22.54% | 3.9418 | 3.5833 | 11.4225 | 0.003816 | 41.9727 | FALSE | FALSE | FALSE | FALSE
4 | 13.5096 | 1 | 1.2 | 1.15 | 16.2115 | 81.7687 | 1.2 | 88.17% | 11.83% | 0.26146 | 2.1959 | 5.0391 | 8.5805 | 13.5096 | 13.5096 | 10% | 20.33% | 11.83% | 0% | 11.83% | 3.9751 | 3.8333 | 11.4225 | 0.003816 | 42.3545 | FALSE | FALSE | FALSE | FALSE
4 | 13.5096 | 1 | 1.2 | 1.2 | 16.2115 | 85.3238 | 1.2 | 95.06% | 4.94% | 0.084191 | 0 | 2.9086 | 6.6041 | 0 | 13.5096 | 10.07% | 23.2% | 4.94% | 0% | 4.94% | 3.9915 | 4 | 11.4225 | 0.003816 | 42.5318 | TRUE | FALSE | FALSE | FALSE
4 | 13.5096 | 1 | 1.2 | 1.25 | 16.2115 | 88.879 | 1.25 | 98.49% | 1.51% | 0.020222 | 0 | 0.79196 | 4.6276 | 0 | 9.5035 | 12.89% | 25.88% | 1.51% | 0% | 1.51% | 3.9978 | 4 | 11.4225 | 0.003816 | 42.5957 | TRUE | FALSE | FALSE | FALSE
4 | 13.5096 | 1 | 1.2 | 1.3 | 16.2115 | 92.4342 | 1.3 | 99.69% | 0.31% | 0.002745 | 0 | 0 | 2.6512 | 0 | 0 | 15.49% | 28.32% | 0.31% | 0% | 0.31% | 3.9996 | 4 | 11.4225 | 0.003816 | 42.6132 | TRUE | TRUE | FALSE | FALSE
4 | 13.5096 | 1 | 1.2 | 1.35 | 16.2115 | 95.9893 | 1.35 | 99.98% | 0.02% | 0.00010203 | 0 | 0 | 0.67476 | 0 | 0 | 17.93% | 30.63% | 0.02% | 0% | 0.02% | 4 | 4 | 11.4225 | 0.003816 | 42.6159 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.2 | 1.4 | 16.2115 | 99.5445 | 1.4 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 20.2% | 32.74% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.2 | 1.45 | 16.2115 | 103.0996 | 1.45 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 22.29% | 34.69% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.2 | 1.5 | 16.2115 | 106.6548 | 1.5 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 24.22% | 36.51% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.2 | 1.55 | 16.2115 | 110.21 | 1.55 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 26.05% | 38.22% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.2 | 1.6 | 16.2115 | 113.7651 | 1.6 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 27.77% | 39.84% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.2 | 1.65 | 16.2115 | 117.3203 | 1.65 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 29.38% | 41.38% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.2 | 1.7 | 16.2115 | 120.8754 | 1.7 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 30.91% | 42.8% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.2 | 1.75 | 16.2115 | 124.4306 | 1.75 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 32.33% | 44.15% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.2 | 1.8 | 16.2115 | 127.9858 | 1.8 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 33.66% | 45.41% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.225 | 1 | 16.5493 | 71.1032 | 1.225 | 49.73% | 50.27% | 2.4166 | 8.9091 | 11.3949 | 14.5098 | 13.5096 | 13.5096 | 10% | 10% | 50.27% | 0% | 50.27% | 3.796 | 3.25 | 11.4225 | 0.003816 | 40.1994 | FALSE | FALSE | FALSE | FALSE
4 | 13.5096 | 1 | 1.225 | 1.05 | 16.5493 | 74.6584 | 1.225 | 62.23% | 37.77% | 1.3478 | 6.6654 | 9.274 | 12.5334 | 13.5096 | 13.5096 | 10% | 13.69% | 37.77% | 0% | 37.77% | 3.8821 | 3.4167 | 11.4225 | 0.003816 | 41.2682 | FALSE | FALSE | FALSE | FALSE
4 | 13.5096 | 1 | 1.225 | 1.1 | 16.5493 | 78.2135 | 1.225 | 77.46% | 22.54% | 0.64327 | 4.4345 | 7.1591 | 10.5569 | 13.5096 | 13.5096 | 10% | 17.14% | 22.54% | 0% | 22.54% | 3.9418 | 3.5833 | 11.4225 | 0.003816 | 41.9727 | FALSE | FALSE | FALSE | FALSE
4 | 13.5096 | 1 | 1.225 | 1.15 | 16.5493 | 81.7687 | 1.225 | 88.17% | 11.83% | 0.26146 | 2.1959 | 5.0391 | 8.5805 | 13.5096 | 13.5096 | 10% | 20.33% | 11.83% | 0% | 11.83% | 3.9751 | 3.8333 | 11.4225 | 0.003816 | 42.3545 | FALSE | FALSE | FALSE | FALSE
4 | 13.5096 | 1 | 1.225 | 1.2 | 16.5493 | 85.3238 | 1.225 | 95.06% | 4.94% | 0.084191 | 0 | 2.9086 | 6.6041 | 0 | 13.5096 | 10.07% | 23.2% | 4.94% | 0% | 4.94% | 3.9915 | 4 | 11.4225 | 0.003816 | 42.5318 | TRUE | FALSE | FALSE | FALSE
4 | 13.5096 | 1 | 1.225 | 1.25 | 16.5493 | 88.879 | 1.25 | 98.49% | 1.51% | 0.020222 | 0 | 0.79196 | 4.6276 | 0 | 9.5035 | 12.89% | 25.88% | 1.51% | 0% | 1.51% | 3.9978 | 4 | 11.4225 | 0.003816 | 42.5957 | TRUE | FALSE | FALSE | FALSE
4 | 13.5096 | 1 | 1.225 | 1.3 | 16.5493 | 92.4342 | 1.3 | 99.69% | 0.31% | 0.002745 | 0 | 0 | 2.6512 | 0 | 0 | 15.49% | 28.32% | 0.31% | 0% | 0.31% | 3.9996 | 4 | 11.4225 | 0.003816 | 42.6132 | TRUE | TRUE | FALSE | FALSE
4 | 13.5096 | 1 | 1.225 | 1.35 | 16.5493 | 95.9893 | 1.35 | 99.98% | 0.02% | 0.00010203 | 0 | 0 | 0.67476 | 0 | 0 | 17.93% | 30.63% | 0.02% | 0% | 0.02% | 4 | 4 | 11.4225 | 0.003816 | 42.6159 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.225 | 1.4 | 16.5493 | 99.5445 | 1.4 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 20.2% | 32.74% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.225 | 1.45 | 16.5493 | 103.0996 | 1.45 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 22.29% | 34.69% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.225 | 1.5 | 16.5493 | 106.6548 | 1.5 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 24.22% | 36.51% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.225 | 1.55 | 16.5493 | 110.21 | 1.55 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 26.05% | 38.22% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.225 | 1.6 | 16.5493 | 113.7651 | 1.6 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 27.77% | 39.84% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.225 | 1.65 | 16.5493 | 117.3203 | 1.65 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 29.38% | 41.38% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.225 | 1.7 | 16.5493 | 120.8754 | 1.7 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 30.91% | 42.8% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.225 | 1.75 | 16.5493 | 124.4306 | 1.75 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 32.33% | 44.15% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.225 | 1.8 | 16.5493 | 127.9858 | 1.8 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 33.66% | 45.41% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.25 | 1 | 16.887 | 71.1032 | 1.25 | 49.73% | 50.27% | 2.4166 | 8.9091 | 11.3949 | 14.5098 | 13.5096 | 13.5096 | 10% | 10% | 50.27% | 0% | 50.27% | 3.796 | 3.25 | 11.4225 | 0.003816 | 40.1994 | FALSE | FALSE | FALSE | FALSE
4 | 13.5096 | 1 | 1.25 | 1.05 | 16.887 | 74.6584 | 1.25 | 62.23% | 37.77% | 1.3478 | 6.6654 | 9.274 | 12.5334 | 13.5096 | 13.5096 | 10% | 13.69% | 37.77% | 0% | 37.77% | 3.8821 | 3.4167 | 11.4225 | 0.003816 | 41.2682 | FALSE | FALSE | FALSE | FALSE
4 | 13.5096 | 1 | 1.25 | 1.1 | 16.887 | 78.2135 | 1.25 | 77.46% | 22.54% | 0.64327 | 4.4345 | 7.1591 | 10.5569 | 13.5096 | 13.5096 | 10% | 17.14% | 22.54% | 0% | 22.54% | 3.9418 | 3.5833 | 11.4225 | 0.003816 | 41.9727 | FALSE | FALSE | FALSE | FALSE
4 | 13.5096 | 1 | 1.25 | 1.15 | 16.887 | 81.7687 | 1.25 | 88.17% | 11.83% | 0.26146 | 2.1959 | 5.0391 | 8.5805 | 13.5096 | 13.5096 | 10% | 20.33% | 11.83% | 0% | 11.83% | 3.9751 | 3.8333 | 11.4225 | 0.003816 | 42.3545 | FALSE | FALSE | FALSE | FALSE
4 | 13.5096 | 1 | 1.25 | 1.2 | 16.887 | 85.3238 | 1.25 | 95.06% | 4.94% | 0.084191 | 0 | 2.9086 | 6.6041 | 0 | 13.5096 | 10.07% | 23.2% | 4.94% | 0% | 4.94% | 3.9915 | 4 | 11.4225 | 0.003816 | 42.5318 | TRUE | FALSE | FALSE | FALSE
4 | 13.5096 | 1 | 1.25 | 1.25 | 16.887 | 88.879 | 1.25 | 98.49% | 1.51% | 0.020222 | 0 | 0.79196 | 4.6276 | 0 | 9.5035 | 12.89% | 25.88% | 1.51% | 0% | 1.51% | 3.9978 | 4 | 11.4225 | 0.003816 | 42.5957 | TRUE | FALSE | FALSE | FALSE
4 | 13.5096 | 1 | 1.25 | 1.3 | 16.887 | 92.4342 | 1.3 | 99.69% | 0.31% | 0.002745 | 0 | 0 | 2.6512 | 0 | 0 | 15.49% | 28.32% | 0.31% | 0% | 0.31% | 3.9996 | 4 | 11.4225 | 0.003816 | 42.6132 | TRUE | TRUE | FALSE | FALSE
4 | 13.5096 | 1 | 1.25 | 1.35 | 16.887 | 95.9893 | 1.35 | 99.98% | 0.02% | 0.00010203 | 0 | 0 | 0.67476 | 0 | 0 | 17.93% | 30.63% | 0.02% | 0% | 0.02% | 4 | 4 | 11.4225 | 0.003816 | 42.6159 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.25 | 1.4 | 16.887 | 99.5445 | 1.4 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 20.2% | 32.74% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.25 | 1.45 | 16.887 | 103.0996 | 1.45 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 22.29% | 34.69% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.25 | 1.5 | 16.887 | 106.6548 | 1.5 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 24.22% | 36.51% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.25 | 1.55 | 16.887 | 110.21 | 1.55 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 26.05% | 38.22% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.25 | 1.6 | 16.887 | 113.7651 | 1.6 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 27.77% | 39.84% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.25 | 1.65 | 16.887 | 117.3203 | 1.65 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 29.38% | 41.38% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.25 | 1.7 | 16.887 | 120.8754 | 1.7 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 30.91% | 42.8% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.25 | 1.75 | 16.887 | 124.4306 | 1.75 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 32.33% | 44.15% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE
4 | 13.5096 | 1 | 1.25 | 1.8 | 16.887 | 127.9858 | 1.8 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 33.66% | 45.41% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | FALSE

## Pareto_Designs
OutageDurationHours | PVCapacityMW | PVCapacityRatioToDC | PowerMultiplier | EnergyMultiplier | BatteryPowerMW | BatteryInstalledMWh | MaxRelativeOversize | SuccessRate | FailureRate | MeanUnservedEnergyMWh | P95UnservedEnergyMWh | P99UnservedEnergyMWh | MaximumUnservedEnergyMWh | P95PeakUnservedPowerMW | P99PeakUnservedPowerMW | P05MinimumSOCFraction | P50MinimumSOCFraction | MinimumSOCHitRate | PCSConstraintEncounterRate | EnergyConstraintEncounterRate | MeanEnduranceHours | P05EnduranceHours | MeanPVDirectMWh | MeanPVChargeToBatteryACMWh | MeanBatteryDeliveredMWh | Meets_95_0pct | Meets_99_0pct | Meets_99_9pct | ParetoEfficient
4 | 0 | 0 | 1 | 1 | 13.5096 | 71.1032 | 1 | 0% | 100% | 5.1257 | 10.3385 | 12.1842 | 14.5098 | 13.5096 | 13.5096 | 10% | 10% | 91.63% | 100% | 91.63% | 0 | 0 | 0 | 0 | 48.9128 | FALSE | FALSE | FALSE | TRUE
4 | 0 | 0 | 1.025 | 1 | 13.8473 | 71.1032 | 1.025 | 2.24% | 97.76% | 5.0711 | 10.3385 | 12.1842 | 14.5098 | 13.5096 | 13.5096 | 10% | 10% | 96.27% | 26.34% | 96.27% | 2.6399 | 0 | 0 | 0 | 48.9673 | FALSE | FALSE | FALSE | TRUE
4 | 0 | 0 | 1.025 | 1.05 | 13.8473 | 74.6584 | 1.05 | 16.62% | 83.38% | 2.9545 | 8.1535 | 10.0915 | 12.5334 | 13.5096 | 13.5096 | 10% | 10% | 76.15% | 26.34% | 76.15% | 2.7625 | 0 | 0 | 0 | 51.0839 | FALSE | FALSE | FALSE | TRUE
4 | 0 | 0 | 1.025 | 1.1 | 13.8473 | 78.2135 | 1.1 | 37.85% | 62.15% | 1.4986 | 5.9685 | 7.9987 | 10.5569 | 13.5096 | 13.5096 | 10% | 10.33% | 47.44% | 26.34% | 47.44% | 2.8526 | 0 | 0 | 0 | 52.5399 | FALSE | FALSE | FALSE | TRUE
4 | 0 | 0 | 1.025 | 1.15 | 13.8473 | 81.7687 | 1.15 | 54.44% | 45.56% | 0.68704 | 3.7835 | 5.906 | 8.5805 | 13.5096 | 13.5096 | 10% | 13.66% | 24.95% | 26.34% | 24.95% | 2.9053 | 0 | 0 | 0 | 53.3514 | FALSE | FALSE | FALSE | TRUE
4 | 0 | 0 | 1.025 | 1.2 | 13.8473 | 85.3238 | 1.2 | 65.16% | 34.84% | 0.30433 | 1.5985 | 3.8133 | 6.6041 | 13.5096 | 13.5096 | 10% | 16.73% | 10.89% | 26.34% | 10.89% | 2.9319 | 0 | 0 | 0 | 53.7341 | FALSE | FALSE | FALSE | TRUE
4 | 0 | 0 | 1.025 | 1.25 | 13.8473 | 88.879 | 1.25 | 70.94% | 29.06% | 0.16403 | 0.92667 | 1.7206 | 4.6276 | 0.26411 | 13.5096 | 10.88% | 19.56% | 3.33% | 26.34% | 3.33% | 2.9426 | 0 | 0 | 0 | 53.8744 | FALSE | FALSE | FALSE | TRUE
4 | 0 | 0 | 1.025 | 1.3 | 13.8473 | 92.4342 | 1.3 | 73.14% | 26.86% | 0.12696 | 0.79759 | 1.163 | 2.6512 | 0.2066 | 0.31396 | 13.53% | 22.16% | 0.66% | 26.34% | 0.66% | 2.9459 | 0 | 0 | 0 | 53.9115 | FALSE | FALSE | FALSE | TRUE
4 | 0 | 0 | 1.025 | 1.35 | 13.8473 | 95.9893 | 1.35 | 73.64% | 26.36% | 0.12224 | 0.78865 | 1.1278 | 1.3818 | 0.1975 | 0.28269 | 15.98% | 24.58% | 0.02% | 26.34% | 0.02% | 2.9464 | 0 | 0 | 0 | 53.9162 | FALSE | FALSE | FALSE | TRUE
4 | 0 | 0 | 1.025 | 1.4 | 13.8473 | 99.5445 | 1.4 | 73.66% | 26.34% | 0.12214 | 0.78865 | 1.1278 | 1.3818 | 0.19716 | 0.28194 | 18.26% | 26.82% | 0% | 26.34% | 0% | 2.9464 | 0 | 0 | 0 | 53.9163 | FALSE | FALSE | FALSE | TRUE
4 | 0 | 0 | 1.05 | 1 | 14.1851 | 71.1032 | 1.05 | 3.19% | 96.81% | 5.0646 | 10.3385 | 12.1842 | 14.5098 | 13.5096 | 13.5096 | 10% | 10% | 96.81% | 0.2% | 96.81% | 3.5772 | 3.1667 | 0 | 0 | 48.9738 | FALSE | FALSE | FALSE | TRUE
4 | 0 | 0 | 1.05 | 1.05 | 14.1851 | 74.6584 | 1.05 | 22.62% | 77.38% | 2.9217 | 8.1535 | 10.0915 | 12.5334 | 13.5096 | 13.5096 | 10% | 10% | 77.34% | 0.2% | 77.34% | 3.743 | 3.3333 | 0 | 0 | 51.1168 | FALSE | FALSE | FALSE | TRUE
4 | 0 | 0 | 1.05 | 1.1 | 14.1851 | 78.2135 | 1.1 | 51.16% | 48.84% | 1.4325 | 5.9685 | 7.9987 | 10.5569 | 13.5096 | 13.5096 | 10% | 10.15% | 48.74% | 0.2% | 48.74% | 3.865 | 3.5 | 0 | 0 | 52.6059 | FALSE | FALSE | FALSE | TRUE
4 | 0 | 0 | 1.05 | 1.15 | 14.1851 | 81.7687 | 1.15 | 73.91% | 26.09% | 0.59376 | 3.7835 | 5.906 | 8.5805 | 13.5096 | 13.5096 | 10% | 13.51% | 25.96% | 0.2% | 25.96% | 3.9368 | 3.6667 | 0 | 0 | 53.4447 | FALSE | FALSE | FALSE | TRUE
4 | 0 | 0 | 1.05 | 1.2 | 14.1851 | 85.3238 | 1.2 | 88.42% | 11.58% | 0.19352 | 1.5985 | 3.8133 | 6.6041 | 13.5096 | 13.5096 | 10% | 16.59% | 11.4% | 0.2% | 11.4% | 3.9726 | 3.8333 | 0 | 0 | 53.8449 | FALSE | FALSE | FALSE | TRUE
4 | 0 | 0 | 1.05 | 1.25 | 14.1851 | 88.879 | 1.25 | 96.25% | 3.75% | 0.045179 | 0 | 1.7206 | 4.6276 | 0 | 13.5096 | 10.74% | 19.42% | 3.55% | 0.2% | 3.55% | 3.987 | 4 | 0 | 0 | 53.9933 | TRUE | FALSE | FALSE | TRUE
4 | 0 | 0 | 1.05 | 1.3 | 14.1851 | 92.4342 | 1.3 | 99.11% | 0.89% | 0.0055399 | 0 | 0 | 2.6512 | 0 | 0 | 13.4% | 22.04% | 0.69% | 0.2% | 0.69% | 3.9912 | 4 | 0 | 0 | 54.0329 | TRUE | TRUE | FALSE | TRUE
4 | 0 | 0 | 1.05 | 1.35 | 14.1851 | 95.9893 | 1.35 | 99.78% | 0.22% | 0.00018231 | 0 | 0 | 0.67476 | 0 | 0 | 15.85% | 24.45% | 0.02% | 0.2% | 0.02% | 3.992 | 4 | 0 | 0 | 54.0383 | TRUE | TRUE | FALSE | TRUE
4 | 0 | 0 | 1.05 | 1.4 | 14.1851 | 99.5445 | 1.4 | 99.8% | 0.2% | 8.0281e-05 | 0 | 0 | 0.097512 | 0 | 0 | 18.13% | 26.7% | 0% | 0.2% | 0% | 3.992 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | FALSE | TRUE
4 | 0 | 0 | 1.075 | 1.05 | 14.5228 | 74.6584 | 1.075 | 22.66% | 77.34% | 2.9217 | 8.1535 | 10.0915 | 12.5334 | 13.5096 | 13.5096 | 10% | 10% | 77.34% | 0% | 77.34% | 3.7505 | 3.3333 | 0 | 0 | 51.1168 | FALSE | FALSE | FALSE | TRUE
4 | 0 | 0 | 1.075 | 1.1 | 14.5228 | 78.2135 | 1.1 | 51.26% | 48.74% | 1.4325 | 5.9685 | 7.9987 | 10.5569 | 13.5096 | 13.5096 | 10% | 10.15% | 48.74% | 0% | 48.74% | 3.8727 | 3.5 | 0 | 0 | 52.6059 | FALSE | FALSE | FALSE | TRUE
4 | 0 | 0 | 1.075 | 1.15 | 14.5228 | 81.7687 | 1.15 | 74.04% | 25.96% | 0.5937 | 3.7835 | 5.906 | 8.5805 | 13.5096 | 13.5096 | 10% | 13.51% | 25.96% | 0% | 25.96% | 3.9447 | 3.6667 | 0 | 0 | 53.4447 | FALSE | FALSE | FALSE | TRUE
4 | 0 | 0 | 1.075 | 1.2 | 14.5228 | 85.3238 | 1.2 | 88.6% | 11.4% | 0.19344 | 1.5985 | 3.8133 | 6.6041 | 13.5096 | 13.5096 | 10% | 16.59% | 11.4% | 0% | 11.4% | 3.9805 | 3.8333 | 0 | 0 | 53.845 | FALSE | FALSE | FALSE | TRUE
4 | 0 | 0 | 1.075 | 1.25 | 14.5228 | 88.879 | 1.25 | 96.45% | 3.55% | 0.045098 | 0 | 1.7206 | 4.6276 | 0 | 13.5096 | 10.74% | 19.42% | 3.55% | 0% | 3.55% | 3.995 | 4 | 0 | 0 | 53.9933 | TRUE | FALSE | FALSE | TRUE
4 | 0 | 0 | 1.075 | 1.3 | 14.5228 | 92.4342 | 1.3 | 99.31% | 0.69% | 0.0054596 | 0 | 0 | 2.6512 | 0 | 0 | 13.4% | 22.04% | 0.69% | 0% | 0.69% | 3.9992 | 4 | 0 | 0 | 54.033 | TRUE | TRUE | FALSE | TRUE
4 | 0 | 0 | 1.075 | 1.35 | 14.5228 | 95.9893 | 1.35 | 99.98% | 0.02% | 0.00010203 | 0 | 0 | 0.67476 | 0 | 0 | 15.85% | 24.45% | 0.02% | 0% | 0.02% | 4 | 4 | 0 | 0 | 54.0383 | TRUE | TRUE | TRUE | TRUE
4 | 0 | 0 | 1.075 | 1.4 | 14.5228 | 99.5445 | 1.4 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 18.13% | 26.7% | 0% | 0% | 0% | 4 | 4 | 0 | 0 | 54.0384 | TRUE | TRUE | TRUE | TRUE
4 | 6.7548 | 0.5 | 1 | 1 | 13.5096 | 71.1032 | 1 | 30.4% | 69.6% | 2.7623 | 9.0815 | 11.5056 | 14.5098 | 13.5096 | 13.5096 | 10% | 10% | 54.65% | 68.9% | 54.65% | 1.5676 | 0 | 5.7131 | 0 | 45.563 | FALSE | FALSE | FALSE | TRUE
4 | 6.7548 | 0.5 | 1 | 1.05 | 13.5096 | 74.6584 | 1.05 | 30.95% | 69.05% | 1.6612 | 6.839 | 9.4017 | 12.5334 | 13.5096 | 13.5096 | 10% | 12.7% | 37.12% | 68.9% | 37.12% | 1.5686 | 0 | 5.7131 | 0 | 46.6641 | FALSE | FALSE | FALSE | TRUE
4 | 6.7548 | 0.5 | 1 | 1.1 | 13.5096 | 78.2135 | 1.1 | 31.09% | 68.91% | 0.9969 | 4.5962 | 7.2761 | 10.5569 | 13.5096 | 13.5096 | 10% | 16.16% | 20.77% | 68.9% | 20.77% | 1.5688 | 0 | 5.7131 | 0 | 47.3284 | FALSE | FALSE | FALSE | TRUE
4 | 6.7548 | 0.5 | 1 | 1.15 | 13.5096 | 81.7687 | 1.15 | 31.1% | 68.9% | 0.65981 | 2.472 | 5.1506 | 8.5805 | 13.5096 | 13.5096 | 10% | 19.31% | 9.91% | 68.9% | 9.91% | 1.5688 | 0 | 5.7131 | 0 | 47.6655 | FALSE | FALSE | FALSE | TRUE
4 | 6.7548 | 0.5 | 1.025 | 1 | 13.8473 | 71.1032 | 1.025 | 39.21% | 60.79% | 2.7171 | 9.0815 | 11.5056 | 14.5098 | 13.5096 | 13.5096 | 10% | 10% | 57.46% | 17.84% | 57.46% | 3.2094 | 0 | 5.7131 | 0 | 45.6082 | FALSE | FALSE | FALSE | TRUE
4 | 6.7548 | 0.5 | 1.025 | 1.05 | 13.8473 | 74.6584 | 1.05 | 50.92% | 49.08% | 1.5174 | 6.839 | 9.4017 | 12.5334 | 13.5096 | 13.5096 | 10% | 11.81% | 41.44% | 17.84% | 41.44% | 3.2824 | 0 | 5.7131 | 0 | 46.8079 | FALSE | FALSE | FALSE | TRUE
4 | 6.7548 | 0.5 | 1.025 | 1.1 | 13.8473 | 78.2135 | 1.1 | 63.46% | 36.54% | 0.74497 | 4.5962 | 7.2761 | 10.5569 | 13.5096 | 13.5096 | 10% | 15.33% | 24.71% | 17.84% | 24.71% | 3.3315 | 0 | 5.7131 | 0 | 47.5803 | FALSE | FALSE | FALSE | TRUE
4 | 6.7548 | 0.5 | 1.025 | 1.15 | 13.8473 | 81.7687 | 1.15 | 72.71% | 27.29% | 0.33319 | 2.362 | 5.1506 | 8.5805 | 13.5096 | 13.5096 | 10% | 18.52% | 12.47% | 17.84% | 12.47% | 3.359 | 0 | 5.7131 | 0 | 47.9921 | FALSE | FALSE | FALSE | TRUE
4 | 6.7548 | 0.5 | 1.025 | 1.2 | 13.8473 | 85.3238 | 1.2 | 78.24% | 21.76% | 0.14691 | 0.85068 | 3.0276 | 6.6041 | 0.35297 | 13.5096 | 10% | 21.47% | 5.09% | 17.84% | 5.09% | 3.3721 | 0 | 5.7131 | 0 | 48.1784 | FALSE | FALSE | FALSE | TRUE
4 | 6.7548 | 0.5 | 1.025 | 1.25 | 13.8473 | 88.879 | 1.25 | 80.86% | 19.14% | 0.08165 | 0.56053 | 1.1998 | 4.6276 | 0.19517 | 10.0913 | 12.79% | 24.17% | 1.54% | 17.84% | 1.54% | 3.377 | 0 | 5.7131 | 0 | 48.2436 | FALSE | FALSE | FALSE | TRUE
4 | 6.7548 | 0.5 | 1.025 | 1.3 | 13.8473 | 92.4342 | 1.3 | 81.91% | 18.09% | 0.063761 | 0.48725 | 0.98409 | 2.6512 | 0.16581 | 0.28194 | 15.42% | 26.66% | 0.31% | 17.84% | 0.31% | 3.3786 | 0 | 5.7131 | 0 | 48.2615 | FALSE | FALSE | FALSE | TRUE
4 | 6.7548 | 0.5 | 1.025 | 1.35 | 13.8473 | 95.9893 | 1.35 | 82.14% | 17.86% | 0.061284 | 0.47347 | 0.95681 | 1.3818 | 0.15934 | 0.26942 | 17.84% | 28.94% | 0.02% | 17.84% | 0.02% | 3.3789 | 0 | 5.7131 | 0 | 48.264 | FALSE | FALSE | FALSE | TRUE
4 | 6.7548 | 0.5 | 1.025 | 1.4 | 13.8473 | 99.5445 | 1.4 | 82.16% | 17.84% | 0.061182 | 0.47302 | 0.95681 | 1.3818 | 0.15916 | 0.26936 | 20.08% | 31.08% | 0% | 17.84% | 0% | 3.3789 | 0 | 5.7131 | 0 | 48.2641 | FALSE | FALSE | FALSE | TRUE
4 | 6.7548 | 0.5 | 1.05 | 1 | 14.1851 | 71.1032 | 1.05 | 42.13% | 57.87% | 2.7115 | 9.0815 | 11.5056 | 14.5098 | 13.5096 | 13.5096 | 10% | 10% | 57.85% | 0.15% | 57.85% | 3.7659 | 3.25 | 5.7131 | 0 | 45.6138 | FALSE | FALSE | FALSE | TRUE
4 | 6.7548 | 0.5 | 1.05 | 1.05 | 14.1851 | 74.6584 | 1.05 | 57.86% | 42.14% | 1.4976 | 6.839 | 9.4017 | 12.5334 | 13.5096 | 13.5096 | 10% | 11.69% | 42.1% | 0.15% | 42.1% | 3.864 | 3.4167 | 5.7131 | 0 | 46.8277 | FALSE | FALSE | FALSE | TRUE
4 | 6.7548 | 0.5 | 1.05 | 1.1 | 14.1851 | 78.2135 | 1.1 | 74.57% | 25.43% | 0.71006 | 4.5962 | 7.2761 | 10.5569 | 13.5096 | 13.5096 | 10% | 15.21% | 25.34% | 0.15% | 25.34% | 3.9303 | 3.5833 | 5.7131 | 0 | 47.6152 | FALSE | FALSE | FALSE | TRUE
4 | 6.7548 | 0.5 | 1.05 | 1.15 | 14.1851 | 81.7687 | 1.15 | 86.93% | 13.07% | 0.28585 | 2.362 | 5.1506 | 8.5805 | 13.5096 | 13.5096 | 10% | 18.44% | 12.96% | 0.15% | 12.96% | 3.9675 | 3.75 | 5.7131 | 0 | 48.0394 | FALSE | FALSE | FALSE | TRUE
4 | 6.7548 | 0.5 | 1.05 | 1.2 | 14.1851 | 85.3238 | 1.2 | 94.52% | 5.48% | 0.091108 | 0.12812 | 3.0276 | 6.6041 | 1.5374 | 13.5096 | 10% | 21.38% | 5.34% | 0.15% | 5.34% | 3.9854 | 3.9167 | 5.7131 | 0 | 48.2342 | FALSE | FALSE | FALSE | TRUE
4 | 6.7548 | 0.5 | 1.05 | 1.25 | 14.1851 | 88.879 | 1.25 | 98.18% | 1.82% | 0.021838 | 0 | 0.91294 | 4.6276 | 0 | 10.9552 | 12.68% | 24.08% | 1.67% | 0.15% | 1.67% | 3.9921 | 4 | 5.7131 | 0 | 48.3035 | TRUE | FALSE | FALSE | TRUE
4 | 6.7548 | 0.5 | 1.05 | 1.3 | 14.1851 | 92.4342 | 1.3 | 99.52% | 0.48% | 0.0029617 | 0 | 0 | 2.6512 | 0 | 0 | 15.27% | 26.55% | 0.33% | 0.15% | 0.33% | 3.9942 | 4 | 5.7131 | 0 | 48.3223 | TRUE | TRUE | FALSE | TRUE
4 | 6.7548 | 0.5 | 1.05 | 1.35 | 14.1851 | 95.9893 | 1.35 | 99.83% | 0.17% | 0.00014487 | 0 | 0 | 0.67476 | 0 | 0 | 17.71% | 28.86% | 0.02% | 0.15% | 0.02% | 3.9945 | 4 | 5.7131 | 0 | 48.3251 | TRUE | TRUE | FALSE | TRUE
4 | 6.7548 | 0.5 | 1.05 | 1.4 | 14.1851 | 99.5445 | 1.4 | 99.85% | 0.15% | 4.2843e-05 | 0 | 0 | 0.097512 | 0 | 0 | 19.93% | 31% | 0% | 0.15% | 0% | 3.9946 | 4 | 5.7131 | 0 | 48.3252 | TRUE | TRUE | FALSE | TRUE
4 | 6.7548 | 0.5 | 1.075 | 1 | 14.5228 | 71.1032 | 1.075 | 42.15% | 57.85% | 2.7115 | 9.0815 | 11.5056 | 14.5098 | 13.5096 | 13.5096 | 10% | 10% | 57.85% | 0% | 57.85% | 3.7708 | 3.25 | 5.7131 | 0 | 45.6138 | FALSE | FALSE | FALSE | TRUE
4 | 6.7548 | 0.5 | 1.075 | 1.05 | 14.5228 | 74.6584 | 1.075 | 57.9% | 42.1% | 1.4976 | 6.839 | 9.4017 | 12.5334 | 13.5096 | 13.5096 | 10% | 11.69% | 42.1% | 0% | 42.1% | 3.8691 | 3.4167 | 5.7131 | 0 | 46.8277 | FALSE | FALSE | FALSE | TRUE
4 | 6.7548 | 0.5 | 1.075 | 1.1 | 14.5228 | 78.2135 | 1.1 | 74.66% | 25.34% | 0.71003 | 4.5962 | 7.2761 | 10.5569 | 13.5096 | 13.5096 | 10% | 15.21% | 25.34% | 0% | 25.34% | 3.9356 | 3.5833 | 5.7131 | 0 | 47.6153 | FALSE | FALSE | FALSE | TRUE
4 | 6.7548 | 0.5 | 1.075 | 1.15 | 14.5228 | 81.7687 | 1.15 | 87.04% | 12.96% | 0.28582 | 2.362 | 5.1506 | 8.5805 | 13.5096 | 13.5096 | 10% | 18.44% | 12.96% | 0% | 12.96% | 3.9729 | 3.75 | 5.7131 | 0 | 48.0395 | FALSE | FALSE | FALSE | TRUE
4 | 6.7548 | 0.5 | 1.075 | 1.2 | 14.5228 | 85.3238 | 1.2 | 94.66% | 5.34% | 0.09107 | 0.12812 | 3.0276 | 6.6041 | 1.5374 | 13.5096 | 10% | 21.38% | 5.34% | 0% | 5.34% | 3.9908 | 3.9167 | 5.7131 | 0 | 48.2342 | FALSE | FALSE | FALSE | TRUE
4 | 6.7548 | 0.5 | 1.075 | 1.25 | 14.5228 | 88.879 | 1.25 | 98.33% | 1.67% | 0.021795 | 0 | 0.91294 | 4.6276 | 0 | 10.9552 | 12.68% | 24.08% | 1.67% | 0% | 1.67% | 3.9976 | 4 | 5.7131 | 0 | 48.3035 | TRUE | FALSE | FALSE | TRUE
4 | 6.7548 | 0.5 | 1.075 | 1.3 | 14.5228 | 92.4342 | 1.3 | 99.67% | 0.33% | 0.0029188 | 0 | 0 | 2.6512 | 0 | 0 | 15.27% | 26.55% | 0.33% | 0% | 0.33% | 3.9996 | 4 | 5.7131 | 0 | 48.3224 | TRUE | TRUE | FALSE | TRUE
4 | 6.7548 | 0.5 | 1.075 | 1.35 | 14.5228 | 95.9893 | 1.35 | 99.98% | 0.02% | 0.00010203 | 0 | 0 | 0.67476 | 0 | 0 | 17.71% | 28.86% | 0.02% | 0% | 0.02% | 4 | 4 | 5.7131 | 0 | 48.3252 | TRUE | TRUE | TRUE | TRUE
4 | 6.7548 | 0.5 | 1.075 | 1.4 | 14.5228 | 99.5445 | 1.4 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 19.93% | 31% | 0% | 0% | 0% | 4 | 4 | 5.7131 | 0 | 48.3253 | TRUE | TRUE | TRUE | TRUE
4 | 13.5096 | 1 | 1 | 1 | 13.5096 | 71.1032 | 1 | 32.33% | 67.67% | 2.4843 | 8.9091 | 11.3949 | 14.5098 | 13.5096 | 13.5096 | 10% | 11.04% | 47.26% | 67.67% | 47.26% | 1.6207 | 0 | 11.4225 | 0.003816 | 40.1317 | FALSE | FALSE | FALSE | TRUE
4 | 13.5096 | 1 | 1.025 | 1 | 13.8473 | 71.1032 | 1.025 | 45.14% | 54.86% | 2.4249 | 8.9091 | 11.3949 | 14.5098 | 13.5096 | 13.5096 | 10% | 10.07% | 49.86% | 17.62% | 49.86% | 3.2384 | 0 | 11.4225 | 0.003816 | 40.1911 | FALSE | FALSE | FALSE | TRUE
4 | 13.5096 | 1 | 1.025 | 1.05 | 13.8473 | 74.6584 | 1.05 | 54.37% | 45.63% | 1.369 | 6.6654 | 9.274 | 12.5334 | 13.5096 | 13.5096 | 10% | 13.85% | 37.15% | 17.62% | 37.15% | 3.3023 | 0 | 11.4225 | 0.003816 | 41.247 | FALSE | FALSE | FALSE | TRUE
4 | 13.5096 | 1 | 1.025 | 1.1 | 13.8473 | 78.2135 | 1.1 | 65.84% | 34.16% | 0.67883 | 4.4345 | 7.1591 | 10.5569 | 13.5096 | 13.5096 | 10% | 17.3% | 21.91% | 17.62% | 21.91% | 3.3464 | 0 | 11.4225 | 0.003816 | 41.9371 | FALSE | FALSE | FALSE | TRUE
4 | 13.5096 | 1 | 1.025 | 1.15 | 13.8473 | 81.7687 | 1.15 | 73.74% | 26.26% | 0.30891 | 2.1959 | 5.0391 | 8.5805 | 13.5096 | 13.5096 | 10% | 20.46% | 11.37% | 17.62% | 11.37% | 3.3709 | 0 | 11.4225 | 0.003816 | 42.307 | FALSE | FALSE | FALSE | TRUE
4 | 13.5096 | 1 | 1.025 | 1.2 | 13.8473 | 85.3238 | 1.2 | 78.73% | 21.27% | 0.13958 | 0.81254 | 2.9086 | 6.6041 | 0.3023 | 13.5096 | 10.26% | 23.35% | 4.7% | 17.62% | 4.7% | 3.3828 | 0 | 11.4225 | 0.003816 | 42.4764 | FALSE | FALSE | FALSE | TRUE
4 | 13.5096 | 1 | 1.025 | 1.25 | 13.8473 | 88.879 | 1.25 | 81.21% | 18.79% | 0.079393 | 0.55326 | 1.171 | 4.6276 | 0.19123 | 8.964 | 13.06% | 26% | 1.4% | 17.62% | 1.4% | 3.3875 | 0 | 11.4225 | 0.003816 | 42.5366 | FALSE | FALSE | FALSE | TRUE
4 | 13.5096 | 1 | 1.025 | 1.3 | 13.8473 | 92.4342 | 1.3 | 82.14% | 17.86% | 0.062843 | 0.47814 | 0.9831 | 2.6512 | 0.16314 | 0.28062 | 15.69% | 28.47% | 0.29% | 17.62% | 0.29% | 3.3889 | 0 | 11.4225 | 0.003816 | 42.5531 | FALSE | FALSE | FALSE | TRUE
4 | 13.5096 | 1 | 1.025 | 1.35 | 13.8473 | 95.9893 | 1.35 | 82.36% | 17.64% | 0.060528 | 0.46442 | 0.94985 | 1.3818 | 0.15857 | 0.26938 | 18.07% | 30.75% | 0.02% | 17.62% | 0.02% | 3.3891 | 0 | 11.4225 | 0.003816 | 42.5554 | FALSE | FALSE | FALSE | TRUE
4 | 13.5096 | 1 | 1.025 | 1.4 | 13.8473 | 99.5445 | 1.4 | 82.38% | 17.62% | 0.060426 | 0.46424 | 0.94985 | 1.3818 | 0.158 | 0.26931 | 20.33% | 32.84% | 0% | 17.62% | 0% | 3.3892 | 0 | 11.4225 | 0.003816 | 42.5555 | FALSE | FALSE | FALSE | TRUE
4 | 13.5096 | 1 | 1.05 | 1 | 14.1851 | 71.1032 | 1.05 | 49.69% | 50.31% | 2.4166 | 8.9091 | 11.3949 | 14.5098 | 13.5096 | 13.5096 | 10% | 10% | 50.27% | 0.15% | 50.27% | 3.791 | 3.25 | 11.4225 | 0.003816 | 40.1994 | FALSE | FALSE | FALSE | TRUE
4 | 13.5096 | 1 | 1.05 | 1.05 | 14.1851 | 74.6584 | 1.05 | 62.18% | 37.82% | 1.3478 | 6.6654 | 9.274 | 12.5334 | 13.5096 | 13.5096 | 10% | 13.69% | 37.77% | 0.15% | 37.77% | 3.8769 | 3.4167 | 11.4225 | 0.003816 | 41.2682 | FALSE | FALSE | FALSE | TRUE
4 | 13.5096 | 1 | 1.05 | 1.1 | 14.1851 | 78.2135 | 1.1 | 77.36% | 22.64% | 0.6433 | 4.4345 | 7.1591 | 10.5569 | 13.5096 | 13.5096 | 10% | 17.14% | 22.54% | 0.15% | 22.54% | 3.9365 | 3.5833 | 11.4225 | 0.003816 | 41.9727 | FALSE | FALSE | FALSE | TRUE
4 | 13.5096 | 1 | 1.05 | 1.15 | 14.1851 | 81.7687 | 1.15 | 88.05% | 11.95% | 0.2615 | 2.1959 | 5.0391 | 8.5805 | 13.5096 | 13.5096 | 10% | 20.33% | 11.83% | 0.15% | 11.83% | 3.9697 | 3.75 | 11.4225 | 0.003816 | 42.3545 | FALSE | FALSE | FALSE | TRUE
4 | 13.5096 | 1 | 1.05 | 1.2 | 14.1851 | 85.3238 | 1.2 | 94.92% | 5.08% | 0.08423 | 0.0065002 | 2.9086 | 6.6041 | 0.012122 | 13.5096 | 10.07% | 23.2% | 4.94% | 0.15% | 4.94% | 3.9861 | 3.9167 | 11.4225 | 0.003816 | 42.5317 | FALSE | FALSE | FALSE | TRUE
4 | 13.5096 | 1 | 1.05 | 1.25 | 14.1851 | 88.879 | 1.25 | 98.34% | 1.66% | 0.020265 | 0 | 0.79196 | 4.6276 | 0 | 9.5035 | 12.89% | 25.88% | 1.51% | 0.15% | 1.51% | 3.9924 | 4 | 11.4225 | 0.003816 | 42.5957 | TRUE | FALSE | FALSE | TRUE
4 | 13.5096 | 1 | 1.05 | 1.3 | 14.1851 | 92.4342 | 1.3 | 99.54% | 0.46% | 0.0027878 | 0 | 0 | 2.6512 | 0 | 0 | 15.49% | 28.32% | 0.31% | 0.15% | 0.31% | 3.9942 | 4 | 11.4225 | 0.003816 | 42.6132 | TRUE | TRUE | FALSE | TRUE
4 | 13.5096 | 1 | 1.05 | 1.35 | 14.1851 | 95.9893 | 1.35 | 99.83% | 0.17% | 0.00014487 | 0 | 0 | 0.67476 | 0 | 0 | 17.93% | 30.63% | 0.02% | 0.15% | 0.02% | 3.9945 | 4 | 11.4225 | 0.003816 | 42.6158 | TRUE | TRUE | FALSE | TRUE
4 | 13.5096 | 1 | 1.05 | 1.4 | 14.1851 | 99.5445 | 1.4 | 99.85% | 0.15% | 4.2843e-05 | 0 | 0 | 0.097512 | 0 | 0 | 20.2% | 32.74% | 0% | 0.15% | 0% | 3.9946 | 4 | 11.4225 | 0.003816 | 42.6159 | TRUE | TRUE | FALSE | TRUE
4 | 13.5096 | 1 | 1.075 | 1 | 14.5228 | 71.1032 | 1.075 | 49.73% | 50.27% | 2.4166 | 8.9091 | 11.3949 | 14.5098 | 13.5096 | 13.5096 | 10% | 10% | 50.27% | 0% | 50.27% | 3.796 | 3.25 | 11.4225 | 0.003816 | 40.1994 | FALSE | FALSE | FALSE | TRUE
4 | 13.5096 | 1 | 1.075 | 1.05 | 14.5228 | 74.6584 | 1.075 | 62.23% | 37.77% | 1.3478 | 6.6654 | 9.274 | 12.5334 | 13.5096 | 13.5096 | 10% | 13.69% | 37.77% | 0% | 37.77% | 3.8821 | 3.4167 | 11.4225 | 0.003816 | 41.2682 | FALSE | FALSE | FALSE | TRUE
4 | 13.5096 | 1 | 1.075 | 1.1 | 14.5228 | 78.2135 | 1.1 | 77.46% | 22.54% | 0.64327 | 4.4345 | 7.1591 | 10.5569 | 13.5096 | 13.5096 | 10% | 17.14% | 22.54% | 0% | 22.54% | 3.9418 | 3.5833 | 11.4225 | 0.003816 | 41.9727 | FALSE | FALSE | FALSE | TRUE
4 | 13.5096 | 1 | 1.075 | 1.15 | 14.5228 | 81.7687 | 1.15 | 88.17% | 11.83% | 0.26146 | 2.1959 | 5.0391 | 8.5805 | 13.5096 | 13.5096 | 10% | 20.33% | 11.83% | 0% | 11.83% | 3.9751 | 3.8333 | 11.4225 | 0.003816 | 42.3545 | FALSE | FALSE | FALSE | TRUE
4 | 13.5096 | 1 | 1.075 | 1.2 | 14.5228 | 85.3238 | 1.2 | 95.06% | 4.94% | 0.084191 | 0 | 2.9086 | 6.6041 | 0 | 13.5096 | 10.07% | 23.2% | 4.94% | 0% | 4.94% | 3.9915 | 4 | 11.4225 | 0.003816 | 42.5318 | TRUE | FALSE | FALSE | TRUE
4 | 13.5096 | 1 | 1.075 | 1.25 | 14.5228 | 88.879 | 1.25 | 98.49% | 1.51% | 0.020222 | 0 | 0.79196 | 4.6276 | 0 | 9.5035 | 12.89% | 25.88% | 1.51% | 0% | 1.51% | 3.9978 | 4 | 11.4225 | 0.003816 | 42.5957 | TRUE | FALSE | FALSE | TRUE
4 | 13.5096 | 1 | 1.075 | 1.3 | 14.5228 | 92.4342 | 1.3 | 99.69% | 0.31% | 0.002745 | 0 | 0 | 2.6512 | 0 | 0 | 15.49% | 28.32% | 0.31% | 0% | 0.31% | 3.9996 | 4 | 11.4225 | 0.003816 | 42.6132 | TRUE | TRUE | FALSE | TRUE
4 | 13.5096 | 1 | 1.075 | 1.35 | 14.5228 | 95.9893 | 1.35 | 99.98% | 0.02% | 0.00010203 | 0 | 0 | 0.67476 | 0 | 0 | 17.93% | 30.63% | 0.02% | 0% | 0.02% | 4 | 4 | 11.4225 | 0.003816 | 42.6159 | TRUE | TRUE | TRUE | TRUE
4 | 13.5096 | 1 | 1.075 | 1.4 | 14.5228 | 99.5445 | 1.4 | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 20.2% | 32.74% | 0% | 0% | 0% | 4 | 4 | 11.4225 | 0.003816 | 42.616 | TRUE | TRUE | TRUE | TRUE

## Scenario_Bank_Audit
OutageDurationHours | Simulations | MeanStartSOCFraction | P05StartSOCFraction | MeanCapacityDerate | P05CapacityDerate | MeanDischargeEfficiency | P05DischargeEfficiency | MeanPCSAvailability | P05PCSAvailability
4 | 10000 | 86.7% | 78.96% | 95.62% | 91.86% | 0.93963 | 0.91233 | 0.98336 | 0.96137

## Deterministic_Baseline
CandidateKey | GridID | SubstationID | CandidateLineID | BaseDCMW | DeterministicBatteryPowerMW | DeterministicBatteryInstalledMWh
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 13.5096 | 13.5096 | 71.1032

## Assumptions
Item | Value
Final analytical purpose | Find reliability-adjusted BESS MW/MWh designs from the deterministic MILP-1 and MILP-2 results.
Selected site | GSO_122 ¦ line_5852_22 ¦ hvmv_1_22
Fixed DC load | 13.509608 MW
Nominal deterministic BESS | 13.509608 MW / 71.103202 MWh
Reliability targets | [0.95, 0.99, 0.999]
Headline target | 99.0% simulated survival, PV ratio=0%
Recommendation policy | MIN_MAX_RELATIVE_OVERSIZE
Simulations per scenario | 10000
Random seed | 2026
Common random numbers | The same sampled outage starts and engineering uncertainty draws are reused across every BESS/PV design for each outage duration.
Outage start sampling | Uniform with replacement from complete historical starts in the 2024 PV profile.
PV treatment | Real contiguous historical PV blocks. PV serves load first, excess PV charges the battery, and remaining excess is curtailed.
Start SOC triangular | (0.75, 0.9, 0.95)
Battery capacity derate triangular | (0.9, 0.97, 1.0)
Charge efficiency triangular | (0.9, 0.95, 0.97)
Discharge efficiency triangular | (0.9, 0.95, 0.97)
PCS availability triangular | (0.95, 1.0, 1.0)
Critical load factor triangular | (1.0, 1.0, 1.0)
PV output multiplier triangular | (1.0, 1.0, 1.0)
Distribution interpretation | Triangular ranges are explicit stress-test assumptions unless independently supported by measured distributions.
Not randomized | Unresolved station capacity, feeder rerouting, AC voltage/reactive behavior, and protection/short-circuit limits remain unresolved rather than being invented.