## Candidate_Summary
ThermalRank | CandidateKey | GridID | SubstationID | CandidateLineID | CandidateNode | OriginalScreeningHostingMW | CandidateConfidenceFromPriorScreen | ModelStatus | ReviewFlags | Modeled5MinIntervals | ModeledHoursEquivalent | FirmHostingMW | HostingAvailable99PctIntervalsMW | HostingAvailable95PctIntervalsMW | MedianHostingMW | MeanHostingMW | MaximumHostingMW | FirmToMedianGapMW | IntervalsWithNoAdditionalHosting | PctIntervalsWithNoAdditionalHosting | BaselinePathRatingExceedanceIntervals | BaselinePathRatingExceedancePct | MostFrequentLimitingElementID | MostFrequentLimitingElementPct | FirmLimitTimestampUTC | FirmLimitElementID | PathHops | PathLineCount | PathTransformerCount | ParallelAmbiguityOnPath | MeterTopologyMappingPct | MeterBreakerCorrelation | MeterBreakerNMAEPct | FeederIsRadial | CycleRank | SubstationCapacityConstraintApplied | VoltageConstraintApplied | BasePowerFactor
1 | GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | S_nCCTT45 | 13.5096 | High | Ready |  | 105348 | 8779 | 13.5096 | 13.516 | 13.5183 | 13.5228 | 13.5226 | 13.5312 | 0.013224 | 0 | 0 | 0 | 0 | line_5852_22 | 100 | 2024-01-20 07:00 | line_5852_22 | 2 | 1 | 0 | FALSE | 100 | 0.99996 | 3.8462 | TRUE | 0 | FALSE | FALSE | 0.95
2 | GSO_124¦line_6716_22 | GSO_124 | hvmv_1_22 | line_6716_22 | S_nCCTT913 | 13.4085 | High | Ready |  | 105348 | 8779 | 13.4085 | 13.4374 | 13.4467 | 13.4653 | 13.4646 | 13.4947 | 0.056832 | 0 | 0 | 0 | 0 | line_6716_22 | 100 | 2024-01-22 04:00 | line_6716_22 | 2 | 1 | 0 | FALSE | 100 | 0.99997 | 3.8457 | TRUE | 0 | FALSE | FALSE | 0.95
3 | GSO_123¦line_6019_22 | GSO_123 | hvmv_1_22 | line_6019_22 | S_nCCTT521 | 13.1777 | High | Ready |  | 105348 | 8779 | 13.1777 | 13.2323 | 13.2536 | 13.2976 | 13.2942 | 13.3495 | 0.11988 | 0 | 0 | 0 | 0 | line_6019_22 | 100 | 2024-01-22 04:00 | line_6019_22 | 2 | 1 | 0 | FALSE | 100 | 0.99993 | 3.8463 | TRUE | 0 | FALSE | FALSE | 0.95
4 | GSO_121¦line_3530_22 | GSO_121 | hvmv_1_22 | line_3530_22 | S_nCCTT0 | 13.1607 | High | ReadyWithReviewFlags | MeshedTopologyUsesShortestPathTree | 105348 | 8779 | 13.1607 | 13.2094 | 13.2378 | 13.3041 | 13.2977 | 13.3561 | 0.14333 | 0 | 0 | 0 | 0 | line_3530_22 | 100 | 2024-01-17 23:00 | line_3530_22 | 2 | 1 | 0 | FALSE | 100 | 0.98983 | 3.0957 | FALSE | 1 | FALSE | FALSE | 0.95
5 | GSO_144¦line_5978_22 | GSO_144 | hvmv_5_22 | line_5978_22 | S_nCCTT504 | 11.2671 | High | Ready |  | 105348 | 8779 | 11.2671 | 11.2951 | 11.3099 | 11.3464 | 11.3426 | 11.3674 | 0.079236 | 0 | 0 | 0 | 0 | br_024_22 | 100 | 2024-01-20 21:00 | br_024_22 | 2 | 1 | 0 | FALSE | 100 | 0.99998 | 3.8453 | TRUE | 0 | FALSE | FALSE | 0.95
6 | GSO_141¦line_4565_22 | GSO_141 | hvmv_5_22 | line_4565_22 | S_nCCTT1344 | 11.02 | High | Ready |  | 105348 | 8779 | 11.02 | 11.0816 | 11.1093 | 11.1705 | 11.1652 | 11.2388 | 0.15049 | 0 | 0 | 0 | 0 | br_021_22 | 100 | 2024-01-21 01:00 | br_021_22 | 2 | 1 | 0 | FALSE | 100 | 0.99996 | 3.8441 | TRUE | 0 | FALSE | FALSE | 0.95
7 | GSO_145¦line_6170_22 | GSO_145 | hvmv_5_22 | line_6170_22 | S_nCCTT59 | 10.6656 | Medium | ReadyWithReviewFlags | MeterTopologyMapping<95% ¦ MeshedTopologyUsesShortestPathTree | 105348 | 8779 | 10.6656 | 10.7801 | 10.8397 | 10.9717 | 10.9595 | 11.105 | 0.30613 | 0 | 0 | 0 | 0 | br_025_22 | 100 | 2024-01-21 04:00 | br_025_22 | 2 | 1 | 0 | FALSE | 90.9677 | 0.90219 | 4.8665 | FALSE | 1 | FALSE | FALSE | 0.95
8 | GSO_142¦line_5429_22 | GSO_142 | hvmv_5_22 | line_5429_22 | S_nCCTT245 | 10.6074 | High | ReadyWithReviewFlags | MeshedTopologyUsesShortestPathTree | 105348 | 8779 | 10.6074 | 10.7211 | 10.7752 | 10.8838 | 10.8749 | 11.0003 | 0.27642 | 0 | 0 | 0 | 0 | br_022_22 | 100 | 2024-07-09 | br_022_22 | 2 | 1 | 0 | FALSE | 100 | 0.9917 | 3.1071 | FALSE | 2 | FALSE | FALSE | 0.95
9 | GSO_18¦line_108323_21 | GSO_18 | hvmv_4_21 | line_108323_21 | S_nCCTT10746 | 10.3769 | High | ReadyWithReviewFlags | MeshedTopologyUsesShortestPathTree | 105348 | 8779 | 10.3769 | 10.7346 | 10.9536 | 11.5317 | 11.4776 | 11.8543 | 1.1548 | 0 | 0 | 0 | 0 | br_025_21 | 100 | 2024-01-21 | br_025_21 | 2 | 1 | 0 | FALSE | 100 | 0.9914 | 3.2888 | FALSE | 2 | FALSE | FALSE | 0.95
10 | GSO_127¦line_6871_22 | GSO_127 | hvmv_2_22 | line_6871_22 | UCMV43 | 9.4748 | High | Ready |  | 105348 | 8779 | 9.4748 | 9.4814 | 9.4833 | 9.4875 | 9.4874 | 9.4959 | 0.012732 | 0 | 0 | 0 | 0 | br_07_22 | 100 | 2024-01-20 21:00 | br_07_22 | 2 | 1 | 0 | FALSE | 100 | 0.99998 | 3.8459 | TRUE | 0 | FALSE | FALSE | 0.95

## PF_Sensitivity
CandidateKey | GridID | SubstationID | CandidateLineID | PowerFactor | Status | FirmHostingMW | HostingAvailable99PctIntervalsMW | HostingAvailable95PctIntervalsMW | MedianHostingMW | PctIntervalsWithBaselinePathRatingExceedance | MostFrequentLimitingElementID
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 0.9 | Ready | 12.7969 | 12.8033 | 12.8056 | 12.8101 | 0 | line_5852_22
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 0.95 | Ready | 13.5096 | 13.516 | 13.5183 | 13.5228 | 0 | line_5852_22
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 1 | Ready | 14.2224 | 14.2288 | 14.2311 | 14.2356 | 0 | line_5852_22
GSO_124¦line_6716_22 | GSO_124 | hvmv_1_22 | line_6716_22 | 0.9 | Ready | 12.6957 | 12.7246 | 12.7339 | 12.7526 | 0 | line_6716_22
GSO_124¦line_6716_22 | GSO_124 | hvmv_1_22 | line_6716_22 | 0.95 | Ready | 13.4085 | 13.4374 | 13.4467 | 13.4653 | 0 | line_6716_22
GSO_124¦line_6716_22 | GSO_124 | hvmv_1_22 | line_6716_22 | 1 | Ready | 14.1213 | 14.1501 | 14.1594 | 14.1781 | 0 | line_6716_22
GSO_123¦line_6019_22 | GSO_123 | hvmv_1_22 | line_6019_22 | 0.9 | Ready | 12.465 | 12.5196 | 12.5408 | 12.5848 | 0 | line_6019_22
GSO_123¦line_6019_22 | GSO_123 | hvmv_1_22 | line_6019_22 | 0.95 | Ready | 13.1777 | 13.2323 | 13.2536 | 13.2976 | 0 | line_6019_22
GSO_123¦line_6019_22 | GSO_123 | hvmv_1_22 | line_6019_22 | 1 | Ready | 13.8905 | 13.9451 | 13.9664 | 14.0104 | 0 | line_6019_22
GSO_121¦line_3530_22 | GSO_121 | hvmv_1_22 | line_3530_22 | 0.9 | Ready | 12.448 | 12.4966 | 12.5251 | 12.5913 | 0 | line_3530_22
GSO_121¦line_3530_22 | GSO_121 | hvmv_1_22 | line_3530_22 | 0.95 | Ready | 13.1607 | 13.2094 | 13.2378 | 13.3041 | 0 | line_3530_22
GSO_121¦line_3530_22 | GSO_121 | hvmv_1_22 | line_3530_22 | 1 | Ready | 13.8735 | 13.9221 | 13.9506 | 14.0168 | 0 | line_3530_22
GSO_144¦line_5978_22 | GSO_144 | hvmv_5_22 | line_5978_22 | 0.9 | Ready | 10.6671 | 10.6951 | 10.7099 | 10.7464 | 0 | br_024_22
GSO_144¦line_5978_22 | GSO_144 | hvmv_5_22 | line_5978_22 | 0.95 | Ready | 11.2671 | 11.2951 | 11.3099 | 11.3464 | 0 | br_024_22
GSO_144¦line_5978_22 | GSO_144 | hvmv_5_22 | line_5978_22 | 1 | Ready | 11.8671 | 11.8951 | 11.9099 | 11.9464 | 0 | br_024_22
GSO_141¦line_4565_22 | GSO_141 | hvmv_5_22 | line_4565_22 | 0.9 | Ready | 10.42 | 10.4816 | 10.5093 | 10.5705 | 0 | br_021_22
GSO_141¦line_4565_22 | GSO_141 | hvmv_5_22 | line_4565_22 | 0.95 | Ready | 11.02 | 11.0816 | 11.1093 | 11.1705 | 0 | br_021_22
GSO_141¦line_4565_22 | GSO_141 | hvmv_5_22 | line_4565_22 | 1 | Ready | 11.62 | 11.6816 | 11.7093 | 11.7705 | 0 | br_021_22
GSO_145¦line_6170_22 | GSO_145 | hvmv_5_22 | line_6170_22 | 0.9 | Ready | 10.0656 | 10.1801 | 10.2397 | 10.3717 | 0 | br_025_22
GSO_145¦line_6170_22 | GSO_145 | hvmv_5_22 | line_6170_22 | 0.95 | Ready | 10.6656 | 10.7801 | 10.8397 | 10.9717 | 0 | br_025_22
GSO_145¦line_6170_22 | GSO_145 | hvmv_5_22 | line_6170_22 | 1 | Ready | 11.2656 | 11.3801 | 11.4397 | 11.5717 | 0 | br_025_22
GSO_142¦line_5429_22 | GSO_142 | hvmv_5_22 | line_5429_22 | 0.9 | Ready | 10.0074 | 10.1211 | 10.1752 | 10.2838 | 0 | br_022_22
GSO_142¦line_5429_22 | GSO_142 | hvmv_5_22 | line_5429_22 | 0.95 | Ready | 10.6074 | 10.7211 | 10.7752 | 10.8838 | 0 | br_022_22
GSO_142¦line_5429_22 | GSO_142 | hvmv_5_22 | line_5429_22 | 1 | Ready | 11.2074 | 11.3211 | 11.3752 | 11.4838 | 0 | br_022_22
GSO_18¦line_108323_21 | GSO_18 | hvmv_4_21 | line_108323_21 | 0.9 | Ready | 9.7102 | 10.0679 | 10.2869 | 10.8651 | 0 | br_025_21
GSO_18¦line_108323_21 | GSO_18 | hvmv_4_21 | line_108323_21 | 0.95 | Ready | 10.3769 | 10.7346 | 10.9536 | 11.5317 | 0 | br_025_21
GSO_18¦line_108323_21 | GSO_18 | hvmv_4_21 | line_108323_21 | 1 | Ready | 11.0436 | 11.4012 | 11.6203 | 12.1984 | 0 | br_025_21
GSO_127¦line_6871_22 | GSO_127 | hvmv_2_22 | line_6871_22 | 0.9 | Ready | 8.9748 | 8.9814 | 8.9833 | 8.9875 | 0 | br_07_22
GSO_127¦line_6871_22 | GSO_127 | hvmv_2_22 | line_6871_22 | 0.95 | Ready | 9.4748 | 9.4814 | 9.4833 | 9.4875 | 0 | br_07_22
GSO_127¦line_6871_22 | GSO_127 | hvmv_2_22 | line_6871_22 | 1 | Ready | 9.9748 | 9.9814 | 9.9833 | 9.9875 | 0 | br_07_22

## Test_DC_Levels
CandidateKey | GridID | SubstationID | CandidateLineID | TestDCLoadMW | FeasibleIntervals | ConstrainedIntervals | FeasiblePctIntervals | ConstrainedPctIntervals | ConstrainedHoursEquivalent
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 5 | 105348 | 0 | 100 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 7.5 | 105348 | 0 | 100 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 10 | 105348 | 0 | 100 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 12.5 | 105348 | 0 | 100 | 0 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 15 | 0 | 105348 | 0 | 100 | 8779
GSO_124¦line_6716_22 | GSO_124 | hvmv_1_22 | line_6716_22 | 5 | 105348 | 0 | 100 | 0 | 0
GSO_124¦line_6716_22 | GSO_124 | hvmv_1_22 | line_6716_22 | 7.5 | 105348 | 0 | 100 | 0 | 0
GSO_124¦line_6716_22 | GSO_124 | hvmv_1_22 | line_6716_22 | 10 | 105348 | 0 | 100 | 0 | 0
GSO_124¦line_6716_22 | GSO_124 | hvmv_1_22 | line_6716_22 | 12.5 | 105348 | 0 | 100 | 0 | 0
GSO_124¦line_6716_22 | GSO_124 | hvmv_1_22 | line_6716_22 | 15 | 0 | 105348 | 0 | 100 | 8779
GSO_123¦line_6019_22 | GSO_123 | hvmv_1_22 | line_6019_22 | 5 | 105348 | 0 | 100 | 0 | 0
GSO_123¦line_6019_22 | GSO_123 | hvmv_1_22 | line_6019_22 | 7.5 | 105348 | 0 | 100 | 0 | 0
GSO_123¦line_6019_22 | GSO_123 | hvmv_1_22 | line_6019_22 | 10 | 105348 | 0 | 100 | 0 | 0
GSO_123¦line_6019_22 | GSO_123 | hvmv_1_22 | line_6019_22 | 12.5 | 105348 | 0 | 100 | 0 | 0
GSO_123¦line_6019_22 | GSO_123 | hvmv_1_22 | line_6019_22 | 15 | 0 | 105348 | 0 | 100 | 8779
GSO_121¦line_3530_22 | GSO_121 | hvmv_1_22 | line_3530_22 | 5 | 105348 | 0 | 100 | 0 | 0
GSO_121¦line_3530_22 | GSO_121 | hvmv_1_22 | line_3530_22 | 7.5 | 105348 | 0 | 100 | 0 | 0
GSO_121¦line_3530_22 | GSO_121 | hvmv_1_22 | line_3530_22 | 10 | 105348 | 0 | 100 | 0 | 0
GSO_121¦line_3530_22 | GSO_121 | hvmv_1_22 | line_3530_22 | 12.5 | 105348 | 0 | 100 | 0 | 0
GSO_121¦line_3530_22 | GSO_121 | hvmv_1_22 | line_3530_22 | 15 | 0 | 105348 | 0 | 100 | 8779
GSO_144¦line_5978_22 | GSO_144 | hvmv_5_22 | line_5978_22 | 5 | 105348 | 0 | 100 | 0 | 0
GSO_144¦line_5978_22 | GSO_144 | hvmv_5_22 | line_5978_22 | 7.5 | 105348 | 0 | 100 | 0 | 0
GSO_144¦line_5978_22 | GSO_144 | hvmv_5_22 | line_5978_22 | 10 | 105348 | 0 | 100 | 0 | 0
GSO_144¦line_5978_22 | GSO_144 | hvmv_5_22 | line_5978_22 | 12.5 | 0 | 105348 | 0 | 100 | 8779
GSO_144¦line_5978_22 | GSO_144 | hvmv_5_22 | line_5978_22 | 15 | 0 | 105348 | 0 | 100 | 8779
GSO_141¦line_4565_22 | GSO_141 | hvmv_5_22 | line_4565_22 | 5 | 105348 | 0 | 100 | 0 | 0
GSO_141¦line_4565_22 | GSO_141 | hvmv_5_22 | line_4565_22 | 7.5 | 105348 | 0 | 100 | 0 | 0
GSO_141¦line_4565_22 | GSO_141 | hvmv_5_22 | line_4565_22 | 10 | 105348 | 0 | 100 | 0 | 0
GSO_141¦line_4565_22 | GSO_141 | hvmv_5_22 | line_4565_22 | 12.5 | 0 | 105348 | 0 | 100 | 8779
GSO_141¦line_4565_22 | GSO_141 | hvmv_5_22 | line_4565_22 | 15 | 0 | 105348 | 0 | 100 | 8779
GSO_145¦line_6170_22 | GSO_145 | hvmv_5_22 | line_6170_22 | 5 | 105348 | 0 | 100 | 0 | 0
GSO_145¦line_6170_22 | GSO_145 | hvmv_5_22 | line_6170_22 | 7.5 | 105348 | 0 | 100 | 0 | 0
GSO_145¦line_6170_22 | GSO_145 | hvmv_5_22 | line_6170_22 | 10 | 105348 | 0 | 100 | 0 | 0
GSO_145¦line_6170_22 | GSO_145 | hvmv_5_22 | line_6170_22 | 12.5 | 0 | 105348 | 0 | 100 | 8779
GSO_145¦line_6170_22 | GSO_145 | hvmv_5_22 | line_6170_22 | 15 | 0 | 105348 | 0 | 100 | 8779
GSO_142¦line_5429_22 | GSO_142 | hvmv_5_22 | line_5429_22 | 5 | 105348 | 0 | 100 | 0 | 0
GSO_142¦line_5429_22 | GSO_142 | hvmv_5_22 | line_5429_22 | 7.5 | 105348 | 0 | 100 | 0 | 0
GSO_142¦line_5429_22 | GSO_142 | hvmv_5_22 | line_5429_22 | 10 | 105348 | 0 | 100 | 0 | 0
GSO_142¦line_5429_22 | GSO_142 | hvmv_5_22 | line_5429_22 | 12.5 | 0 | 105348 | 0 | 100 | 8779
GSO_142¦line_5429_22 | GSO_142 | hvmv_5_22 | line_5429_22 | 15 | 0 | 105348 | 0 | 100 | 8779
GSO_18¦line_108323_21 | GSO_18 | hvmv_4_21 | line_108323_21 | 5 | 105348 | 0 | 100 | 0 | 0
GSO_18¦line_108323_21 | GSO_18 | hvmv_4_21 | line_108323_21 | 7.5 | 105348 | 0 | 100 | 0 | 0
GSO_18¦line_108323_21 | GSO_18 | hvmv_4_21 | line_108323_21 | 10 | 105348 | 0 | 100 | 0 | 0
GSO_18¦line_108323_21 | GSO_18 | hvmv_4_21 | line_108323_21 | 12.5 | 0 | 105348 | 0 | 100 | 8779
GSO_18¦line_108323_21 | GSO_18 | hvmv_4_21 | line_108323_21 | 15 | 0 | 105348 | 0 | 100 | 8779
GSO_127¦line_6871_22 | GSO_127 | hvmv_2_22 | line_6871_22 | 5 | 105348 | 0 | 100 | 0 | 0
GSO_127¦line_6871_22 | GSO_127 | hvmv_2_22 | line_6871_22 | 7.5 | 105348 | 0 | 100 | 0 | 0
GSO_127¦line_6871_22 | GSO_127 | hvmv_2_22 | line_6871_22 | 10 | 0 | 105348 | 0 | 100 | 8779
GSO_127¦line_6871_22 | GSO_127 | hvmv_2_22 | line_6871_22 | 12.5 | 0 | 105348 | 0 | 100 | 8779
GSO_127¦line_6871_22 | GSO_127 | hvmv_2_22 | line_6871_22 | 15 | 0 | 105348 | 0 | 100 | 8779

## Path_Constraints
CandidateKey | GridID | SubstationID | CandidateLineID | PowerFactor | ElementID | ElementType | ElementClass | CapacityMW | PeakExistingAbsMW | PeakExistingSignedMW | P95ExistingAbsMW | MinimumIncrementalHeadroomMW | BaselineRatingExceedanceIntervals | BaselineRatingExceedancePct | PeakTimestampUTC | RatingA | VoltageKV | RatingKVA | PhaseCount | CapacityMethod | ParallelElementCount | ParallelElementIDs
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 0.9 | br_02_22 | CircuitBreaker | Breaker | 13.5 | 0.03276 | 0.03276 | 0.024036 | 13.4672 | 0 | 0 | 2024-01-20 07:00 |  |  | 15000 | 3 | Breaker_kVA_x_PF | 1 | br_02_22
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 0.9 | line_5852_22 | ACLineSegment | Line | 12.8296 | 0.03276 | 0.03276 | 0.024036 | 12.7969 | 0 | 0 | 2024-01-20 07:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I_x_PF | 1 | line_5852_22
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 0.95 | br_02_22 | CircuitBreaker | Breaker | 14.25 | 0.03276 | 0.03276 | 0.024036 | 14.2172 | 0 | 0 | 2024-01-20 07:00 |  |  | 15000 | 3 | Breaker_kVA_x_PF | 1 | br_02_22
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 0.95 | line_5852_22 | ACLineSegment | Line | 13.5424 | 0.03276 | 0.03276 | 0.024036 | 13.5096 | 0 | 0 | 2024-01-20 07:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I_x_PF | 1 | line_5852_22
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 1 | br_02_22 | CircuitBreaker | Breaker | 15 | 0.03276 | 0.03276 | 0.024036 | 14.9672 | 0 | 0 | 2024-01-20 07:00 |  |  | 15000 | 3 | Breaker_kVA_x_PF | 1 | br_02_22
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 1 | line_5852_22 | ACLineSegment | Line | 14.2551 | 0.03276 | 0.03276 | 0.024036 | 14.2224 | 0 | 0 | 2024-01-20 07:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I_x_PF | 1 | line_5852_22
GSO_124¦line_6716_22 | GSO_124 | hvmv_1_22 | line_6716_22 | 0.9 | br_04_22 | CircuitBreaker | Breaker | 13.5 | 0.13387 | 0.13387 | 0.0957 | 13.3661 | 0 | 0 | 2024-01-22 04:00 |  |  | 15000 | 3 | Breaker_kVA_x_PF | 1 | br_04_22
GSO_124¦line_6716_22 | GSO_124 | hvmv_1_22 | line_6716_22 | 0.9 | line_6716_22 | ACLineSegment | Line | 12.8296 | 0.13387 | 0.13387 | 0.0957 | 12.6957 | 0 | 0 | 2024-01-22 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I_x_PF | 1 | line_6716_22
GSO_124¦line_6716_22 | GSO_124 | hvmv_1_22 | line_6716_22 | 0.95 | br_04_22 | CircuitBreaker | Breaker | 14.25 | 0.13387 | 0.13387 | 0.0957 | 14.1161 | 0 | 0 | 2024-01-22 04:00 |  |  | 15000 | 3 | Breaker_kVA_x_PF | 1 | br_04_22
GSO_124¦line_6716_22 | GSO_124 | hvmv_1_22 | line_6716_22 | 0.95 | line_6716_22 | ACLineSegment | Line | 13.5424 | 0.13387 | 0.13387 | 0.0957 | 13.4085 | 0 | 0 | 2024-01-22 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I_x_PF | 1 | line_6716_22
GSO_124¦line_6716_22 | GSO_124 | hvmv_1_22 | line_6716_22 | 1 | br_04_22 | CircuitBreaker | Breaker | 15 | 0.13387 | 0.13387 | 0.0957 | 14.8661 | 0 | 0 | 2024-01-22 04:00 |  |  | 15000 | 3 | Breaker_kVA_x_PF | 1 | br_04_22
GSO_124¦line_6716_22 | GSO_124 | hvmv_1_22 | line_6716_22 | 1 | line_6716_22 | ACLineSegment | Line | 14.2551 | 0.13387 | 0.13387 | 0.0957 | 14.1213 | 0 | 0 | 2024-01-22 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I_x_PF | 1 | line_6716_22
GSO_123¦line_6019_22 | GSO_123 | hvmv_1_22 | line_6019_22 | 0.9 | br_03_22 | CircuitBreaker | Breaker | 13.5 | 0.36464 | 0.36464 | 0.28877 | 13.1354 | 0 | 0 | 2024-01-22 04:00 |  |  | 15000 | 3 | Breaker_kVA_x_PF | 1 | br_03_22
GSO_123¦line_6019_22 | GSO_123 | hvmv_1_22 | line_6019_22 | 0.9 | line_6019_22 | ACLineSegment | Line | 12.8296 | 0.36464 | 0.36464 | 0.28877 | 12.465 | 0 | 0 | 2024-01-22 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I_x_PF | 1 | line_6019_22
GSO_123¦line_6019_22 | GSO_123 | hvmv_1_22 | line_6019_22 | 0.95 | br_03_22 | CircuitBreaker | Breaker | 14.25 | 0.36464 | 0.36464 | 0.28877 | 13.8854 | 0 | 0 | 2024-01-22 04:00 |  |  | 15000 | 3 | Breaker_kVA_x_PF | 1 | br_03_22
GSO_123¦line_6019_22 | GSO_123 | hvmv_1_22 | line_6019_22 | 0.95 | line_6019_22 | ACLineSegment | Line | 13.5424 | 0.36464 | 0.36464 | 0.28877 | 13.1777 | 0 | 0 | 2024-01-22 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I_x_PF | 1 | line_6019_22
GSO_123¦line_6019_22 | GSO_123 | hvmv_1_22 | line_6019_22 | 1 | br_03_22 | CircuitBreaker | Breaker | 15 | 0.36464 | 0.36464 | 0.28877 | 14.6354 | 0 | 0 | 2024-01-22 04:00 |  |  | 15000 | 3 | Breaker_kVA_x_PF | 1 | br_03_22
GSO_123¦line_6019_22 | GSO_123 | hvmv_1_22 | line_6019_22 | 1 | line_6019_22 | ACLineSegment | Line | 14.2551 | 0.36464 | 0.36464 | 0.28877 | 13.8905 | 0 | 0 | 2024-01-22 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I_x_PF | 1 | line_6019_22
GSO_121¦line_3530_22 | GSO_121 | hvmv_1_22 | line_3530_22 | 0.9 | br_01_22 | CircuitBreaker | Breaker | 13.5 | 0.38162 | 0.38162 | 0.30456 | 13.1184 | 0 | 0 | 2024-01-17 23:00 |  |  | 15000 | 3 | Breaker_kVA_x_PF | 1 | br_01_22
GSO_121¦line_3530_22 | GSO_121 | hvmv_1_22 | line_3530_22 | 0.9 | line_3530_22 | ACLineSegment | Line | 12.8296 | 0.38162 | 0.38162 | 0.30456 | 12.448 | 0 | 0 | 2024-01-17 23:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I_x_PF | 1 | line_3530_22
GSO_121¦line_3530_22 | GSO_121 | hvmv_1_22 | line_3530_22 | 0.95 | br_01_22 | CircuitBreaker | Breaker | 14.25 | 0.38162 | 0.38162 | 0.30456 | 13.8684 | 0 | 0 | 2024-01-17 23:00 |  |  | 15000 | 3 | Breaker_kVA_x_PF | 1 | br_01_22
GSO_121¦line_3530_22 | GSO_121 | hvmv_1_22 | line_3530_22 | 0.95 | line_3530_22 | ACLineSegment | Line | 13.5424 | 0.38162 | 0.38162 | 0.30456 | 13.1607 | 0 | 0 | 2024-01-17 23:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I_x_PF | 1 | line_3530_22
GSO_121¦line_3530_22 | GSO_121 | hvmv_1_22 | line_3530_22 | 1 | br_01_22 | CircuitBreaker | Breaker | 15 | 0.38162 | 0.38162 | 0.30456 | 14.6184 | 0 | 0 | 2024-01-17 23:00 |  |  | 15000 | 3 | Breaker_kVA_x_PF | 1 | br_01_22
GSO_121¦line_3530_22 | GSO_121 | hvmv_1_22 | line_3530_22 | 1 | line_3530_22 | ACLineSegment | Line | 14.2551 | 0.38162 | 0.38162 | 0.30456 | 13.8735 | 0 | 0 | 2024-01-17 23:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I_x_PF | 1 | line_3530_22
GSO_144¦line_5978_22 | GSO_144 | hvmv_5_22 | line_5978_22 | 0.9 | br_024_22 | CircuitBreaker | Breaker | 10.8 | 0.13286 | 0.13286 | 0.090084 | 10.6671 | 0 | 0 | 2024-01-20 21:00 |  |  | 12000 | 3 | Breaker_kVA_x_PF | 1 | br_024_22
GSO_144¦line_5978_22 | GSO_144 | hvmv_5_22 | line_5978_22 | 0.9 | line_5978_22 | ACLineSegment | Line | 11.6633 | 0.13286 | 0.13286 | 0.090084 | 11.5304 | 0 | 0 | 2024-01-20 21:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I_x_PF | 1 | line_5978_22
GSO_144¦line_5978_22 | GSO_144 | hvmv_5_22 | line_5978_22 | 0.95 | br_024_22 | CircuitBreaker | Breaker | 11.4 | 0.13286 | 0.13286 | 0.090084 | 11.2671 | 0 | 0 | 2024-01-20 21:00 |  |  | 12000 | 3 | Breaker_kVA_x_PF | 1 | br_024_22
GSO_144¦line_5978_22 | GSO_144 | hvmv_5_22 | line_5978_22 | 0.95 | line_5978_22 | ACLineSegment | Line | 12.3112 | 0.13286 | 0.13286 | 0.090084 | 12.1784 | 0 | 0 | 2024-01-20 21:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I_x_PF | 1 | line_5978_22
GSO_144¦line_5978_22 | GSO_144 | hvmv_5_22 | line_5978_22 | 1 | br_024_22 | CircuitBreaker | Breaker | 12 | 0.13286 | 0.13286 | 0.090084 | 11.8671 | 0 | 0 | 2024-01-20 21:00 |  |  | 12000 | 3 | Breaker_kVA_x_PF | 1 | br_024_22
GSO_144¦line_5978_22 | GSO_144 | hvmv_5_22 | line_5978_22 | 1 | line_5978_22 | ACLineSegment | Line | 12.9592 | 0.13286 | 0.13286 | 0.090084 | 12.8263 | 0 | 0 | 2024-01-20 21:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I_x_PF | 1 | line_5978_22
GSO_141¦line_4565_22 | GSO_141 | hvmv_5_22 | line_4565_22 | 0.9 | br_021_22 | CircuitBreaker | Breaker | 10.8 | 0.37996 | 0.37996 | 0.29074 | 10.42 | 0 | 0 | 2024-01-21 01:00 |  |  | 12000 | 3 | Breaker_kVA_x_PF | 1 | br_021_22
GSO_141¦line_4565_22 | GSO_141 | hvmv_5_22 | line_4565_22 | 0.9 | line_4565_22 | ACLineSegment | Line | 12.8296 | 0.37996 | 0.37996 | 0.29074 | 12.4497 | 0 | 0 | 2024-01-21 01:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I_x_PF | 1 | line_4565_22
GSO_141¦line_4565_22 | GSO_141 | hvmv_5_22 | line_4565_22 | 0.95 | br_021_22 | CircuitBreaker | Breaker | 11.4 | 0.37996 | 0.37996 | 0.29074 | 11.02 | 0 | 0 | 2024-01-21 01:00 |  |  | 12000 | 3 | Breaker_kVA_x_PF | 1 | br_021_22
GSO_141¦line_4565_22 | GSO_141 | hvmv_5_22 | line_4565_22 | 0.95 | line_4565_22 | ACLineSegment | Line | 13.5424 | 0.37996 | 0.37996 | 0.29074 | 13.1624 | 0 | 0 | 2024-01-21 01:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I_x_PF | 1 | line_4565_22
GSO_141¦line_4565_22 | GSO_141 | hvmv_5_22 | line_4565_22 | 1 | br_021_22 | CircuitBreaker | Breaker | 12 | 0.37996 | 0.37996 | 0.29074 | 11.62 | 0 | 0 | 2024-01-21 01:00 |  |  | 12000 | 3 | Breaker_kVA_x_PF | 1 | br_021_22
GSO_141¦line_4565_22 | GSO_141 | hvmv_5_22 | line_4565_22 | 1 | line_4565_22 | ACLineSegment | Line | 14.2551 | 0.37996 | 0.37996 | 0.29074 | 13.8752 | 0 | 0 | 2024-01-21 01:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I_x_PF | 1 | line_4565_22
GSO_145¦line_6170_22 | GSO_145 | hvmv_5_22 | line_6170_22 | 0.9 | br_025_22 | CircuitBreaker | Breaker | 10.8 | 0.73442 | 0.73442 | 0.56032 | 10.0656 | 0 | 0 | 2024-01-21 04:00 |  |  | 12000 | 3 | Breaker_kVA_x_PF | 1 | br_025_22
GSO_145¦line_6170_22 | GSO_145 | hvmv_5_22 | line_6170_22 | 0.9 | line_6170_22 | ACLineSegment | Line | 12.8296 | 0.69166 | 0.69166 | 0.52887 | 12.1379 | 0 | 0 | 2024-01-21 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I_x_PF | 1 | line_6170_22
GSO_145¦line_6170_22 | GSO_145 | hvmv_5_22 | line_6170_22 | 0.95 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 0.73442 | 0.56032 | 10.6656 | 0 | 0 | 2024-01-21 04:00 |  |  | 12000 | 3 | Breaker_kVA_x_PF | 1 | br_025_22
GSO_145¦line_6170_22 | GSO_145 | hvmv_5_22 | line_6170_22 | 0.95 | line_6170_22 | ACLineSegment | Line | 13.5424 | 0.69166 | 0.69166 | 0.52887 | 12.8507 | 0 | 0 | 2024-01-21 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I_x_PF | 1 | line_6170_22
GSO_145¦line_6170_22 | GSO_145 | hvmv_5_22 | line_6170_22 | 1 | br_025_22 | CircuitBreaker | Breaker | 12 | 0.73442 | 0.73442 | 0.56032 | 11.2656 | 0 | 0 | 2024-01-21 04:00 |  |  | 12000 | 3 | Breaker_kVA_x_PF | 1 | br_025_22
GSO_145¦line_6170_22 | GSO_145 | hvmv_5_22 | line_6170_22 | 1 | line_6170_22 | ACLineSegment | Line | 14.2551 | 0.69166 | 0.69166 | 0.52887 | 13.5635 | 0 | 0 | 2024-01-21 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I_x_PF | 1 | line_6170_22
GSO_142¦line_5429_22 | GSO_142 | hvmv_5_22 | line_5429_22 | 0.9 | br_022_22 | CircuitBreaker | Breaker | 10.8 | 0.79259 | 0.79259 | 0.62478 | 10.0074 | 0 | 0 | 2024-07-09 |  |  | 12000 | 3 | Breaker_kVA_x_PF | 1 | br_022_22
GSO_142¦line_5429_22 | GSO_142 | hvmv_5_22 | line_5429_22 | 0.9 | line_5429_22 | ACLineSegment | Line | 12.8296 | 0.79259 | 0.79259 | 0.62478 | 12.037 | 0 | 0 | 2024-07-09 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I_x_PF | 1 | line_5429_22
GSO_142¦line_5429_22 | GSO_142 | hvmv_5_22 | line_5429_22 | 0.95 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 0.79259 | 0.62478 | 10.6074 | 0 | 0 | 2024-07-09 |  |  | 12000 | 3 | Breaker_kVA_x_PF | 1 | br_022_22
GSO_142¦line_5429_22 | GSO_142 | hvmv_5_22 | line_5429_22 | 0.95 | line_5429_22 | ACLineSegment | Line | 13.5424 | 0.79259 | 0.79259 | 0.62478 | 12.7498 | 0 | 0 | 2024-07-09 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I_x_PF | 1 | line_5429_22
GSO_142¦line_5429_22 | GSO_142 | hvmv_5_22 | line_5429_22 | 1 | br_022_22 | CircuitBreaker | Breaker | 12 | 0.79259 | 0.79259 | 0.62478 | 11.2074 | 0 | 0 | 2024-07-09 |  |  | 12000 | 3 | Breaker_kVA_x_PF | 1 | br_022_22
GSO_142¦line_5429_22 | GSO_142 | hvmv_5_22 | line_5429_22 | 1 | line_5429_22 | ACLineSegment | Line | 14.2551 | 0.79259 | 0.79259 | 0.62478 | 13.4625 | 0 | 0 | 2024-07-09 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I_x_PF | 1 | line_5429_22
GSO_18¦line_108323_21 | GSO_18 | hvmv_4_21 | line_108323_21 | 0.9 | br_025_21 | CircuitBreaker | Breaker | 12 | 2.2897 | 2.2897 | 1.713 | 9.7102 | 0 | 0 | 2024-01-21 |  |  | 13333.3 | 3 | Breaker_kVA_x_PF | 1 | br_025_21
GSO_18¦line_108323_21 | GSO_18 | hvmv_4_21 | line_108323_21 | 0.9 | line_108323_21 | ACLineSegment | Line | 12.8296 | 2.2897 | 2.2897 | 1.713 | 10.5399 | 0 | 0 | 2024-01-21 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I_x_PF | 1 | line_108323_21
GSO_18¦line_108323_21 | GSO_18 | hvmv_4_21 | line_108323_21 | 0.95 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 2.2897 | 1.713 | 10.3769 | 0 | 0 | 2024-01-21 |  |  | 13333.3 | 3 | Breaker_kVA_x_PF | 1 | br_025_21
GSO_18¦line_108323_21 | GSO_18 | hvmv_4_21 | line_108323_21 | 0.95 | line_108323_21 | ACLineSegment | Line | 13.5424 | 2.2897 | 2.2897 | 1.713 | 11.2526 | 0 | 0 | 2024-01-21 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I_x_PF | 1 | line_108323_21
GSO_18¦line_108323_21 | GSO_18 | hvmv_4_21 | line_108323_21 | 1 | br_025_21 | CircuitBreaker | Breaker | 13.3333 | 2.2897 | 2.2897 | 1.713 | 11.0436 | 0 | 0 | 2024-01-21 |  |  | 13333.3 | 3 | Breaker_kVA_x_PF | 1 | br_025_21
GSO_18¦line_108323_21 | GSO_18 | hvmv_4_21 | line_108323_21 | 1 | line_108323_21 | ACLineSegment | Line | 14.2551 | 2.2897 | 2.2897 | 1.713 | 11.9654 | 0 | 0 | 2024-01-21 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I_x_PF | 1 | line_108323_21
GSO_127¦line_6871_22 | GSO_127 | hvmv_2_22 | line_6871_22 | 0.9 | br_07_22 | CircuitBreaker | Breaker | 9 | 0.025212 | 0.025212 | 0.016656 | 8.9748 | 0 | 0 | 2024-01-20 21:00 |  |  | 10000 | 3 | Breaker_kVA_x_PF | 1 | br_07_22
GSO_127¦line_6871_22 | GSO_127 | hvmv_2_22 | line_6871_22 | 0.9 | line_6871_22 | ACLineSegment | Line | 12.8296 | 0.025212 | 0.025212 | 0.016656 | 12.8044 | 0 | 0 | 2024-01-20 21:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I_x_PF | 1 | line_6871_22
GSO_127¦line_6871_22 | GSO_127 | hvmv_2_22 | line_6871_22 | 0.95 | br_07_22 | CircuitBreaker | Breaker | 9.5 | 0.025212 | 0.025212 | 0.016656 | 9.4748 | 0 | 0 | 2024-01-20 21:00 |  |  | 10000 | 3 | Breaker_kVA_x_PF | 1 | br_07_22
GSO_127¦line_6871_22 | GSO_127 | hvmv_2_22 | line_6871_22 | 0.95 | line_6871_22 | ACLineSegment | Line | 13.5424 | 0.025212 | 0.025212 | 0.016656 | 13.5172 | 0 | 0 | 2024-01-20 21:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I_x_PF | 1 | line_6871_22
GSO_127¦line_6871_22 | GSO_127 | hvmv_2_22 | line_6871_22 | 1 | br_07_22 | CircuitBreaker | Breaker | 10 | 0.025212 | 0.025212 | 0.016656 | 9.9748 | 0 | 0 | 2024-01-20 21:00 |  |  | 10000 | 3 | Breaker_kVA_x_PF | 1 | br_07_22
GSO_127¦line_6871_22 | GSO_127 | hvmv_2_22 | line_6871_22 | 1 | line_6871_22 | ACLineSegment | Line | 14.2551 | 0.025212 | 0.025212 | 0.016656 | 14.2299 | 0 | 0 | 2024-01-20 21:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I_x_PF | 1 | line_6871_22

## Feeder_Diagnostics
GridID | BreakerID | RootNode | FeederIsRadialAfterOpenSwitchRemoval | CycleRank | GraphNodesConnectedToRoot | GraphEdgesConnectedToRoot | MeterTopologyMappingPct | MaxHourlyRootShareConservationError | BaselineRatingExceedanceElements | BaselineRatingExceedanceElementsOnSelectedPaths | ParallelNodePairCount | SkippedOpenSwitches | SkippedMissingTerminalElements | BreakerSourceCount | BreakerMedianRawIntervalMinutes | BreakerExpected5MinIntervals | BreakerAccepted5MinIntervals | Breaker5MinCoveragePct | BreakerMissingSourceCellsBeforeFill | BreakerMissingSourceCellsAfterLimitedFill | BreakerPeakMW | BreakerP95AbsMW | MeterCount | MeterSourceCount | MetersWithoutKWhSource | MetersWithMultipleKWhSources | TotalMeterHourCells | MissingMeterHourCellsBeforeFill | MissingMeterHourCellsAfterFill | MeterHourCellsFilled | MeterHourFillPct | NegativeMeterHourCells | NegativeMeterHourPct | DirectMeterWeightHours | FallbackMeterWeightHours | MaxHourlyMeterWeightSumError | ExtremeCalibrationHours | MeterBreakerCorrelation | MeterBreakerNMAEPct | MeterBreakerEnergyRatio | MeterBreakerMatchedHours
GSO_122 | br_02_22 | S_nSSEE0_12.47 | TRUE | 0 | 11 | 10 | 100 | 2.2204e-16 | 0 | 0 | 0 | 0 | 0 | 3 | 5 | 105348 | 105348 | 100 | 0 | 0 | 0.03276 | 0.024036 | 3 | 3 | 0 | 0 | 26337 | 0 | 0 | 0 | 0 | 0 | 0 | 8779 | 0 | 2.2204e-16 | 0 | 0.99996 | 3.8462 | 0.96154 | 8779
GSO_124 | br_04_22 | S_nSSEE0_12.47 | TRUE | 0 | 58 | 57 | 100 | 5.5511e-16 | 0 | 0 | 0 | 0 | 0 | 3 | 5 | 105348 | 105348 | 100 | 0 | 0 | 0.13387 | 0.0957 | 16 | 16 | 0 | 0 | 140464 | 0 | 0 | 0 | 0 | 0 | 0 | 8779 | 0 | 6.6613e-16 | 0 | 0.99997 | 3.8457 | 0.96154 | 8779
GSO_123 | br_03_22 | S_nSSEE0_12.47 | TRUE | 0 | 183 | 182 | 100 | 8.8818e-16 | 1 | 0 | 0 | 0 | 0 | 3 | 5 | 105348 | 105348 | 100 | 0 | 0 | 0.36464 | 0.28877 | 47 | 47 | 0 | 0 | 412613 | 0 | 0 | 0 | 0 | 0 | 0 | 8779 | 0 | 8.8818e-16 | 0 | 0.99993 | 3.8463 | 0.96154 | 8779
GSO_121 | br_01_22 | S_nSSEE0_12.47 | FALSE | 1 | 280 | 280 | 100 | 8.8818e-16 | 2 | 0 | 0 | 0 | 0 | 3 | 5 | 105348 | 105348 | 100 | 0 | 0 | 0.38162 | 0.30456 | 72 | 74 | 0 | 2 | 632088 | 0 | 0 | 0 | 0 | 0 | 0 | 8779 | 0 | 1.1102e-15 | 0 | 0.98983 | 3.0957 | 0.9715 | 8779
GSO_144 | br_024_22 | S_nSSEE4_12.47 | TRUE | 0 | 80 | 79 | 100 | 6.6613e-16 | 2 | 0 | 0 | 0 | 0 | 3 | 5 | 105348 | 105348 | 100 | 0 | 0 | 0.13286 | 0.090084 | 32 | 32 | 0 | 0 | 280928 | 0 | 0 | 0 | 0 | 0 | 0 | 8779 | 0 | 7.7716e-16 | 0 | 0.99998 | 3.8453 | 0.96155 | 8779
GSO_141 | br_021_22 | S_nSSEE4_12.47 | TRUE | 0 | 240 | 239 | 100 | 9.992e-16 | 3 | 0 | 0 | 0 | 0 | 3 | 5 | 105348 | 105348 | 100 | 0 | 0 | 0.37996 | 0.29074 | 68 | 68 | 0 | 0 | 596972 | 0 | 0 | 0 | 0 | 0 | 0 | 8779 | 0 | 1.1102e-15 | 0 | 0.99996 | 3.8441 | 0.96156 | 8779
GSO_145 | br_025_22 | S_nSSEE4_12.47 | FALSE | 1 | 455 | 455 | 90.9677 | 1.5543e-15 | 4 | 0 | 0 | 0 | 0 | 3 | 5 | 105348 | 105348 | 100 | 0 | 0 | 0.73442 | 0.56032 | 155 | 157 | 0 | 2 | 1360745 | 0 | 0 | 0 | 0 | 0 | 0 | 8779 | 0 | 1.5543e-15 | 0 | 0.90219 | 4.8665 | 1.0486 | 8779
GSO_142 | br_022_22 | S_nSSEE4_12.47 | FALSE | 2 | 563 | 564 | 100 | 1.3323e-15 | 7 | 0 | 0 | 0 | 0 | 3 | 5 | 105348 | 105348 | 100 | 0 | 0 | 0.79259 | 0.62478 | 140 | 141 | 0 | 1 | 1229060 | 0 | 0 | 0 | 0 | 0 | 0 | 8779 | 0 | 2.1094e-15 | 0 | 0.9917 | 3.1071 | 0.96924 | 8779
GSO_18 | br_025_21 | S_nSSEE11_12.47 | FALSE | 2 | 1416 | 1417 | 100 | 2.6645e-15 | 55 | 0 | 0 | 0 | 0 | 3 | 5 | 105348 | 105348 | 100 | 0 | 0 | 2.2897 | 1.713 | 584 | 589 | 0 | 5 | 5126936 | 0 | 0 | 0 | 0 | 0 | 0 | 8779 | 0 | 8.6597e-15 | 0 | 0.9914 | 3.2888 | 0.97819 | 8779
GSO_127 | br_07_22 | S_nSSEE1_12.47 | TRUE | 0 | 3 | 2 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 5 | 105348 | 105348 | 100 | 0 | 0 | 0.025212 | 0.016656 | 1 | 1 | 0 | 0 | 8779 | 0 | 0 | 0 | 0 | 0 | 0 | 8779 | 0 | 0 | 0 | 0.99998 | 3.8459 | 0.96154 | 8779

## Reconciliation_Audit
GridID | MeterBreakerCorrelation | MeterBreakerNMAEPct | MeterBreakerEnergyRatio | MeterBreakerMatchedHours
GSO_122 | 0.99996 | 3.8462 | 0.96154 | 8779
GSO_124 | 0.99997 | 3.8457 | 0.96154 | 8779
GSO_123 | 0.99993 | 3.8463 | 0.96154 | 8779
GSO_121 | 0.98983 | 3.0957 | 0.9715 | 8779
GSO_144 | 0.99998 | 3.8453 | 0.96155 | 8779
GSO_141 | 0.99996 | 3.8441 | 0.96156 | 8779
GSO_145 | 0.90219 | 4.8665 | 1.0486 | 8779
GSO_142 | 0.9917 | 3.1071 | 0.96924 | 8779
GSO_18 | 0.9914 | 3.2888 | 0.97819 | 8779
GSO_127 | 0.99998 | 3.8459 | 0.96154 | 8779

## Element_Load_Summary
GridID | GridElementID | ElementType | ElementClass | CapacityMW_BasePF | PeakExistingAbsMW | PeakExistingSignedMW | P95ExistingAbsMW | PeakUtilizationPct | RatingExceedanceIntervals | RatingExceedanceHoursEquivalent | RatingExceedancePctIntervals | PeakTimestampUTC | OnSelectedCandidatePath | ParallelElementCount | ParallelElementIDs | CapacityMethod | AuditInterpretation
GSO_122 | line_2430_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2430_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_122 | line_5871_22 | ACLineSegment | Line | 0.51338 | 0.0053565 | 0.0053565 | 0.0037537 | 1.0434 | 0 | 0 | 0 | 2024-01-20 18:50 | FALSE | 1 | line_5871_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_122 | tr_993_22 | Transformer | Transformer | 0.285 | 0.0053565 | 0.0053565 | 0.0037537 | 1.8795 | 0 | 0 | 0 | 2024-01-20 18:50 | FALSE | 1 | tr_993_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_122 | line_2978_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2978_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_122 | line_5379_22 | ACLineSegment | Line | 0.034884 | 0.0048476 | 0.0048476 | 0.0033764 | 13.8965 | 0 | 0 | 0 | 2024-01-20 18:50 | FALSE | 1 | line_5379_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_122 | tr_741_22 | Transformer | Transformer | 0.02375 | 0.0048476 | 0.0048476 | 0.0033764 | 20.4109 | 0 | 0 | 0 | 2024-01-20 18:50 | FALSE | 1 | tr_741_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_122 | line_5376_22 | ACLineSegment | Line | 13.5424 | 0.029143 | 0.029143 | 0.020841 | 0.2152 | 0 | 0 | 0 | 2024-01-20 07:00 | FALSE | 1 | line_5376_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_122 | line_5377_22 | ACLineSegment | Line | 13.5424 | 0.02651 | 0.02651 | 0.017992 | 0.19576 | 0 | 0 | 0 | 2024-01-20 07:00 | FALSE | 1 | line_5377_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_122 | line_5852_22 | ACLineSegment | Line | 13.5424 | 0.03276 | 0.03276 | 0.024036 | 0.24191 | 0 | 0 | 0 | 2024-01-20 07:00 | TRUE | 1 | line_5852_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_124 | tr_183_22 | Transformer | Transformer | 0.02375 | 0.0055535 | 0.0055535 | 0.0028529 | 23.3832 | 0 | 0 | 0 | 2024-01-20 07:00 | FALSE | 1 | tr_183_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_124 | line_3767_22 | ACLineSegment | Line | 13.5424 | 0.04621 | 0.04621 | 0.035667 | 0.34122 | 0 | 0 | 0 | 2024-07-16 01:00 | FALSE | 1 | line_3767_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_124 | line_3830_22 | ACLineSegment | Line | 13.5424 | 0.053606 | 0.053606 | 0.04099 | 0.39584 | 0 | 0 | 0 | 2024-01-17 13:00 | FALSE | 1 | line_3830_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_124 | tr_1387_22 | Transformer | Transformer | 0.095 | 0.0057829 | 0.0057829 | 0.0041323 | 6.0873 | 0 | 0 | 0 | 2024-07-14 11:00 | FALSE | 1 | tr_1387_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_124 | line_1276_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1276_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_124 | line_3768_22 | ACLineSegment | Line | 0.034884 | 0.00811 | 0.00811 | 0.0045139 | 23.2489 | 0 | 0 | 0 | 2024-07-15 10:10 | FALSE | 1 | line_3768_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_124 | tr_87_22 | Transformer | Transformer | 0.02375 | 0.00811 | 0.00811 | 0.0045139 | 34.1475 | 0 | 0 | 0 | 2024-07-15 10:10 | FALSE | 1 | tr_87_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_124 | line_1278_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1278_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_124 | line_3774_22 | ACLineSegment | Line | 0.51338 | 0.0076731 | 0.0076731 | 0.0050931 | 1.4946 | 0 | 0 | 0 | 2024-01-20 09:55 | FALSE | 1 | line_3774_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_124 | tr_89_22 | Transformer | Transformer | 0.95 | 0.0076731 | 0.0076731 | 0.0050931 | 0.8077 | 0 | 0 | 0 | 2024-01-20 09:55 | FALSE | 1 | tr_89_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_124 | line_1299_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1299_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_124 | line_3832_22 | ACLineSegment | Line | 0.51338 | 0.007017 | 0.007017 | 0.0049376 | 1.3668 | 0 | 0 | 0 | 2024-01-20 20:00 | FALSE | 1 | line_3832_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_124 | tr_107_22 | Transformer | Transformer | 0.95 | 0.007017 | 0.007017 | 0.0049376 | 0.73863 | 0 | 0 | 0 | 2024-01-20 20:00 | FALSE | 1 | tr_107_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_124 | line_1332_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1332_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_124 | line_6708_22 | ACLineSegment | Line | 0.51338 | 0.0078364 | 0.0078364 | 0.00567 | 1.5264 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_6708_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_124 | tr_1498_22 | Transformer | Transformer | 0.95 | 0.0078364 | 0.0078364 | 0.00567 | 0.82489 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | tr_1498_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_124 | line_1442_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1442_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_124 | line_4021_22 | ACLineSegment | Line | 0.034884 | 0.0055535 | 0.0055535 | 0.0028529 | 15.9202 | 0 | 0 | 0 | 2024-01-20 07:00 | FALSE | 1 | line_4021_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_124 | line_1545_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1545_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_124 | line_4131_22 | ACLineSegment | Line | 0.51338 | 0.008343 | 0.008343 | 0.0061165 | 1.6251 | 0 | 0 | 0 | 2024-01-20 16:50 | FALSE | 1 | line_4131_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_124 | tr_231_22 | Transformer | Transformer | 0.475 | 0.008343 | 0.008343 | 0.0061165 | 1.7564 | 0 | 0 | 0 | 2024-01-20 16:50 | FALSE | 1 | tr_231_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_124 | line_2873_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2873_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_124 | line_2874_22 | ACLineSegment | Line | 0.038174 | 0.023422 | 0.023422 | 0.019139 | 61.3556 | 0 | 0 | 0 | 2024-08-29 13:00 | FALSE | 1 | line_2874_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_124 | line_2875_22 | ACLineSegment | Line | 0.025406 | 0.019574 | 0.019574 | 0.0166 | 77.0461 | 0 | 0 | 0 | 2024-01-16 07:00 | FALSE | 1 | line_2875_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_124 | line_2876_22 | ACLineSegment | Line | 0.025406 | 0.0068927 | 0.0068927 | 0.0036664 | 27.1305 | 0 | 0 | 0 | 2024-01-17 13:00 | FALSE | 1 | line_2876_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_124 | tr_831_22 | Transformer | Transformer | 0.0475 | 0.023422 | 0.023422 | 0.019139 | 49.3098 | 0 | 0 | 0 | 2024-08-29 13:00 | FALSE | 1 | tr_831_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_124 | line_3009_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_3009_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_124 | line_5396_22 | ACLineSegment | Line | 0.51338 | 0.0079031 | 0.0079031 | 0.0056219 | 1.5394 | 0 | 0 | 0 | 2024-07-06 02:10 | FALSE | 1 | line_5396_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_124 | tr_748_22 | Transformer | Transformer | 0.07125 | 0.0079031 | 0.0079031 | 0.0056219 | 11.092 | 0 | 0 | 0 | 2024-07-06 02:10 | FALSE | 1 | tr_748_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_124 | line_3246_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_3246_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_124 | line_5689_22 | ACLineSegment | Line | 0.22905 | 0.0064744 | 0.0064744 | 0.0046777 | 2.8267 | 0 | 0 | 0 | 2024-01-20 06:55 | FALSE | 1 | line_5689_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_124 | tr_904_22 | Transformer | Transformer | 0.07125 | 0.0064744 | 0.0064744 | 0.0046777 | 9.0869 | 0 | 0 | 0 | 2024-01-20 06:55 | FALSE | 1 | tr_904_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_124 | line_3766_22 | ACLineSegment | Line | 13.5424 | 0.040408 | 0.040408 | 0.032481 | 0.29838 | 0 | 0 | 0 | 2024-01-17 13:00 | FALSE | 1 | line_3766_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_124 | line_5515_22 | ACLineSegment | Line | 13.5424 | 0.034497 | 0.034497 | 0.027413 | 0.25473 | 0 | 0 | 0 | 2024-06-30 07:00 | FALSE | 1 | line_5515_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_124 | tr_1156_22 | Transformer | Transformer | 0.02375 | 0.0091627 | 0.0091627 | 0.0066391 | 38.5798 | 0 | 0 | 0 | 2024-07-15 06:55 | FALSE | 1 | tr_1156_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_124 | line_3772_22 | ACLineSegment | Line | 13.5424 | 0.0078364 | 0.0078364 | 0.00567 | 0.057866 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_3772_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_124 | line_3773_22 | ACLineSegment | Line | 13.5424 | 0.013211 | 0.013211 | 0.0099086 | 0.097555 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_3773_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_124 | line_4130_22 | ACLineSegment | Line | 13.5424 | 0.073518 | 0.073518 | 0.047798 | 0.54287 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_4130_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_124 | line_5663_22 | ACLineSegment | Line | 13.5424 | 0.029251 | 0.029251 | 0.021061 | 0.216 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_5663_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_124 | line_3829_22 | ACLineSegment | Line | 13.5424 | 0.078693 | 0.078693 | 0.052153 | 0.58109 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_3829_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_124 | line_3831_22 | ACLineSegment | Line | 13.5424 | 0.12932 | 0.12932 | 0.092842 | 0.95494 | 0 | 0 | 0 | 2024-01-22 04:00 | FALSE | 1 | line_3831_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_124 | line_6716_22 | ACLineSegment | Line | 13.5424 | 0.13387 | 0.13387 | 0.0957 | 0.98854 | 0 | 0 | 0 | 2024-01-22 04:00 | TRUE | 1 | line_6716_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_124 | tr_1508_22 | Transformer | Transformer | 0.02375 | 0.0054276 | 0.0054276 | 0.0033647 | 22.853 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | tr_1508_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_124 | line_454_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_454_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_124 | line_6185_22 | ACLineSegment | Line | 0.034884 | 0.0091627 | 0.0091627 | 0.0066391 | 26.2666 | 0 | 0 | 0 | 2024-07-15 06:55 | FALSE | 1 | line_6185_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_124 | line_476_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_476_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_124 | line_6130_22 | ACLineSegment | Line | 0.51338 | 0.0071623 | 0.0071623 | 0.0048941 | 1.3951 | 0 | 0 | 0 | 2024-01-20 07:00 | FALSE | 1 | line_6130_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_124 | tr_1129_22 | Transformer | Transformer | 0.475 | 0.0071623 | 0.0071623 | 0.0048941 | 1.5078 | 0 | 0 | 0 | 2024-01-20 07:00 | FALSE | 1 | tr_1129_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_124 | line_5514_22 | ACLineSegment | Line | 12.3112 | 0.0071623 | 0.0071623 | 0.0048941 | 0.058177 | 0 | 0 | 0 | 2024-01-20 07:00 | FALSE | 1 | line_5514_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_124 | line_5664_22 | ACLineSegment | Line | 13.5424 | 0.025158 | 0.025158 | 0.017201 | 0.18577 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_5664_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_124 | line_6560_22 | ACLineSegment | Line | 0.51338 | 0.0057829 | 0.0057829 | 0.0041323 | 1.1264 | 0 | 0 | 0 | 2024-07-14 11:00 | FALSE | 1 | line_6560_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_124 | line_809_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_809_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_124 | line_6717_22 | ACLineSegment | Line | 0.034884 | 0.0054276 | 0.0054276 | 0.0033647 | 15.5592 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_6717_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_123 | line_1133_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1133_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_123 | line_3593_22 | ACLineSegment | Line | 0.51338 | 0.0058073 | 0.0058073 | 0.0043735 | 1.1312 | 0 | 0 | 0 | 2024-01-20 06:00 | FALSE | 1 | line_3593_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | tr_25_22 | Transformer | Transformer | 0.095 | 0.0058073 | 0.0058073 | 0.0043735 | 6.113 | 0 | 0 | 0 | 2024-01-20 06:00 | FALSE | 1 | tr_25_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_123 | line_1134_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1134_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_123 | line_3607_22 | ACLineSegment | Line | 0.51338 | 0.0068882 | 0.0068882 | 0.0050667 | 1.3417 | 0 | 0 | 0 | 2024-01-20 13:55 | FALSE | 1 | line_3607_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | tr_30_22 | Transformer | Transformer | 0.285 | 0.0068882 | 0.0068882 | 0.0050667 | 2.4169 | 0 | 0 | 0 | 2024-01-20 13:55 | FALSE | 1 | tr_30_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_123 | line_1272_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1272_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_123 | line_3732_22 | ACLineSegment | Line | 0.51338 | 0.0065818 | 0.0065818 | 0.0050164 | 1.2821 | 0 | 0 | 0 | 2024-01-20 08:55 | FALSE | 1 | line_3732_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | tr_74_22 | Transformer | Transformer | 0.095 | 0.0065818 | 0.0065818 | 0.0050164 | 6.9283 | 0 | 0 | 0 | 2024-01-20 08:55 | FALSE | 1 | tr_74_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_123 | line_1281_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1281_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_123 | line_3744_22 | ACLineSegment | Line | 0.51338 | 0.0073729 | 0.0073729 | 0.0055724 | 1.4362 | 0 | 0 | 0 | 2024-01-21 03:50 | FALSE | 1 | line_3744_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | tr_78_22 | Transformer | Transformer | 0.1425 | 0.0073729 | 0.0073729 | 0.0055724 | 5.174 | 0 | 0 | 0 | 2024-01-21 03:50 | FALSE | 1 | tr_78_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_123 | line_1288_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1288_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_123 | line_3746_22 | ACLineSegment | Line | 0.51338 | 0.0040871 | 0.0040871 | 0.0029841 | 0.79612 | 0 | 0 | 0 | 2024-07-15 11:45 | FALSE | 1 | line_3746_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | tr_79_22 | Transformer | Transformer | 0.285 | 0.0040871 | 0.0040871 | 0.0029841 | 1.4341 | 0 | 0 | 0 | 2024-07-15 11:45 | FALSE | 1 | tr_79_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_123 | line_1333_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1333_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_123 | line_6711_22 | ACLineSegment | Line | 0.51338 | 0.0045313 | 0.0045313 | 0.0031899 | 0.88263 | 0 | 0 | 0 | 2024-01-20 17:00 | FALSE | 1 | line_6711_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | tr_1502_22 | Transformer | Transformer | 0.285 | 0.0045313 | 0.0045313 | 0.0031899 | 1.5899 | 0 | 0 | 0 | 2024-01-20 17:00 | FALSE | 1 | tr_1502_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_123 | line_1337_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1337_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_123 | line_6709_22 | ACLineSegment | Line | 0.51338 | 0.0060491 | 0.0060491 | 0.0044848 | 1.1783 | 0 | 0 | 0 | 2024-01-20 08:55 | FALSE | 1 | line_6709_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | tr_1499_22 | Transformer | Transformer | 0.07125 | 0.0060491 | 0.0060491 | 0.0044848 | 8.49 | 0 | 0 | 0 | 2024-01-20 08:55 | FALSE | 1 | tr_1499_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_123 | line_1357_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1357_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_123 | line_6729_22 | ACLineSegment | Line | 0.034884 | 0.0088929 | 0.0088929 | 0.0059474 | 25.4933 | 0 | 0 | 0 | 2024-01-20 07:55 | FALSE | 1 | line_6729_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_123 | tr_1520_22 | Transformer | Transformer | 0.0475 | 0.0088929 | 0.0088929 | 0.0059474 | 18.722 | 0 | 0 | 0 | 2024-01-20 07:55 | FALSE | 1 | tr_1520_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_123 | line_1376_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1376_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_123 | line_3879_22 | ACLineSegment | Line | 0.51338 | 0.0096356 | 0.0096356 | 0.006417 | 1.8769 | 0 | 0 | 0 | 2024-01-20 13:55 | FALSE | 1 | line_3879_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | tr_123_22 | Transformer | Transformer | 0.285 | 0.0096356 | 0.0096356 | 0.006417 | 3.3809 | 0 | 0 | 0 | 2024-01-20 13:55 | FALSE | 1 | tr_123_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_123 | line_1418_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1418_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_123 | line_3955_22 | ACLineSegment | Line | 0.51338 | 0.0063484 | 0.0063484 | 0.0042738 | 1.2366 | 0 | 0 | 0 | 2024-01-21 01:00 | FALSE | 1 | line_3955_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | tr_154_22 | Transformer | Transformer | 0.07125 | 0.0063484 | 0.0063484 | 0.0042738 | 8.91 | 0 | 0 | 0 | 2024-01-21 01:00 | FALSE | 1 | tr_154_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_123 | line_1439_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1439_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_123 | line_4023_22 | ACLineSegment | Line | 0.51338 | 0.028257 | 0.028257 | 0.018087 | 5.5041 | 0 | 0 | 0 | 2024-01-21 02:50 | FALSE | 1 | line_4023_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | tr_184_22 | Transformer | Transformer | 0.95 | 0.028257 | 0.028257 | 0.018087 | 2.9744 | 0 | 0 | 0 | 2024-01-21 02:50 | FALSE | 1 | tr_184_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_123 | line_1444_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1444_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_123 | line_4034_22 | ACLineSegment | Line | 0.51338 | 0.0090183 | 0.0090183 | 0.0056124 | 1.7567 | 0 | 0 | 0 | 2024-07-10 17:00 | FALSE | 1 | line_4034_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | tr_188_22 | Transformer | Transformer | 0.07125 | 0.0090183 | 0.0090183 | 0.0056124 | 12.6573 | 0 | 0 | 0 | 2024-07-10 17:00 | FALSE | 1 | tr_188_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_123 | line_1477_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1477_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_123 | line_4048_22 | ACLineSegment | Line | 0.51338 | 0.0068314 | 0.0068314 | 0.0051789 | 1.3307 | 0 | 0 | 0 | 2024-07-15 19:00 | FALSE | 1 | line_4048_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | tr_195_22 | Transformer | Transformer | 0.285 | 0.0068314 | 0.0068314 | 0.0051789 | 2.397 | 0 | 0 | 0 | 2024-07-15 19:00 | FALSE | 1 | tr_195_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_123 | line_1546_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1546_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_123 | line_4143_22 | ACLineSegment | Line | 0.025406 | 0.00332 | 0.00332 | 0.001856 | 13.0678 | 0 | 0 | 0 | 2024-01-20 09:50 | FALSE | 1 | line_4143_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_123 | tr_236_22 | Transformer | Transformer | 0.02375 | 0.00332 | 0.00332 | 0.001856 | 13.9788 | 0 | 0 | 0 | 2024-01-20 09:50 | FALSE | 1 | tr_236_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_123 | line_1639_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1639_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_123 | line_4181_22 | ACLineSegment | Line | 0.51338 | 0.028571 | 0.028571 | 0.01686 | 5.5652 | 0 | 0 | 0 | 2024-01-21 03:50 | FALSE | 1 | line_4181_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | tr_250_22 | Transformer | Transformer | 0.285 | 0.028571 | 0.028571 | 0.01686 | 10.0248 | 0 | 0 | 0 | 2024-01-21 03:50 | FALSE | 1 | tr_250_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_123 | line_1642_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1642_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_123 | line_4186_22 | ACLineSegment | Line | 0.51338 | 0.00783 | 0.00783 | 0.0051353 | 1.5252 | 0 | 0 | 0 | 2024-01-20 13:55 | FALSE | 1 | line_4186_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | tr_252_22 | Transformer | Transformer | 0.1425 | 0.00783 | 0.00783 | 0.0051353 | 5.4948 | 0 | 0 | 0 | 2024-01-20 13:55 | FALSE | 1 | tr_252_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_123 | line_1769_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1769_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_123 | line_4390_22 | ACLineSegment | Line | 0.51338 | 0.005754 | 0.005754 | 0.004357 | 1.1208 | 0 | 0 | 0 | 2024-01-20 20:55 | FALSE | 1 | line_4390_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | tr_320_22 | Transformer | Transformer | 0.095 | 0.005754 | 0.005754 | 0.004357 | 6.0568 | 0 | 0 | 0 | 2024-01-20 20:55 | FALSE | 1 | tr_320_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_123 | line_1926_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1926_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_123 | line_4426_22 | ACLineSegment | Line | 0.51338 | 0.0088484 | 0.0088484 | 0.0066104 | 1.7236 | 0 | 0 | 0 | 2024-01-20 21:00 | FALSE | 1 | line_4426_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | tr_334_22 | Transformer | Transformer | 0.07125 | 0.0088484 | 0.0088484 | 0.0066104 | 12.4188 | 0 | 0 | 0 | 2024-01-20 21:00 | FALSE | 1 | tr_334_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_123 | line_1948_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1948_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_123 | line_4508_22 | ACLineSegment | Line | 0.51338 | 0.024001 | 0.024001 | 0.017537 | 4.6752 | 0 | 0 | 0 | 2024-01-18 00:45 | FALSE | 1 | line_4508_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | tr_365_22 | Transformer | Transformer | 0.07125 | 0.024001 | 0.024001 | 0.017537 | 33.6861 | 0 | 0 | 0 | 2024-01-18 00:45 | FALSE | 1 | tr_365_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_123 | line_1992_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1992_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_123 | line_4629_22 | ACLineSegment | Line | 0.51338 | 0.0063913 | 0.0063913 | 0.0043975 | 1.245 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_4629_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | tr_411_22 | Transformer | Transformer | 0.285 | 0.0063913 | 0.0063913 | 0.0043975 | 2.2426 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | tr_411_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_123 | line_2094_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2094_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_123 | line_4781_22 | ACLineSegment | Line | 0.51338 | 0.027864 | 0.027864 | 0.019965 | 5.4276 | 0 | 0 | 0 | 2024-07-16 02:10 | FALSE | 1 | line_4781_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | tr_475_22 | Transformer | Transformer | 0.285 | 0.027864 | 0.027864 | 0.019965 | 9.7769 | 0 | 0 | 0 | 2024-07-16 02:10 | FALSE | 1 | tr_475_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_123 | line_2180_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2180_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_123 | line_5159_22 | ACLineSegment | Line | 0.51338 | 0.0082159 | 0.0082159 | 0.0061698 | 1.6004 | 0 | 0 | 0 | 2024-01-20 19:00 | FALSE | 1 | line_5159_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | tr_648_22 | Transformer | Transformer | 0.475 | 0.0082159 | 0.0082159 | 0.0061698 | 1.7297 | 0 | 0 | 0 | 2024-01-20 19:00 | FALSE | 1 | tr_648_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_123 | line_2708_22 | ACLineSegment | Line | 0.51338 | 0.0077764 | 0.0077764 | 0.0055752 | 1.5147 | 0 | 0 | 0 | 2024-07-15 22:20 | FALSE | 1 | line_2708_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | line_2709_22 | ACLineSegment | Line | 0.51338 | 0.0077764 | 0.0077764 | 0.0055752 | 1.5147 | 0 | 0 | 0 | 2024-07-15 22:20 | FALSE | 1 | line_2709_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | tr_768_22 | Transformer | Transformer | 0.475 | 0.0077764 | 0.0077764 | 0.0055752 | 1.6371 | 0 | 0 | 0 | 2024-07-15 22:20 | FALSE | 1 | tr_768_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_123 | line_2812_22 | ACLineSegment | Line | 0.22905 | 0.0066159 | 0.0066159 | 0.0045624 | 2.8885 | 0 | 0 | 0 | 2024-01-20 15:00 | FALSE | 1 | line_2812_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | line_2813_22 | ACLineSegment | Line | 0.22905 | 0.0066159 | 0.0066159 | 0.0045624 | 2.8885 | 0 | 0 | 0 | 2024-01-20 15:00 | FALSE | 1 | line_2813_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | tr_812_22 | Transformer | Transformer | 0.07125 | 0.0066159 | 0.0066159 | 0.0045624 | 9.2855 | 0 | 0 | 0 | 2024-01-20 15:00 | FALSE | 1 | tr_812_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_123 | line_3104_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_3104_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_123 | line_5693_22 | ACLineSegment | Line | 0.034884 | 0.004616 | 0.004616 | 0.0032014 | 13.2326 | 0 | 0 | 0 | 2024-01-20 12:05 | FALSE | 1 | line_5693_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_123 | tr_917_22 | Transformer | Transformer | 0.02375 | 0.004616 | 0.004616 | 0.0032014 | 19.4357 | 0 | 0 | 0 | 2024-01-20 12:05 | FALSE | 1 | tr_917_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_123 | line_3120_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_3120_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_123 | line_5722_22 | ACLineSegment | Line | 0.034884 | 0.005215 | 0.005215 | 0.0030148 | 14.9498 | 0 | 0 | 0 | 2024-07-16 01:45 | FALSE | 1 | line_5722_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_123 | tr_930_22 | Transformer | Transformer | 0.02375 | 0.005215 | 0.005215 | 0.0030148 | 21.9579 | 0 | 0 | 0 | 2024-07-16 01:45 | FALSE | 1 | tr_930_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_123 | line_3224_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_3224_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_123 | line_5589_22 | ACLineSegment | Line | 0.51338 | 0.0072673 | 0.0072673 | 0.0050178 | 1.4156 | 0 | 0 | 0 | 2024-06-27 03:00 | FALSE | 1 | line_5589_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | tr_869_22 | Transformer | Transformer | 0.1425 | 0.0072673 | 0.0072673 | 0.0050178 | 5.0998 | 0 | 0 | 0 | 2024-06-27 03:00 | FALSE | 1 | tr_869_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_123 | line_3366_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_3366_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_123 | line_5914_22 | ACLineSegment | Line | 0.034884 | 0.0071397 | 0.0071397 | 0.0053818 | 20.4673 | 0 | 0 | 0 | 2024-01-21 00:50 | FALSE | 1 | line_5914_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_123 | tr_1023_22 | Transformer | Transformer | 0.02375 | 0.0071397 | 0.0071397 | 0.0053818 | 30.0619 | 0 | 0 | 0 | 2024-01-21 00:50 | FALSE | 1 | tr_1023_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_123 | line_344_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_344_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_123 | line_6009_22 | ACLineSegment | Line | 0.51338 | 0.0059204 | 0.0059204 | 0.0041282 | 1.1532 | 0 | 0 | 0 | 2024-07-16 03:00 | FALSE | 1 | line_6009_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | tr_1067_22 | Transformer | Transformer | 0.095 | 0.0059204 | 0.0059204 | 0.0041282 | 6.232 | 0 | 0 | 0 | 2024-07-16 03:00 | FALSE | 1 | tr_1067_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_123 | line_3471_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_3471_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_123 | line_5853_22 | ACLineSegment | Line | 0.51338 | 0.02225 | 0.02225 | 0.016774 | 4.334 | 0 | 0 | 0 | 2024-07-11 01:00 | FALSE | 1 | line_5853_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | tr_994_22 | Transformer | Transformer | 0.07125 | 0.02225 | 0.02225 | 0.016774 | 31.2277 | 0 | 0 | 0 | 2024-07-11 01:00 | FALSE | 1 | tr_994_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_123 | line_3493_22 | ACLineSegment | Line | 0.034884 | 0.007423 | 0.007423 | 0.0035184 | 21.2794 | 0 | 0 | 0 | 2024-01-20 16:50 | FALSE | 1 | line_3493_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_123 | line_3494_22 | ACLineSegment | Line | 0.034884 | 0.007423 | 0.007423 | 0.0035184 | 21.2794 | 0 | 0 | 0 | 2024-01-20 16:50 | FALSE | 1 | line_3494_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_123 | line_3495_22 | ACLineSegment | Line | 0.034884 | 0.0077987 | 0.0077987 | 0.0048851 | 22.3564 | 0 | 0 | 0 | 2024-01-21 03:50 | FALSE | 1 | line_3495_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_123 | tr_990_22 | Transformer | Transformer | 0.0475 | 0.012493 | 0.012493 | 0.0077362 | 26.3015 | 0 | 0 | 0 | 2024-01-20 16:50 | FALSE | 1 | tr_990_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_123 | line_3496_22 | ACLineSegment | Line | 0.034884 | 0.0077987 | 0.0077987 | 0.0048851 | 22.3564 | 0 | 0 | 0 | 2024-01-21 03:50 | FALSE | 1 | line_3496_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_123 | line_357_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_357_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_123 | line_6020_22 | ACLineSegment | Line | 0.51338 | 0.010494 | 0.010494 | 0.0071482 | 2.0442 | 0 | 0 | 0 | 2024-07-10 17:00 | FALSE | 1 | line_6020_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | tr_1073_22 | Transformer | Transformer | 0.475 | 0.010494 | 0.010494 | 0.0071482 | 2.2094 | 0 | 0 | 0 | 2024-07-10 17:00 | FALSE | 1 | tr_1073_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_123 | line_3591_22 | ACLineSegment | Line | 13.5424 | 0.1752 | 0.1752 | 0.13944 | 1.2937 | 0 | 0 | 0 | 2024-01-22 03:50 | FALSE | 1 | line_3591_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | line_3592_22 | ACLineSegment | Line | 13.5424 | 0.17198 | 0.17198 | 0.13572 | 1.27 | 0 | 0 | 0 | 2024-01-22 03:50 | FALSE | 1 | line_3592_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | line_4185_22 | ACLineSegment | Line | 13.5424 | 0.17994 | 0.17994 | 0.14361 | 1.3287 | 0 | 0 | 0 | 2024-01-20 14:00 | FALSE | 1 | line_4185_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | line_6181_22 | ACLineSegment | Line | 13.5424 | 0.039763 | 0.039763 | 0.025802 | 0.29362 | 0 | 0 | 0 | 2024-01-21 03:50 | FALSE | 1 | line_6181_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | line_3605_22 | ACLineSegment | Line | 13.5424 | 0.3312 | 0.3312 | 0.26308 | 2.4457 | 0 | 0 | 0 | 2024-01-22 04:00 | FALSE | 1 | line_3605_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | line_3606_22 | ACLineSegment | Line | 13.5424 | 0.33729 | 0.33729 | 0.2674 | 2.4907 | 0 | 0 | 0 | 2024-01-22 04:00 | FALSE | 1 | line_3606_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | line_5721_22 | ACLineSegment | Line | 13.5424 | 0.31532 | 0.31532 | 0.24976 | 2.3284 | 0 | 0 | 0 | 2024-01-22 04:00 | FALSE | 1 | line_5721_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | line_4780_22 | ACLineSegment | Line | 13.5424 | 0.027864 | 0.027864 | 0.019965 | 0.20575 | 0 | 0 | 0 | 2024-07-16 02:10 | FALSE | 1 | line_4780_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | line_6019_22 | ACLineSegment | Line | 13.5424 | 0.36464 | 0.36464 | 0.28877 | 2.6926 | 0 | 0 | 0 | 2024-01-22 04:00 | TRUE | 1 | line_6019_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | line_368_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_368_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_123 | line_6076_22 | ACLineSegment | Line | 0.51338 | 0.0077103 | 0.0077103 | 0.005807 | 1.5019 | 0 | 0 | 0 | 2024-07-15 17:05 | FALSE | 1 | line_6076_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | tr_1103_22 | Transformer | Transformer | 0.07125 | 0.0077103 | 0.0077103 | 0.005807 | 10.8214 | 0 | 0 | 0 | 2024-07-15 17:05 | FALSE | 1 | tr_1103_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_123 | line_3731_22 | ACLineSegment | Line | 13.5424 | 0.0065818 | 0.0065818 | 0.0050164 | 0.048602 | 0 | 0 | 0 | 2024-01-20 08:55 | FALSE | 1 | line_3731_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | line_5692_22 | ACLineSegment | Line | 13.5424 | 0.010303 | 0.010303 | 0.0076999 | 0.076082 | 0 | 0 | 0 | 2024-01-20 17:00 | FALSE | 1 | line_5692_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | line_3742_22 | ACLineSegment | Line | 13.5424 | 0.11188 | 0.11188 | 0.089881 | 0.82615 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_3742_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | line_3743_22 | ACLineSegment | Line | 13.5424 | 0.10712 | 0.10712 | 0.085541 | 0.79099 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_3743_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | line_6691_22 | ACLineSegment | Line | 13.5424 | 0.11683 | 0.11683 | 0.093171 | 0.86273 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_6691_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | tr_1486_22 | Transformer | Transformer | 0.095 | 0.0055019 | 0.0055019 | 0.0040185 | 5.7915 | 0 | 0 | 0 | 2024-01-20 18:55 | FALSE | 1 | tr_1486_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_123 | line_6670_22 | ACLineSegment | Line | 13.5424 | 0.10385 | 0.10385 | 0.081748 | 0.76683 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_6670_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | line_3745_22 | ACLineSegment | Line | 13.5424 | 0.0040871 | 0.0040871 | 0.0029841 | 0.03018 | 0 | 0 | 0 | 2024-07-15 11:45 | FALSE | 1 | line_3745_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | line_6357_22 | ACLineSegment | Line | 13.5424 | 0.097306 | 0.097306 | 0.075848 | 0.71853 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_6357_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | tr_1474_22 | Transformer | Transformer | 0.475 | 0.0060937 | 0.0060937 | 0.0044475 | 1.2829 | 0 | 0 | 0 | 2024-07-15 13:55 | FALSE | 1 | tr_1474_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_123 | line_3878_22 | ACLineSegment | Line | 13.5424 | 0.0096356 | 0.0096356 | 0.006417 | 0.071152 | 0 | 0 | 0 | 2024-01-20 13:55 | FALSE | 1 | line_3878_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | line_3953_22 | ACLineSegment | Line | 13.5424 | 0.27499 | 0.27499 | 0.21864 | 2.0306 | 0 | 0 | 0 | 2024-01-22 04:00 | FALSE | 1 | line_3953_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | line_3954_22 | ACLineSegment | Line | 13.5424 | 0.27754 | 0.27754 | 0.22211 | 2.0494 | 0 | 0 | 0 | 2024-01-22 04:00 | FALSE | 1 | line_3954_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | line_4022_22 | ACLineSegment | Line | 13.5424 | 0.26041 | 0.26041 | 0.20376 | 1.9229 | 0 | 0 | 0 | 2024-01-22 04:00 | FALSE | 1 | line_4022_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | line_5430_22 | ACLineSegment | Line | 13.5424 | 0.28527 | 0.28527 | 0.22655 | 2.1065 | 0 | 0 | 0 | 2024-01-22 04:00 | FALSE | 1 | line_5430_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | line_4389_22 | ACLineSegment | Line | 13.5424 | 0.25698 | 0.25698 | 0.20029 | 1.8976 | 0 | 0 | 0 | 2024-01-22 04:00 | FALSE | 1 | line_4389_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | line_4032_22 | ACLineSegment | Line | 13.5424 | 0.12015 | 0.12015 | 0.095886 | 0.8872 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_4032_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | line_4033_22 | ACLineSegment | Line | 13.5424 | 0.12495 | 0.12495 | 0.10016 | 0.92268 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_4033_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | line_4047_22 | ACLineSegment | Line | 13.5424 | 0.0068314 | 0.0068314 | 0.0051789 | 0.050444 | 0 | 0 | 0 | 2024-07-15 19:00 | FALSE | 1 | line_4047_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | line_6584_22 | ACLineSegment | Line | 13.5424 | 0.053598 | 0.053598 | 0.037753 | 0.39578 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_6584_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | line_6585_22 | ACLineSegment | Line | 13.5424 | 0.022136 | 0.022136 | 0.015819 | 0.16346 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_6585_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | tr_1402_22 | Transformer | Transformer | 0.02375 | 0.026622 | 0.026622 | 0.021056 | 112.0922 | 863 | 71.9167 | 0.81919 | 2024-01-17 22:25 | FALSE | 1 | tr_1402_22 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_123 | line_4141_22 | ACLineSegment | Line | 12.3112 | 0.033888 | 0.033888 | 0.021938 | 0.27526 | 0 | 0 | 0 | 2024-01-22 03:50 | FALSE | 1 | line_4141_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | line_4142_22 | ACLineSegment | Line | 13.5424 | 0.036526 | 0.036526 | 0.023433 | 0.26972 | 0 | 0 | 0 | 2024-01-21 03:50 | FALSE | 1 | line_4142_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | tr_1153_22 | Transformer | Transformer | 0.02375 | 0.005634 | 0.005634 | 0.003011 | 23.7219 | 0 | 0 | 0 | 2024-01-18 03:00 | FALSE | 1 | tr_1153_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_123 | line_4507_22 | ACLineSegment | Line | 13.5424 | 0.19873 | 0.19873 | 0.15771 | 1.4675 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_4507_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | line_5492_22 | ACLineSegment | Line | 13.5424 | 0.062884 | 0.062884 | 0.046928 | 0.46435 | 0 | 0 | 0 | 2024-07-08 19:00 | FALSE | 1 | line_5492_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | tr_1336_22 | Transformer | Transformer | 0.1425 | 0.0092671 | 0.0092671 | 0.0069587 | 6.5032 | 0 | 0 | 0 | 2024-07-15 11:45 | FALSE | 1 | tr_1336_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_123 | line_4425_22 | ACLineSegment | Line | 13.5424 | 0.0088484 | 0.0088484 | 0.0066104 | 0.065338 | 0 | 0 | 0 | 2024-01-20 21:00 | FALSE | 1 | line_4425_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | line_4627_22 | ACLineSegment | Line | 13.5424 | 0.30455 | 0.30455 | 0.24163 | 2.2489 | 0 | 0 | 0 | 2024-01-22 04:00 | FALSE | 1 | line_4627_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | line_4628_22 | ACLineSegment | Line | 13.5424 | 0.29843 | 0.29843 | 0.23786 | 2.2037 | 0 | 0 | 0 | 2024-01-22 04:00 | FALSE | 1 | line_4628_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | line_5588_22 | ACLineSegment | Line | 13.5424 | 0.2944 | 0.2944 | 0.23473 | 2.1739 | 0 | 0 | 0 | 2024-01-22 04:00 | FALSE | 1 | line_5588_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | line_5158_22 | ACLineSegment | Line | 13.5424 | 0.0082159 | 0.0082159 | 0.0061698 | 0.060668 | 0 | 0 | 0 | 2024-01-20 19:00 | FALSE | 1 | line_5158_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | line_6075_22 | ACLineSegment | Line | 13.5424 | 0.070774 | 0.070774 | 0.054383 | 0.52261 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_6075_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | line_6628_22 | ACLineSegment | Line | 13.5424 | 0.060267 | 0.060267 | 0.045308 | 0.44502 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_6628_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | line_5587_22 | ACLineSegment | Line | 13.5424 | 0.28995 | 0.28995 | 0.23101 | 2.1411 | 0 | 0 | 0 | 2024-01-22 04:00 | FALSE | 1 | line_5587_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | line_5491_22 | ACLineSegment | Line | 13.5424 | 0.057943 | 0.057943 | 0.043551 | 0.42787 | 0 | 0 | 0 | 2024-07-08 19:00 | FALSE | 1 | line_5491_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | line_6329_22 | ACLineSegment | Line | 13.5424 | 0.034974 | 0.034974 | 0.025937 | 0.25825 | 0 | 0 | 0 | 2024-09-22 22:00 | FALSE | 1 | line_6329_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | tr_1230_22 | Transformer | Transformer | 0.095 | 0.031665 | 0.031665 | 0.02277 | 33.3315 | 0 | 0 | 0 | 2024-01-22 04:00 | FALSE | 1 | tr_1230_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_123 | line_5844_22 | ACLineSegment | Line | 13.5424 | 0.085055 | 0.085055 | 0.06559 | 0.62807 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_5844_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | tr_1247_22 | Transformer | Transformer | 0.285 | 0.0054921 | 0.0054921 | 0.0040182 | 1.9271 | 0 | 0 | 0 | 2024-01-20 14:00 | FALSE | 1 | tr_1247_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_123 | line_5843_22 | ACLineSegment | Line | 13.5424 | 0.075744 | 0.075744 | 0.058797 | 0.55931 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_5843_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | line_587_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_587_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_123 | line_6330_22 | ACLineSegment | Line | 0.51338 | 0.031665 | 0.031665 | 0.02277 | 6.1679 | 0 | 0 | 0 | 2024-01-22 04:00 | FALSE | 1 | line_6330_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | line_588_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_588_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_123 | line_6358_22 | ACLineSegment | Line | 0.51338 | 0.0054921 | 0.0054921 | 0.0040182 | 1.0698 | 0 | 0 | 0 | 2024-01-20 14:00 | FALSE | 1 | line_6358_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | line_6182_22 | ACLineSegment | Line | 0.034884 | 0.005634 | 0.005634 | 0.003011 | 16.1508 | 0 | 0 | 0 | 2024-01-18 03:00 | FALSE | 1 | line_6182_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_123 | line_6642_22 | ACLineSegment | Line | 13.5424 | 0.0060145 | 0.0060145 | 0.004437 | 0.044413 | 0 | 0 | 0 | 2024-01-20 23:50 | FALSE | 1 | line_6642_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | tr_1451_22 | Transformer | Transformer | 0.07125 | 0.030841 | 0.030841 | 0.022527 | 43.2853 | 0 | 0 | 0 | 2024-10-06 09:00 | FALSE | 1 | tr_1451_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_123 | line_6463_22 | ACLineSegment | Line | 13.5424 | 0.009503 | 0.009503 | 0.0068173 | 0.070172 | 0 | 0 | 0 | 2024-01-17 20:55 | FALSE | 1 | line_6463_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | tr_1314_22 | Transformer | Transformer | 0.285 | 0.009503 | 0.009503 | 0.0068173 | 3.3344 | 0 | 0 | 0 | 2024-01-17 20:55 | FALSE | 1 | tr_1314_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_123 | tr_1439_22 | Transformer | Transformer | 0.285 | 0.0049455 | 0.0049455 | 0.0032101 | 1.7352 | 0 | 0 | 0 | 2024-01-20 19:00 | FALSE | 1 | tr_1439_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_123 | line_6464_22 | ACLineSegment | Line | 0.51338 | 0.009503 | 0.009503 | 0.0068173 | 1.8511 | 0 | 0 | 0 | 2024-01-17 20:55 | FALSE | 1 | line_6464_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | line_699_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_699_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_123 | line_6502_22 | ACLineSegment | Line | 0.51338 | 0.0092671 | 0.0092671 | 0.0069587 | 1.8051 | 0 | 0 | 0 | 2024-07-15 11:45 | FALSE | 1 | line_6502_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | line_737_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_737_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_123 | line_6586_22 | ACLineSegment | Line | 0.034884 | 0.026622 | 0.026622 | 0.021056 | 76.3166 | 0 | 0 | 0 | 2024-01-17 22:25 | FALSE | 1 | line_6586_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_123 | line_807_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_807_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_123 | line_6629_22 | ACLineSegment | Line | 0.51338 | 0.0049455 | 0.0049455 | 0.0032101 | 0.96331 | 0 | 0 | 0 | 2024-01-20 19:00 | FALSE | 1 | line_6629_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | line_864_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_864_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_123 | tr_1593_22 | Transformer | Transformer | 0.475 | 0.0060145 | 0.0060145 | 0.004437 | 1.2662 | 0 | 0 | 0 | 2024-01-20 23:50 | FALSE | 1 | tr_1593_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_123 | line_6643_22 | ACLineSegment | Line | 0.51338 | 0.030841 | 0.030841 | 0.022527 | 6.0074 | 0 | 0 | 0 | 2024-10-06 09:00 | FALSE | 1 | line_6643_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | line_913_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_913_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_123 | line_6671_22 | ACLineSegment | Line | 0.51338 | 0.0060937 | 0.0060937 | 0.0044475 | 1.187 | 0 | 0 | 0 | 2024-07-15 13:55 | FALSE | 1 | line_6671_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | line_897_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_897_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_123 | line_6692_22 | ACLineSegment | Line | 0.51338 | 0.0055019 | 0.0055019 | 0.0040185 | 1.0717 | 0 | 0 | 0 | 2024-01-20 18:55 | FALSE | 1 | line_6692_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | line_957_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_957_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_123 | line_6858_22 | ACLineSegment | Line | 0.51338 | 0.0060145 | 0.0060145 | 0.004437 | 1.1716 | 0 | 0 | 0 | 2024-01-20 23:50 | FALSE | 1 | line_6858_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_123 | line_998_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_998_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_5619_22 | ACLineSegment | Line | 13.5424 | 0.12069 | 0.12069 | 0.087474 | 0.89119 | 0 | 0 | 0 | 2024-01-20 13:20 | FALSE | 1 | line_5619_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | line_6085_22 | ACLineSegment | Line | 13.5424 | 0.095783 | 0.095783 | 0.070616 | 0.70729 | 0 | 0 | 0 | 2024-01-20 22:00 | FALSE | 1 | line_6085_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | tr_1107_22 | Transformer | Transformer | 0.02375 | 0.019996 | 0.019996 | 0.011302 | 84.1932 | 0 | 0 | 0 | 2024-01-20 13:20 | FALSE | 1 | tr_1107_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_121 | line_6086_22 | ACLineSegment | Line | 0.94778 | 0.013407 | 0.013407 | 0.0075641 | 1.4146 | 0 | 0 | 0 | 2024-07-05 22:55 | FALSE | 1 | line_6086_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_4865_22 | ACLineSegment | Line | 12.3112 | 0.061731 | 0.061731 | 0.045613 | 0.50142 | 0 | 0 | 0 | 2024-07-15 22:55 | FALSE | 1 | line_4865_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | tr_512_22 | Transformer | Transformer | 0.095 | 0.0052787 | 0.0052787 | 0.004041 | 5.5565 | 0 | 0 | 0 | 2024-06-26 21:00 | FALSE | 1 | tr_512_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_121 | line_4867_22 | ACLineSegment | Line | 2.3694 | 0.009247 | 0.009247 | 0.00538 | 0.39026 | 0 | 0 | 0 | 2024-01-21 01:10 | FALSE | 1 | line_4867_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_11_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_11_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_5902_22 | ACLineSegment | Line | 0.51338 | 0.0058374 | 0.0058374 | 0.0044749 | 1.137 | 0 | 0 | 0 | 2024-07-16 01:00 | FALSE | 1 | line_5902_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | tr_1016_22 | Transformer | Transformer | 0.07125 | 0.0058374 | 0.0058374 | 0.0044749 | 8.1928 | 0 | 0 | 0 | 2024-07-16 01:00 | FALSE | 1 | tr_1016_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_121 | line_1940_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1940_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_4475_22 | ACLineSegment | Line | 0.51338 | 0.0059863 | 0.0059863 | 0.0042924 | 1.1661 | 0 | 0 | 0 | 2024-06-23 00:55 | FALSE | 1 | line_4475_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | tr_353_22 | Transformer | Transformer | 0.095 | 0.0059863 | 0.0059863 | 0.0042924 | 6.3014 | 0 | 0 | 0 | 2024-06-23 00:55 | FALSE | 1 | tr_353_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_121 | line_1950_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1950_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_4574_22 | ACLineSegment | Line | 0.51338 | 0.022508 | 0.022508 | 0.01645 | 4.3842 | 0 | 0 | 0 | 2024-07-15 22:55 | FALSE | 1 | line_4574_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | tr_389_22 | Transformer | Transformer | 0.285 | 0.022508 | 0.022508 | 0.01645 | 7.8975 | 0 | 0 | 0 | 2024-07-15 22:55 | FALSE | 1 | tr_389_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_121 | line_1951_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1951_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_4515_22 | ACLineSegment | Line | 0.51338 | 0.0085955 | 0.0085955 | 0.0059791 | 1.6743 | 0 | 0 | 0 | 2024-01-20 12:00 | FALSE | 1 | line_4515_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | tr_367_22 | Transformer | Transformer | 0.07125 | 0.0085955 | 0.0085955 | 0.0059791 | 12.0639 | 0 | 0 | 0 | 2024-01-20 12:00 | FALSE | 1 | tr_367_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_121 | line_1996_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1996_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_4640_22 | ACLineSegment | Line | 0.51338 | 0.0050362 | 0.0050362 | 0.0038659 | 0.98099 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | line_4640_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | tr_415_22 | Transformer | Transformer | 0.07125 | 0.0050362 | 0.0050362 | 0.0038659 | 7.0684 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | tr_415_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_121 | line_2002_22 | ACLineSegment | Line | 0.025406 | 0.0080858 | 0.0080858 | 0.0039963 | 31.8265 | 0 | 0 | 0 | 2024-01-21 02:55 | FALSE | 1 | line_2002_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_2003_22 | ACLineSegment | Line | 0.025406 | 0.0080858 | 0.0080858 | 0.0039963 | 31.8265 | 0 | 0 | 0 | 2024-01-21 02:55 | FALSE | 1 | line_2003_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_2004_22 | ACLineSegment | Line | 0.025406 | 0.0057078 | 0.0057078 | 0.0032043 | 22.4667 | 0 | 0 | 0 | 2024-01-20 22:00 | FALSE | 1 | line_2004_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | tr_407_22 | Transformer | Transformer | 0.02375 | 0.013153 | 0.013153 | 0.0069768 | 55.3811 | 0 | 0 | 0 | 2024-01-21 02:55 | FALSE | 1 | tr_407_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_121 | line_2005_22 | ACLineSegment | Line | 0.025406 | 0.0057078 | 0.0057078 | 0.0032043 | 22.4667 | 0 | 0 | 0 | 2024-01-20 22:00 | FALSE | 1 | line_2005_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_2044_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2044_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_4702_22 | ACLineSegment | Line | 0.025406 | 0.0074813 | 0.0074813 | 0.0048739 | 29.4471 | 0 | 0 | 0 | 2024-01-20 10:50 | FALSE | 1 | line_4702_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | tr_441_22 | Transformer | Transformer | 0.02375 | 0.0074813 | 0.0074813 | 0.0048739 | 31.5 | 0 | 0 | 0 | 2024-01-20 10:50 | FALSE | 1 | tr_441_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_121 | line_2054_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2054_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_4708_22 | ACLineSegment | Line | 0.51338 | 0.0060212 | 0.0060212 | 0.0037662 | 1.1728 | 0 | 0 | 0 | 2024-01-20 05:05 | FALSE | 1 | line_4708_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | tr_444_22 | Transformer | Transformer | 0.07125 | 0.0060212 | 0.0060212 | 0.0037662 | 8.4507 | 0 | 0 | 0 | 2024-01-20 05:05 | FALSE | 1 | tr_444_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_121 | line_2073_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2073_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_4839_22 | ACLineSegment | Line | 0.025406 | 0.0055128 | 0.0055128 | 0.0031959 | 21.699 | 0 | 0 | 0 | 2024-05-08 17:55 | FALSE | 1 | line_4839_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | tr_499_22 | Transformer | Transformer | 0.02375 | 0.0055128 | 0.0055128 | 0.0031959 | 23.2117 | 0 | 0 | 0 | 2024-05-08 17:55 | FALSE | 1 | tr_499_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_121 | line_2107_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2107_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_4868_22 | ACLineSegment | Line | 0.51338 | 0.0052787 | 0.0052787 | 0.004041 | 1.0282 | 0 | 0 | 0 | 2024-06-26 21:00 | FALSE | 1 | line_4868_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | line_2381_22 | ACLineSegment | Line | 0.025406 | 0.004458 | 0.004458 | 0.0024565 | 17.5472 | 0 | 0 | 0 | 2024-01-17 20:35 | FALSE | 1 | line_2381_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_2382_22 | ACLineSegment | Line | 0.025406 | 0.004458 | 0.004458 | 0.0024565 | 17.5472 | 0 | 0 | 0 | 2024-01-17 20:35 | FALSE | 1 | line_2382_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_2397_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2397_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_5662_22 | ACLineSegment | Line | 0.025406 | 0.0069851 | 0.0069851 | 0.0050208 | 27.4942 | 0 | 0 | 0 | 2024-01-20 13:20 | FALSE | 1 | line_5662_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | tr_893_22 | Transformer | Transformer | 0.02375 | 0.010809 | 0.010809 | 0.0069525 | 45.5125 | 0 | 0 | 0 | 2024-01-20 13:20 | FALSE | 1 | tr_893_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_121 | line_2411_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2411_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_5824_22 | ACLineSegment | Line | 0.034884 | 0.0055385 | 0.0055385 | 0.0027578 | 15.8772 | 0 | 0 | 0 | 2024-07-05 22:55 | FALSE | 1 | line_5824_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | tr_971_22 | Transformer | Transformer | 0.02375 | 0.0055385 | 0.0055385 | 0.0027578 | 23.3202 | 0 | 0 | 0 | 2024-07-05 22:55 | FALSE | 1 | tr_971_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_121 | line_2445_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2445_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_5716_22 | ACLineSegment | Line | 0.025406 | 0.0026701 | 0.0026701 | 0.0013236 | 10.5098 | 0 | 0 | 0 | 2024-01-17 21:00 | FALSE | 1 | line_5716_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | tr_915_22 | Transformer | Transformer | 0.02375 | 0.0026701 | 0.0026701 | 0.0013236 | 11.2425 | 0 | 0 | 0 | 2024-01-17 21:00 | FALSE | 1 | tr_915_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_121 | line_2494_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2494_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_5569_22 | ACLineSegment | Line | 0.025406 | 0.008281 | 0.008281 | 0.0041582 | 32.5951 | 0 | 0 | 0 | 2024-01-21 03:05 | FALSE | 1 | line_5569_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | tr_849_22 | Transformer | Transformer | 0.02375 | 0.008281 | 0.008281 | 0.0041582 | 34.8675 | 0 | 0 | 0 | 2024-01-21 03:05 | FALSE | 1 | tr_849_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_121 | line_2523_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2523_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_3531_22 | ACLineSegment | Line | 0.51338 | 0.015014 | 0.015014 | 0.011521 | 2.9246 | 0 | 0 | 0 | 2024-01-17 23:00 | FALSE | 1 | line_3531_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | tr_1_22 | Transformer | Transformer | 0.95 | 0.015014 | 0.015014 | 0.011521 | 1.5804 | 0 | 0 | 0 | 2024-01-17 23:00 | FALSE | 1 | tr_1_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_121 | line_2772_22 | ACLineSegment | Line | 0.51338 | 0.0076477 | 0.0076477 | 0.0049381 | 1.4897 | 0 | 0 | 0 | 2024-01-20 08:00 | FALSE | 1 | line_2772_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | line_2773_22 | ACLineSegment | Line | 0.51338 | 0.0076477 | 0.0076477 | 0.0049381 | 1.4897 | 0 | 0 | 0 | 2024-01-20 08:00 | FALSE | 1 | line_2773_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | tr_803_22 | Transformer | Transformer | 0.475 | 0.0076477 | 0.0076477 | 0.0049381 | 1.61 | 0 | 0 | 0 | 2024-01-20 08:00 | FALSE | 1 | tr_803_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_121 | line_2810_22 | ACLineSegment | Line | 0.51338 | 0.010033 | 0.010033 | 0.007365 | 1.9543 | 0 | 0 | 0 | 2024-07-15 15:00 | FALSE | 1 | line_2810_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | line_2811_22 | ACLineSegment | Line | 0.51338 | 0.010033 | 0.010033 | 0.007365 | 1.9543 | 0 | 0 | 0 | 2024-07-15 15:00 | FALSE | 1 | line_2811_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | tr_806_22 | Transformer | Transformer | 0.475 | 0.010033 | 0.010033 | 0.007365 | 2.1122 | 0 | 0 | 0 | 2024-07-15 15:00 | FALSE | 1 | tr_806_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_121 | line_295_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_295_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_6018_22 | ACLineSegment | Line | 0.025406 | 0.0025108 | 0.0025108 | 0.0015069 | 9.883 | 0 | 0 | 0 | 2024-01-20 22:00 | FALSE | 1 | line_6018_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | tr_1072_22 | Transformer | Transformer | 0.02375 | 0.0025108 | 0.0025108 | 0.0015069 | 10.5719 | 0 | 0 | 0 | 2024-01-20 22:00 | FALSE | 1 | tr_1072_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_121 | line_2964_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2964_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_5373_22 | ACLineSegment | Line | 0.51338 | 0.0070665 | 0.0070665 | 0.0050816 | 1.3765 | 0 | 0 | 0 | 2024-01-18 00:55 | FALSE | 1 | line_5373_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | tr_739_22 | Transformer | Transformer | 0.07125 | 0.0070665 | 0.0070665 | 0.0050816 | 9.9178 | 0 | 0 | 0 | 2024-01-18 00:55 | FALSE | 1 | tr_739_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_121 | line_3149_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_3149_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_5742_22 | ACLineSegment | Line | 0.51338 | 0.007763 | 0.007763 | 0.0053781 | 1.5121 | 0 | 0 | 0 | 2024-01-21 14:55 | FALSE | 1 | line_5742_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | tr_941_22 | Transformer | Transformer | 0.095 | 0.007763 | 0.007763 | 0.0053781 | 8.1716 | 0 | 0 | 0 | 2024-01-21 14:55 | FALSE | 1 | tr_941_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_121 | line_3161_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_3161_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_5526_22 | ACLineSegment | Line | 0.51338 | 0.0075269 | 0.0075269 | 0.0054992 | 1.4661 | 0 | 0 | 0 | 2024-01-20 15:00 | FALSE | 1 | line_5526_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | tr_837_22 | Transformer | Transformer | 0.1425 | 0.0075269 | 0.0075269 | 0.0054992 | 5.282 | 0 | 0 | 0 | 2024-01-20 15:00 | FALSE | 1 | tr_837_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_121 | line_3_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_3_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_5899_22 | ACLineSegment | Line | 0.025406 | 0.0063161 | 0.0063161 | 0.0045266 | 24.861 | 0 | 0 | 0 | 2024-01-20 06:50 | FALSE | 1 | line_5899_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | tr_1004_22 | Transformer | Transformer | 0.02375 | 0.0063161 | 0.0063161 | 0.0045266 | 26.5941 | 0 | 0 | 0 | 2024-01-20 06:50 | FALSE | 1 | tr_1004_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_121 | line_3230_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_3230_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_5851_22 | ACLineSegment | Line | 0.51338 | 0.0049309 | 0.0049309 | 0.0037256 | 0.96047 | 0 | 0 | 0 | 2024-07-10 22:55 | FALSE | 1 | line_5851_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | tr_982_22 | Transformer | Transformer | 0.285 | 0.0049309 | 0.0049309 | 0.0037256 | 1.7301 | 0 | 0 | 0 | 2024-07-10 22:55 | FALSE | 1 | tr_982_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_121 | line_3233_22 | ACLineSegment | Line | 0.034884 | 0.0034581 | 0.0034581 | 0.0020136 | 9.9132 | 0 | 0 | 0 | 2024-01-21 01:10 | FALSE | 1 | line_3233_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_3234_22 | ACLineSegment | Line | 0.034884 | 0.0034581 | 0.0034581 | 0.0020136 | 9.9132 | 0 | 0 | 0 | 2024-01-21 01:10 | FALSE | 1 | line_3234_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_3235_22 | ACLineSegment | Line | 0.034884 | 0.0059466 | 0.0059466 | 0.0027514 | 17.0469 | 0 | 0 | 0 | 2024-01-20 14:55 | FALSE | 1 | line_3235_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | tr_881_22 | Transformer | Transformer | 0.02375 | 0.0084669 | 0.0084669 | 0.0045371 | 35.6502 | 0 | 0 | 0 | 2024-01-21 01:10 | FALSE | 1 | tr_881_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_121 | line_3236_22 | ACLineSegment | Line | 0.034884 | 0.0059466 | 0.0059466 | 0.0027514 | 17.0469 | 0 | 0 | 0 | 2024-01-20 14:55 | FALSE | 1 | line_3236_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_3243_22 | ACLineSegment | Line | 0.025406 | 0.0035004 | 0.0035004 | 0.0019305 | 13.778 | 0 | 0 | 0 | 2024-01-17 14:55 | FALSE | 1 | line_3243_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_3244_22 | ACLineSegment | Line | 0.025406 | 0.0035004 | 0.0035004 | 0.0019305 | 13.778 | 0 | 0 | 0 | 2024-01-17 14:55 | FALSE | 1 | line_3244_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_3245_22 | ACLineSegment | Line | 0.025406 | 0.0035004 | 0.0035004 | 0.0019305 | 13.778 | 0 | 0 | 0 | 2024-01-17 14:55 | FALSE | 1 | line_3245_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_5636_22 | ACLineSegment | Line | 0.025406 | 0.0043491 | 0.0043491 | 0.0020691 | 17.1185 | 0 | 0 | 0 | 2024-01-20 12:00 | FALSE | 1 | line_5636_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | tr_889_22 | Transformer | Transformer | 0.02375 | 0.0066718 | 0.0066718 | 0.0037996 | 28.0916 | 0 | 0 | 0 | 2024-01-20 12:00 | FALSE | 1 | tr_889_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_121 | line_3259_22 | ACLineSegment | Line | 0.025406 | 0.0031204 | 0.0031204 | 0.0017221 | 12.2824 | 0 | 0 | 0 | 2024-01-20 05:05 | FALSE | 1 | line_3259_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_3260_22 | ACLineSegment | Line | 0.025406 | 0.0031204 | 0.0031204 | 0.0017221 | 12.2824 | 0 | 0 | 0 | 2024-01-20 05:05 | FALSE | 1 | line_3260_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_3277_22 | ACLineSegment | Line | 0.025406 | 0.0073237 | 0.0073237 | 0.0035767 | 28.8269 | 0 | 0 | 0 | 2024-01-20 21:25 | FALSE | 1 | line_3277_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | tr_926_22 | Transformer | Transformer | 0.02375 | 0.010205 | 0.010205 | 0.0051277 | 42.9663 | 0 | 0 | 0 | 2024-01-20 21:25 | FALSE | 1 | tr_926_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_121 | line_3276_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_3276_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_3279_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_3279_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_5639_22 | ACLineSegment | Line | 0.025406 | 0.0040434 | 0.0040434 | 0.0020651 | 15.9154 | 0 | 0 | 0 | 2024-01-20 08:00 | FALSE | 1 | line_5639_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_5640_22 | ACLineSegment | Line | 0.025406 | 0.0036157 | 0.0036157 | 0.001953 | 14.232 | 0 | 0 | 0 | 2024-01-17 18:05 | FALSE | 1 | line_5640_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | tr_891_22 | Transformer | Transformer | 0.02375 | 0.0072593 | 0.0072593 | 0.0038502 | 30.5655 | 0 | 0 | 0 | 2024-01-20 08:00 | FALSE | 1 | tr_891_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_121 | line_3278_22 | ACLineSegment | Line | 0.025406 | 0.0073237 | 0.0073237 | 0.0035767 | 28.8269 | 0 | 0 | 0 | 2024-01-20 21:25 | FALSE | 1 | line_3278_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_3296_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_3296_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_5666_22 | ACLineSegment | Line | 0.51338 | 0.0085546 | 0.0085546 | 0.006241 | 1.6663 | 0 | 0 | 0 | 2024-01-20 08:00 | FALSE | 1 | line_5666_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | tr_905_22 | Transformer | Transformer | 0.285 | 0.0085546 | 0.0085546 | 0.006241 | 3.0016 | 0 | 0 | 0 | 2024-01-20 08:00 | FALSE | 1 | tr_905_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_121 | line_3339_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_3339_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_5921_22 | ACLineSegment | Line | 0.025406 | 0.0069211 | 0.0069211 | 0.0047361 | 27.2425 | 0 | 0 | 0 | 2024-01-20 06:50 | FALSE | 1 | line_5921_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | tr_1015_22 | Transformer | Transformer | 0.02375 | 0.0069211 | 0.0069211 | 0.0047361 | 29.1417 | 0 | 0 | 0 | 2024-01-20 06:50 | FALSE | 1 | tr_1015_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_121 | line_3355_22 | ACLineSegment | Line | 0.025406 | 0.0041472 | 0.0041472 | 0.0023334 | 16.324 | 0 | 0 | 0 | 2024-01-17 22:55 | FALSE | 1 | line_3355_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_3356_22 | ACLineSegment | Line | 0.025406 | 0.0041472 | 0.0041472 | 0.0023334 | 16.324 | 0 | 0 | 0 | 2024-01-17 22:55 | FALSE | 1 | line_3356_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_3385_22 | ACLineSegment | Line | 0.025406 | 0.016582 | 0.016582 | 0.0096722 | 65.2672 | 0 | 0 | 0 | 2024-01-20 13:20 | FALSE | 1 | line_3385_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | tr_1060_22 | Transformer | Transformer | 0.02375 | 0.019615 | 0.019615 | 0.011815 | 82.5914 | 0 | 0 | 0 | 2024-01-20 13:20 | FALSE | 1 | tr_1060_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_121 | line_3370_22 | ACLineSegment | Line | 0.025406 | 0.0045745 | 0.0045745 | 0.0027557 | 18.0057 | 0 | 0 | 0 | 2024-01-20 12:00 | FALSE | 1 | line_3370_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_3371_22 | ACLineSegment | Line | 0.025406 | 0.0045745 | 0.0045745 | 0.0027557 | 18.0057 | 0 | 0 | 0 | 2024-01-20 12:00 | FALSE | 1 | line_3371_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_3384_22 | ACLineSegment | Line | 0.025406 | 0.0093969 | 0.0093969 | 0.0057806 | 36.9873 | 0 | 0 | 0 | 2024-01-20 08:00 | FALSE | 1 | line_3384_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_3400_22 | ACLineSegment | Line | 0.025406 | 0.0060786 | 0.0060786 | 0.0033001 | 23.9262 | 0 | 0 | 0 | 2024-01-20 15:00 | FALSE | 1 | line_3400_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_3386_22 | ACLineSegment | Line | 0.025406 | 0.0079537 | 0.0079537 | 0.0041394 | 31.3066 | 0 | 0 | 0 | 2024-01-20 22:00 | FALSE | 1 | line_3386_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_3413_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_3413_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_5788_22 | ACLineSegment | Line | 0.025406 | 0.0055199 | 0.0055199 | 0.0027972 | 21.727 | 0 | 0 | 0 | 2024-01-20 20:40 | FALSE | 1 | line_5788_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | tr_966_22 | Transformer | Transformer | 0.02375 | 0.0055199 | 0.0055199 | 0.0027972 | 23.2417 | 0 | 0 | 0 | 2024-01-20 20:40 | FALSE | 1 | tr_966_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_121 | line_346_22 | ACLineSegment | Line | 0.025406 | 0.0039577 | 0.0039577 | 0.0022199 | 15.578 | 0 | 0 | 0 | 2024-01-20 08:00 | FALSE | 1 | line_346_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_347_22 | ACLineSegment | Line | 0.025406 | 0.0039577 | 0.0039577 | 0.0022199 | 15.578 | 0 | 0 | 0 | 2024-01-20 08:00 | FALSE | 1 | line_347_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_352_22 | ACLineSegment | Line | 0.025406 | 0.0069087 | 0.0069087 | 0.0038103 | 27.1935 | 0 | 0 | 0 | 2024-01-21 00:55 | FALSE | 1 | line_352_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_353_22 | ACLineSegment | Line | 0.025406 | 0.00322 | 0.00322 | 0.0017018 | 12.6742 | 0 | 0 | 0 | 2024-01-21 00:55 | FALSE | 1 | line_353_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_348_22 | ACLineSegment | Line | 0.025406 | 0.0047585 | 0.0047585 | 0.0027074 | 18.73 | 0 | 0 | 0 | 2024-01-20 23:50 | FALSE | 1 | line_348_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_349_22 | ACLineSegment | Line | 0.025406 | 0.0047585 | 0.0047585 | 0.0027074 | 18.73 | 0 | 0 | 0 | 2024-01-20 23:50 | FALSE | 1 | line_349_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_350_22 | ACLineSegment | Line | 0.025406 | 0.0067245 | 0.0067245 | 0.0043406 | 26.4683 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | line_350_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_351_22 | ACLineSegment | Line | 0.025406 | 0.0033548 | 0.0033548 | 0.0017968 | 13.205 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | line_351_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | tr_1080_22 | Transformer | Transformer | 0.02375 | 0.012937 | 0.012937 | 0.0079655 | 54.4716 | 0 | 0 | 0 | 2024-01-21 00:55 | FALSE | 1 | tr_1080_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_121 | line_3529_22 | ACLineSegment | Line | 13.5424 | 0.36661 | 0.36661 | 0.29474 | 2.7071 | 0 | 0 | 0 | 2024-01-17 23:00 | FALSE | 1 | line_3529_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | line_3530_22 | ACLineSegment | Line | 13.5424 | 0.38162 | 0.38162 | 0.30456 | 2.818 | 0 | 0 | 0 | 2024-01-17 23:00 | TRUE | 1 | line_3530_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | line_5665_22 | ACLineSegment | Line | 13.5424 | 0.3602 | 0.3602 | 0.28976 | 2.6598 | 0 | 0 | 0 | 2024-01-17 23:00 | FALSE | 1 | line_5665_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | line_382_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_382_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_6089_22 | ACLineSegment | Line | 0.51338 | 0.017575 | 0.017575 | 0.013743 | 3.4233 | 0 | 0 | 0 | 2024-01-21 17:00 | FALSE | 1 | line_6089_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | tr_1108_22 | Transformer | Transformer | 0.1425 | 0.017575 | 0.017575 | 0.013743 | 12.3331 | 0 | 0 | 0 | 2024-01-21 17:00 | FALSE | 1 | tr_1108_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_121 | line_385_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_385_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_6053_22 | ACLineSegment | Line | 0.025406 | 0.036599 | 0.036599 | 0.022557 | 144.0575 | 3054 | 254.5 | 2.899 | 2024-07-05 23:05 | FALSE | 1 | line_6053_22 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_121 | tr_1094_22 | Transformer | Transformer | 0.02375 | 0.036599 | 0.036599 | 0.022557 | 154.1004 | 4046 | 337.1667 | 3.8406 | 2024-07-05 23:05 | FALSE | 1 | tr_1094_22 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_121 | line_399_22 | ACLineSegment | Line | 0.034884 | 0.0087831 | 0.0087831 | 0.004057 | 25.1783 | 0 | 0 | 0 | 2024-01-20 22:00 | FALSE | 1 | line_399_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_400_22 | ACLineSegment | Line | 0.034884 | 0.0087831 | 0.0087831 | 0.004057 | 25.1783 | 0 | 0 | 0 | 2024-01-20 22:00 | FALSE | 1 | line_400_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_401_22 | ACLineSegment | Line | 0.034884 | 0.0075896 | 0.0075896 | 0.0040615 | 21.7569 | 0 | 0 | 0 | 2024-07-15 11:30 | FALSE | 1 | line_401_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_403_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_403_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_6087_22 | ACLineSegment | Line | 0.034884 | 0.0069567 | 0.0069567 | 0.0039619 | 19.9428 | 0 | 0 | 0 | 2024-01-20 23:50 | FALSE | 1 | line_6087_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_402_22 | ACLineSegment | Line | 0.034884 | 0.0075896 | 0.0075896 | 0.0040615 | 21.7569 | 0 | 0 | 0 | 2024-07-15 11:30 | FALSE | 1 | line_402_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_4473_22 | ACLineSegment | Line | 12.3112 | 0.04594 | 0.04594 | 0.033063 | 0.37316 | 0 | 0 | 0 | 2024-07-15 22:55 | FALSE | 1 | line_4473_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | line_4474_22 | ACLineSegment | Line | 12.3112 | 0.04052 | 0.04052 | 0.029089 | 0.32913 | 0 | 0 | 0 | 2024-07-15 22:55 | FALSE | 1 | line_4474_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | tr_1462_22 | Transformer | Transformer | 0.475 | 0.0061985 | 0.0061985 | 0.0043875 | 1.3049 | 0 | 0 | 0 | 2024-01-20 15:00 | FALSE | 1 | tr_1462_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_121 | line_4512_22 | ACLineSegment | Line | 13.5424 | 0.11401 | 0.11401 | 0.085177 | 0.8419 | 0 | 0 | 0 | 2024-01-20 21:25 | FALSE | 1 | line_4512_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | line_4513_22 | ACLineSegment | Line | 13.5424 | 0.11775 | 0.11775 | 0.090119 | 0.86949 | 0 | 0 | 0 | 2024-01-20 21:25 | FALSE | 1 | line_4513_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | line_4707_22 | ACLineSegment | Line | 12.3112 | 0.11931 | 0.11931 | 0.093089 | 0.96911 | 0 | 0 | 0 | 2024-01-20 21:25 | FALSE | 1 | line_4707_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | line_4572_22 | ACLineSegment | Line | 12.3112 | 0.019158 | 0.019158 | 0.010693 | 0.15561 | 0 | 0 | 0 | 2024-01-20 08:00 | FALSE | 1 | line_4572_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | line_4573_22 | ACLineSegment | Line | 12.3112 | 0.037683 | 0.037683 | 0.025449 | 0.30609 | 0 | 0 | 0 | 2024-07-15 22:55 | FALSE | 1 | line_4573_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | line_4618_22 | ACLineSegment | Line | 2.3694 | 0.023703 | 0.023703 | 0.014643 | 1.0004 | 0 | 0 | 0 | 2024-01-21 02:55 | FALSE | 1 | line_4618_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_4619_22 | ACLineSegment | Line | 2.3694 | 0.012937 | 0.012937 | 0.0079655 | 0.54599 | 0 | 0 | 0 | 2024-01-21 00:55 | FALSE | 1 | line_4619_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_4639_22 | ACLineSegment | Line | 12.3112 | 0.11035 | 0.11035 | 0.081996 | 0.89635 | 0 | 0 | 0 | 2024-01-20 21:25 | FALSE | 1 | line_4639_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | line_4700_22 | ACLineSegment | Line | 2.3694 | 0.010809 | 0.010809 | 0.0069525 | 0.45619 | 0 | 0 | 0 | 2024-01-20 13:20 | FALSE | 1 | line_4700_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_4701_22 | ACLineSegment | Line | 2.3694 | 0.017608 | 0.017608 | 0.011021 | 0.74313 | 0 | 0 | 0 | 2024-01-20 10:50 | FALSE | 1 | line_4701_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_482_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_482_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_6145_22 | ACLineSegment | Line | 0.51338 | 0.0052371 | 0.0052371 | 0.0038242 | 1.0201 | 0 | 0 | 0 | 2024-01-17 20:35 | FALSE | 1 | line_6145_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | tr_1138_22 | Transformer | Transformer | 0.285 | 0.0052371 | 0.0052371 | 0.0038242 | 1.8376 | 0 | 0 | 0 | 2024-01-17 20:35 | FALSE | 1 | tr_1138_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_121 | line_4836_22 | ACLineSegment | Line | 2.3694 | 0.045152 | 0.045152 | 0.030131 | 1.9056 | 0 | 0 | 0 | 2024-01-20 22:00 | FALSE | 1 | line_4836_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_5553_22 | ACLineSegment | Line | 2.3694 | 0.039042 | 0.039042 | 0.026279 | 1.6477 | 0 | 0 | 0 | 2024-01-20 08:00 | FALSE | 1 | line_5553_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_4837_22 | ACLineSegment | Line | 2.3694 | 0.011129 | 0.011129 | 0.0062774 | 0.46967 | 0 | 0 | 0 | 2024-01-20 21:25 | FALSE | 1 | line_4837_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_4838_22 | ACLineSegment | Line | 2.3694 | 0.056736 | 0.056736 | 0.037741 | 2.3945 | 0 | 0 | 0 | 2024-01-20 22:00 | FALSE | 1 | line_4838_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_4866_22 | ACLineSegment | Line | 12.3112 | 0.0512 | 0.0512 | 0.037618 | 0.41588 | 0 | 0 | 0 | 2024-07-15 22:55 | FALSE | 1 | line_4866_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | tr_1022_22 | Transformer | Transformer | 0.02375 | 0.009247 | 0.009247 | 0.00538 | 38.9348 | 0 | 0 | 0 | 2024-01-21 01:10 | FALSE | 1 | tr_1022_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_121 | line_499_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_499_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_6236_22 | ACLineSegment | Line | 0.51338 | 0.0062259 | 0.0062259 | 0.0042418 | 1.2127 | 0 | 0 | 0 | 2024-01-20 22:00 | FALSE | 1 | line_6236_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | tr_1178_22 | Transformer | Transformer | 0.1425 | 0.0062259 | 0.0062259 | 0.0042418 | 4.3691 | 0 | 0 | 0 | 2024-01-20 22:00 | FALSE | 1 | tr_1178_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_121 | line_5372_22 | ACLineSegment | Line | 12.3112 | 0.06601 | 0.06601 | 0.049543 | 0.53618 | 0 | 0 | 0 | 2024-01-20 21:25 | FALSE | 1 | line_5372_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | line_539_22 | ACLineSegment | Line | 0.025406 | 0.0067916 | 0.0067916 | 0.0037021 | 26.7326 | 0 | 0 | 0 | 2024-01-20 15:00 | FALSE | 1 | line_539_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_540_22 | ACLineSegment | Line | 0.025406 | 0.0067916 | 0.0067916 | 0.0037021 | 26.7326 | 0 | 0 | 0 | 2024-01-20 15:00 | FALSE | 1 | line_540_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_541_22 | ACLineSegment | Line | 0.034884 | 0.011118 | 0.011118 | 0.007211 | 31.8732 | 0 | 0 | 0 | 2024-01-20 14:55 | FALSE | 1 | line_541_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | tr_1185_22 | Transformer | Transformer | 0.02375 | 0.017057 | 0.017057 | 0.0099181 | 71.8191 | 0 | 0 | 0 | 2024-01-20 15:00 | FALSE | 1 | tr_1185_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_121 | line_542_22 | ACLineSegment | Line | 0.034884 | 0.011118 | 0.011118 | 0.007211 | 31.8732 | 0 | 0 | 0 | 2024-01-20 14:55 | FALSE | 1 | line_542_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_5478_22 | ACLineSegment | Line | 2.3694 | 0.0072593 | 0.0072593 | 0.0038502 | 0.30637 | 0 | 0 | 0 | 2024-01-20 08:00 | FALSE | 1 | line_5478_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_5479_22 | ACLineSegment | Line | 12.3112 | 0.014907 | 0.014907 | 0.0082319 | 0.12108 | 0 | 0 | 0 | 2024-01-20 08:00 | FALSE | 1 | line_5479_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | line_5483_22 | ACLineSegment | Line | 12.3112 | 0.10319 | 0.10319 | 0.076185 | 0.83819 | 0 | 0 | 0 | 2024-01-20 21:25 | FALSE | 1 | line_5483_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | line_6051_22 | ACLineSegment | Line | 12.3112 | 0.041188 | 0.041188 | 0.027146 | 0.33456 | 0 | 0 | 0 | 2024-01-17 23:00 | FALSE | 1 | line_6051_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | tr_1312_22 | Transformer | Transformer | 0.285 | 0.0064058 | 0.0064058 | 0.0049432 | 2.2477 | 0 | 0 | 0 | 2024-01-20 22:00 | FALSE | 1 | tr_1312_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_121 | line_5524_22 | ACLineSegment | Line | 13.5424 | 0.024856 | 0.024856 | 0.018917 | 0.18354 | 0 | 0 | 0 | 2024-01-20 17:00 | FALSE | 1 | line_5524_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | line_6088_22 | ACLineSegment | Line | 13.5424 | 0.019359 | 0.019359 | 0.014806 | 0.14295 | 0 | 0 | 0 | 2024-01-20 17:00 | FALSE | 1 | line_6088_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | tr_1365_22 | Transformer | Transformer | 0.285 | 0.0072368 | 0.0072368 | 0.0048802 | 2.5392 | 0 | 0 | 0 | 2024-01-20 12:00 | FALSE | 1 | tr_1365_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_121 | line_5525_22 | ACLineSegment | Line | 13.5424 | 0.030923 | 0.030923 | 0.023643 | 0.22834 | 0 | 0 | 0 | 2024-07-15 15:00 | FALSE | 1 | line_5525_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | line_5826_22 | ACLineSegment | Line | 13.5424 | 0.034613 | 0.034613 | 0.026993 | 0.25559 | 0 | 0 | 0 | 2024-07-15 15:00 | FALSE | 1 | line_5826_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | tr_1413_22 | Transformer | Transformer | 0.475 | 0.0060159 | 0.0060159 | 0.0042914 | 1.2665 | 0 | 0 | 0 | 2024-01-20 16:55 | FALSE | 1 | tr_1413_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_121 | line_553_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_553_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_6266_22 | ACLineSegment | Line | 0.51338 | 0.0051936 | 0.0051936 | 0.0039878 | 1.0116 | 0 | 0 | 0 | 2024-01-20 09:05 | FALSE | 1 | line_6266_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | tr_1197_22 | Transformer | Transformer | 0.475 | 0.0051936 | 0.0051936 | 0.0039878 | 1.0934 | 0 | 0 | 0 | 2024-01-20 09:05 | FALSE | 1 | tr_1197_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_121 | line_5618_22 | ACLineSegment | Line | 13.5424 | 0.12537 | 0.12537 | 0.091848 | 0.92579 | 0 | 0 | 0 | 2024-01-20 22:00 | FALSE | 1 | line_5618_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | line_5800_22 | ACLineSegment | Line | 13.5424 | 0.14736 | 0.14736 | 0.11043 | 1.0882 | 0 | 0 | 0 | 2024-07-16 01:00 | FALSE | 1 | line_5800_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | line_5801_22 | ACLineSegment | Line | 13.5424 | 0.026 | 0.026 | 0.019389 | 0.19199 | 0 | 0 | 0 | 2024-08-02 23:00 | FALSE | 1 | line_5801_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | line_5634_22 | ACLineSegment | Line | 2.3694 | 0.080282 | 0.080282 | 0.056115 | 3.3882 | 0 | 0 | 0 | 2024-01-20 12:00 | FALSE | 1 | line_5634_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_5872_22 | ACLineSegment | Line | 13.5424 | 0.091472 | 0.091472 | 0.067402 | 0.67545 | 0 | 0 | 0 | 2024-01-20 22:00 | FALSE | 1 | line_5872_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | line_5635_22 | ACLineSegment | Line | 2.3694 | 0.073611 | 0.073611 | 0.052527 | 3.1067 | 0 | 0 | 0 | 2024-01-20 12:00 | FALSE | 1 | line_5635_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | tr_1401_22 | Transformer | Transformer | 0.02375 | 0.0081148 | 0.0081148 | 0.0059214 | 34.1677 | 0 | 0 | 0 | 2024-01-21 05:45 | FALSE | 1 | tr_1401_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_121 | line_6422_22 | ACLineSegment | Line | 13.5424 | 0.15605 | 0.15605 | 0.12311 | 1.1523 | 0 | 0 | 0 | 2024-01-20 21:25 | FALSE | 1 | line_6422_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | tr_1286_22 | Transformer | Transformer | 0.1425 | 0.030486 | 0.030486 | 0.021435 | 21.3936 | 0 | 0 | 0 | 2024-01-17 10:10 | FALSE | 1 | tr_1286_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_121 | line_5690_22 | ACLineSegment | Line | 2.3694 | 0.010205 | 0.010205 | 0.0051277 | 0.43067 | 0 | 0 | 0 | 2024-01-20 21:25 | FALSE | 1 | line_5690_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_6235_22 | ACLineSegment | Line | 13.5424 | 0.15492 | 0.15492 | 0.1163 | 1.144 | 0 | 0 | 0 | 2024-07-16 01:00 | FALSE | 1 | line_6235_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | tr_1458_22 | Transformer | Transformer | 0.02375 | 0.011668 | 0.011668 | 0.0066889 | 49.1277 | 0 | 0 | 0 | 2024-01-17 22:55 | FALSE | 1 | tr_1458_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_121 | line_5825_22 | ACLineSegment | Line | 13.5424 | 0.0389 | 0.0389 | 0.030129 | 0.28725 | 0 | 0 | 0 | 2024-07-15 15:00 | FALSE | 1 | line_5825_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | line_6144_22 | ACLineSegment | Line | 13.5424 | 0.042764 | 0.042764 | 0.033198 | 0.31578 | 0 | 0 | 0 | 2024-07-15 15:00 | FALSE | 1 | line_6144_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | line_5873_22 | ACLineSegment | Line | 12.3112 | 0.011832 | 0.011832 | 0.0085901 | 0.096107 | 0 | 0 | 0 | 2024-01-20 17:00 | FALSE | 1 | line_5873_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | line_6017_22 | ACLineSegment | Line | 12.3112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_6017_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | tr_1302_22 | Transformer | Transformer | 0.1425 | 0.0072849 | 0.0072849 | 0.0053675 | 5.1122 | 0 | 0 | 0 | 2024-07-15 21:30 | FALSE | 1 | tr_1302_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_121 | line_5900_22 | ACLineSegment | Line | 2.3694 | 0.0069211 | 0.0069211 | 0.0047361 | 0.2921 | 0 | 0 | 0 | 2024-01-20 06:50 | FALSE | 1 | line_5900_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_5901_22 | ACLineSegment | Line | 12.3112 | 0.1236 | 0.1236 | 0.096666 | 1.004 | 0 | 0 | 0 | 2024-07-15 23:00 | FALSE | 1 | line_5901_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | line_5912_22 | ACLineSegment | Line | 0.025406 | 0.0049867 | 0.0049867 | 0.0025629 | 19.6284 | 0 | 0 | 0 | 2024-07-15 21:30 | FALSE | 1 | line_5912_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_5913_22 | ACLineSegment | Line | 0.025406 | 0.0061824 | 0.0061824 | 0.0030357 | 24.3348 | 0 | 0 | 0 | 2024-01-20 21:25 | FALSE | 1 | line_5913_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_6016_22 | ACLineSegment | Line | 12.3112 | 0.0025108 | 0.0025108 | 0.0015069 | 0.020395 | 0 | 0 | 0 | 2024-01-20 22:00 | FALSE | 1 | line_6016_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | tr_1447_22 | Transformer | Transformer | 0.02375 | 0.013407 | 0.013407 | 0.0075641 | 56.4505 | 0 | 0 | 0 | 2024-07-05 22:55 | FALSE | 1 | tr_1447_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_121 | line_6234_22 | ACLineSegment | Line | 13.5424 | 0.19861 | 0.19861 | 0.15134 | 1.4666 | 0 | 0 | 0 | 2024-01-20 22:00 | FALSE | 1 | line_6234_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | line_6249_22 | ACLineSegment | Line | 13.5424 | 0.13891 | 0.13891 | 0.10862 | 1.0258 | 0 | 0 | 0 | 2024-01-20 21:25 | FALSE | 1 | line_6249_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | line_6474_22 | ACLineSegment | Line | 13.5424 | 0.1447 | 0.1447 | 0.11372 | 1.0685 | 0 | 0 | 0 | 2024-01-20 21:25 | FALSE | 1 | line_6474_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | tr_1317_22 | Transformer | Transformer | 0.285 | 0.0086104 | 0.0086104 | 0.0062797 | 3.0212 | 0 | 0 | 0 | 2024-07-16 03:00 | FALSE | 1 | tr_1317_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_121 | line_6250_22 | ACLineSegment | Line | 12.3112 | 0.12825 | 0.12825 | 0.1012 | 1.0418 | 0 | 0 | 0 | 2024-01-20 21:25 | FALSE | 1 | line_6250_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | tr_1384_22 | Transformer | Transformer | 0.02375 | 0.0072874 | 0.0072874 | 0.0057495 | 30.6836 | 0 | 0 | 0 | 2024-06-24 12:00 | FALSE | 1 | tr_1384_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_121 | line_6423_22 | ACLineSegment | Line | 0.51338 | 0.030486 | 0.030486 | 0.021435 | 5.9383 | 0 | 0 | 0 | 2024-01-17 10:10 | FALSE | 1 | line_6423_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | line_671_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_671_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_6448_22 | ACLineSegment | Line | 0.51338 | 0.0072849 | 0.0072849 | 0.0053675 | 1.419 | 0 | 0 | 0 | 2024-07-15 21:30 | FALSE | 1 | line_6448_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | line_664_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_664_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_6460_22 | ACLineSegment | Line | 0.51338 | 0.0064058 | 0.0064058 | 0.0049432 | 1.2478 | 0 | 0 | 0 | 2024-01-20 22:00 | FALSE | 1 | line_6460_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | line_724_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_724_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_6475_22 | ACLineSegment | Line | 0.51338 | 0.0086104 | 0.0086104 | 0.0062797 | 1.6772 | 0 | 0 | 0 | 2024-07-16 03:00 | FALSE | 1 | line_6475_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | line_715_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_715_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_6536_22 | ACLineSegment | Line | 0.51338 | 0.0072368 | 0.0072368 | 0.0048802 | 1.4096 | 0 | 0 | 0 | 2024-01-20 12:00 | FALSE | 1 | line_6536_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | line_759_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_759_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_6558_22 | ACLineSegment | Line | 0.025406 | 0.0072874 | 0.0072874 | 0.0057495 | 28.6839 | 0 | 0 | 0 | 2024-06-24 12:00 | FALSE | 1 | line_6558_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_799_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_799_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_6583_22 | ACLineSegment | Line | 0.025406 | 0.0081148 | 0.0081148 | 0.0059214 | 31.9409 | 0 | 0 | 0 | 2024-01-21 05:45 | FALSE | 1 | line_6583_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_792_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_792_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_6587_22 | ACLineSegment | Line | 0.51338 | 0.0069882 | 0.0069882 | 0.0053039 | 1.3612 | 0 | 0 | 0 | 2024-01-20 12:00 | FALSE | 1 | line_6587_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | line_821_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_821_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | tr_1403_22 | Transformer | Transformer | 0.07125 | 0.0069882 | 0.0069882 | 0.0053039 | 9.8079 | 0 | 0 | 0 | 2024-01-20 12:00 | FALSE | 1 | tr_1403_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_121 | line_6599_22 | ACLineSegment | Line | 0.51338 | 0.0060159 | 0.0060159 | 0.0042914 | 1.1718 | 0 | 0 | 0 | 2024-01-20 16:55 | FALSE | 1 | line_6599_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | line_796_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_796_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_6655_22 | ACLineSegment | Line | 0.51338 | 0.0061985 | 0.0061985 | 0.0043875 | 1.2074 | 0 | 0 | 0 | 2024-01-20 15:00 | FALSE | 1 | line_6655_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_121 | line_911_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_911_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_870_22 | ACLineSegment | Line | 0.034884 | 0.0082129 | 0.0082129 | 0.0040148 | 23.5437 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_870_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_871_22 | ACLineSegment | Line | 0.034884 | 0.0082129 | 0.0082129 | 0.0040148 | 23.5437 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_871_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_872_22 | ACLineSegment | Line | 0.034884 | 0.0067902 | 0.0067902 | 0.0050297 | 19.4654 | 0 | 0 | 0 | 2024-01-17 16:00 | FALSE | 1 | line_872_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_873_22 | ACLineSegment | Line | 0.034884 | 0.0067902 | 0.0067902 | 0.0050297 | 19.4654 | 0 | 0 | 0 | 2024-01-17 16:00 | FALSE | 1 | line_873_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_898_22 | ACLineSegment | Line | 0.034884 | 0.0054116 | 0.0054116 | 0.0029957 | 15.5134 | 0 | 0 | 0 | 2024-05-20 17:55 | FALSE | 1 | line_898_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_899_22 | ACLineSegment | Line | 0.034884 | 0.0054116 | 0.0054116 | 0.0029957 | 15.5134 | 0 | 0 | 0 | 2024-05-20 17:55 | FALSE | 1 | line_899_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_901_22 | ACLineSegment | Line | 0.034884 | 0.0090016 | 0.0090016 | 0.0048712 | 25.8048 | 0 | 0 | 0 | 2024-01-20 19:55 | FALSE | 1 | line_901_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_121 | line_902_22 | ACLineSegment | Line | 0.034884 | 0.0090016 | 0.0090016 | 0.0048712 | 25.8048 | 0 | 0 | 0 | 2024-01-20 19:55 | FALSE | 1 | line_902_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_144 | line_5978_22 | ACLineSegment | Line | 12.3112 | 0.13286 | 0.13286 | 0.090084 | 1.0792 | 0 | 0 | 0 | 2024-01-20 21:00 | TRUE | 1 | line_5978_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_144 | tr_1054_22 | Transformer | Transformer | 0.02375 | 0.019434 | 0.019434 | 0.011932 | 81.8263 | 0 | 0 | 0 | 2024-01-20 21:00 | FALSE | 1 | tr_1054_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_144 | line_5977_22 | ACLineSegment | Line | 2.3694 | 0.11487 | 0.11487 | 0.078413 | 4.8479 | 0 | 0 | 0 | 2024-01-20 06:05 | FALSE | 1 | line_5977_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_144 | line_270_22 | ACLineSegment | Line | 0.025406 | 0.0072657 | 0.0072657 | 0.0041526 | 28.5987 | 0 | 0 | 0 | 2024-01-20 06:05 | FALSE | 1 | line_270_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_144 | line_271_22 | ACLineSegment | Line | 0.025406 | 0.014098 | 0.014098 | 0.0079545 | 55.4906 | 0 | 0 | 0 | 2024-07-15 12:55 | FALSE | 1 | line_271_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_144 | line_272_22 | ACLineSegment | Line | 0.025406 | 0.0072505 | 0.0072505 | 0.0040667 | 28.5389 | 0 | 0 | 0 | 2024-01-17 12:55 | FALSE | 1 | line_272_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_144 | line_276_22 | ACLineSegment | Line | 0.025406 | 0.0072657 | 0.0072657 | 0.0041526 | 28.5987 | 0 | 0 | 0 | 2024-01-20 06:05 | FALSE | 1 | line_276_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_144 | line_280_22 | ACLineSegment | Line | 0.025406 | 0.017008 | 0.017008 | 0.010238 | 66.9442 | 0 | 0 | 0 | 2024-07-15 12:55 | FALSE | 1 | line_280_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_144 | line_287_22 | ACLineSegment | Line | 0.025406 | 0.0042388 | 0.0042388 | 0.0024335 | 16.6846 | 0 | 0 | 0 | 2024-01-20 05:55 | FALSE | 1 | line_287_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_144 | line_273_22 | ACLineSegment | Line | 0.025406 | 0.004574 | 0.004574 | 0.0026355 | 18.004 | 0 | 0 | 0 | 2024-07-15 16:55 | FALSE | 1 | line_273_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_144 | line_274_22 | ACLineSegment | Line | 0.025406 | 0.004574 | 0.004574 | 0.0026355 | 18.004 | 0 | 0 | 0 | 2024-07-15 16:55 | FALSE | 1 | line_274_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_144 | line_277_22 | ACLineSegment | Line | 0.025406 | 0.0094777 | 0.0094777 | 0.0058324 | 37.3054 | 0 | 0 | 0 | 2024-01-20 07:00 | FALSE | 1 | line_277_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_144 | line_286_22 | ACLineSegment | Line | 0.025406 | 0.0062262 | 0.0062262 | 0.0034674 | 24.5069 | 0 | 0 | 0 | 2024-01-21 01:05 | FALSE | 1 | line_286_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_144 | line_278_22 | ACLineSegment | Line | 0.025406 | 0.012413 | 0.012413 | 0.0079309 | 48.8589 | 0 | 0 | 0 | 2024-07-16 01:55 | FALSE | 1 | line_278_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_144 | line_279_22 | ACLineSegment | Line | 0.025406 | 0.0046854 | 0.0046854 | 0.0022771 | 18.4425 | 0 | 0 | 0 | 2024-07-15 04:55 | FALSE | 1 | line_279_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_144 | line_283_22 | ACLineSegment | Line | 0.025406 | 0.031335 | 0.031335 | 0.019196 | 123.3377 | 184 | 15.3333 | 0.17466 | 2024-01-20 06:05 | FALSE | 1 | line_283_22 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_144 | line_289_22 | ACLineSegment | Line | 0.038174 | 0.041391 | 0.041391 | 0.02691 | 108.4263 | 11 | 0.91667 | 0.010442 | 2024-01-20 06:05 | FALSE | 1 | line_289_22 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_144 | line_281_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_281_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_144 | line_282_22 | ACLineSegment | Line | 0.025406 | 0.0054189 | 0.0054189 | 0.0028296 | 21.3293 | 0 | 0 | 0 | 2024-01-17 10:00 | FALSE | 1 | line_282_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_144 | line_284_22 | ACLineSegment | Line | 0.025406 | 0.004883 | 0.004883 | 0.0028261 | 19.2201 | 0 | 0 | 0 | 2024-01-20 05:55 | FALSE | 1 | line_284_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_144 | line_285_22 | ACLineSegment | Line | 0.025406 | 0.0074275 | 0.0074275 | 0.0040965 | 29.2357 | 0 | 0 | 0 | 2024-01-20 17:05 | FALSE | 1 | line_285_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_144 | line_288_22 | ACLineSegment | Line | 0.025406 | 0.0054189 | 0.0054189 | 0.0028296 | 21.3293 | 0 | 0 | 0 | 2024-01-17 10:00 | FALSE | 1 | line_288_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_144 | line_5983_22 | ACLineSegment | Line | 0.025406 | 0.0058735 | 0.0058735 | 0.003321 | 23.1188 | 0 | 0 | 0 | 2024-07-16 02:45 | FALSE | 1 | line_5983_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_144 | tr_1055_22 | Transformer | Transformer | 0.0475 | 0.04474 | 0.04474 | 0.030063 | 94.1893 | 0 | 0 | 0 | 2024-01-20 06:05 | FALSE | 1 | tr_1055_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_144 | line_297_22 | ACLineSegment | Line | 0.025406 | 0.0081668 | 0.0081668 | 0.0043024 | 32.1455 | 0 | 0 | 0 | 2024-01-21 00:55 | FALSE | 1 | line_297_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_144 | line_298_22 | ACLineSegment | Line | 0.025406 | 0.0081668 | 0.0081668 | 0.0043024 | 32.1455 | 0 | 0 | 0 | 2024-01-21 00:55 | FALSE | 1 | line_298_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_144 | line_300_22 | ACLineSegment | Line | 0.025406 | 0.0081668 | 0.0081668 | 0.0043024 | 32.1455 | 0 | 0 | 0 | 2024-01-21 00:55 | FALSE | 1 | line_300_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_144 | line_299_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_299_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_144 | line_301_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_301_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_144 | line_5979_22 | ACLineSegment | Line | 0.025406 | 0.0042527 | 0.0042527 | 0.0025161 | 16.7393 | 0 | 0 | 0 | 2024-07-15 17:00 | FALSE | 1 | line_5979_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_144 | line_5980_22 | ACLineSegment | Line | 0.025406 | 0.0048239 | 0.0048239 | 0.002389 | 18.9875 | 0 | 0 | 0 | 2024-01-21 00:55 | FALSE | 1 | line_5980_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_144 | line_5981_22 | ACLineSegment | Line | 0.025406 | 0.0062296 | 0.0062296 | 0.0033576 | 24.5206 | 0 | 0 | 0 | 2024-07-15 13:00 | FALSE | 1 | line_5981_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_144 | line_304_22 | ACLineSegment | Line | 0.025406 | 0.01782 | 0.01782 | 0.010846 | 70.1412 | 0 | 0 | 0 | 2024-07-16 03:00 | FALSE | 1 | line_304_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_144 | line_305_22 | ACLineSegment | Line | 0.025406 | 0.01782 | 0.01782 | 0.010846 | 70.1412 | 0 | 0 | 0 | 2024-07-16 03:00 | FALSE | 1 | line_305_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_144 | line_307_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_307_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_144 | line_315_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_315_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_144 | line_316_22 | ACLineSegment | Line | 0.025406 | 0.0065291 | 0.0065291 | 0.0031648 | 25.6993 | 0 | 0 | 0 | 2024-01-21 02:00 | FALSE | 1 | line_316_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_144 | line_317_22 | ACLineSegment | Line | 0.025406 | 0.0046215 | 0.0046215 | 0.0025291 | 18.1908 | 0 | 0 | 0 | 2024-01-21 03:55 | FALSE | 1 | line_317_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_144 | line_318_22 | ACLineSegment | Line | 0.025406 | 0.005307 | 0.005307 | 0.002792 | 20.889 | 0 | 0 | 0 | 2024-07-16 03:00 | FALSE | 1 | line_318_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_144 | line_319_22 | ACLineSegment | Line | 0.025406 | 0.0064546 | 0.0064546 | 0.003006 | 25.406 | 0 | 0 | 0 | 2024-01-20 06:05 | FALSE | 1 | line_319_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_144 | line_306_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_306_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_144 | line_309_22 | ACLineSegment | Line | 0.025406 | 0.013588 | 0.013588 | 0.0081035 | 53.4843 | 0 | 0 | 0 | 2024-01-20 17:05 | FALSE | 1 | line_309_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_144 | line_320_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_320_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_144 | line_321_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_321_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_144 | line_5987_22 | ACLineSegment | Line | 0.025406 | 0.0022403 | 0.0022403 | 0.0011597 | 8.818 | 0 | 0 | 0 | 2024-01-20 11:50 | FALSE | 1 | line_5987_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_144 | line_5988_22 | ACLineSegment | Line | 0.025406 | 0.0061245 | 0.0061245 | 0.0034277 | 24.1066 | 0 | 0 | 0 | 2024-07-15 20:00 | FALSE | 1 | line_5988_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_144 | line_5989_22 | ACLineSegment | Line | 0.025406 | 0.0066313 | 0.0066313 | 0.0035876 | 26.1016 | 0 | 0 | 0 | 2024-01-20 13:10 | FALSE | 1 | line_5989_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_144 | line_5990_22 | ACLineSegment | Line | 0.025406 | 0.0066001 | 0.0066001 | 0.0037803 | 25.9788 | 0 | 0 | 0 | 2024-01-20 17:05 | FALSE | 1 | line_5990_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_144 | tr_1057_22 | Transformer | Transformer | 0.0475 | 0.045992 | 0.045992 | 0.029987 | 96.8248 | 0 | 0 | 0 | 2024-01-20 21:00 | FALSE | 1 | tr_1057_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_144 | line_308_22 | ACLineSegment | Line | 0.025406 | 0.013588 | 0.013588 | 0.0081035 | 53.4843 | 0 | 0 | 0 | 2024-01-20 17:05 | FALSE | 1 | line_308_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_144 | line_310_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_310_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_144 | line_311_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_311_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_144 | line_312_22 | ACLineSegment | Line | 0.025406 | 0.0036128 | 0.0036128 | 0.0020196 | 14.2203 | 0 | 0 | 0 | 2024-01-20 12:25 | FALSE | 1 | line_312_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_144 | line_313_22 | ACLineSegment | Line | 0.025406 | 0.0079113 | 0.0079113 | 0.0039886 | 31.1398 | 0 | 0 | 0 | 2024-01-20 17:05 | FALSE | 1 | line_313_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_144 | line_314_22 | ACLineSegment | Line | 0.025406 | 0.0042005 | 0.0042005 | 0.0024955 | 16.5336 | 0 | 0 | 0 | 2024-07-15 07:55 | FALSE | 1 | line_314_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_144 | line_331_22 | ACLineSegment | Line | 0.025406 | 0.0071538 | 0.0071538 | 0.0040869 | 28.1581 | 0 | 0 | 0 | 2024-07-15 08:00 | FALSE | 1 | line_331_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_144 | line_332_22 | ACLineSegment | Line | 0.025406 | 0.0071538 | 0.0071538 | 0.0040869 | 28.1581 | 0 | 0 | 0 | 2024-07-15 08:00 | FALSE | 1 | line_332_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_144 | line_333_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_333_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_144 | line_334_22 | ACLineSegment | Line | 0.025406 | 0.0037608 | 0.0037608 | 0.0020324 | 14.8028 | 0 | 0 | 0 | 2024-01-17 08:00 | FALSE | 1 | line_334_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_144 | line_335_22 | ACLineSegment | Line | 0.025406 | 0.0041494 | 0.0041494 | 0.0022105 | 16.3324 | 0 | 0 | 0 | 2024-01-21 01:05 | FALSE | 1 | line_335_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_144 | line_336_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_336_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_144 | line_342_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_342_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_144 | line_5984_22 | ACLineSegment | Line | 0.025406 | 0.0069277 | 0.0069277 | 0.0037252 | 27.2681 | 0 | 0 | 0 | 2024-01-20 21:00 | FALSE | 1 | line_5984_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_144 | line_5985_22 | ACLineSegment | Line | 0.025406 | 0.0062336 | 0.0062336 | 0.0036339 | 24.5362 | 0 | 0 | 0 | 2024-01-21 02:00 | FALSE | 1 | line_5985_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_144 | line_5986_22 | ACLineSegment | Line | 0.025406 | 0.0041366 | 0.0041366 | 0.0022909 | 16.2821 | 0 | 0 | 0 | 2024-01-21 03:55 | FALSE | 1 | line_5986_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_144 | tr_1056_22 | Transformer | Transformer | 0.02375 | 0.022338 | 0.022338 | 0.013093 | 94.0528 | 0 | 0 | 0 | 2024-01-20 21:00 | FALSE | 1 | tr_1056_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_144 | line_3345_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_3345_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_144 | line_3347_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_3347_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_144 | line_5975_22 | ACLineSegment | Line | 0.025406 | 0.0061564 | 0.0061564 | 0.00315 | 24.2324 | 0 | 0 | 0 | 2024-01-20 07:00 | FALSE | 1 | line_5975_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_144 | line_5976_22 | ACLineSegment | Line | 0.025406 | 0.0058072 | 0.0058072 | 0.003055 | 22.8579 | 0 | 0 | 0 | 2024-01-20 12:25 | FALSE | 1 | line_5976_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_144 | tr_1053_22 | Transformer | Transformer | 0.02375 | 0.010353 | 0.010353 | 0.0059585 | 43.5907 | 0 | 0 | 0 | 2024-01-20 09:25 | FALSE | 1 | tr_1053_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_144 | line_5973_22 | ACLineSegment | Line | 2.3694 | 0.055889 | 0.055889 | 0.035648 | 2.3587 | 0 | 0 | 0 | 2024-01-20 17:05 | FALSE | 1 | line_5973_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_144 | line_5974_22 | ACLineSegment | Line | 2.3694 | 0.045992 | 0.045992 | 0.029987 | 1.941 | 0 | 0 | 0 | 2024-01-20 21:00 | FALSE | 1 | line_5974_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_144 | line_5982_22 | ACLineSegment | Line | 2.3694 | 0.075697 | 0.075697 | 0.048333 | 3.1947 | 0 | 0 | 0 | 2024-01-20 21:00 | FALSE | 1 | line_5982_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_4758_22 | ACLineSegment | Line | 12.3112 | 0.023552 | 0.023552 | 0.015139 | 0.19131 | 0 | 0 | 0 | 2024-01-21 01:00 | FALSE | 1 | line_4758_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | tr_464_22 | Transformer | Transformer | 0.285 | 0.0053636 | 0.0053636 | 0.0038106 | 1.882 | 0 | 0 | 0 | 2024-01-22 04:00 | FALSE | 1 | tr_464_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_141 | line_4258_22 | ACLineSegment | Line | 0.94778 | 0.019182 | 0.019182 | 0.0119 | 2.0239 | 0 | 0 | 0 | 2024-01-21 01:00 | FALSE | 1 | line_4258_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_1653_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1653_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_4269_22 | ACLineSegment | Line | 0.034884 | 0.0037074 | 0.0037074 | 0.0020932 | 10.628 | 0 | 0 | 0 | 2024-01-21 02:15 | FALSE | 1 | line_4269_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | tr_275_22 | Transformer | Transformer | 0.02375 | 0.0037074 | 0.0037074 | 0.0020932 | 15.6102 | 0 | 0 | 0 | 2024-01-21 02:15 | FALSE | 1 | tr_275_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_141 | line_1662_22 | ACLineSegment | Line | 0.034884 | 0.0030658 | 0.0030658 | 0.0018386 | 8.7887 | 0 | 0 | 0 | 2024-07-15 14:00 | FALSE | 1 | line_1662_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_1663_22 | ACLineSegment | Line | 0.034884 | 0.0030658 | 0.0030658 | 0.0018386 | 8.7887 | 0 | 0 | 0 | 2024-07-15 14:00 | FALSE | 1 | line_1663_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_1664_22 | ACLineSegment | Line | 0.034884 | 0.0030658 | 0.0030658 | 0.0018386 | 8.7887 | 0 | 0 | 0 | 2024-07-15 14:00 | FALSE | 1 | line_1664_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_4252_22 | ACLineSegment | Line | 0.034884 | 0.0042436 | 0.0042436 | 0.002585 | 12.165 | 0 | 0 | 0 | 2024-07-15 16:05 | FALSE | 1 | line_4252_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | tr_269_22 | Transformer | Transformer | 0.02375 | 0.0068455 | 0.0068455 | 0.0042376 | 28.8231 | 0 | 0 | 0 | 2024-01-20 23:55 | FALSE | 1 | tr_269_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_141 | line_1731_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1731_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_4301_22 | ACLineSegment | Line | 0.51338 | 0.0051448 | 0.0051448 | 0.0036271 | 1.0021 | 0 | 0 | 0 | 2024-07-15 20:55 | FALSE | 1 | line_4301_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | tr_287_22 | Transformer | Transformer | 0.1425 | 0.0051448 | 0.0051448 | 0.0036271 | 3.6104 | 0 | 0 | 0 | 2024-07-15 20:55 | FALSE | 1 | tr_287_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_141 | line_1732_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1732_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_4371_22 | ACLineSegment | Line | 0.51338 | 0.01003 | 0.01003 | 0.0053962 | 1.9536 | 0 | 0 | 0 | 2024-01-20 14:00 | FALSE | 1 | line_4371_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | tr_312_22 | Transformer | Transformer | 0.285 | 0.01003 | 0.01003 | 0.0053962 | 3.5191 | 0 | 0 | 0 | 2024-01-20 14:00 | FALSE | 1 | tr_312_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_141 | line_1844_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1844_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_4362_22 | ACLineSegment | Line | 0.51338 | 0.0071607 | 0.0071607 | 0.0051278 | 1.3948 | 0 | 0 | 0 | 2024-01-21 16:00 | FALSE | 1 | line_4362_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | tr_309_22 | Transformer | Transformer | 0.095 | 0.0071607 | 0.0071607 | 0.0051278 | 7.5376 | 0 | 0 | 0 | 2024-01-21 16:00 | FALSE | 1 | tr_309_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_141 | line_1881_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1881_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_4915_22 | ACLineSegment | Line | 0.51338 | 0.0082446 | 0.0082446 | 0.0056223 | 1.606 | 0 | 0 | 0 | 2024-01-20 18:55 | FALSE | 1 | line_4915_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | tr_534_22 | Transformer | Transformer | 0.07125 | 0.0082446 | 0.0082446 | 0.0056223 | 11.5714 | 0 | 0 | 0 | 2024-01-20 18:55 | FALSE | 1 | tr_534_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_141 | line_1888_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1888_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_4888_22 | ACLineSegment | Line | 0.51338 | 0.0061623 | 0.0061623 | 0.004174 | 1.2003 | 0 | 0 | 0 | 2024-07-15 17:00 | FALSE | 1 | line_4888_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | tr_521_22 | Transformer | Transformer | 0.07125 | 0.0061623 | 0.0061623 | 0.004174 | 8.6488 | 0 | 0 | 0 | 2024-07-15 17:00 | FALSE | 1 | tr_521_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_141 | line_1906_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1906_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_4503_22 | ACLineSegment | Line | 0.51338 | 0.0062041 | 0.0062041 | 0.0042226 | 1.2085 | 0 | 0 | 0 | 2024-01-20 05:00 | FALSE | 1 | line_4503_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | tr_363_22 | Transformer | Transformer | 0.1425 | 0.0062041 | 0.0062041 | 0.0042226 | 4.3537 | 0 | 0 | 0 | 2024-01-20 05:00 | FALSE | 1 | tr_363_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_141 | line_19_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_19_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_4552_22 | ACLineSegment | Line | 0.51338 | 0.0055053 | 0.0055053 | 0.004177 | 1.0724 | 0 | 0 | 0 | 2024-01-20 11:40 | FALSE | 1 | line_4552_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | tr_370_22 | Transformer | Transformer | 0.07125 | 0.0055053 | 0.0055053 | 0.004177 | 7.7267 | 0 | 0 | 0 | 2024-01-20 11:40 | FALSE | 1 | tr_370_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_141 | line_1991_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1991_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_4603_22 | ACLineSegment | Line | 0.034884 | 0.0091993 | 0.0091993 | 0.0067561 | 26.3715 | 0 | 0 | 0 | 2024-01-20 10:50 | FALSE | 1 | line_4603_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | tr_401_22 | Transformer | Transformer | 0.0475 | 0.0091993 | 0.0091993 | 0.0067561 | 19.367 | 0 | 0 | 0 | 2024-01-20 10:50 | FALSE | 1 | tr_401_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_141 | line_2040_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2040_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_4759_22 | ACLineSegment | Line | 0.51338 | 0.0053636 | 0.0053636 | 0.0038106 | 1.0448 | 0 | 0 | 0 | 2024-01-22 04:00 | FALSE | 1 | line_4759_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | line_2063_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2063_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_4711_22 | ACLineSegment | Line | 0.51338 | 0.0071631 | 0.0071631 | 0.0053864 | 1.3953 | 0 | 0 | 0 | 2024-06-26 10:10 | FALSE | 1 | line_4711_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | tr_445_22 | Transformer | Transformer | 0.07125 | 0.0071631 | 0.0071631 | 0.0053864 | 10.0535 | 0 | 0 | 0 | 2024-06-26 10:10 | FALSE | 1 | tr_445_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_141 | line_2074_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2074_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_4816_22 | ACLineSegment | Line | 0.51338 | 0.0084379 | 0.0084379 | 0.0062062 | 1.6436 | 0 | 0 | 0 | 2024-01-21 19:05 | FALSE | 1 | line_4816_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | tr_489_22 | Transformer | Transformer | 0.07125 | 0.0084379 | 0.0084379 | 0.0062062 | 11.8426 | 0 | 0 | 0 | 2024-01-21 19:05 | FALSE | 1 | tr_489_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_141 | line_2077_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2077_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_4850_22 | ACLineSegment | Line | 0.51338 | 0.0051229 | 0.0051229 | 0.0036267 | 0.99787 | 0 | 0 | 0 | 2024-01-17 21:00 | FALSE | 1 | line_4850_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | tr_504_22 | Transformer | Transformer | 0.285 | 0.0051229 | 0.0051229 | 0.0036267 | 1.7975 | 0 | 0 | 0 | 2024-01-17 21:00 | FALSE | 1 | tr_504_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_141 | line_2082_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2082_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_4804_22 | ACLineSegment | Line | 0.51338 | 0.0074419 | 0.0074419 | 0.0054359 | 1.4496 | 0 | 0 | 0 | 2024-07-15 08:45 | FALSE | 1 | line_4804_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | tr_484_22 | Transformer | Transformer | 0.285 | 0.0074419 | 0.0074419 | 0.0054359 | 2.6112 | 0 | 0 | 0 | 2024-07-15 08:45 | FALSE | 1 | tr_484_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_141 | line_232_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_232_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_4897_22 | ACLineSegment | Line | 0.51338 | 0.0029982 | 0.0029982 | 0.0021964 | 0.584 | 0 | 0 | 0 | 2024-07-15 09:30 | FALSE | 1 | line_4897_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | tr_514_22 | Transformer | Transformer | 0.285 | 0.0029982 | 0.0029982 | 0.0021964 | 1.052 | 0 | 0 | 0 | 2024-07-15 09:30 | FALSE | 1 | tr_514_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_141 | line_2339_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2339_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_6650_22 | ACLineSegment | Line | 0.034884 | 0.0068664 | 0.0068664 | 0.0051092 | 19.6837 | 0 | 0 | 0 | 2024-07-15 23:00 | FALSE | 1 | line_6650_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | tr_1448_22 | Transformer | Transformer | 0.02375 | 0.0068664 | 0.0068664 | 0.0051092 | 28.911 | 0 | 0 | 0 | 2024-07-15 23:00 | FALSE | 1 | tr_1448_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_141 | line_2428_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2428_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_6782_22 | ACLineSegment | Line | 0.51338 | 0.0066116 | 0.0066116 | 0.0046474 | 1.2879 | 0 | 0 | 0 | 2024-01-20 09:00 | FALSE | 1 | line_6782_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | tr_1537_22 | Transformer | Transformer | 0.1425 | 0.0066116 | 0.0066116 | 0.0046474 | 4.6397 | 0 | 0 | 0 | 2024-01-20 09:00 | FALSE | 1 | tr_1537_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_141 | line_2495_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2495_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_4118_22 | ACLineSegment | Line | 0.025406 | 0.0091824 | 0.0091824 | 0.0066427 | 36.1431 | 0 | 0 | 0 | 2024-01-17 07:00 | FALSE | 1 | line_4118_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | tr_214_22 | Transformer | Transformer | 0.02375 | 0.0091824 | 0.0091824 | 0.0066427 | 38.6628 | 0 | 0 | 0 | 2024-01-17 07:00 | FALSE | 1 | tr_214_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_141 | line_2546_22 | ACLineSegment | Line | 0.034884 | 0.007615 | 0.007615 | 0.0043268 | 21.8297 | 0 | 0 | 0 | 2024-07-15 14:00 | FALSE | 1 | line_2546_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_2547_22 | ACLineSegment | Line | 0.034884 | 0.021437 | 0.021437 | 0.012838 | 61.4531 | 0 | 0 | 0 | 2024-01-20 06:10 | FALSE | 1 | line_2547_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_2548_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2548_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_2549_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2549_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_2550_22 | ACLineSegment | Line | 0.034884 | 0.0057273 | 0.0057273 | 0.0028082 | 16.4183 | 0 | 0 | 0 | 2024-01-20 22:05 | FALSE | 1 | line_2550_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_2551_22 | ACLineSegment | Line | 0.034884 | 0.0042001 | 0.0042001 | 0.0020587 | 12.0402 | 0 | 0 | 0 | 2024-01-20 14:00 | FALSE | 1 | line_2551_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_2552_22 | ACLineSegment | Line | 0.034884 | 0.0040318 | 0.0040318 | 0.0020326 | 11.5579 | 0 | 0 | 0 | 2024-01-21 04:05 | FALSE | 1 | line_2552_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_2553_22 | ACLineSegment | Line | 0.034884 | 0.0049782 | 0.0049782 | 0.0025284 | 14.2709 | 0 | 0 | 0 | 2024-01-20 06:10 | FALSE | 1 | line_2553_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_2583_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2583_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_2584_22 | ACLineSegment | Line | 0.034884 | 0.004603 | 0.004603 | 0.0025754 | 13.1953 | 0 | 0 | 0 | 2024-01-20 09:00 | FALSE | 1 | line_2584_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_2585_22 | ACLineSegment | Line | 0.034884 | 0.0033619 | 0.0033619 | 0.0019263 | 9.6376 | 0 | 0 | 0 | 2024-01-20 05:00 | FALSE | 1 | line_2585_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_2561_22 | ACLineSegment | Line | 0.034884 | 0.021437 | 0.021437 | 0.012838 | 61.4531 | 0 | 0 | 0 | 2024-01-20 06:10 | FALSE | 1 | line_2561_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_2560_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2560_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_2562_22 | ACLineSegment | Line | 0.034884 | 0.029892 | 0.029892 | 0.019289 | 85.6911 | 0 | 0 | 0 | 2024-01-20 06:10 | FALSE | 1 | line_2562_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_2563_22 | ACLineSegment | Line | 0.034884 | 0.0097932 | 0.0097932 | 0.0053921 | 28.074 | 0 | 0 | 0 | 2024-01-21 01:00 | FALSE | 1 | line_2563_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_2564_22 | ACLineSegment | Line | 0.034884 | 0.0024248 | 0.0024248 | 0.0014311 | 6.9512 | 0 | 0 | 0 | 2024-01-20 06:10 | FALSE | 1 | line_2564_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_2643_22 | ACLineSegment | Line | 0.034884 | 0.029892 | 0.029892 | 0.019289 | 85.6911 | 0 | 0 | 0 | 2024-01-20 06:10 | FALSE | 1 | line_2643_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_2598_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2598_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_2599_22 | ACLineSegment | Line | 0.034884 | 0.032455 | 0.032455 | 0.021036 | 93.0394 | 0 | 0 | 0 | 2024-01-21 01:00 | FALSE | 1 | line_2599_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_2600_22 | ACLineSegment | Line | 0.034884 | 0.024069 | 0.024069 | 0.015203 | 68.9982 | 0 | 0 | 0 | 2024-01-20 17:50 | FALSE | 1 | line_2600_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_2601_22 | ACLineSegment | Line | 0.034884 | 0.0054455 | 0.0054455 | 0.0030605 | 15.6104 | 0 | 0 | 0 | 2024-01-20 16:00 | FALSE | 1 | line_2601_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_2602_22 | ACLineSegment | Line | 0.034884 | 0.0065448 | 0.0065448 | 0.0034409 | 18.7619 | 0 | 0 | 0 | 2024-01-18 02:55 | FALSE | 1 | line_2602_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_2644_22 | ACLineSegment | Line | 0.034884 | 0.039198 | 0.039198 | 0.025568 | 112.3694 | 106 | 8.8333 | 0.10062 | 2024-01-20 14:00 | FALSE | 1 | line_2644_22 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_141 | line_2822_22 | ACLineSegment | Line | 0.034884 | 0.069344 | 0.069344 | 0.046454 | 198.7868 | 24088 | 2007.3333 | 22.8652 | 2024-01-20 14:00 | FALSE | 1 | line_2822_22 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_141 | line_2727_22 | ACLineSegment | Line | 0.034884 | 0.020019 | 0.020019 | 0.012092 | 57.3887 | 0 | 0 | 0 | 2024-07-15 08:45 | FALSE | 1 | line_2727_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_2904_22 | ACLineSegment | Line | 0.034884 | 0.0057087 | 0.0057087 | 0.0032792 | 16.3651 | 0 | 0 | 0 | 2024-01-20 13:55 | FALSE | 1 | line_2904_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_2621_22 | ACLineSegment | Line | 0.034884 | 0.0056672 | 0.0056672 | 0.0033853 | 16.2461 | 0 | 0 | 0 | 2024-01-21 04:05 | FALSE | 1 | line_2621_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_2622_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2622_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_2623_22 | ACLineSegment | Line | 0.034884 | 0.020019 | 0.020019 | 0.012092 | 57.3887 | 0 | 0 | 0 | 2024-07-15 08:45 | FALSE | 1 | line_2623_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_2624_22 | ACLineSegment | Line | 0.034884 | 0.0048873 | 0.0048873 | 0.0029517 | 14.0103 | 0 | 0 | 0 | 2024-07-15 07:00 | FALSE | 1 | line_2624_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_2625_22 | ACLineSegment | Line | 0.034884 | 0.0072932 | 0.0072932 | 0.003827 | 20.9074 | 0 | 0 | 0 | 2024-07-15 08:45 | FALSE | 1 | line_2625_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_2626_22 | ACLineSegment | Line | 0.034884 | 0.0049228 | 0.0049228 | 0.0026563 | 14.1121 | 0 | 0 | 0 | 2024-01-20 06:10 | FALSE | 1 | line_2626_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_2686_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2686_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_2687_22 | ACLineSegment | Line | 0.034884 | 0.0038966 | 0.0038966 | 0.0020928 | 11.1703 | 0 | 0 | 0 | 2024-01-21 00:55 | FALSE | 1 | line_2687_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_2688_22 | ACLineSegment | Line | 0.034884 | 0.0025192 | 0.0025192 | 0.0014056 | 7.2218 | 0 | 0 | 0 | 2024-01-21 04:05 | FALSE | 1 | line_2688_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_2645_22 | ACLineSegment | Line | 0.034884 | 0.0051299 | 0.0051299 | 0.0029505 | 14.7058 | 0 | 0 | 0 | 2024-01-20 08:55 | FALSE | 1 | line_2645_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_2646_22 | ACLineSegment | Line | 0.034884 | 0.0070464 | 0.0070464 | 0.0039143 | 20.1998 | 0 | 0 | 0 | 2024-01-20 19:05 | FALSE | 1 | line_2646_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_2663_22 | ACLineSegment | Line | 0.51338 | 0.0048252 | 0.0048252 | 0.0035415 | 0.93988 | 0 | 0 | 0 | 2024-01-21 17:50 | FALSE | 1 | line_2663_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | line_2664_22 | ACLineSegment | Line | 0.51338 | 0.0048252 | 0.0048252 | 0.0035415 | 0.93988 | 0 | 0 | 0 | 2024-01-21 17:50 | FALSE | 1 | line_2664_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | tr_763_22 | Transformer | Transformer | 0.1425 | 0.0048252 | 0.0048252 | 0.0035415 | 3.3861 | 0 | 0 | 0 | 2024-01-21 17:50 | FALSE | 1 | tr_763_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_141 | line_2696_22 | ACLineSegment | Line | 0.51338 | 0.0045842 | 0.0045842 | 0.003218 | 0.89295 | 0 | 0 | 0 | 2024-06-26 04:55 | FALSE | 1 | line_2696_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | line_2697_22 | ACLineSegment | Line | 0.51338 | 0.0045842 | 0.0045842 | 0.003218 | 0.89295 | 0 | 0 | 0 | 2024-06-26 04:55 | FALSE | 1 | line_2697_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | tr_781_22 | Transformer | Transformer | 0.95 | 0.0045842 | 0.0045842 | 0.003218 | 0.48255 | 0 | 0 | 0 | 2024-06-26 04:55 | FALSE | 1 | tr_781_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_141 | line_5505_22 | ACLineSegment | Line | 0.034884 | 0.0045498 | 0.0045498 | 0.0027201 | 13.0429 | 0 | 0 | 0 | 2024-01-20 23:55 | FALSE | 1 | line_5505_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | tr_815_22 | Transformer | Transformer | 0.0475 | 0.072525 | 0.072525 | 0.049025 | 152.6847 | 6385 | 532.0833 | 6.0609 | 2024-01-20 19:05 | FALSE | 1 | tr_815_22 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_141 | line_3111_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_3111_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_5678_22 | ACLineSegment | Line | 0.51338 | 0.020444 | 0.020444 | 0.015067 | 3.9823 | 0 | 0 | 0 | 2024-01-17 21:00 | FALSE | 1 | line_5678_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | tr_910_22 | Transformer | Transformer | 0.1425 | 0.020444 | 0.020444 | 0.015067 | 14.3468 | 0 | 0 | 0 | 2024-01-17 21:00 | FALSE | 1 | tr_910_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_141 | line_3151_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_3151_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_5744_22 | ACLineSegment | Line | 0.51338 | 0.0049972 | 0.0049972 | 0.0038592 | 0.9734 | 0 | 0 | 0 | 2024-01-20 22:05 | FALSE | 1 | line_5744_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | tr_942_22 | Transformer | Transformer | 0.285 | 0.0049972 | 0.0049972 | 0.0038592 | 1.7534 | 0 | 0 | 0 | 2024-01-20 22:05 | FALSE | 1 | tr_942_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_141 | line_3360_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_3360_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_5933_22 | ACLineSegment | Line | 0.51338 | 0.0061867 | 0.0061867 | 0.0045559 | 1.2051 | 0 | 0 | 0 | 2024-01-21 00:55 | FALSE | 1 | line_5933_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | tr_1033_22 | Transformer | Transformer | 0.285 | 0.0061867 | 0.0061867 | 0.0045559 | 2.1708 | 0 | 0 | 0 | 2024-01-21 00:55 | FALSE | 1 | tr_1033_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_141 | line_343_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_343_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_6008_22 | ACLineSegment | Line | 0.51338 | 0.0050718 | 0.0050718 | 0.003867 | 0.98792 | 0 | 0 | 0 | 2024-01-17 15:55 | FALSE | 1 | line_6008_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | tr_1066_22 | Transformer | Transformer | 0.285 | 0.0050718 | 0.0050718 | 0.003867 | 1.7796 | 0 | 0 | 0 | 2024-01-17 15:55 | FALSE | 1 | tr_1066_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_141 | line_377_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_377_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_6061_22 | ACLineSegment | Line | 0.51338 | 0.0066813 | 0.0066813 | 0.0044224 | 1.3014 | 0 | 0 | 0 | 2024-01-21 02:15 | FALSE | 1 | line_6061_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | tr_1097_22 | Transformer | Transformer | 0.285 | 0.0066813 | 0.0066813 | 0.0044224 | 2.3443 | 0 | 0 | 0 | 2024-01-21 02:15 | FALSE | 1 | tr_1097_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_141 | line_4094_22 | ACLineSegment | Line | 12.3112 | 0.098457 | 0.098457 | 0.075822 | 0.79973 | 0 | 0 | 0 | 2024-07-16 03:00 | FALSE | 1 | line_4094_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | line_4095_22 | ACLineSegment | Line | 12.3112 | 0.12006 | 0.12006 | 0.092876 | 0.97522 | 0 | 0 | 0 | 2024-07-16 03:00 | FALSE | 1 | line_4095_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | line_4096_22 | ACLineSegment | Line | 12.3112 | 0.017496 | 0.017496 | 0.013196 | 0.14211 | 0 | 0 | 0 | 2024-01-20 22:05 | FALSE | 1 | line_4096_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | line_4250_22 | ACLineSegment | Line | 13.5424 | 0.22449 | 0.22449 | 0.17326 | 1.6577 | 0 | 0 | 0 | 2024-01-20 14:00 | FALSE | 1 | line_4250_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | line_4251_22 | ACLineSegment | Line | 13.5424 | 0.22027 | 0.22027 | 0.16925 | 1.6265 | 0 | 0 | 0 | 2024-01-20 14:00 | FALSE | 1 | line_4251_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | line_4401_22 | ACLineSegment | Line | 13.5424 | 0.23111 | 0.23111 | 0.18037 | 1.7066 | 0 | 0 | 0 | 2024-01-20 14:00 | FALSE | 1 | line_4401_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | line_4803_22 | ACLineSegment | Line | 13.5424 | 0.0048252 | 0.0048252 | 0.0035415 | 0.03563 | 0 | 0 | 0 | 2024-01-21 17:50 | FALSE | 1 | line_4803_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | line_4361_22 | ACLineSegment | Line | 13.5424 | 0.15363 | 0.15363 | 0.12106 | 1.1345 | 0 | 0 | 0 | 2024-07-16 03:00 | FALSE | 1 | line_4361_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | line_4257_22 | ACLineSegment | Line | 0.94778 | 0.016183 | 0.016183 | 0.0099006 | 1.7075 | 0 | 0 | 0 | 2024-07-16 03:00 | FALSE | 1 | line_4257_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | tr_271_22 | Transformer | Transformer | 0.02375 | 0.0036565 | 0.0036565 | 0.0021107 | 15.3959 | 0 | 0 | 0 | 2024-01-20 08:55 | FALSE | 1 | tr_271_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_141 | line_4268_22 | ACLineSegment | Line | 0.94778 | 0.0037074 | 0.0037074 | 0.0020932 | 0.39117 | 0 | 0 | 0 | 2024-01-21 02:15 | FALSE | 1 | line_4268_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_4437_22 | ACLineSegment | Line | 0.94778 | 0.011708 | 0.011708 | 0.006322 | 1.2353 | 0 | 0 | 0 | 2024-01-20 14:00 | FALSE | 1 | line_4437_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | tr_338_22 | Transformer | Transformer | 0.02375 | 0.0030027 | 0.0030027 | 0.0018066 | 12.643 | 0 | 0 | 0 | 2024-01-21 03:55 | FALSE | 1 | tr_338_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_141 | line_4259_22 | ACLineSegment | Line | 0.034884 | 0.0036565 | 0.0036565 | 0.0021107 | 10.4821 | 0 | 0 | 0 | 2024-01-20 08:55 | FALSE | 1 | line_4259_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_4300_22 | ACLineSegment | Line | 12.3112 | 0.094852 | 0.094852 | 0.07287 | 0.77045 | 0 | 0 | 0 | 2024-07-16 03:00 | FALSE | 1 | line_4300_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | line_4360_22 | ACLineSegment | Line | 13.5424 | 0.14805 | 0.14805 | 0.11703 | 1.0932 | 0 | 0 | 0 | 2024-07-16 03:00 | FALSE | 1 | line_4360_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | line_4370_22 | ACLineSegment | Line | 12.3112 | 0.01003 | 0.01003 | 0.0053962 | 0.081466 | 0 | 0 | 0 | 2024-01-20 14:00 | FALSE | 1 | line_4370_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | line_4403_22 | ACLineSegment | Line | 13.5424 | 0.23548 | 0.23548 | 0.18434 | 1.7388 | 0 | 0 | 0 | 2024-07-16 03:00 | FALSE | 1 | line_4403_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | tr_325_22 | Transformer | Transformer | 0.02375 | 0.007003 | 0.007003 | 0.0049792 | 29.4862 | 0 | 0 | 0 | 2024-01-20 13:55 | FALSE | 1 | tr_325_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_141 | line_4710_22 | ACLineSegment | Line | 13.5424 | 0.2409 | 0.2409 | 0.18864 | 1.7789 | 0 | 0 | 0 | 2024-07-16 03:00 | FALSE | 1 | line_4710_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | line_4431_22 | ACLineSegment | Line | 0.034884 | 0.007003 | 0.007003 | 0.0049792 | 20.0753 | 0 | 0 | 0 | 2024-01-20 13:55 | FALSE | 1 | line_4431_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_75_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_75_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | tr_755_22 | Transformer | Transformer | 0.02375 | 0.011708 | 0.011708 | 0.006322 | 49.298 | 0 | 0 | 0 | 2024-01-20 14:00 | FALSE | 1 | tr_755_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_141 | line_4438_22 | ACLineSegment | Line | 0.034884 | 0.0030027 | 0.0030027 | 0.0018066 | 8.6078 | 0 | 0 | 0 | 2024-01-21 03:55 | FALSE | 1 | line_4438_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_4502_22 | ACLineSegment | Line | 12.3112 | 0.0062041 | 0.0062041 | 0.0042226 | 0.050394 | 0 | 0 | 0 | 2024-01-20 05:00 | FALSE | 1 | line_4502_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | tr_1157_22 | Transformer | Transformer | 0.285 | 0.0064219 | 0.0064219 | 0.0042494 | 2.2533 | 0 | 0 | 0 | 2024-01-20 10:50 | FALSE | 1 | tr_1157_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_141 | line_4522_22 | ACLineSegment | Line | 13.5424 | 0.010978 | 0.010978 | 0.0085069 | 0.081063 | 0 | 0 | 0 | 2024-06-26 19:55 | FALSE | 1 | line_4522_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | line_4523_22 | ACLineSegment | Line | 13.5424 | 0.015786 | 0.015786 | 0.012194 | 0.11657 | 0 | 0 | 0 | 2024-07-15 19:55 | FALSE | 1 | line_4523_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | line_4602_22 | ACLineSegment | Line | 13.5424 | 0.0029982 | 0.0029982 | 0.0021964 | 0.022139 | 0 | 0 | 0 | 2024-07-15 09:30 | FALSE | 1 | line_4602_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | line_4815_22 | ACLineSegment | Line | 12.3112 | 0.026174 | 0.026174 | 0.019994 | 0.2126 | 0 | 0 | 0 | 2024-01-20 09:00 | FALSE | 1 | line_4815_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | line_4887_22 | ACLineSegment | Line | 12.3112 | 0.0082446 | 0.0082446 | 0.0056223 | 0.066968 | 0 | 0 | 0 | 2024-01-20 18:55 | FALSE | 1 | line_4887_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | line_455_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_455_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_6186_22 | ACLineSegment | Line | 0.51338 | 0.0064219 | 0.0064219 | 0.0042494 | 1.2509 | 0 | 0 | 0 | 2024-01-20 10:50 | FALSE | 1 | line_6186_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | line_4565_22 | ACLineSegment | Line | 13.5424 | 0.37996 | 0.37996 | 0.29074 | 2.8057 | 0 | 0 | 0 | 2024-01-21 01:00 | TRUE | 1 | line_4565_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | line_4566_22 | ACLineSegment | Line | 13.5424 | 0.37396 | 0.37396 | 0.28738 | 2.7614 | 0 | 0 | 0 | 2024-07-16 03:00 | FALSE | 1 | line_4566_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | tr_386_22 | Transformer | Transformer | 0.02375 | 0.0073526 | 0.0073526 | 0.0037103 | 30.9584 | 0 | 0 | 0 | 2024-01-21 00:55 | FALSE | 1 | tr_386_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_141 | line_5449_22 | ACLineSegment | Line | 13.5424 | 0.030887 | 0.030887 | 0.020664 | 0.22807 | 0 | 0 | 0 | 2024-07-15 07:00 | FALSE | 1 | line_5449_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | line_6472_22 | ACLineSegment | Line | 13.5424 | 0.32057 | 0.32057 | 0.2506 | 2.3672 | 0 | 0 | 0 | 2024-01-21 01:00 | FALSE | 1 | line_6472_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | line_4567_22 | ACLineSegment | Line | 0.034884 | 0.0073526 | 0.0073526 | 0.0037103 | 21.0776 | 0 | 0 | 0 | 2024-01-21 00:55 | FALSE | 1 | line_4567_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_4709_22 | ACLineSegment | Line | 13.5424 | 0.24557 | 0.24557 | 0.19307 | 1.8133 | 0 | 0 | 0 | 2024-07-16 03:00 | FALSE | 1 | line_4709_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | line_5743_22 | ACLineSegment | Line | 13.5424 | 0.24864 | 0.24864 | 0.19631 | 1.836 | 0 | 0 | 0 | 2024-07-16 03:00 | FALSE | 1 | line_5743_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | line_474_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_474_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_6119_22 | ACLineSegment | Line | 0.025406 | 0.0043165 | 0.0043165 | 0.0024277 | 16.9903 | 0 | 0 | 0 | 2024-01-17 18:55 | FALSE | 1 | line_6119_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | tr_1124_22 | Transformer | Transformer | 0.02375 | 0.0043165 | 0.0043165 | 0.0024277 | 18.1747 | 0 | 0 | 0 | 2024-01-17 18:55 | FALSE | 1 | tr_1124_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_141 | line_4849_22 | ACLineSegment | Line | 12.3112 | 0.0051229 | 0.0051229 | 0.0036267 | 0.041611 | 0 | 0 | 0 | 2024-01-17 21:00 | FALSE | 1 | line_4849_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | line_6059_22 | ACLineSegment | Line | 12.3112 | 0.03108 | 0.03108 | 0.021918 | 0.25245 | 0 | 0 | 0 | 2024-01-20 05:00 | FALSE | 1 | line_6059_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | line_6060_22 | ACLineSegment | Line | 12.3112 | 0.038301 | 0.038301 | 0.028522 | 0.3111 | 0 | 0 | 0 | 2024-01-21 02:15 | FALSE | 1 | line_6060_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | line_4878_22 | ACLineSegment | Line | 12.3112 | 0.26537 | 0.26537 | 0.20991 | 2.1555 | 0 | 0 | 0 | 2024-07-16 03:00 | FALSE | 1 | line_4878_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | line_4879_22 | ACLineSegment | Line | 13.5424 | 0.26085 | 0.26085 | 0.20674 | 1.9262 | 0 | 0 | 0 | 2024-01-20 09:00 | FALSE | 1 | line_4879_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | tr_518_22 | Transformer | Transformer | 0.02375 | 0.0062082 | 0.0062082 | 0.0035792 | 26.1399 | 0 | 0 | 0 | 2024-07-16 03:00 | FALSE | 1 | tr_518_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_141 | line_4880_22 | ACLineSegment | Line | 0.025406 | 0.0062082 | 0.0062082 | 0.0035792 | 24.4363 | 0 | 0 | 0 | 2024-07-16 03:00 | FALSE | 1 | line_4880_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_493_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_493_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_6176_22 | ACLineSegment | Line | 0.51338 | 0.0085008 | 0.0085008 | 0.0060878 | 1.6559 | 0 | 0 | 0 | 2024-07-15 05:00 | FALSE | 1 | line_6176_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | tr_1150_22 | Transformer | Transformer | 0.285 | 0.0085008 | 0.0085008 | 0.0060878 | 2.9827 | 0 | 0 | 0 | 2024-07-15 05:00 | FALSE | 1 | tr_1150_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_141 | line_524_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_524_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_6242_22 | ACLineSegment | Line | 0.51338 | 0.0078751 | 0.0078751 | 0.0055104 | 1.534 | 0 | 0 | 0 | 2024-01-20 20:50 | FALSE | 1 | line_6242_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | tr_1181_22 | Transformer | Transformer | 0.285 | 0.0078751 | 0.0078751 | 0.0055104 | 2.7632 | 0 | 0 | 0 | 2024-01-20 20:50 | FALSE | 1 | tr_1181_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_141 | line_5409_22 | ACLineSegment | Line | 0.034884 | 0.008265 | 0.008265 | 0.0041476 | 23.6933 | 0 | 0 | 0 | 2024-01-20 14:00 | FALSE | 1 | line_5409_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_5410_22 | ACLineSegment | Line | 0.034884 | 0.0040546 | 0.0040546 | 0.0024322 | 11.6232 | 0 | 0 | 0 | 2024-01-20 22:05 | FALSE | 1 | line_5410_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_5448_22 | ACLineSegment | Line | 13.5424 | 0.027468 | 0.027468 | 0.018167 | 0.20283 | 0 | 0 | 0 | 2024-07-15 07:00 | FALSE | 1 | line_5448_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | line_565_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_565_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_6295_22 | ACLineSegment | Line | 0.025406 | 0.0049908 | 0.0049908 | 0.0037974 | 19.6443 | 0 | 0 | 0 | 2024-07-10 10:10 | FALSE | 1 | line_6295_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | tr_1211_22 | Transformer | Transformer | 0.02375 | 0.0049908 | 0.0049908 | 0.0037974 | 21.0138 | 0 | 0 | 0 | 2024-07-10 10:10 | FALSE | 1 | tr_1211_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_141 | line_5658_22 | ACLineSegment | Line | 12.3112 | 0.26974 | 0.26974 | 0.21347 | 2.191 | 0 | 0 | 0 | 2024-07-16 03:00 | FALSE | 1 | line_5658_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | line_6471_22 | ACLineSegment | Line | 12.3112 | 0.31559 | 0.31559 | 0.24645 | 2.5634 | 0 | 0 | 0 | 2024-07-16 03:00 | FALSE | 1 | line_6471_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | line_6887_22 | ACLineSegment | Line | 12.3112 | 0.018488 | 0.018488 | 0.012598 | 0.15017 | 0 | 0 | 0 | 2024-07-15 07:00 | FALSE | 1 | line_6887_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | line_5659_22 | ACLineSegment | Line | 0.51338 | 0.0055294 | 0.0055294 | 0.0042874 | 1.0771 | 0 | 0 | 0 | 2024-01-20 13:55 | FALSE | 1 | line_5659_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | tr_900_22 | Transformer | Transformer | 0.095 | 0.0055294 | 0.0055294 | 0.0042874 | 5.8204 | 0 | 0 | 0 | 2024-01-20 13:55 | FALSE | 1 | tr_900_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_141 | line_5676_22 | ACLineSegment | Line | 12.3112 | 0.073923 | 0.073923 | 0.056258 | 0.60045 | 0 | 0 | 0 | 2024-01-21 01:00 | FALSE | 1 | line_5676_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | line_5677_22 | ACLineSegment | Line | 12.3112 | 0.090468 | 0.090468 | 0.069187 | 0.73484 | 0 | 0 | 0 | 2024-07-16 03:00 | FALSE | 1 | line_5677_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | line_5932_22 | ACLineSegment | Line | 12.3112 | 0.0061867 | 0.0061867 | 0.0045559 | 0.050253 | 0 | 0 | 0 | 2024-01-21 00:55 | FALSE | 1 | line_5932_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | line_6241_22 | ACLineSegment | Line | 12.3112 | 0.012054 | 0.012054 | 0.0093405 | 0.097914 | 0 | 0 | 0 | 2024-07-05 09:05 | FALSE | 1 | line_6241_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | line_6007_22 | ACLineSegment | Line | 12.3112 | 0.07026 | 0.07026 | 0.053005 | 0.57069 | 0 | 0 | 0 | 2024-01-21 01:00 | FALSE | 1 | line_6007_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | line_6175_22 | ACLineSegment | Line | 12.3112 | 0.05168 | 0.05168 | 0.039114 | 0.41978 | 0 | 0 | 0 | 2024-01-21 01:00 | FALSE | 1 | line_6175_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | tr_1378_22 | Transformer | Transformer | 0.02375 | 0.008913 | 0.008913 | 0.0063672 | 37.5285 | 0 | 0 | 0 | 2024-06-23 19:00 | FALSE | 1 | tr_1378_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_141 | line_6118_22 | ACLineSegment | Line | 12.3112 | 0.013056 | 0.013056 | 0.007307 | 0.10605 | 0 | 0 | 0 | 2024-01-20 14:00 | FALSE | 1 | line_6118_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | line_6174_22 | ACLineSegment | Line | 12.3112 | 0.045255 | 0.045255 | 0.034352 | 0.36759 | 0 | 0 | 0 | 2024-01-21 02:15 | FALSE | 1 | line_6174_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | tr_1306_22 | Transformer | Transformer | 0.1425 | 0.0049194 | 0.0049194 | 0.0033721 | 3.4522 | 0 | 0 | 0 | 2024-06-27 02:55 | FALSE | 1 | tr_1306_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_141 | line_6294_22 | ACLineSegment | Line | 12.3112 | 0.042027 | 0.042027 | 0.03171 | 0.34137 | 0 | 0 | 0 | 2024-01-21 01:00 | FALSE | 1 | line_6294_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | line_631_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_631_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_6363_22 | ACLineSegment | Line | 0.51338 | 0.010267 | 0.010267 | 0.0068012 | 1.9998 | 0 | 0 | 0 | 2024-01-18 01:45 | FALSE | 1 | line_6363_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | tr_1250_22 | Transformer | Transformer | 0.285 | 0.010267 | 0.010267 | 0.0068012 | 3.6023 | 0 | 0 | 0 | 2024-01-18 01:45 | FALSE | 1 | tr_1250_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_141 | line_6454_22 | ACLineSegment | Line | 0.51338 | 0.0049194 | 0.0049194 | 0.0033721 | 0.95824 | 0 | 0 | 0 | 2024-06-27 02:55 | FALSE | 1 | line_6454_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | line_689_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_689_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | tr_1316_22 | Transformer | Transformer | 0.95 | 0.0069202 | 0.0069202 | 0.0052351 | 0.72845 | 0 | 0 | 0 | 2024-07-10 21:00 | FALSE | 1 | tr_1316_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_141 | line_6473_22 | ACLineSegment | Line | 0.51338 | 0.0069202 | 0.0069202 | 0.0052351 | 1.348 | 0 | 0 | 0 | 2024-07-10 21:00 | FALSE | 1 | line_6473_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_141 | line_708_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_708_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_6551_22 | ACLineSegment | Line | 0.025406 | 0.008913 | 0.008913 | 0.0063672 | 35.0827 | 0 | 0 | 0 | 2024-06-23 19:00 | FALSE | 1 | line_6551_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_141 | line_786_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_786_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_4226_22 | ACLineSegment | Line | 13.5424 | 0.49088 | 0.49088 | 0.37482 | 3.6247 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_4226_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | tr_1353_22 | Transformer | Transformer | 0.1425 | 0.0039172 | 0.0039172 | 0.0028356 | 2.7489 | 0 | 0 | 0 | 2024-07-14 08:45 | FALSE | 1 | tr_1353_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_5362_22 | ACLineSegment | Line | 0.94778 | 0.0091306 | 0.0091306 | 0.0061492 | 0.96337 | 0 | 0 | 0 | 2024-01-20 11:05 | FALSE | 1 | line_5362_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_5834_22 | ACLineSegment | Line | 13.5424 | 0.0068818 | 0.0068818 | 0.0050127 | 0.050817 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_5834_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | tr_987_22 | Transformer | Transformer | 0.07125 | 0.0059606 | 0.0059606 | 0.0044451 | 8.3658 | 0 | 0 | 0 | 2024-01-20 09:00 | FALSE | 1 | tr_987_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_5835_22 | ACLineSegment | Line | 0.94778 | 0.0013657 | 0.0013657 | 0.00081676 | 0.1441 | 0 | 0 | 0 | 2024-01-20 11:05 | FALSE | 1 | line_5835_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_4225_22 | ACLineSegment | Line | 13.5424 | 0.49814 | 0.49814 | 0.38038 | 3.6784 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_4225_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | tr_262_22 | Transformer | Transformer | 0.02375 | 0.007818 | 0.007818 | 0.0051576 | 32.918 | 0 | 0 | 0 | 2024-01-20 13:10 | FALSE | 1 | tr_262_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_4219_22 | ACLineSegment | Line | 0.94778 | 0.0029266 | 0.0029266 | 0.001882 | 0.30879 | 0 | 0 | 0 | 2024-01-20 23:00 | FALSE | 1 | line_4219_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | tr_676_22 | Transformer | Transformer | 0.02375 | 0.0058053 | 0.0058053 | 0.0034832 | 24.4432 | 0 | 0 | 0 | 2024-01-17 14:20 | FALSE | 1 | tr_676_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_4287_22 | ACLineSegment | Line | 0.94778 | 0.014165 | 0.014165 | 0.0084446 | 1.4946 | 0 | 0 | 0 | 2024-07-15 05:55 | FALSE | 1 | line_4287_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | tr_285_22 | Transformer | Transformer | 0.02375 | 0.01109 | 0.01109 | 0.0049083 | 46.6929 | 0 | 0 | 0 | 2024-01-20 18:00 | FALSE | 1 | tr_285_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_5816_22 | ACLineSegment | Line | 13.5424 | 0.042475 | 0.042475 | 0.027919 | 0.31364 | 0 | 0 | 0 | 2024-07-15 08:50 | FALSE | 1 | line_5816_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_6370_22 | ACLineSegment | Line | 13.5424 | 0.029496 | 0.029496 | 0.019935 | 0.21781 | 0 | 0 | 0 | 2024-01-17 08:55 | FALSE | 1 | line_6370_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | tr_1416_22 | Transformer | Transformer | 0.095 | 0.0085742 | 0.0085742 | 0.0051561 | 9.0255 | 0 | 0 | 0 | 2024-07-15 08:50 | FALSE | 1 | tr_1416_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | tr_394_22 | Transformer | Transformer | 0.02375 | 0.0043783 | 0.0043783 | 0.0022745 | 18.4348 | 0 | 0 | 0 | 2024-01-21 01:35 | FALSE | 1 | tr_394_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_5474_22 | ACLineSegment | Line | 13.5424 | 0.0070376 | 0.0070376 | 0.003882 | 0.051967 | 0 | 0 | 0 | 2024-01-22 04:00 | FALSE | 1 | line_5474_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_6492_22 | ACLineSegment | Line | 13.5424 | 0.013062 | 0.013062 | 0.0081847 | 0.096456 | 0 | 0 | 0 | 2024-01-22 04:00 | FALSE | 1 | line_6492_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | tr_1329_22 | Transformer | Transformer | 0.1425 | 0.0041358 | 0.0041358 | 0.0028901 | 2.9023 | 0 | 0 | 0 | 2024-01-21 02:00 | FALSE | 1 | tr_1329_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_4785_22 | ACLineSegment | Line | 13.5424 | 0.052526 | 0.052526 | 0.036225 | 0.38786 | 0 | 0 | 0 | 2024-07-15 08:50 | FALSE | 1 | line_4785_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_4787_22 | ACLineSegment | Line | 13.5424 | 0.045187 | 0.045187 | 0.030566 | 0.33367 | 0 | 0 | 0 | 2024-07-15 08:50 | FALSE | 1 | line_4787_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_4788_22 | ACLineSegment | Line | 13.5424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_4788_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | tr_477_22 | Transformer | Transformer | 0.07125 | 0.0051753 | 0.0051753 | 0.0037804 | 7.2635 | 0 | 0 | 0 | 2024-01-20 11:05 | FALSE | 1 | tr_477_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_4786_22 | ACLineSegment | Line | 0.94778 | 0.0057052 | 0.0057052 | 0.0027806 | 0.60195 | 0 | 0 | 0 | 2024-01-20 10:55 | FALSE | 1 | line_4786_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_5164_22 | ACLineSegment | Line | 13.5424 | 0.62178 | 0.62178 | 0.47622 | 4.5914 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_5164_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_5166_22 | ACLineSegment | Line | 13.5424 | 0.65006 | 0.65006 | 0.49885 | 4.8002 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_5166_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | tr_651_22 | Transformer | Transformer | 0.02375 | 0.0064133 | 0.0064133 | 0.0035128 | 27.0032 | 0 | 0 | 0 | 2024-01-21 03:55 | FALSE | 1 | tr_651_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_5165_22 | ACLineSegment | Line | 0.94778 | 0.030559 | 0.030559 | 0.020499 | 3.2242 | 0 | 0 | 0 | 2024-01-21 02:00 | FALSE | 1 | line_5165_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_1021_22 | ACLineSegment | Line | 0.034884 | 0.030965 | 0.030965 | 0.019661 | 88.767 | 0 | 0 | 0 | 2024-01-20 19:00 | FALSE | 1 | line_1021_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_1022_22 | ACLineSegment | Line | 0.034884 | 0.0047111 | 0.0047111 | 0.0025248 | 13.5053 | 0 | 0 | 0 | 2024-07-15 13:00 | FALSE | 1 | line_1022_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_925_22 | ACLineSegment | Line | 0.034884 | 0.015369 | 0.015369 | 0.0093397 | 44.0593 | 0 | 0 | 0 | 2024-01-20 18:00 | FALSE | 1 | line_925_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_938_22 | ACLineSegment | Line | 0.034884 | 0.012546 | 0.012546 | 0.0083183 | 35.9643 | 0 | 0 | 0 | 2024-01-17 14:20 | FALSE | 1 | line_938_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_950_22 | ACLineSegment | Line | 0.034884 | 0.012719 | 0.012719 | 0.0081869 | 36.4611 | 0 | 0 | 0 | 2024-07-15 10:05 | FALSE | 1 | line_950_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_963_22 | ACLineSegment | Line | 0.034884 | 0.0047812 | 0.0047812 | 0.0027151 | 13.7062 | 0 | 0 | 0 | 2024-07-16 00:50 | FALSE | 1 | line_963_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | tr_1148_22 | Transformer | Transformer | 0.0475 | 0.042793 | 0.042793 | 0.030221 | 90.0906 | 0 | 0 | 0 | 2024-01-20 19:00 | FALSE | 1 | tr_1148_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_1045_22 | ACLineSegment | Line | 0.034884 | 0.0051828 | 0.0051828 | 0.0026571 | 14.8575 | 0 | 0 | 0 | 2024-01-20 06:45 | FALSE | 1 | line_1045_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_983_22 | ACLineSegment | Line | 0.034884 | 0.0051828 | 0.0051828 | 0.0026571 | 14.8575 | 0 | 0 | 0 | 2024-01-20 06:45 | FALSE | 1 | line_983_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_1719_22 | ACLineSegment | Line | 0.034884 | 0.0039631 | 0.0039631 | 0.0019959 | 11.361 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_1719_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_1720_22 | ACLineSegment | Line | 0.025406 | 0.0039631 | 0.0039631 | 0.0019959 | 15.5992 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_1720_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_1721_22 | ACLineSegment | Line | 0.034884 | 0.0067689 | 0.0067689 | 0.0037327 | 19.4043 | 0 | 0 | 0 | 2024-01-20 15:00 | FALSE | 1 | line_1721_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | tr_282_22 | Transformer | Transformer | 0.02375 | 0.0093887 | 0.0093887 | 0.0055312 | 39.5313 | 0 | 0 | 0 | 2024-07-15 05:55 | FALSE | 1 | tr_282_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_1722_22 | ACLineSegment | Line | 0.034884 | 0.0067689 | 0.0067689 | 0.0037327 | 19.4043 | 0 | 0 | 0 | 2024-01-20 15:00 | FALSE | 1 | line_1722_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_1729_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1729_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_4295_22 | ACLineSegment | Line | 0.034884 | 0.01109 | 0.01109 | 0.0049083 | 31.7903 | 0 | 0 | 0 | 2024-01-20 18:00 | FALSE | 1 | line_4295_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_1774_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1774_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_4398_22 | ACLineSegment | Line | 0.22905 | 0.0077473 | 0.0077473 | 0.0056486 | 3.3824 | 0 | 0 | 0 | 2024-01-20 21:05 | FALSE | 1 | line_4398_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | tr_323_22 | Transformer | Transformer | 0.07125 | 0.0077473 | 0.0077473 | 0.0056486 | 10.8734 | 0 | 0 | 0 | 2024-01-20 21:05 | FALSE | 1 | tr_323_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_1835_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1835_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_4374_22 | ACLineSegment | Line | 0.51338 | 0.0052685 | 0.0052685 | 0.0037608 | 1.0262 | 0 | 0 | 0 | 2024-01-22 04:00 | FALSE | 1 | line_4374_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | tr_313_22 | Transformer | Transformer | 0.1425 | 0.0052685 | 0.0052685 | 0.0037608 | 3.6972 | 0 | 0 | 0 | 2024-01-22 04:00 | FALSE | 1 | tr_313_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_1925_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1925_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_4472_22 | ACLineSegment | Line | 0.22905 | 0.021032 | 0.021032 | 0.016836 | 9.1824 | 0 | 0 | 0 | 2024-07-15 22:55 | FALSE | 1 | line_4472_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | tr_352_22 | Transformer | Transformer | 0.07125 | 0.021032 | 0.021032 | 0.016836 | 29.5187 | 0 | 0 | 0 | 2024-07-15 22:55 | FALSE | 1 | tr_352_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_1960_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1960_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_4517_22 | ACLineSegment | Line | 0.51338 | 0.0086021 | 0.0086021 | 0.0058481 | 1.6756 | 0 | 0 | 0 | 2024-01-21 06:55 | FALSE | 1 | line_4517_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | tr_368_22 | Transformer | Transformer | 0.285 | 0.0086021 | 0.0086021 | 0.0058481 | 3.0183 | 0 | 0 | 0 | 2024-01-21 06:55 | FALSE | 1 | tr_368_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_1985_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1985_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_4586_22 | ACLineSegment | Line | 0.034884 | 0.0043783 | 0.0043783 | 0.0022745 | 12.5511 | 0 | 0 | 0 | 2024-01-21 01:35 | FALSE | 1 | line_4586_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2000_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2000_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_4636_22 | ACLineSegment | Line | 0.51338 | 0.0058464 | 0.0058464 | 0.0042459 | 1.1388 | 0 | 0 | 0 | 2024-01-17 20:05 | FALSE | 1 | line_4636_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | tr_413_22 | Transformer | Transformer | 0.475 | 0.0058464 | 0.0058464 | 0.0042459 | 1.2308 | 0 | 0 | 0 | 2024-01-17 20:05 | FALSE | 1 | tr_413_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_2035_22 | ACLineSegment | Line | 0.51338 | 0.0054797 | 0.0054797 | 0.0037311 | 1.0674 | 0 | 0 | 0 | 2024-07-16 03:00 | FALSE | 1 | line_2035_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_2036_22 | ACLineSegment | Line | 0.51338 | 0.0054797 | 0.0054797 | 0.0037311 | 1.0674 | 0 | 0 | 0 | 2024-07-16 03:00 | FALSE | 1 | line_2036_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_2037_22 | ACLineSegment | Line | 0.51338 | 0.02875 | 0.02875 | 0.020898 | 5.6001 | 0 | 0 | 0 | 2024-01-22 04:00 | FALSE | 1 | line_2037_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_2038_22 | ACLineSegment | Line | 0.51338 | 0.025803 | 0.025803 | 0.017703 | 5.0262 | 0 | 0 | 0 | 2024-01-22 04:00 | FALSE | 1 | line_2038_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | tr_453_22 | Transformer | Transformer | 0.095 | 0.02875 | 0.02875 | 0.020898 | 30.2631 | 0 | 0 | 0 | 2024-01-22 04:00 | FALSE | 1 | tr_453_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_2057_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2057_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_4720_22 | ACLineSegment | Line | 0.51338 | 0.0070475 | 0.0070475 | 0.0043437 | 1.3728 | 0 | 0 | 0 | 2024-07-16 03:00 | FALSE | 1 | line_4720_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | tr_449_22 | Transformer | Transformer | 0.285 | 0.0070475 | 0.0070475 | 0.0043437 | 2.4728 | 0 | 0 | 0 | 2024-07-16 03:00 | FALSE | 1 | tr_449_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_2064_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2064_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_4734_22 | ACLineSegment | Line | 0.51338 | 0.0054469 | 0.0054469 | 0.0038812 | 1.061 | 0 | 0 | 0 | 2024-01-21 01:35 | FALSE | 1 | line_4734_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | tr_455_22 | Transformer | Transformer | 0.07125 | 0.0054469 | 0.0054469 | 0.0038812 | 7.6448 | 0 | 0 | 0 | 2024-01-21 01:35 | FALSE | 1 | tr_455_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_2095_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2095_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_4789_22 | ACLineSegment | Line | 0.51338 | 0.0051753 | 0.0051753 | 0.0037804 | 1.0081 | 0 | 0 | 0 | 2024-01-20 11:05 | FALSE | 1 | line_4789_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_2170_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2170_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_5167_22 | ACLineSegment | Line | 0.034884 | 0.0064133 | 0.0064133 | 0.0035128 | 18.3848 | 0 | 0 | 0 | 2024-01-21 03:55 | FALSE | 1 | line_5167_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_239_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_239_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_5248_22 | ACLineSegment | Line | 0.51338 | 0.0067317 | 0.0067317 | 0.0046434 | 1.3112 | 0 | 0 | 0 | 2024-07-14 22:55 | FALSE | 1 | line_5248_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | tr_685_22 | Transformer | Transformer | 0.07125 | 0.0067317 | 0.0067317 | 0.0046434 | 9.448 | 0 | 0 | 0 | 2024-07-14 22:55 | FALSE | 1 | tr_685_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_256_22 | ACLineSegment | Line | 0.034884 | 0.0092477 | 0.0092477 | 0.0058223 | 26.5103 | 0 | 0 | 0 | 2024-01-21 13:00 | FALSE | 1 | line_256_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_257_22 | ACLineSegment | Line | 0.034884 | 0.0092477 | 0.0092477 | 0.0058223 | 26.5103 | 0 | 0 | 0 | 2024-01-21 13:00 | FALSE | 1 | line_257_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_258_22 | ACLineSegment | Line | 0.034884 | 0.0092477 | 0.0092477 | 0.0058223 | 26.5103 | 0 | 0 | 0 | 2024-01-21 13:00 | FALSE | 1 | line_258_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_260_22 | ACLineSegment | Line | 0.034884 | 0.0052281 | 0.0052281 | 0.0026971 | 14.9873 | 0 | 0 | 0 | 2024-01-20 20:50 | FALSE | 1 | line_260_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_5274_22 | ACLineSegment | Line | 0.034884 | 0.035834 | 0.035834 | 0.022146 | 102.7257 | 6 | 0.5 | 0.0056954 | 2024-01-17 23:00 | FALSE | 1 | line_5274_22 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_145 | tr_695_22 | Transformer | Transformer | 0.0475 | 0.044962 | 0.044962 | 0.028667 | 94.6563 | 0 | 0 | 0 | 2024-01-17 23:00 | FALSE | 1 | tr_695_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_261_22 | ACLineSegment | Line | 0.025406 | 0.0052281 | 0.0052281 | 0.0026971 | 20.5784 | 0 | 0 | 0 | 2024-01-20 20:50 | FALSE | 1 | line_261_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2605_22 | ACLineSegment | Line | 0.51338 | 0.024716 | 0.024716 | 0.015807 | 4.8143 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_2605_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_2606_22 | ACLineSegment | Line | 0.51338 | 0.024716 | 0.024716 | 0.015807 | 4.8143 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_2606_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | tr_681_22 | Transformer | Transformer | 0.285 | 0.024716 | 0.024716 | 0.015807 | 8.6722 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | tr_681_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_263_22 | ACLineSegment | Line | 0.034884 | 0.0038377 | 0.0038377 | 0.0023554 | 11.0014 | 0 | 0 | 0 | 2024-01-17 20:05 | FALSE | 1 | line_263_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_264_22 | ACLineSegment | Line | 0.034884 | 0.0038377 | 0.0038377 | 0.0023554 | 11.0014 | 0 | 0 | 0 | 2024-01-17 20:05 | FALSE | 1 | line_264_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_267_22 | ACLineSegment | Line | 0.034884 | 0.0038377 | 0.0038377 | 0.0023554 | 11.0014 | 0 | 0 | 0 | 2024-01-17 20:05 | FALSE | 1 | line_267_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2633_22 | ACLineSegment | Line | 0.034884 | 0.0028844 | 0.0028844 | 0.0015535 | 8.2686 | 0 | 0 | 0 | 2024-07-15 05:55 | FALSE | 1 | line_2633_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2634_22 | ACLineSegment | Line | 0.034884 | 0.0028844 | 0.0028844 | 0.0015535 | 8.2686 | 0 | 0 | 0 | 2024-07-15 05:55 | FALSE | 1 | line_2634_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2635_22 | ACLineSegment | Line | 0.034884 | 0.0032534 | 0.0032534 | 0.0017472 | 9.3265 | 0 | 0 | 0 | 2024-01-20 09:00 | FALSE | 1 | line_2635_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | tr_679_22 | Transformer | Transformer | 0.02375 | 0.0056763 | 0.0056763 | 0.0031201 | 23.9001 | 0 | 0 | 0 | 2024-01-20 10:55 | FALSE | 1 | tr_679_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_2636_22 | ACLineSegment | Line | 0.034884 | 0.0032534 | 0.0032534 | 0.0017472 | 9.3265 | 0 | 0 | 0 | 2024-01-20 09:00 | FALSE | 1 | line_2636_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2649_22 | ACLineSegment | Line | 0.025406 | 0.0025636 | 0.0025636 | 0.0014176 | 10.0905 | 0 | 0 | 0 | 2024-01-20 20:50 | FALSE | 1 | line_2649_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2650_22 | ACLineSegment | Line | 0.025406 | 0.0058053 | 0.0058053 | 0.0034832 | 22.8502 | 0 | 0 | 0 | 2024-01-17 14:20 | FALSE | 1 | line_2650_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2651_22 | ACLineSegment | Line | 0.025406 | 0.0037444 | 0.0037444 | 0.0021939 | 14.7385 | 0 | 0 | 0 | 2024-07-15 06:45 | FALSE | 1 | line_2651_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2652_22 | ACLineSegment | Line | 0.025406 | 0.0025636 | 0.0025636 | 0.0014176 | 10.0905 | 0 | 0 | 0 | 2024-01-20 20:50 | FALSE | 1 | line_2652_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_265_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_265_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_266_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_266_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_5270_22 | ACLineSegment | Line | 0.034884 | 0.0060053 | 0.0060053 | 0.0034645 | 17.2152 | 0 | 0 | 0 | 2024-01-20 14:45 | FALSE | 1 | line_5270_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_5271_22 | ACLineSegment | Line | 0.034884 | 0.0036351 | 0.0036351 | 0.0018087 | 10.4206 | 0 | 0 | 0 | 2024-01-20 10:55 | FALSE | 1 | line_5271_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_5272_22 | ACLineSegment | Line | 0.034884 | 0.0045317 | 0.0045317 | 0.0023392 | 12.9908 | 0 | 0 | 0 | 2024-01-20 10:55 | FALSE | 1 | line_5272_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | tr_694_22 | Transformer | Transformer | 0.02375 | 0.016107 | 0.016107 | 0.0094003 | 67.8204 | 0 | 0 | 0 | 2024-01-20 10:55 | FALSE | 1 | tr_694_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_2657_22 | ACLineSegment | Line | 0.51338 | 0.028234 | 0.028234 | 0.017875 | 5.4996 | 0 | 0 | 0 | 2024-01-20 10:55 | FALSE | 1 | line_2657_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_2658_22 | ACLineSegment | Line | 0.51338 | 0.028234 | 0.028234 | 0.017875 | 5.4996 | 0 | 0 | 0 | 2024-01-20 10:55 | FALSE | 1 | line_2658_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | tr_786_22 | Transformer | Transformer | 0.285 | 0.028234 | 0.028234 | 0.017875 | 9.9066 | 0 | 0 | 0 | 2024-01-20 10:55 | FALSE | 1 | tr_786_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_2766_22 | ACLineSegment | Line | 0.51338 | 0.0070376 | 0.0070376 | 0.003882 | 1.3708 | 0 | 0 | 0 | 2024-01-22 04:00 | FALSE | 1 | line_2766_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_2767_22 | ACLineSegment | Line | 0.51338 | 0.0070376 | 0.0070376 | 0.003882 | 1.3708 | 0 | 0 | 0 | 2024-01-22 04:00 | FALSE | 1 | line_2767_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | tr_800_22 | Transformer | Transformer | 0.07125 | 0.0070376 | 0.0070376 | 0.003882 | 9.8774 | 0 | 0 | 0 | 2024-01-22 04:00 | FALSE | 1 | tr_800_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_2778_22 | ACLineSegment | Line | 0.034884 | 0.0050367 | 0.0050367 | 0.0025409 | 14.4385 | 0 | 0 | 0 | 2024-01-20 16:45 | FALSE | 1 | line_2778_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2779_22 | ACLineSegment | Line | 0.034884 | 0.0076329 | 0.0076329 | 0.0045635 | 21.8811 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_2779_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2780_22 | ACLineSegment | Line | 0.034884 | 0.0038824 | 0.0038824 | 0.0023373 | 11.1295 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_2780_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2787_22 | ACLineSegment | Line | 0.034884 | 0.0050367 | 0.0050367 | 0.0025409 | 14.4385 | 0 | 0 | 0 | 2024-01-20 16:45 | FALSE | 1 | line_2787_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2784_22 | ACLineSegment | Line | 0.034884 | 0.010971 | 0.010971 | 0.0069041 | 31.4504 | 0 | 0 | 0 | 2024-01-20 10:55 | FALSE | 1 | line_2784_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | tr_805_22 | Transformer | Transformer | 0.02375 | 0.017942 | 0.017942 | 0.011249 | 75.5467 | 0 | 0 | 0 | 2024-01-20 10:55 | FALSE | 1 | tr_805_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_2781_22 | ACLineSegment | Line | 0.034884 | 0.0063943 | 0.0063943 | 0.0038103 | 18.3306 | 0 | 0 | 0 | 2024-01-17 17:20 | FALSE | 1 | line_2781_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2782_22 | ACLineSegment | Line | 0.034884 | 0.0036377 | 0.0036377 | 0.0021193 | 10.4283 | 0 | 0 | 0 | 2024-01-17 17:20 | FALSE | 1 | line_2782_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2783_22 | ACLineSegment | Line | 0.034884 | 0.0033255 | 0.0033255 | 0.0018083 | 9.5332 | 0 | 0 | 0 | 2024-01-20 13:10 | FALSE | 1 | line_2783_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2785_22 | ACLineSegment | Line | 0.034884 | 0.0058088 | 0.0058088 | 0.0032564 | 16.6519 | 0 | 0 | 0 | 2024-01-20 10:55 | FALSE | 1 | line_2785_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2786_22 | ACLineSegment | Line | 0.034884 | 0.0036377 | 0.0036377 | 0.0021193 | 10.4283 | 0 | 0 | 0 | 2024-01-17 17:20 | FALSE | 1 | line_2786_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2820_22 | ACLineSegment | Line | 0.51338 | 0.0073503 | 0.0073503 | 0.0051892 | 1.4317 | 0 | 0 | 0 | 2024-01-17 10:40 | FALSE | 1 | line_2820_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_2821_22 | ACLineSegment | Line | 0.51338 | 0.0073503 | 0.0073503 | 0.0051892 | 1.4317 | 0 | 0 | 0 | 2024-01-17 10:40 | FALSE | 1 | line_2821_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | tr_802_22 | Transformer | Transformer | 0.1425 | 0.0073503 | 0.0073503 | 0.0051892 | 5.1581 | 0 | 0 | 0 | 2024-01-17 10:40 | FALSE | 1 | tr_802_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_2851_22 | ACLineSegment | Line | 0.51338 | 0.0054663 | 0.0054663 | 0.004137 | 1.0648 | 0 | 0 | 0 | 2024-07-06 02:05 | FALSE | 1 | line_2851_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_2852_22 | ACLineSegment | Line | 0.51338 | 0.0054663 | 0.0054663 | 0.004137 | 1.0648 | 0 | 0 | 0 | 2024-07-06 02:05 | FALSE | 1 | line_2852_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | tr_819_22 | Transformer | Transformer | 0.07125 | 0.0054663 | 0.0054663 | 0.004137 | 7.672 | 0 | 0 | 0 | 2024-07-06 02:05 | FALSE | 1 | tr_819_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_2877_22 | ACLineSegment | Line | 0.034884 | 0.0048244 | 0.0048244 | 0.0030955 | 13.83 | 0 | 0 | 0 | 2024-05-13 16:00 | FALSE | 1 | line_2877_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2878_22 | ACLineSegment | Line | 0.034884 | 0.027944 | 0.027944 | 0.017829 | 80.1074 | 0 | 0 | 0 | 2024-01-20 11:05 | FALSE | 1 | line_2878_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2879_22 | ACLineSegment | Line | 0.034884 | 0.019464 | 0.019464 | 0.01275 | 55.7976 | 0 | 0 | 0 | 2024-01-20 23:00 | FALSE | 1 | line_2879_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2880_22 | ACLineSegment | Line | 0.034884 | 0.0073842 | 0.0073842 | 0.0038279 | 21.1682 | 0 | 0 | 0 | 2024-07-15 04:00 | FALSE | 1 | line_2880_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2881_22 | ACLineSegment | Line | 0.034884 | 0.0048244 | 0.0048244 | 0.0030955 | 13.83 | 0 | 0 | 0 | 2024-05-13 16:00 | FALSE | 1 | line_2881_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2885_22 | ACLineSegment | Line | 0.034884 | 0.022344 | 0.022344 | 0.014703 | 64.0546 | 0 | 0 | 0 | 2024-01-20 11:05 | FALSE | 1 | line_2885_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2886_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2886_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2887_22 | ACLineSegment | Line | 0.046073 | 0.056556 | 0.056556 | 0.037052 | 122.7542 | 553 | 46.0833 | 0.52493 | 2024-01-20 11:05 | FALSE | 1 | line_2887_22 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_145 | line_2888_22 | ACLineSegment | Line | 0.034884 | 0.0051582 | 0.0051582 | 0.0026043 | 14.7869 | 0 | 0 | 0 | 2024-01-20 23:00 | FALSE | 1 | line_2888_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2889_22 | ACLineSegment | Line | 0.034884 | 0.0051968 | 0.0051968 | 0.0027956 | 14.8975 | 0 | 0 | 0 | 2024-01-20 17:50 | FALSE | 1 | line_2889_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2894_22 | ACLineSegment | Line | 0.034884 | 0.014367 | 0.014367 | 0.0086598 | 41.1855 | 0 | 0 | 0 | 2024-01-20 22:50 | FALSE | 1 | line_2894_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2895_22 | ACLineSegment | Line | 0.034884 | 0.0074795 | 0.0074795 | 0.0043797 | 21.4415 | 0 | 0 | 0 | 2024-01-20 23:00 | FALSE | 1 | line_2895_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2882_22 | ACLineSegment | Line | 0.034884 | 0.0083979 | 0.0083979 | 0.0048742 | 24.0742 | 0 | 0 | 0 | 2024-07-15 10:05 | FALSE | 1 | line_2882_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2883_22 | ACLineSegment | Line | 0.034884 | 0.0035959 | 0.0035959 | 0.002072 | 10.3084 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | line_2883_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2884_22 | ACLineSegment | Line | 0.034884 | 0.0056522 | 0.0056522 | 0.003003 | 16.203 | 0 | 0 | 0 | 2024-01-17 14:20 | FALSE | 1 | line_2884_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2899_22 | ACLineSegment | Line | 0.034884 | 0.0083979 | 0.0083979 | 0.0048742 | 24.0742 | 0 | 0 | 0 | 2024-07-15 10:05 | FALSE | 1 | line_2899_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2890_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2890_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2891_22 | ACLineSegment | Line | 0.034884 | 0.012677 | 0.012677 | 0.0078114 | 36.3417 | 0 | 0 | 0 | 2024-07-15 10:05 | FALSE | 1 | line_2891_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2892_22 | ACLineSegment | Line | 0.034884 | 0.0074377 | 0.0074377 | 0.0041728 | 21.3216 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_2892_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2893_22 | ACLineSegment | Line | 0.034884 | 0.0061335 | 0.0061335 | 0.0031961 | 17.5829 | 0 | 0 | 0 | 2024-07-15 22:55 | FALSE | 1 | line_2893_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | tr_724_22 | Transformer | Transformer | 0.0475 | 0.056556 | 0.056556 | 0.037052 | 119.0653 | 302 | 25.1667 | 0.28667 | 2024-01-20 11:05 | FALSE | 1 | tr_724_22 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_145 | line_2900_22 | ACLineSegment | Line | 0.034884 | 0.010677 | 0.010677 | 0.0062481 | 30.6075 | 0 | 0 | 0 | 2024-07-15 10:05 | FALSE | 1 | line_2900_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2901_22 | ACLineSegment | Line | 0.034884 | 0.0032307 | 0.0032307 | 0.0017148 | 9.2615 | 0 | 0 | 0 | 2024-01-21 02:00 | FALSE | 1 | line_2901_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2897_22 | ACLineSegment | Line | 0.034884 | 0.010858 | 0.010858 | 0.0069324 | 31.1268 | 0 | 0 | 0 | 2024-01-20 06:45 | FALSE | 1 | line_2897_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2905_22 | ACLineSegment | Line | 0.034884 | 0.0037386 | 0.0037386 | 0.001908 | 10.7172 | 0 | 0 | 0 | 2024-01-20 22:50 | FALSE | 1 | line_2905_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2896_22 | ACLineSegment | Line | 0.034884 | 0.006419 | 0.006419 | 0.0035796 | 18.4012 | 0 | 0 | 0 | 2024-01-21 00:55 | FALSE | 1 | line_2896_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2898_22 | ACLineSegment | Line | 0.034884 | 0.0062493 | 0.0062493 | 0.0036628 | 17.9149 | 0 | 0 | 0 | 2024-01-20 12:05 | FALSE | 1 | line_2898_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2903_22 | ACLineSegment | Line | 0.034884 | 0.006419 | 0.006419 | 0.0035796 | 18.4012 | 0 | 0 | 0 | 2024-01-21 00:55 | FALSE | 1 | line_2903_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2902_22 | ACLineSegment | Line | 0.034884 | 0.0026843 | 0.0026843 | 0.0015478 | 7.6951 | 0 | 0 | 0 | 2024-07-15 21:00 | FALSE | 1 | line_2902_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2907_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2907_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_5349_22 | ACLineSegment | Line | 0.51338 | 0.0087768 | 0.0087768 | 0.0057313 | 1.7096 | 0 | 0 | 0 | 2024-01-20 17:50 | FALSE | 1 | line_5349_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | tr_726_22 | Transformer | Transformer | 0.285 | 0.0087768 | 0.0087768 | 0.0057313 | 3.0796 | 0 | 0 | 0 | 2024-01-20 17:50 | FALSE | 1 | tr_726_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_2923_22 | ACLineSegment | Line | 0.034884 | 0.0131 | 0.0131 | 0.0076638 | 37.5535 | 0 | 0 | 0 | 2024-01-20 19:00 | FALSE | 1 | line_2923_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2924_22 | ACLineSegment | Line | 0.034884 | 0.01888 | 0.01888 | 0.011258 | 54.1238 | 0 | 0 | 0 | 2024-01-20 07:55 | FALSE | 1 | line_2924_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2925_22 | ACLineSegment | Line | 0.034884 | 0.0032494 | 0.0032494 | 0.0018809 | 9.3151 | 0 | 0 | 0 | 2024-01-21 00:55 | FALSE | 1 | line_2925_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2926_22 | ACLineSegment | Line | 0.034884 | 0.0041636 | 0.0041636 | 0.0020789 | 11.9358 | 0 | 0 | 0 | 2024-01-20 11:05 | FALSE | 1 | line_2926_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2936_22 | ACLineSegment | Line | 0.034884 | 0.0131 | 0.0131 | 0.0076638 | 37.5535 | 0 | 0 | 0 | 2024-01-20 19:00 | FALSE | 1 | line_2936_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2951_22 | ACLineSegment | Line | 0.034884 | 0.022033 | 0.022033 | 0.013504 | 63.1613 | 0 | 0 | 0 | 2024-01-20 07:55 | FALSE | 1 | line_2951_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2952_22 | ACLineSegment | Line | 0.034884 | 0.0057352 | 0.0057352 | 0.002537 | 16.4409 | 0 | 0 | 0 | 2024-01-21 00:55 | FALSE | 1 | line_2952_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2927_22 | ACLineSegment | Line | 0.034884 | 0.03099 | 0.03099 | 0.019553 | 88.8375 | 0 | 0 | 0 | 2024-01-20 20:50 | FALSE | 1 | line_2927_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2928_22 | ACLineSegment | Line | 0.034884 | 0.03099 | 0.03099 | 0.019553 | 88.8375 | 0 | 0 | 0 | 2024-01-20 20:50 | FALSE | 1 | line_2928_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2947_22 | ACLineSegment | Line | 0.034884 | 0.028688 | 0.028688 | 0.017475 | 82.2408 | 0 | 0 | 0 | 2024-01-20 18:00 | FALSE | 1 | line_2947_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2950_22 | ACLineSegment | Line | 0.034884 | 0.0046534 | 0.0046534 | 0.0022974 | 13.3397 | 0 | 0 | 0 | 2024-01-20 16:45 | FALSE | 1 | line_2950_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_5402_22 | ACLineSegment | Line | 0.034884 | 0.0042708 | 0.0042708 | 0.0023958 | 12.243 | 0 | 0 | 0 | 2024-01-21 03:55 | FALSE | 1 | line_5402_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | tr_751_22 | Transformer | Transformer | 0.0475 | 0.0546 | 0.0546 | 0.035167 | 114.9464 | 104 | 8.6667 | 0.09872 | 2024-01-21 03:55 | FALSE | 1 | tr_751_22 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_145 | line_2929_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2929_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2930_22 | ACLineSegment | Line | 0.034884 | 0.017785 | 0.017785 | 0.0091564 | 50.9854 | 0 | 0 | 0 | 2024-01-20 18:00 | FALSE | 1 | line_2930_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2931_22 | ACLineSegment | Line | 0.034884 | 0.026052 | 0.026052 | 0.015399 | 74.6842 | 0 | 0 | 0 | 2024-01-20 20:50 | FALSE | 1 | line_2931_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2932_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2932_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2933_22 | ACLineSegment | Line | 0.034884 | 0.0048262 | 0.0048262 | 0.0021695 | 13.8351 | 0 | 0 | 0 | 2024-01-20 23:00 | FALSE | 1 | line_2933_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2934_22 | ACLineSegment | Line | 0.034884 | 0.0039494 | 0.0039494 | 0.0019651 | 11.3218 | 0 | 0 | 0 | 2024-01-21 01:35 | FALSE | 1 | line_2934_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2935_22 | ACLineSegment | Line | 0.034884 | 0.0053011 | 0.0053011 | 0.0028351 | 15.1965 | 0 | 0 | 0 | 2024-01-20 20:50 | FALSE | 1 | line_2935_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2937_22 | ACLineSegment | Line | 0.034884 | 0.01192 | 0.01192 | 0.0054743 | 34.1703 | 0 | 0 | 0 | 2024-01-20 18:00 | FALSE | 1 | line_2937_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2942_22 | ACLineSegment | Line | 0.034884 | 0.0075017 | 0.0075017 | 0.0040637 | 21.5049 | 0 | 0 | 0 | 2024-01-21 03:55 | FALSE | 1 | line_2942_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2948_22 | ACLineSegment | Line | 0.034884 | 0.0039337 | 0.0039337 | 0.0022279 | 11.2766 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | line_2948_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2940_22 | ACLineSegment | Line | 0.034884 | 0.0067735 | 0.0067735 | 0.0039621 | 19.4175 | 0 | 0 | 0 | 2024-01-20 09:00 | FALSE | 1 | line_2940_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2941_22 | ACLineSegment | Line | 0.034884 | 0.0080209 | 0.0080209 | 0.0039722 | 22.9933 | 0 | 0 | 0 | 2024-01-20 19:00 | FALSE | 1 | line_2941_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2938_22 | ACLineSegment | Line | 0.034884 | 0.009112 | 0.009112 | 0.0036333 | 26.1211 | 0 | 0 | 0 | 2024-01-20 18:00 | FALSE | 1 | line_2938_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2939_22 | ACLineSegment | Line | 0.034884 | 0.0037848 | 0.0037848 | 0.00201 | 10.8499 | 0 | 0 | 0 | 2024-01-20 12:05 | FALSE | 1 | line_2939_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2949_22 | ACLineSegment | Line | 0.034884 | 0.009112 | 0.009112 | 0.0036333 | 26.1211 | 0 | 0 | 0 | 2024-01-20 18:00 | FALSE | 1 | line_2949_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2943_22 | ACLineSegment | Line | 0.034884 | 0.0025516 | 0.0025516 | 0.0013967 | 7.3147 | 0 | 0 | 0 | 2024-01-20 15:00 | FALSE | 1 | line_2943_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2946_22 | ACLineSegment | Line | 0.034884 | 0.0046846 | 0.0046846 | 0.0027338 | 13.4292 | 0 | 0 | 0 | 2024-07-15 21:00 | FALSE | 1 | line_2946_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2944_22 | ACLineSegment | Line | 0.034884 | 0.0025516 | 0.0025516 | 0.0013967 | 7.3147 | 0 | 0 | 0 | 2024-01-20 15:00 | FALSE | 1 | line_2944_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_2981_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2981_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_5365_22 | ACLineSegment | Line | 0.51338 | 0.0053537 | 0.0053537 | 0.00392 | 1.0428 | 0 | 0 | 0 | 2024-06-26 22:55 | FALSE | 1 | line_5365_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | tr_734_22 | Transformer | Transformer | 0.285 | 0.0053537 | 0.0053537 | 0.00392 | 1.8785 | 0 | 0 | 0 | 2024-06-26 22:55 | FALSE | 1 | tr_734_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_3004_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_3004_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_5368_22 | ACLineSegment | Line | 0.51338 | 0.0060784 | 0.0060784 | 0.0041751 | 1.184 | 0 | 0 | 0 | 2024-07-06 01:05 | FALSE | 1 | line_5368_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | tr_735_22 | Transformer | Transformer | 0.1425 | 0.0060784 | 0.0060784 | 0.0041751 | 4.2655 | 0 | 0 | 0 | 2024-07-06 01:05 | FALSE | 1 | tr_735_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_3008_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_3008_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_5392_22 | ACLineSegment | Line | 0.51338 | 0.0050705 | 0.0050705 | 0.0036385 | 0.98768 | 0 | 0 | 0 | 2024-01-20 06:45 | FALSE | 1 | line_5392_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | tr_746_22 | Transformer | Transformer | 0.285 | 0.0050705 | 0.0050705 | 0.0036385 | 1.7791 | 0 | 0 | 0 | 2024-01-20 06:45 | FALSE | 1 | tr_746_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_3299_22 | ACLineSegment | Line | 0.034884 | 0.010448 | 0.010448 | 0.0057277 | 29.9517 | 0 | 0 | 0 | 2024-07-15 06:45 | FALSE | 1 | line_3299_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_3300_22 | ACLineSegment | Line | 0.034884 | 0.010448 | 0.010448 | 0.0057277 | 29.9517 | 0 | 0 | 0 | 2024-07-15 06:45 | FALSE | 1 | line_3300_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_3309_22 | ACLineSegment | Line | 0.034884 | 0.015321 | 0.015321 | 0.0093242 | 43.921 | 0 | 0 | 0 | 2024-07-14 23:10 | FALSE | 1 | line_3309_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_3310_22 | ACLineSegment | Line | 0.034884 | 0.008268 | 0.008268 | 0.0051557 | 23.7019 | 0 | 0 | 0 | 2024-07-10 22:55 | FALSE | 1 | line_3310_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_3313_22 | ACLineSegment | Line | 0.034884 | 0.0041153 | 0.0041153 | 0.0020598 | 11.7972 | 0 | 0 | 0 | 2024-01-20 19:00 | FALSE | 1 | line_3313_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_3314_22 | ACLineSegment | Line | 0.034884 | 0.0078348 | 0.0078348 | 0.0038371 | 22.4599 | 0 | 0 | 0 | 2024-01-21 02:00 | FALSE | 1 | line_3314_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_3301_22 | ACLineSegment | Line | 0.034884 | 0.010625 | 0.010625 | 0.0066542 | 30.4572 | 0 | 0 | 0 | 2024-07-16 00:50 | FALSE | 1 | line_3301_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_3302_22 | ACLineSegment | Line | 0.034884 | 0.0037391 | 0.0037391 | 0.0019294 | 10.7187 | 0 | 0 | 0 | 2024-01-17 16:05 | FALSE | 1 | line_3302_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_3303_22 | ACLineSegment | Line | 0.034884 | 0.017678 | 0.017678 | 0.011867 | 50.6779 | 0 | 0 | 0 | 2024-01-21 02:00 | FALSE | 1 | line_3303_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_3304_22 | ACLineSegment | Line | 0.034884 | 0.0062339 | 0.0062339 | 0.003765 | 17.8708 | 0 | 0 | 0 | 2024-07-15 10:05 | FALSE | 1 | line_3304_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_3305_22 | ACLineSegment | Line | 0.034884 | 0.004741 | 0.004741 | 0.0026953 | 13.5909 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | line_3305_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_3306_22 | ACLineSegment | Line | 0.034884 | 0.0069194 | 0.0069194 | 0.0041585 | 19.8358 | 0 | 0 | 0 | 2024-07-16 00:50 | FALSE | 1 | line_3306_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_3308_22 | ACLineSegment | Line | 0.034884 | 0.0037391 | 0.0037391 | 0.0019294 | 10.7187 | 0 | 0 | 0 | 2024-01-17 16:05 | FALSE | 1 | line_3308_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | tr_903_22 | Transformer | Transformer | 0.0475 | 0.030559 | 0.030559 | 0.020499 | 64.3342 | 0 | 0 | 0 | 2024-01-21 02:00 | FALSE | 1 | tr_903_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_3307_22 | ACLineSegment | Line | 0.034884 | 0.004741 | 0.004741 | 0.0026953 | 13.5909 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | line_3307_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_3317_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_3317_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_5956_22 | ACLineSegment | Line | 0.51338 | 0.0027211 | 0.0027211 | 0.0021023 | 0.53003 | 0 | 0 | 0 | 2024-01-20 18:00 | FALSE | 1 | line_5956_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | tr_1044_22 | Transformer | Transformer | 0.285 | 0.0027211 | 0.0027211 | 0.0021023 | 0.95477 | 0 | 0 | 0 | 2024-01-20 18:00 | FALSE | 1 | tr_1044_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_3367_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_3367_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_5931_22 | ACLineSegment | Line | 0.51338 | 0.0069984 | 0.0069984 | 0.0046798 | 1.3632 | 0 | 0 | 0 | 2024-01-21 03:55 | FALSE | 1 | line_5931_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | tr_1032_22 | Transformer | Transformer | 0.07125 | 0.0069984 | 0.0069984 | 0.0046798 | 9.8223 | 0 | 0 | 0 | 2024-01-21 03:55 | FALSE | 1 | tr_1032_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_3412_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_3412_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_5783_22 | ACLineSegment | Line | 0.025406 | 0.0058267 | 0.0058267 | 0.0042554 | 22.9345 | 0 | 0 | 0 | 2024-01-20 21:05 | FALSE | 1 | line_5783_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | tr_963_22 | Transformer | Transformer | 0.02375 | 0.0058267 | 0.0058267 | 0.0042554 | 24.5333 | 0 | 0 | 0 | 2024-01-20 21:05 | FALSE | 1 | tr_963_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_345_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_345_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_6029_22 | ACLineSegment | Line | 0.22905 | 0.019818 | 0.019818 | 0.013531 | 8.6523 | 0 | 0 | 0 | 2024-01-17 18:55 | FALSE | 1 | line_6029_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | tr_1079_22 | Transformer | Transformer | 0.07125 | 0.019818 | 0.019818 | 0.013531 | 27.8145 | 0 | 0 | 0 | 2024-01-17 18:55 | FALSE | 1 | tr_1079_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_3472_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_3472_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_5817_22 | ACLineSegment | Line | 0.51338 | 0.0046025 | 0.0046025 | 0.0034773 | 0.8965 | 0 | 0 | 0 | 2024-01-21 13:00 | FALSE | 1 | line_5817_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | tr_979_22 | Transformer | Transformer | 0.07125 | 0.0046025 | 0.0046025 | 0.0034773 | 6.4596 | 0 | 0 | 0 | 2024-01-21 13:00 | FALSE | 1 | tr_979_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_3478_22 | ACLineSegment | Line | 0.51338 | 0.0050314 | 0.0050314 | 0.0038125 | 0.98006 | 0 | 0 | 0 | 2024-07-15 10:05 | FALSE | 1 | line_3478_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_3479_22 | ACLineSegment | Line | 0.51338 | 0.0050314 | 0.0050314 | 0.0038125 | 0.98006 | 0 | 0 | 0 | 2024-07-15 10:05 | FALSE | 1 | line_3479_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_3480_22 | ACLineSegment | Line | 0.51338 | 0.003828 | 0.003828 | 0.0028298 | 0.74565 | 0 | 0 | 0 | 2024-01-17 16:05 | FALSE | 1 | line_3480_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | tr_997_22 | Transformer | Transformer | 0.095 | 0.0075031 | 0.0075031 | 0.0059081 | 7.898 | 0 | 0 | 0 | 2024-01-20 12:05 | FALSE | 1 | tr_997_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_3481_22 | ACLineSegment | Line | 0.51338 | 0.003828 | 0.003828 | 0.0028298 | 0.74565 | 0 | 0 | 0 | 2024-01-17 16:05 | FALSE | 1 | line_3481_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_3483_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_3483_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_5865_22 | ACLineSegment | Line | 0.025406 | 0.016092 | 0.016092 | 0.011562 | 63.3382 | 0 | 0 | 0 | 2024-07-15 09:55 | FALSE | 1 | line_5865_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | tr_1000_22 | Transformer | Transformer | 0.02375 | 0.016092 | 0.016092 | 0.011562 | 67.7538 | 0 | 0 | 0 | 2024-07-15 09:55 | FALSE | 1 | tr_1000_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_3520_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_3520_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_5883_22 | ACLineSegment | Line | 0.51338 | 0.0055463 | 0.0055463 | 0.0040001 | 1.0803 | 0 | 0 | 0 | 2024-07-15 03:55 | FALSE | 1 | line_5883_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | tr_1007_22 | Transformer | Transformer | 0.1425 | 0.0055463 | 0.0055463 | 0.0040001 | 3.8921 | 0 | 0 | 0 | 2024-07-15 03:55 | FALSE | 1 | tr_1007_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_359_22 | ACLineSegment | Line | 0.025406 | 0.011318 | 0.011318 | 0.0099284 | 44.5479 | 0 | 0 | 0 | 2024-07-14 22:55 | FALSE | 1 | line_359_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_360_22 | ACLineSegment | Line | 0.025406 | 0.011318 | 0.011318 | 0.0099284 | 44.5479 | 0 | 0 | 0 | 2024-07-14 22:55 | FALSE | 1 | line_360_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_361_22 | ACLineSegment | Line | 0.025406 | 0.0052238 | 0.0052238 | 0.0030728 | 20.5615 | 0 | 0 | 0 | 2024-07-15 05:55 | FALSE | 1 | line_361_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | tr_1086_22 | Transformer | Transformer | 0.0475 | 0.015565 | 0.015565 | 0.012227 | 32.7687 | 0 | 0 | 0 | 2024-01-17 20:05 | FALSE | 1 | tr_1086_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_362_22 | ACLineSegment | Line | 0.025406 | 0.0052238 | 0.0052238 | 0.0030728 | 20.5615 | 0 | 0 | 0 | 2024-07-15 05:55 | FALSE | 1 | line_362_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_378_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_378_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_6071_22 | ACLineSegment | Line | 0.51338 | 0.01777 | 0.01777 | 0.012414 | 3.4614 | 0 | 0 | 0 | 2024-01-20 21:05 | FALSE | 1 | line_6071_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | tr_1101_22 | Transformer | Transformer | 0.285 | 0.01777 | 0.01777 | 0.012414 | 6.2351 | 0 | 0 | 0 | 2024-01-20 21:05 | FALSE | 1 | tr_1101_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | tr_260_22 | Transformer | Transformer | 0.02375 | 0.0029266 | 0.0029266 | 0.001882 | 12.3225 | 0 | 0 | 0 | 2024-01-20 23:00 | FALSE | 1 | tr_260_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_4220_22 | ACLineSegment | Line | 0.034884 | 0.0029266 | 0.0029266 | 0.001882 | 8.3896 | 0 | 0 | 0 | 2024-01-20 23:00 | FALSE | 1 | line_4220_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_4279_22 | ACLineSegment | Line | 12.3112 | 0.50234 | 0.50234 | 0.3838 | 4.0803 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_4279_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | tr_279_22 | Transformer | Transformer | 0.1425 | 0.0057166 | 0.0057166 | 0.004261 | 4.0117 | 0 | 0 | 0 | 2024-07-05 07:00 | FALSE | 1 | tr_279_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_4227_22 | ACLineSegment | Line | 0.034884 | 0.007818 | 0.007818 | 0.0051576 | 22.4118 | 0 | 0 | 0 | 2024-01-20 13:10 | FALSE | 1 | line_4227_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_4242_22 | ACLineSegment | Line | 13.5424 | 0.28642 | 0.28642 | 0.21686 | 2.115 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_4242_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_4243_22 | ACLineSegment | Line | 13.5424 | 0.30488 | 0.30488 | 0.23169 | 2.2513 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_4243_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | tr_266_22 | Transformer | Transformer | 0.07125 | 0.0088625 | 0.0088625 | 0.0067385 | 12.4386 | 0 | 0 | 0 | 2024-01-17 12:30 | FALSE | 1 | tr_266_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_4396_22 | ACLineSegment | Line | 13.5424 | 0.16283 | 0.16283 | 0.12055 | 1.2024 | 0 | 0 | 0 | 2024-01-17 23:00 | FALSE | 1 | line_4396_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_4397_22 | ACLineSegment | Line | 13.5424 | 0.12395 | 0.12395 | 0.094374 | 0.91526 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_4397_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_5609_22 | ACLineSegment | Line | 13.5424 | 0.30733 | 0.30733 | 0.23454 | 2.2694 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_5609_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | tr_878_22 | Transformer | Transformer | 0.07125 | 0.0047254 | 0.0047254 | 0.0034882 | 6.6321 | 0 | 0 | 0 | 2024-01-20 17:50 | FALSE | 1 | tr_878_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_4244_22 | ACLineSegment | Line | 13.5424 | 0.019063 | 0.019063 | 0.011375 | 0.14077 | 0 | 0 | 0 | 2024-07-17 22:55 | FALSE | 1 | line_4244_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_5671_22 | ACLineSegment | Line | 13.5424 | 0.012234 | 0.012234 | 0.006147 | 0.090341 | 0 | 0 | 0 | 2024-07-05 21:10 | FALSE | 1 | line_5671_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_4245_22 | ACLineSegment | Line | 0.51338 | 0.0088625 | 0.0088625 | 0.0067385 | 1.7263 | 0 | 0 | 0 | 2024-01-17 12:30 | FALSE | 1 | line_4245_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_4280_22 | ACLineSegment | Line | 0.51338 | 0.0057166 | 0.0057166 | 0.004261 | 1.1135 | 0 | 0 | 0 | 2024-07-05 07:00 | FALSE | 1 | line_4280_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_4288_22 | ACLineSegment | Line | 0.94778 | 0.0056763 | 0.0056763 | 0.0031201 | 0.5989 | 0 | 0 | 0 | 2024-01-20 10:55 | FALSE | 1 | line_4288_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_4319_22 | ACLineSegment | Line | 0.94778 | 0.0036432 | 0.0036432 | 0.0022154 | 0.38439 | 0 | 0 | 0 | 2024-01-21 03:55 | FALSE | 1 | line_4319_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | tr_295_22 | Transformer | Transformer | 0.02375 | 0.0036432 | 0.0036432 | 0.0022154 | 15.3398 | 0 | 0 | 0 | 2024-01-21 03:55 | FALSE | 1 | tr_295_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | tr_733_22 | Transformer | Transformer | 0.02375 | 0.006334 | 0.006334 | 0.0040792 | 26.6693 | 0 | 0 | 0 | 2024-07-14 11:00 | FALSE | 1 | tr_733_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_4320_22 | ACLineSegment | Line | 0.025406 | 0.0036432 | 0.0036432 | 0.0022154 | 14.3401 | 0 | 0 | 0 | 2024-01-21 03:55 | FALSE | 1 | line_4320_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_433_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_433_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_6099_22 | ACLineSegment | Line | 0.51338 | 0.0067717 | 0.0067717 | 0.0040779 | 1.319 | 0 | 0 | 0 | 2024-07-14 03:55 | FALSE | 1 | line_6099_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | tr_1114_22 | Transformer | Transformer | 0.1425 | 0.0067717 | 0.0067717 | 0.0040779 | 4.7521 | 0 | 0 | 0 | 2024-07-14 03:55 | FALSE | 1 | tr_1114_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_4372_22 | ACLineSegment | Line | 12.3112 | 0.45307 | 0.45307 | 0.34199 | 3.6801 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_4372_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_4373_22 | ACLineSegment | Line | 12.3112 | 0.45803 | 0.45803 | 0.34525 | 3.7204 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_4373_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_6028_22 | ACLineSegment | Line | 13.5424 | 0.14606 | 0.14606 | 0.1095 | 1.0786 | 0 | 0 | 0 | 2024-01-17 23:00 | FALSE | 1 | line_6028_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_6138_22 | ACLineSegment | Line | 13.5424 | 0.1186 | 0.1186 | 0.090852 | 0.8758 | 0 | 0 | 0 | 2024-01-20 18:00 | FALSE | 1 | line_6138_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | tr_1134_22 | Transformer | Transformer | 0.07125 | 0.006119 | 0.006119 | 0.0045371 | 8.588 | 0 | 0 | 0 | 2024-01-22 04:00 | FALSE | 1 | tr_1134_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_4471_22 | ACLineSegment | Line | 13.5424 | 0.021032 | 0.021032 | 0.016836 | 0.15531 | 0 | 0 | 0 | 2024-07-15 22:55 | FALSE | 1 | line_4471_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_5366_22 | ACLineSegment | Line | 13.5424 | 0.037523 | 0.037523 | 0.029339 | 0.27708 | 0 | 0 | 0 | 2024-07-15 16:00 | FALSE | 1 | line_5366_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | tr_1371_22 | Transformer | Transformer | 0.285 | 0.008147 | 0.008147 | 0.0061029 | 2.8586 | 0 | 0 | 0 | 2024-07-15 06:45 | FALSE | 1 | tr_1371_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_4633_22 | ACLineSegment | Line | 13.5424 | 0.5295 | 0.5295 | 0.40912 | 3.9099 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_4633_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_4634_22 | ACLineSegment | Line | 13.5424 | 0.52167 | 0.52167 | 0.40302 | 3.8521 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_4634_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_4635_22 | ACLineSegment | Line | 13.5424 | 0.004563 | 0.004563 | 0.0034043 | 0.033694 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | line_4635_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_6069_22 | ACLineSegment | Line | 13.5424 | 0.0058091 | 0.0058091 | 0.0044928 | 0.042896 | 0 | 0 | 0 | 2024-07-06 00:55 | FALSE | 1 | line_6069_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_6070_22 | ACLineSegment | Line | 13.5424 | 0.54693 | 0.54693 | 0.42285 | 4.0387 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_6070_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | tr_1205_22 | Transformer | Transformer | 0.1425 | 0.0061468 | 0.0061468 | 0.0046499 | 4.3135 | 0 | 0 | 0 | 2024-01-20 07:55 | FALSE | 1 | tr_1205_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | tr_1449_22 | Transformer | Transformer | 0.475 | 0.004563 | 0.004563 | 0.0034043 | 0.96063 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | tr_1449_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_4718_22 | ACLineSegment | Line | 12.3112 | 0.020923 | 0.020923 | 0.016051 | 0.16995 | 0 | 0 | 0 | 2024-07-16 03:00 | FALSE | 1 | line_4718_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_4719_22 | ACLineSegment | Line | 12.3112 | 0.016214 | 0.016214 | 0.012419 | 0.1317 | 0 | 0 | 0 | 2024-01-20 21:05 | FALSE | 1 | line_4719_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_4729_22 | ACLineSegment | Line | 12.3112 | 0.02875 | 0.02875 | 0.020898 | 0.23353 | 0 | 0 | 0 | 2024-01-22 04:00 | FALSE | 1 | line_4729_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_4733_22 | ACLineSegment | Line | 13.5424 | 0.0054469 | 0.0054469 | 0.0038812 | 0.040222 | 0 | 0 | 0 | 2024-01-21 01:35 | FALSE | 1 | line_4733_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_5247_22 | ACLineSegment | Line | 13.5424 | 0.0067317 | 0.0067317 | 0.0046434 | 0.049708 | 0 | 0 | 0 | 2024-07-14 22:55 | FALSE | 1 | line_5247_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_5497_22 | ACLineSegment | Line | 13.5424 | 0.014211 | 0.014211 | 0.011291 | 0.10494 | 0 | 0 | 0 | 2024-01-17 15:55 | FALSE | 1 | line_5497_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_5401_22 | ACLineSegment | Line | 13.5424 | 0.098809 | 0.098809 | 0.069422 | 0.72963 | 0 | 0 | 0 | 2024-01-20 18:00 | FALSE | 1 | line_5401_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | tr_935_22 | Transformer | Transformer | 0.02375 | 0.0057052 | 0.0057052 | 0.0027806 | 24.0217 | 0 | 0 | 0 | 2024-01-20 10:55 | FALSE | 1 | tr_935_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_5672_22 | ACLineSegment | Line | 13.5424 | 0.0044328 | 0.0044328 | 0.0023726 | 0.032733 | 0 | 0 | 0 | 2024-01-20 12:05 | FALSE | 1 | line_5672_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | tr_1264_22 | Transformer | Transformer | 0.02375 | 0.0044328 | 0.0044328 | 0.0023726 | 18.6643 | 0 | 0 | 0 | 2024-01-20 12:05 | FALSE | 1 | tr_1264_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_481_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_481_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_6139_22 | ACLineSegment | Line | 0.51338 | 0.006119 | 0.006119 | 0.0045371 | 1.1919 | 0 | 0 | 0 | 2024-01-22 04:00 | FALSE | 1 | line_6139_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_4812_22 | ACLineSegment | Line | 13.5424 | 0.10807 | 0.10807 | 0.082819 | 0.79798 | 0 | 0 | 0 | 2024-07-16 00:50 | FALSE | 1 | line_4812_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_4813_22 | ACLineSegment | Line | 13.5424 | 0.10535 | 0.10535 | 0.08003 | 0.77795 | 0 | 0 | 0 | 2024-01-17 23:00 | FALSE | 1 | line_4813_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | tr_488_22 | Transformer | Transformer | 0.07125 | 0.0044543 | 0.0044543 | 0.0034342 | 6.2516 | 0 | 0 | 0 | 2024-07-16 00:50 | FALSE | 1 | tr_488_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_6309_22 | ACLineSegment | Line | 13.5424 | 0.12344 | 0.12344 | 0.095597 | 0.9115 | 0 | 0 | 0 | 2024-01-17 23:00 | FALSE | 1 | line_6309_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | tr_1323_22 | Transformer | Transformer | 0.02375 | 0.0048042 | 0.0048042 | 0.0026522 | 20.2284 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | tr_1323_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_5367_22 | ACLineSegment | Line | 13.5424 | 0.10131 | 0.10131 | 0.076649 | 0.74807 | 0 | 0 | 0 | 2024-01-17 23:00 | FALSE | 1 | line_5367_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | tr_1414_22 | Transformer | Transformer | 0.02375 | 0.0064021 | 0.0064021 | 0.0039522 | 26.9564 | 0 | 0 | 0 | 2024-01-21 03:55 | FALSE | 1 | tr_1414_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_4814_22 | ACLineSegment | Line | 0.51338 | 0.0044543 | 0.0044543 | 0.0034342 | 0.86764 | 0 | 0 | 0 | 2024-07-16 00:50 | FALSE | 1 | line_4814_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_494_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_494_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_6195_22 | ACLineSegment | Line | 0.51338 | 0.0041942 | 0.0041942 | 0.0030209 | 0.81698 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | line_6195_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | tr_1163_22 | Transformer | Transformer | 0.07125 | 0.0041942 | 0.0041942 | 0.0030209 | 5.8866 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | tr_1163_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_507_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_507_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_6264_22 | ACLineSegment | Line | 0.51338 | 0.0043182 | 0.0043182 | 0.0030723 | 0.84114 | 0 | 0 | 0 | 2024-01-17 16:05 | FALSE | 1 | line_6264_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | tr_1195_22 | Transformer | Transformer | 0.07125 | 0.0043182 | 0.0043182 | 0.0030723 | 6.0607 | 0 | 0 | 0 | 2024-01-17 16:05 | FALSE | 1 | tr_1195_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_5344_22 | ACLineSegment | Line | 13.5424 | 0.57322 | 0.57322 | 0.43987 | 4.2328 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_5344_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_6170_22 | ACLineSegment | Line | 13.5424 | 0.69166 | 0.69166 | 0.52887 | 5.1074 | 0 | 0 | 0 | 2024-01-21 04:00 | TRUE | 1 | line_6170_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_521_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_521_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_6237_22 | ACLineSegment | Line | 0.51338 | 0.0058091 | 0.0058091 | 0.0044928 | 1.1315 | 0 | 0 | 0 | 2024-07-06 00:55 | FALSE | 1 | line_6237_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | tr_1179_22 | Transformer | Transformer | 0.475 | 0.0058091 | 0.0058091 | 0.0044928 | 1.223 | 0 | 0 | 0 | 2024-07-06 00:55 | FALSE | 1 | tr_1179_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_5232_22 | ACLineSegment | Line | 12.3112 | 0.022568 | 0.022568 | 0.014818 | 0.18331 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_5232_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_5239_22 | ACLineSegment | Line | 12.3112 | 0.031376 | 0.031376 | 0.022858 | 0.25485 | 0 | 0 | 0 | 2024-07-15 05:55 | FALSE | 1 | line_5239_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_5240_22 | ACLineSegment | Line | 12.3112 | 0.053843 | 0.053843 | 0.036724 | 0.43735 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_5240_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_5457_22 | ACLineSegment | Line | 12.3112 | 0.069712 | 0.069712 | 0.051896 | 0.56625 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_5457_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_5267_22 | ACLineSegment | Line | 13.5424 | 0.054428 | 0.054428 | 0.035807 | 0.40191 | 0 | 0 | 0 | 2024-01-17 23:00 | FALSE | 1 | line_5267_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_5268_22 | ACLineSegment | Line | 13.5424 | 0.069364 | 0.069364 | 0.046036 | 0.5122 | 0 | 0 | 0 | 2024-01-17 23:00 | FALSE | 1 | line_5268_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_5269_22 | ACLineSegment | Line | 13.5424 | 0.0043182 | 0.0043182 | 0.0030723 | 0.031887 | 0 | 0 | 0 | 2024-01-17 16:05 | FALSE | 1 | line_5269_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_5273_22 | ACLineSegment | Line | 13.5424 | 0.01305 | 0.01305 | 0.0088598 | 0.096363 | 0 | 0 | 0 | 2024-01-17 10:40 | FALSE | 1 | line_5273_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_6194_22 | ACLineSegment | Line | 13.5424 | 0.0041942 | 0.0041942 | 0.0030209 | 0.030971 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | line_6194_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | tr_1322_22 | Transformer | Transformer | 0.02375 | 0.010091 | 0.010091 | 0.0062569 | 42.4891 | 0 | 0 | 0 | 2024-01-17 10:40 | FALSE | 1 | tr_1322_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_5482_22 | ACLineSegment | Line | 13.5424 | 0.55581 | 0.55581 | 0.42882 | 4.1042 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_5482_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_5347_22 | ACLineSegment | Line | 2.3694 | 0.0058267 | 0.0058267 | 0.0042554 | 0.24591 | 0 | 0 | 0 | 2024-01-20 21:05 | FALSE | 1 | line_5347_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_5348_22 | ACLineSegment | Line | 12.3112 | 0.012812 | 0.012812 | 0.0091585 | 0.10407 | 0 | 0 | 0 | 2024-01-20 21:05 | FALSE | 1 | line_5348_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | tr_1344_22 | Transformer | Transformer | 0.02375 | 0.0050845 | 0.0050845 | 0.0039226 | 21.4082 | 0 | 0 | 0 | 2024-01-20 13:10 | FALSE | 1 | tr_1344_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_5363_22 | ACLineSegment | Line | 0.034884 | 0.0038167 | 0.0038167 | 0.0021516 | 10.9411 | 0 | 0 | 0 | 2024-07-16 03:00 | FALSE | 1 | line_5363_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_5364_22 | ACLineSegment | Line | 0.034884 | 0.0039623 | 0.0039623 | 0.0021371 | 11.3586 | 0 | 0 | 0 | 2024-01-20 11:05 | FALSE | 1 | line_5364_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_6314_22 | ACLineSegment | Line | 13.5424 | 0.029899 | 0.029899 | 0.022479 | 0.22078 | 0 | 0 | 0 | 2024-01-21 09:00 | FALSE | 1 | line_6314_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | tr_1443_22 | Transformer | Transformer | 0.475 | 0.0042812 | 0.0042812 | 0.0031568 | 0.90131 | 0 | 0 | 0 | 2024-01-20 15:00 | FALSE | 1 | tr_1443_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_5477_22 | ACLineSegment | Line | 12.3112 | 0.0073503 | 0.0073503 | 0.0051892 | 0.059704 | 0 | 0 | 0 | 2024-01-17 10:40 | FALSE | 1 | line_5477_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_5955_22 | ACLineSegment | Line | 13.5424 | 0.55381 | 0.55381 | 0.42712 | 4.0895 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_5955_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_5536_22 | ACLineSegment | Line | 13.5424 | 0.025219 | 0.025219 | 0.018491 | 0.18622 | 0 | 0 | 0 | 2024-01-20 15:00 | FALSE | 1 | line_5536_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | tr_841_22 | Transformer | Transformer | 0.07125 | 0.025219 | 0.025219 | 0.018491 | 35.3954 | 0 | 0 | 0 | 2024-01-20 15:00 | FALSE | 1 | tr_841_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | tr_1222_22 | Transformer | Transformer | 0.07125 | 0.0072454 | 0.0072454 | 0.0050582 | 10.1689 | 0 | 0 | 0 | 2024-01-22 04:00 | FALSE | 1 | tr_1222_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_5537_22 | ACLineSegment | Line | 0.22905 | 0.025219 | 0.025219 | 0.018491 | 11.0105 | 0 | 0 | 0 | 2024-01-20 15:00 | FALSE | 1 | line_5537_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_5610_22 | ACLineSegment | Line | 0.51338 | 0.0047254 | 0.0047254 | 0.0034882 | 0.92044 | 0 | 0 | 0 | 2024-01-20 17:50 | FALSE | 1 | line_5610_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_561_22 | ACLineSegment | Line | 0.51338 | 0.0045197 | 0.0045197 | 0.0030696 | 0.88038 | 0 | 0 | 0 | 2024-01-20 10:55 | FALSE | 1 | line_561_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_562_22 | ACLineSegment | Line | 0.51338 | 0.0045197 | 0.0045197 | 0.0030696 | 0.88038 | 0 | 0 | 0 | 2024-01-20 10:55 | FALSE | 1 | line_562_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | tr_1202_22 | Transformer | Transformer | 0.285 | 0.0045197 | 0.0045197 | 0.0030696 | 1.5859 | 0 | 0 | 0 | 2024-01-20 10:55 | FALSE | 1 | tr_1202_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | tr_908_22 | Transformer | Transformer | 0.02375 | 0.0095907 | 0.0095907 | 0.0048069 | 40.3818 | 0 | 0 | 0 | 2024-07-17 23:00 | FALSE | 1 | tr_908_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_5673_22 | ACLineSegment | Line | 0.034884 | 0.0095907 | 0.0095907 | 0.0048069 | 27.4934 | 0 | 0 | 0 | 2024-07-17 23:00 | FALSE | 1 | line_5673_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_5730_22 | ACLineSegment | Line | 0.034884 | 0.0057052 | 0.0057052 | 0.0027806 | 16.3549 | 0 | 0 | 0 | 2024-01-20 10:55 | FALSE | 1 | line_5730_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_576_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_576_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_6271_22 | ACLineSegment | Line | 0.51338 | 0.0060528 | 0.0060528 | 0.003488 | 1.179 | 0 | 0 | 0 | 2024-01-20 10:55 | FALSE | 1 | line_6271_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | tr_1199_22 | Transformer | Transformer | 0.095 | 0.0060528 | 0.0060528 | 0.003488 | 6.3714 | 0 | 0 | 0 | 2024-01-20 10:55 | FALSE | 1 | tr_1199_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_578_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_578_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_6281_22 | ACLineSegment | Line | 0.51338 | 0.0061468 | 0.0061468 | 0.0046499 | 1.1973 | 0 | 0 | 0 | 2024-01-20 07:55 | FALSE | 1 | line_6281_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_580_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_580_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_6310_22 | ACLineSegment | Line | 0.51338 | 0.022626 | 0.022626 | 0.016377 | 4.4072 | 0 | 0 | 0 | 2024-06-24 23:05 | FALSE | 1 | line_6310_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | tr_1220_22 | Transformer | Transformer | 0.07125 | 0.022626 | 0.022626 | 0.016377 | 31.7556 | 0 | 0 | 0 | 2024-06-24 23:05 | FALSE | 1 | tr_1220_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | tr_1255_22 | Transformer | Transformer | 0.1425 | 0.024461 | 0.024461 | 0.015342 | 17.1658 | 0 | 0 | 0 | 2024-07-15 08:50 | FALSE | 1 | tr_1255_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | tr_1373_22 | Transformer | Transformer | 0.02375 | 0.0013657 | 0.0013657 | 0.00081676 | 5.7504 | 0 | 0 | 0 | 2024-01-20 11:05 | FALSE | 1 | tr_1373_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_5836_22 | ACLineSegment | Line | 0.22905 | 0.0059606 | 0.0059606 | 0.0044451 | 2.6024 | 0 | 0 | 0 | 2024-01-20 09:00 | FALSE | 1 | line_5836_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_5863_22 | ACLineSegment | Line | 12.3112 | 0.47897 | 0.47897 | 0.36355 | 3.8905 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_5863_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_5864_22 | ACLineSegment | Line | 12.3112 | 0.46752 | 0.46752 | 0.35432 | 3.7975 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_5864_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | tr_1281_22 | Transformer | Transformer | 0.1425 | 0.0086569 | 0.0086569 | 0.0060557 | 6.075 | 0 | 0 | 0 | 2024-07-16 03:00 | FALSE | 1 | tr_1281_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_5881_22 | ACLineSegment | Line | 12.3112 | 0.44777 | 0.44777 | 0.33804 | 3.6371 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_5881_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_5882_22 | ACLineSegment | Line | 12.3112 | 0.37455 | 0.37455 | 0.28484 | 3.0423 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_5882_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_6098_22 | ACLineSegment | Line | 12.3112 | 0.37124 | 0.37124 | 0.28162 | 3.0155 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_6098_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | tr_1334_22 | Transformer | Transformer | 0.285 | 0.0078295 | 0.0078295 | 0.0053322 | 2.7472 | 0 | 0 | 0 | 2024-01-17 14:20 | FALSE | 1 | tr_1334_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_6040_22 | ACLineSegment | Line | 12.3112 | 0.34233 | 0.34233 | 0.26096 | 2.7806 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_6040_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | tr_1331_22 | Transformer | Transformer | 0.07125 | 0.0067082 | 0.0067082 | 0.0051113 | 9.4151 | 0 | 0 | 0 | 2024-06-27 02:00 | FALSE | 1 | tr_1331_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_145 | line_6270_22 | ACLineSegment | Line | 12.3112 | 0.48173 | 0.48173 | 0.36648 | 3.913 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_6270_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_6277_22 | ACLineSegment | Line | 12.3112 | 0.36912 | 0.36912 | 0.27945 | 2.9983 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_6277_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_6315_22 | ACLineSegment | Line | 0.51338 | 0.0072454 | 0.0072454 | 0.0050582 | 1.4113 | 0 | 0 | 0 | 2024-01-22 04:00 | FALSE | 1 | line_6315_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_6371_22 | ACLineSegment | Line | 0.51338 | 0.024461 | 0.024461 | 0.015342 | 4.7647 | 0 | 0 | 0 | 2024-07-15 08:50 | FALSE | 1 | line_6371_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_6392_22 | ACLineSegment | Line | 0.034884 | 0.0044328 | 0.0044328 | 0.0023726 | 12.7074 | 0 | 0 | 0 | 2024-01-20 12:05 | FALSE | 1 | line_6392_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_6416_22 | ACLineSegment | Line | 0.51338 | 0.0086569 | 0.0086569 | 0.0060557 | 1.6863 | 0 | 0 | 0 | 2024-07-16 03:00 | FALSE | 1 | line_6416_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_673_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_673_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_6480_22 | ACLineSegment | Line | 0.034884 | 0.0064616 | 0.0064616 | 0.0038041 | 18.5233 | 0 | 0 | 0 | 2024-01-17 07:00 | FALSE | 1 | line_6480_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_6481_22 | ACLineSegment | Line | 0.034884 | 0.0048113 | 0.0048113 | 0.0026765 | 13.7926 | 0 | 0 | 0 | 2024-01-20 19:00 | FALSE | 1 | line_6481_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_709_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_709_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_710_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_710_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_6482_22 | ACLineSegment | Line | 0.034884 | 0.0048042 | 0.0048042 | 0.0026522 | 13.7722 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | line_6482_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_726_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_726_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_6493_22 | ACLineSegment | Line | 0.51338 | 0.0041358 | 0.0041358 | 0.0028901 | 0.80559 | 0 | 0 | 0 | 2024-01-21 02:00 | FALSE | 1 | line_6493_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_733_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_733_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_6495_22 | ACLineSegment | Line | 12.3112 | 0.3467 | 0.3467 | 0.26513 | 2.8161 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_6495_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_6496_22 | ACLineSegment | Line | 0.51338 | 0.0067082 | 0.0067082 | 0.0051113 | 1.3067 | 0 | 0 | 0 | 2024-06-27 02:00 | FALSE | 1 | line_6496_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_697_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_697_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_6500_22 | ACLineSegment | Line | 0.51338 | 0.0078295 | 0.0078295 | 0.0053322 | 1.5251 | 0 | 0 | 0 | 2024-01-17 14:20 | FALSE | 1 | line_6500_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_711_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_711_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_6513_22 | ACLineSegment | Line | 0.025406 | 0.0050845 | 0.0050845 | 0.0039226 | 20.013 | 0 | 0 | 0 | 2024-01-20 13:10 | FALSE | 1 | line_6513_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_747_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_747_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_6521_22 | ACLineSegment | Line | 0.51338 | 0.0039172 | 0.0039172 | 0.0028356 | 0.76303 | 0 | 0 | 0 | 2024-07-14 08:45 | FALSE | 1 | line_6521_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_760_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_760_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_6542_22 | ACLineSegment | Line | 0.51338 | 0.008147 | 0.008147 | 0.0061029 | 1.5869 | 0 | 0 | 0 | 2024-07-15 06:45 | FALSE | 1 | line_6542_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_781_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_781_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_6545_22 | ACLineSegment | Line | 0.034884 | 0.0013657 | 0.0013657 | 0.00081676 | 3.9151 | 0 | 0 | 0 | 2024-01-20 11:05 | FALSE | 1 | line_6545_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_6600_22 | ACLineSegment | Line | 0.034884 | 0.0064021 | 0.0064021 | 0.0039522 | 18.3529 | 0 | 0 | 0 | 2024-01-21 03:55 | FALSE | 1 | line_6600_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_6602_22 | ACLineSegment | Line | 0.51338 | 0.0085742 | 0.0085742 | 0.0051561 | 1.6701 | 0 | 0 | 0 | 2024-07-15 08:50 | FALSE | 1 | line_6602_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_867_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_867_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_6635_22 | ACLineSegment | Line | 0.51338 | 0.0042812 | 0.0042812 | 0.0031568 | 0.83393 | 0 | 0 | 0 | 2024-01-20 15:00 | FALSE | 1 | line_6635_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_894_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_894_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_6640_22 | ACLineSegment | Line | 0.51338 | 0.004563 | 0.004563 | 0.0034043 | 0.88882 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | line_6640_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_145 | line_868_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_868_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_924_22 | ACLineSegment | Line | 0.034884 | 0.010549 | 0.010549 | 0.0064948 | 30.242 | 0 | 0 | 0 | 2024-01-20 18:00 | FALSE | 1 | line_924_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_926_22 | ACLineSegment | Line | 0.034884 | 0.0056652 | 0.0056652 | 0.0030776 | 16.2404 | 0 | 0 | 0 | 2024-01-20 08:55 | FALSE | 1 | line_926_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_984_22 | ACLineSegment | Line | 0.034884 | 0.0069944 | 0.0069944 | 0.0040729 | 20.0508 | 0 | 0 | 0 | 2024-01-20 18:00 | FALSE | 1 | line_984_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_937_22 | ACLineSegment | Line | 0.034884 | 0.0098378 | 0.0098378 | 0.0061824 | 28.2019 | 0 | 0 | 0 | 2024-07-15 05:55 | FALSE | 1 | line_937_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_939_22 | ACLineSegment | Line | 0.034884 | 0.0045061 | 0.0045061 | 0.0023055 | 12.9175 | 0 | 0 | 0 | 2024-01-20 23:00 | FALSE | 1 | line_939_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_993_22 | ACLineSegment | Line | 0.034884 | 0.0098378 | 0.0098378 | 0.0061824 | 28.2019 | 0 | 0 | 0 | 2024-07-15 05:55 | FALSE | 1 | line_993_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_949_22 | ACLineSegment | Line | 0.034884 | 0.0079917 | 0.0079917 | 0.0048024 | 22.9097 | 0 | 0 | 0 | 2024-07-15 23:05 | FALSE | 1 | line_949_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_951_22 | ACLineSegment | Line | 0.034884 | 0.0069979 | 0.0069979 | 0.0037754 | 20.0609 | 0 | 0 | 0 | 2024-07-15 10:05 | FALSE | 1 | line_951_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_970_22 | ACLineSegment | Line | 0.034884 | 0.0025031 | 0.0025031 | 0.0015126 | 7.1756 | 0 | 0 | 0 | 2024-07-15 05:55 | FALSE | 1 | line_970_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_971_22 | ACLineSegment | Line | 0.034884 | 0.0064614 | 0.0064614 | 0.0034402 | 18.5228 | 0 | 0 | 0 | 2024-07-15 23:05 | FALSE | 1 | line_971_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_964_22 | ACLineSegment | Line | 0.034884 | 0.0047812 | 0.0047812 | 0.0027151 | 13.7062 | 0 | 0 | 0 | 2024-07-16 00:50 | FALSE | 1 | line_964_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_977_22 | ACLineSegment | Line | 0.034884 | 0.0025031 | 0.0025031 | 0.0015126 | 7.1756 | 0 | 0 | 0 | 2024-07-15 05:55 | FALSE | 1 | line_977_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_994_22 | ACLineSegment | Line | 0.034884 | 0.0032749 | 0.0032749 | 0.0018541 | 9.3881 | 0 | 0 | 0 | 2024-07-16 00:50 | FALSE | 1 | line_994_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_145 | line_995_22 | ACLineSegment | Line | 0.034884 | 0.0074041 | 0.0074041 | 0.0044833 | 21.2252 | 0 | 0 | 0 | 2024-01-17 14:20 | FALSE | 1 | line_995_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_3723_22 | ACLineSegment | Line | 13.5424 | 0.076319 | 0.076319 | 0.057232 | 0.56356 | 0 | 0 | 0 | 2024-01-17 08:00 | FALSE | 1 | line_3723_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_3724_22 | ACLineSegment | Line | 13.5424 | 0.061298 | 0.061298 | 0.04607 | 0.45264 | 0 | 0 | 0 | 2024-01-17 08:00 | FALSE | 1 | line_3724_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_70_22 | Transformer | Transformer | 0.07125 | 0.0087558 | 0.0087558 | 0.0063916 | 12.2888 | 0 | 0 | 0 | 2024-07-10 07:05 | FALSE | 1 | tr_70_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_3690_22 | ACLineSegment | Line | 0.94778 | 0.01263 | 0.01263 | 0.0082942 | 1.3326 | 0 | 0 | 0 | 2024-01-20 09:55 | FALSE | 1 | line_3690_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_4796_22 | ACLineSegment | Line | 13.5424 | 0.011487 | 0.011487 | 0.0089339 | 0.084822 | 0 | 0 | 0 | 2024-07-15 08:00 | FALSE | 1 | line_4796_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_1271_22 | Transformer | Transformer | 0.07125 | 0.0068089 | 0.0068089 | 0.0048442 | 9.5563 | 0 | 0 | 0 | 2024-01-21 16:20 | FALSE | 1 | tr_1271_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_6343_22 | ACLineSegment | Line | 0.94778 | 0.0077562 | 0.0077562 | 0.0048113 | 0.81836 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | line_6343_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_3872_22 | ACLineSegment | Line | 13.5424 | 0.010026 | 0.010026 | 0.0075329 | 0.074038 | 0 | 0 | 0 | 2024-01-20 07:55 | FALSE | 1 | line_3872_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_3873_22 | ACLineSegment | Line | 13.5424 | 0.020116 | 0.020116 | 0.015735 | 0.14854 | 0 | 0 | 0 | 2024-01-20 23:05 | FALSE | 1 | line_3873_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_121_22 | Transformer | Transformer | 0.07125 | 0.0054328 | 0.0054328 | 0.004057 | 7.6249 | 0 | 0 | 0 | 2024-07-14 23:00 | FALSE | 1 | tr_121_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | tr_495_22 | Transformer | Transformer | 0.0475 | 0.0080811 | 0.0080811 | 0.0059834 | 17.0129 | 0 | 0 | 0 | 2024-01-17 08:00 | FALSE | 1 | tr_495_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_4386_22 | ACLineSegment | Line | 13.5424 | 0.082003 | 0.082003 | 0.063114 | 0.60553 | 0 | 0 | 0 | 2024-01-17 16:00 | FALSE | 1 | line_4386_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_4769_22 | ACLineSegment | Line | 13.5424 | 0.1383 | 0.1383 | 0.10737 | 1.0212 | 0 | 0 | 0 | 2024-01-17 16:00 | FALSE | 1 | line_4769_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_4808_22 | ACLineSegment | Line | 13.5424 | 0.029367 | 0.029367 | 0.021907 | 0.21686 | 0 | 0 | 0 | 2024-01-20 19:55 | FALSE | 1 | line_4808_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_486_22 | Transformer | Transformer | 0.095 | 0.029472 | 0.029472 | 0.022371 | 31.0229 | 0 | 0 | 0 | 2024-07-14 07:55 | FALSE | 1 | tr_486_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_3946_22 | ACLineSegment | Line | 0.94778 | 0.0068572 | 0.0068572 | 0.0050809 | 0.7235 | 0 | 0 | 0 | 2024-07-05 05:55 | FALSE | 1 | line_3946_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_3596_22 | ACLineSegment | Line | 13.5424 | 0.0083322 | 0.0083322 | 0.0063091 | 0.061527 | 0 | 0 | 0 | 2024-07-05 22:55 | FALSE | 1 | line_3596_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_26_22 | Transformer | Transformer | 0.07125 | 0.0039418 | 0.0039418 | 0.002626 | 5.5323 | 0 | 0 | 0 | 2024-07-15 08:00 | FALSE | 1 | tr_26_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_3595_22 | ACLineSegment | Line | 0.94778 | 0.0060991 | 0.0060991 | 0.0044623 | 0.64352 | 0 | 0 | 0 | 2024-07-09 09:55 | FALSE | 1 | line_3595_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_4350_22 | ACLineSegment | Line | 13.5424 | 0.027013 | 0.027013 | 0.019786 | 0.19947 | 0 | 0 | 0 | 2024-01-20 11:55 | FALSE | 1 | line_4350_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_306_22 | Transformer | Transformer | 0.07125 | 0.022103 | 0.022103 | 0.016417 | 31.0223 | 0 | 0 | 0 | 2024-01-18 00:05 | FALSE | 1 | tr_306_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_4351_22 | ACLineSegment | Line | 0.94778 | 0.0061846 | 0.0061846 | 0.0044629 | 0.65253 | 0 | 0 | 0 | 2024-01-20 12:00 | FALSE | 1 | line_4351_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_4527_22 | ACLineSegment | Line | 13.5424 | 0.16537 | 0.16537 | 0.097155 | 1.2211 | 0 | 0 | 0 | 2024-10-02 08:00 | FALSE | 1 | line_4527_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_4528_22 | ACLineSegment | Line | 13.5424 | 0.17226 | 0.17226 | 0.10339 | 1.272 | 0 | 0 | 0 | 2024-10-02 08:00 | FALSE | 1 | line_4528_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_372_22 | Transformer | Transformer | 0.07125 | 0.0061569 | 0.0061569 | 0.0038722 | 8.6413 | 0 | 0 | 0 | 2024-07-15 01:55 | FALSE | 1 | tr_372_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | tr_377_22 | Transformer | Transformer | 0.0475 | 0.0073315 | 0.0073315 | 0.0050051 | 15.4348 | 0 | 0 | 0 | 2024-01-21 01:50 | FALSE | 1 | tr_377_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_4716_22 | ACLineSegment | Line | 13.5424 | 0.020807 | 0.020807 | 0.0151 | 0.15364 | 0 | 0 | 0 | 2024-07-15 08:00 | FALSE | 1 | line_4716_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_532_22 | Transformer | Transformer | 0.07125 | 0.01821 | 0.01821 | 0.012808 | 25.5579 | 0 | 0 | 0 | 2024-07-15 08:00 | FALSE | 1 | tr_532_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_4899_22 | ACLineSegment | Line | 0.94778 | 0.0041238 | 0.0041238 | 0.0030987 | 0.4351 | 0 | 0 | 0 | 2024-07-09 | FALSE | 1 | line_4899_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | tr_1437_22 | Transformer | Transformer | 0.285 | 0.0069972 | 0.0069972 | 0.0050948 | 2.4552 | 0 | 0 | 0 | 2024-01-21 04:05 | FALSE | 1 | tr_1437_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_5115_22 | ACLineSegment | Line | 0.94778 | 0.023833 | 0.023833 | 0.017708 | 2.5146 | 0 | 0 | 0 | 2024-01-20 19:55 | FALSE | 1 | line_5115_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_4942_22 | ACLineSegment | Line | 13.5424 | 0.0052359 | 0.0052359 | 0.0038998 | 0.038663 | 0 | 0 | 0 | 2024-01-20 18:05 | FALSE | 1 | line_4942_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_1504_22 | Transformer | Transformer | 0.0475 | 0.02469 | 0.02469 | 0.018655 | 51.9779 | 0 | 0 | 0 | 2024-01-20 17:15 | FALSE | 1 | tr_1504_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_5135_22 | ACLineSegment | Line | 0.94778 | 0.034883 | 0.034883 | 0.02573 | 3.6805 | 0 | 0 | 0 | 2024-01-21 02:00 | FALSE | 1 | line_5135_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_1053_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1053_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_6402_22 | ACLineSegment | Line | 0.51338 | 0.0088988 | 0.0088988 | 0.0061734 | 1.7334 | 0 | 0 | 0 | 2024-01-20 22:55 | FALSE | 1 | line_6402_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_1259_22 | Transformer | Transformer | 0.07125 | 0.0088988 | 0.0088988 | 0.0061734 | 12.4895 | 0 | 0 | 0 | 2024-01-20 22:55 | FALSE | 1 | tr_1259_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_1070_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1070_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_6417_22 | ACLineSegment | Line | 0.51338 | 0.0068089 | 0.0068089 | 0.0048442 | 1.3263 | 0 | 0 | 0 | 2024-01-21 16:20 | FALSE | 1 | line_6417_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_1375_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1375_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_3874_22 | ACLineSegment | Line | 0.51338 | 0.0054328 | 0.0054328 | 0.004057 | 1.0582 | 0 | 0 | 0 | 2024-07-14 23:00 | FALSE | 1 | line_3874_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_1402_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1402_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_3947_22 | ACLineSegment | Line | 0.034884 | 0.0068572 | 0.0068572 | 0.0050809 | 19.6574 | 0 | 0 | 0 | 2024-07-05 05:55 | FALSE | 1 | line_3947_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | tr_151_22 | Transformer | Transformer | 0.0475 | 0.0068572 | 0.0068572 | 0.0050809 | 14.4362 | 0 | 0 | 0 | 2024-07-05 05:55 | FALSE | 1 | tr_151_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_1426_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1426_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_3985_22 | ACLineSegment | Line | 0.51338 | 0.0034045 | 0.0034045 | 0.0025137 | 0.66315 | 0 | 0 | 0 | 2024-01-21 02:00 | FALSE | 1 | line_3985_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_167_22 | Transformer | Transformer | 0.285 | 0.0034045 | 0.0034045 | 0.0025137 | 1.1946 | 0 | 0 | 0 | 2024-01-21 02:00 | FALSE | 1 | tr_167_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_1699_22 | ACLineSegment | Line | 0.025406 | 0.02849 | 0.02849 | 0.018583 | 112.1413 | 98 | 8.1667 | 0.093025 | 2024-01-22 04:00 | FALSE | 1 | line_1699_22 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_142 | line_1700_22 | ACLineSegment | Line | 0.025406 | 0.02849 | 0.02849 | 0.018583 | 112.1413 | 98 | 8.1667 | 0.093025 | 2024-01-22 04:00 | FALSE | 1 | line_1700_22 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_142 | line_1701_22 | ACLineSegment | Line | 0.025406 | 0.02849 | 0.02849 | 0.018583 | 112.1413 | 98 | 8.1667 | 0.093025 | 2024-01-22 04:00 | FALSE | 1 | line_1701_22 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_142 | line_4263_22 | ACLineSegment | Line | 0.025406 | 0.0031932 | 0.0031932 | 0.0018256 | 12.5688 | 0 | 0 | 0 | 2024-01-20 07:55 | FALSE | 1 | line_4263_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | tr_273_22 | Transformer | Transformer | 0.02375 | 0.030493 | 0.030493 | 0.019869 | 128.3925 | 678 | 56.5 | 0.64358 | 2024-01-22 04:00 | FALSE | 1 | tr_273_22 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_142 | line_17_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_17_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_4491_22 | ACLineSegment | Line | 0.034884 | 0.0060415 | 0.0060415 | 0.0043336 | 17.319 | 0 | 0 | 0 | 2024-07-15 12:00 | FALSE | 1 | line_4491_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | tr_348_22 | Transformer | Transformer | 0.0475 | 0.0060415 | 0.0060415 | 0.0043336 | 12.7189 | 0 | 0 | 0 | 2024-07-15 12:00 | FALSE | 1 | tr_348_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_1828_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1828_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_4352_22 | ACLineSegment | Line | 0.51338 | 0.022103 | 0.022103 | 0.016417 | 4.3055 | 0 | 0 | 0 | 2024-01-18 00:05 | FALSE | 1 | line_4352_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_1856_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1856_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_4388_22 | ACLineSegment | Line | 0.51338 | 0.0067119 | 0.0067119 | 0.004751 | 1.3074 | 0 | 0 | 0 | 2024-07-15 01:55 | FALSE | 1 | line_4388_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_319_22 | Transformer | Transformer | 0.07125 | 0.0067119 | 0.0067119 | 0.004751 | 9.4202 | 0 | 0 | 0 | 2024-07-15 01:55 | FALSE | 1 | tr_319_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_1857_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1857_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_4394_22 | ACLineSegment | Line | 0.51338 | 0.0069113 | 0.0069113 | 0.0048111 | 1.3462 | 0 | 0 | 0 | 2024-01-20 13:00 | FALSE | 1 | line_4394_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_321_22 | Transformer | Transformer | 0.07125 | 0.0069113 | 0.0069113 | 0.0048111 | 9.7001 | 0 | 0 | 0 | 2024-01-20 13:00 | FALSE | 1 | tr_321_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_1864_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1864_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_4914_22 | ACLineSegment | Line | 0.51338 | 0.0037471 | 0.0037471 | 0.0026541 | 0.72989 | 0 | 0 | 0 | 2024-01-20 20:00 | FALSE | 1 | line_4914_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_533_22 | Transformer | Transformer | 0.07125 | 0.0037471 | 0.0037471 | 0.0026541 | 5.2591 | 0 | 0 | 0 | 2024-01-20 20:00 | FALSE | 1 | tr_533_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_1865_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1865_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_4912_22 | ACLineSegment | Line | 0.51338 | 0.01821 | 0.01821 | 0.012808 | 3.5471 | 0 | 0 | 0 | 2024-07-15 08:00 | FALSE | 1 | line_4912_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_1866_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1866_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_4922_22 | ACLineSegment | Line | 0.51338 | 0.0060546 | 0.0060546 | 0.0045063 | 1.1794 | 0 | 0 | 0 | 2024-01-20 07:55 | FALSE | 1 | line_4922_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_538_22 | Transformer | Transformer | 0.07125 | 0.0060546 | 0.0060546 | 0.0045063 | 8.4977 | 0 | 0 | 0 | 2024-01-20 07:55 | FALSE | 1 | tr_538_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_1868_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1868_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_4930_22 | ACLineSegment | Line | 0.51338 | 0.006111 | 0.006111 | 0.0040349 | 1.1903 | 0 | 0 | 0 | 2024-07-14 08:05 | FALSE | 1 | line_4930_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_543_22 | Transformer | Transformer | 0.07125 | 0.006111 | 0.006111 | 0.0040349 | 8.5768 | 0 | 0 | 0 | 2024-07-14 08:05 | FALSE | 1 | tr_543_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_1869_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1869_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_4892_22 | ACLineSegment | Line | 0.51338 | 0.0061389 | 0.0061389 | 0.004311 | 1.1958 | 0 | 0 | 0 | 2024-07-14 06:55 | FALSE | 1 | line_4892_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_523_22 | Transformer | Transformer | 0.07125 | 0.0061389 | 0.0061389 | 0.004311 | 8.616 | 0 | 0 | 0 | 2024-07-14 06:55 | FALSE | 1 | tr_523_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_1870_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1870_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_4900_22 | ACLineSegment | Line | 0.034884 | 0.0041238 | 0.0041238 | 0.0030987 | 11.8216 | 0 | 0 | 0 | 2024-07-09 | FALSE | 1 | line_4900_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | tr_526_22 | Transformer | Transformer | 0.02375 | 0.0041238 | 0.0041238 | 0.0030987 | 17.3633 | 0 | 0 | 0 | 2024-07-09 | FALSE | 1 | tr_526_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_1871_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1871_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_4906_22 | ACLineSegment | Line | 0.034884 | 0.0082683 | 0.0082683 | 0.0060231 | 23.7026 | 0 | 0 | 0 | 2024-01-20 06:45 | FALSE | 1 | line_4906_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | tr_529_22 | Transformer | Transformer | 0.0475 | 0.0082683 | 0.0082683 | 0.0060231 | 17.407 | 0 | 0 | 0 | 2024-01-20 06:45 | FALSE | 1 | tr_529_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_1872_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1872_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_4923_22 | ACLineSegment | Line | 0.034884 | 0.0060991 | 0.0060991 | 0.0044623 | 17.4843 | 0 | 0 | 0 | 2024-07-09 09:55 | FALSE | 1 | line_4923_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | tr_539_22 | Transformer | Transformer | 0.02375 | 0.0060991 | 0.0060991 | 0.0044623 | 25.6806 | 0 | 0 | 0 | 2024-07-09 09:55 | FALSE | 1 | tr_539_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_1876_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1876_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_4920_22 | ACLineSegment | Line | 0.51338 | 0.0049261 | 0.0049261 | 0.0033119 | 0.95955 | 0 | 0 | 0 | 2024-06-26 11:55 | FALSE | 1 | line_4920_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_537_22 | Transformer | Transformer | 0.07125 | 0.0049261 | 0.0049261 | 0.0033119 | 6.9139 | 0 | 0 | 0 | 2024-06-26 11:55 | FALSE | 1 | tr_537_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_1877_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1877_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_4890_22 | ACLineSegment | Line | 0.51338 | 0.0073154 | 0.0073154 | 0.0049021 | 1.425 | 0 | 0 | 0 | 2024-01-20 10:00 | FALSE | 1 | line_4890_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_522_22 | Transformer | Transformer | 0.07125 | 0.0073154 | 0.0073154 | 0.0049021 | 10.2673 | 0 | 0 | 0 | 2024-01-20 10:00 | FALSE | 1 | tr_522_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_1882_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1882_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_4911_22 | ACLineSegment | Line | 0.51338 | 0.0064854 | 0.0064854 | 0.0047814 | 1.2633 | 0 | 0 | 0 | 2024-01-17 11:55 | FALSE | 1 | line_4911_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_531_22 | Transformer | Transformer | 0.07125 | 0.0064854 | 0.0064854 | 0.0047814 | 9.1023 | 0 | 0 | 0 | 2024-01-17 11:55 | FALSE | 1 | tr_531_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_1883_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1883_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_4925_22 | ACLineSegment | Line | 0.51338 | 0.0075378 | 0.0075378 | 0.0050201 | 1.4683 | 0 | 0 | 0 | 2024-07-05 05:55 | FALSE | 1 | line_4925_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_540_22 | Transformer | Transformer | 0.07125 | 0.0075378 | 0.0075378 | 0.0050201 | 10.5794 | 0 | 0 | 0 | 2024-07-05 05:55 | FALSE | 1 | tr_540_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_1894_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1894_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_4877_22 | ACLineSegment | Line | 0.034884 | 0.0074425 | 0.0074425 | 0.0037785 | 21.3354 | 0 | 0 | 0 | 2024-01-21 02:00 | FALSE | 1 | line_4877_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | tr_517_22 | Transformer | Transformer | 0.02375 | 0.0074425 | 0.0074425 | 0.0037785 | 31.337 | 0 | 0 | 0 | 2024-01-21 02:00 | FALSE | 1 | tr_517_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_1895_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1895_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_4909_22 | ACLineSegment | Line | 0.029092 | 0.0071784 | 0.0071784 | 0.0055803 | 24.6751 | 0 | 0 | 0 | 2024-07-15 07:55 | FALSE | 1 | line_4909_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | tr_530_22 | Transformer | Transformer | 0.0475 | 0.0071784 | 0.0071784 | 0.0055803 | 15.1124 | 0 | 0 | 0 | 2024-07-15 07:55 | FALSE | 1 | tr_530_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_1899_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1899_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_4936_22 | ACLineSegment | Line | 0.51338 | 0.0056313 | 0.0056313 | 0.0037819 | 1.0969 | 0 | 0 | 0 | 2024-07-16 | FALSE | 1 | line_4936_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_546_22 | Transformer | Transformer | 0.285 | 0.0056313 | 0.0056313 | 0.0037819 | 1.9759 | 0 | 0 | 0 | 2024-07-16 | FALSE | 1 | tr_546_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_1901_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1901_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_4943_22 | ACLineSegment | Line | 0.51338 | 0.0052359 | 0.0052359 | 0.0038998 | 1.0199 | 0 | 0 | 0 | 2024-01-20 18:05 | FALSE | 1 | line_4943_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_549_22 | Transformer | Transformer | 0.475 | 0.0052359 | 0.0052359 | 0.0038998 | 1.1023 | 0 | 0 | 0 | 2024-01-20 18:05 | FALSE | 1 | tr_549_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_1904_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1904_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_4441_22 | ACLineSegment | Line | 0.51338 | 0.0069402 | 0.0069402 | 0.0045352 | 1.3519 | 0 | 0 | 0 | 2024-01-20 20:00 | FALSE | 1 | line_4441_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_339_22 | Transformer | Transformer | 0.095 | 0.0069402 | 0.0069402 | 0.0045352 | 7.3055 | 0 | 0 | 0 | 2024-01-20 20:00 | FALSE | 1 | tr_339_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_1924_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1924_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_4420_22 | ACLineSegment | Line | 0.22905 | 0.0055171 | 0.0055171 | 0.0038878 | 2.4087 | 0 | 0 | 0 | 2024-01-20 20:00 | FALSE | 1 | line_4420_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_331_22 | Transformer | Transformer | 0.07125 | 0.0055171 | 0.0055171 | 0.0038878 | 7.7433 | 0 | 0 | 0 | 2024-01-20 20:00 | FALSE | 1 | tr_331_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_1932_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1932_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_1933_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1933_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_4478_22 | ACLineSegment | Line | 0.51338 | 0.0068803 | 0.0068803 | 0.0043345 | 1.3402 | 0 | 0 | 0 | 2024-01-20 23:05 | FALSE | 1 | line_4478_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_4479_22 | ACLineSegment | Line | 0.51338 | 0.0064665 | 0.0064665 | 0.0045221 | 1.2596 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | line_4479_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_354_22 | Transformer | Transformer | 0.095 | 0.011246 | 0.011246 | 0.0082131 | 11.838 | 0 | 0 | 0 | 2024-01-17 08:00 | FALSE | 1 | tr_354_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_1935_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1935_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_4459_22 | ACLineSegment | Line | 0.034884 | 0.0071179 | 0.0071179 | 0.0051848 | 20.4048 | 0 | 0 | 0 | 2024-01-20 16:55 | FALSE | 1 | line_4459_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | tr_346_22 | Transformer | Transformer | 0.02375 | 0.0071179 | 0.0071179 | 0.0051848 | 29.9702 | 0 | 0 | 0 | 2024-01-20 16:55 | FALSE | 1 | tr_346_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_1953_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1953_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_1954_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1954_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_4550_22 | ACLineSegment | Line | 0.51338 | 0.0067791 | 0.0067791 | 0.004187 | 1.3205 | 0 | 0 | 0 | 2024-07-15 01:55 | FALSE | 1 | line_4550_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_4551_22 | ACLineSegment | Line | 0.51338 | 0.0059609 | 0.0059609 | 0.0045223 | 1.1611 | 0 | 0 | 0 | 2024-07-15 01:55 | FALSE | 1 | line_4551_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_380_22 | Transformer | Transformer | 0.095 | 0.01274 | 0.01274 | 0.0083061 | 13.4105 | 0 | 0 | 0 | 2024-07-15 01:55 | FALSE | 1 | tr_380_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_1963_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1963_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_4529_22 | ACLineSegment | Line | 0.51338 | 0.0061569 | 0.0061569 | 0.0038722 | 1.1993 | 0 | 0 | 0 | 2024-07-15 01:55 | FALSE | 1 | line_4529_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_1967_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1967_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_4542_22 | ACLineSegment | Line | 0.034884 | 0.0073315 | 0.0073315 | 0.0050051 | 21.0172 | 0 | 0 | 0 | 2024-01-21 01:50 | FALSE | 1 | line_4542_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_1968_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1968_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_4547_22 | ACLineSegment | Line | 0.025406 | 0.0034836 | 0.0034836 | 0.0018857 | 13.712 | 0 | 0 | 0 | 2024-07-15 07:55 | FALSE | 1 | line_4547_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | tr_379_22 | Transformer | Transformer | 0.02375 | 0.0034836 | 0.0034836 | 0.0018857 | 14.6679 | 0 | 0 | 0 | 2024-07-15 07:55 | FALSE | 1 | tr_379_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_1975_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1975_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_4563_22 | ACLineSegment | Line | 0.51338 | 0.006143 | 0.006143 | 0.0046048 | 1.1966 | 0 | 0 | 0 | 2024-07-14 15:00 | FALSE | 1 | line_4563_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_385_22 | Transformer | Transformer | 0.1425 | 0.006143 | 0.006143 | 0.0046048 | 4.3109 | 0 | 0 | 0 | 2024-07-14 15:00 | FALSE | 1 | tr_385_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_1976_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1976_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_4571_22 | ACLineSegment | Line | 0.51338 | 0.0061184 | 0.0061184 | 0.004163 | 1.1918 | 0 | 0 | 0 | 2024-01-20 19:55 | FALSE | 1 | line_4571_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_388_22 | Transformer | Transformer | 0.1425 | 0.0061184 | 0.0061184 | 0.004163 | 4.2936 | 0 | 0 | 0 | 2024-01-20 19:55 | FALSE | 1 | tr_388_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_1981_22 | ACLineSegment | Line | 0.029092 | 0.0073886 | 0.0073886 | 0.005567 | 25.3977 | 0 | 0 | 0 | 2024-07-09 12:00 | FALSE | 1 | line_1981_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_1982_22 | ACLineSegment | Line | 0.029092 | 0.0073886 | 0.0073886 | 0.005567 | 25.3977 | 0 | 0 | 0 | 2024-07-09 12:00 | FALSE | 1 | line_1982_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_1983_22 | ACLineSegment | Line | 0.029092 | 0.0037386 | 0.0037386 | 0.0027266 | 12.8511 | 0 | 0 | 0 | 2024-07-05 09:00 | FALSE | 1 | line_1983_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | tr_393_22 | Transformer | Transformer | 0.07125 | 0.010184 | 0.010184 | 0.007852 | 14.2934 | 0 | 0 | 0 | 2024-07-15 20:00 | FALSE | 1 | tr_393_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_1984_22 | ACLineSegment | Line | 0.029092 | 0.0037386 | 0.0037386 | 0.0027266 | 12.8511 | 0 | 0 | 0 | 2024-07-05 09:00 | FALSE | 1 | line_1984_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_1986_22 | ACLineSegment | Line | 0.51338 | 0.0053228 | 0.0053228 | 0.0037886 | 1.0368 | 0 | 0 | 0 | 2024-01-20 12:00 | FALSE | 1 | line_1986_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_1987_22 | ACLineSegment | Line | 0.51338 | 0.0053228 | 0.0053228 | 0.0037886 | 1.0368 | 0 | 0 | 0 | 2024-01-20 12:00 | FALSE | 1 | line_1987_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_1988_22 | ACLineSegment | Line | 0.51338 | 0.0053228 | 0.0053228 | 0.0037886 | 1.0368 | 0 | 0 | 0 | 2024-01-20 12:00 | FALSE | 1 | line_1988_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_4587_22 | ACLineSegment | Line | 0.51338 | 0.0057016 | 0.0057016 | 0.0040295 | 1.1106 | 0 | 0 | 0 | 2024-01-21 00:55 | FALSE | 1 | line_4587_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_395_22 | Transformer | Transformer | 0.095 | 0.010238 | 0.010238 | 0.0072008 | 10.7767 | 0 | 0 | 0 | 2024-01-21 00:55 | FALSE | 1 | tr_395_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_1994_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1994_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_6517_22 | ACLineSegment | Line | 0.51338 | 0.0060558 | 0.0060558 | 0.0041755 | 1.1796 | 0 | 0 | 0 | 2024-01-20 21:45 | FALSE | 1 | line_6517_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_1337_22 | Transformer | Transformer | 0.07125 | 0.0060558 | 0.0060558 | 0.0041755 | 8.4993 | 0 | 0 | 0 | 2024-01-20 21:45 | FALSE | 1 | tr_1337_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_1995_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_1995_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_4679_22 | ACLineSegment | Line | 0.51338 | 0.024552 | 0.024552 | 0.016805 | 4.7824 | 0 | 0 | 0 | 2024-01-17 16:00 | FALSE | 1 | line_4679_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_431_22 | Transformer | Transformer | 0.07125 | 0.024552 | 0.024552 | 0.016805 | 34.4591 | 0 | 0 | 0 | 2024-01-17 16:00 | FALSE | 1 | tr_431_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_2006_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2006_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_6529_22 | ACLineSegment | Line | 0.51338 | 0.0076295 | 0.0076295 | 0.0056026 | 1.4861 | 0 | 0 | 0 | 2024-01-20 22:55 | FALSE | 1 | line_6529_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_1348_22 | Transformer | Transformer | 0.07125 | 0.0076295 | 0.0076295 | 0.0056026 | 10.7081 | 0 | 0 | 0 | 2024-01-20 22:55 | FALSE | 1 | tr_1348_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_2009_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2009_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_4659_22 | ACLineSegment | Line | 0.51338 | 0.0053277 | 0.0053277 | 0.0039015 | 1.0378 | 0 | 0 | 0 | 2024-07-10 05:30 | FALSE | 1 | line_4659_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_422_22 | Transformer | Transformer | 0.285 | 0.0053277 | 0.0053277 | 0.0039015 | 1.8694 | 0 | 0 | 0 | 2024-07-10 05:30 | FALSE | 1 | tr_422_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_20_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_20_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_4637_22 | ACLineSegment | Line | 0.22905 | 0.013386 | 0.013386 | 0.007913 | 5.8444 | 0 | 0 | 0 | 2024-01-18 00:05 | FALSE | 1 | line_4637_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_403_22 | Transformer | Transformer | 0.07125 | 0.013386 | 0.013386 | 0.007913 | 18.7879 | 0 | 0 | 0 | 2024-01-18 00:05 | FALSE | 1 | tr_403_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_2028_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2028_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_4683_22 | ACLineSegment | Line | 0.025406 | 0.008282 | 0.008282 | 0.0057991 | 32.5991 | 0 | 0 | 0 | 2024-07-15 20:00 | FALSE | 1 | line_4683_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | tr_433_22 | Transformer | Transformer | 0.02375 | 0.008282 | 0.008282 | 0.0057991 | 34.8717 | 0 | 0 | 0 | 2024-07-15 20:00 | FALSE | 1 | tr_433_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_2029_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2029_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_4686_22 | ACLineSegment | Line | 0.51338 | 0.0058203 | 0.0058203 | 0.0039323 | 1.1337 | 0 | 0 | 0 | 2024-01-21 03:55 | FALSE | 1 | line_4686_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_434_22 | Transformer | Transformer | 0.07125 | 0.0058203 | 0.0058203 | 0.0039323 | 8.1688 | 0 | 0 | 0 | 2024-01-21 03:55 | FALSE | 1 | tr_434_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_2076_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2076_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_4831_22 | ACLineSegment | Line | 0.51338 | 0.0048017 | 0.0048017 | 0.0037737 | 0.93531 | 0 | 0 | 0 | 2024-07-14 14:55 | FALSE | 1 | line_4831_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_496_22 | Transformer | Transformer | 0.285 | 0.0048017 | 0.0048017 | 0.0037737 | 1.6848 | 0 | 0 | 0 | 2024-07-14 14:55 | FALSE | 1 | tr_496_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_2084_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2084_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_4809_22 | ACLineSegment | Line | 0.51338 | 0.029472 | 0.029472 | 0.022371 | 5.7407 | 0 | 0 | 0 | 2024-07-14 07:55 | FALSE | 1 | line_4809_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_2085_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2085_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_4793_22 | ACLineSegment | Line | 0.51338 | 0.0072827 | 0.0072827 | 0.0054002 | 1.4186 | 0 | 0 | 0 | 2024-07-10 18:55 | FALSE | 1 | line_4793_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_479_22 | Transformer | Transformer | 0.095 | 0.0072827 | 0.0072827 | 0.0054002 | 7.666 | 0 | 0 | 0 | 2024-07-10 18:55 | FALSE | 1 | tr_479_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_2086_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2086_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_4829_22 | ACLineSegment | Line | 0.034884 | 0.0080811 | 0.0080811 | 0.0059834 | 23.166 | 0 | 0 | 0 | 2024-01-17 08:00 | FALSE | 1 | line_4829_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_2088_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2088_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_4794_22 | ACLineSegment | Line | 0.51338 | 0.0091076 | 0.0091076 | 0.005998 | 1.774 | 0 | 0 | 0 | 2024-01-20 20:00 | FALSE | 1 | line_4794_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_480_22 | Transformer | Transformer | 0.095 | 0.0091076 | 0.0091076 | 0.005998 | 9.5869 | 0 | 0 | 0 | 2024-01-20 20:00 | FALSE | 1 | tr_480_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_2106_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2106_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_4856_22 | ACLineSegment | Line | 0.51338 | 0.0059441 | 0.0059441 | 0.0044 | 1.1578 | 0 | 0 | 0 | 2024-07-05 09:00 | FALSE | 1 | line_4856_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_507_22 | Transformer | Transformer | 0.095 | 0.0059441 | 0.0059441 | 0.0044 | 6.2569 | 0 | 0 | 0 | 2024-07-05 09:00 | FALSE | 1 | tr_507_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_2109_22 | ACLineSegment | Line | 0.025406 | 0.0095272 | 0.0095272 | 0.005611 | 37.5002 | 0 | 0 | 0 | 2024-01-21 02:00 | FALSE | 1 | line_2109_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_2110_22 | ACLineSegment | Line | 0.025406 | 0.0095272 | 0.0095272 | 0.005611 | 37.5002 | 0 | 0 | 0 | 2024-01-21 02:00 | FALSE | 1 | line_2110_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_2111_22 | ACLineSegment | Line | 0.025406 | 0.0044742 | 0.0044742 | 0.0023578 | 17.6111 | 0 | 0 | 0 | 2024-01-20 07:55 | FALSE | 1 | line_2111_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | tr_511_22 | Transformer | Transformer | 0.02375 | 0.013275 | 0.013275 | 0.0070118 | 55.894 | 0 | 0 | 0 | 2024-01-21 02:00 | FALSE | 1 | tr_511_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_2112_22 | ACLineSegment | Line | 0.025406 | 0.0044742 | 0.0044742 | 0.0023578 | 17.6111 | 0 | 0 | 0 | 2024-01-20 07:55 | FALSE | 1 | line_2112_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_213_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_213_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_4937_22 | ACLineSegment | Line | 0.22905 | 0.028623 | 0.028623 | 0.0203 | 12.4967 | 0 | 0 | 0 | 2024-01-22 04:00 | FALSE | 1 | line_4937_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_536_22 | Transformer | Transformer | 0.07125 | 0.028623 | 0.028623 | 0.0203 | 40.1729 | 0 | 0 | 0 | 2024-01-22 04:00 | FALSE | 1 | tr_536_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_2136_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2136_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_5100_22 | ACLineSegment | Line | 0.029092 | 0.0072326 | 0.0072326 | 0.0052936 | 24.8614 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | line_5100_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | tr_619_22 | Transformer | Transformer | 0.0475 | 0.0072326 | 0.0072326 | 0.0052936 | 15.2264 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | tr_619_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_2142_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2142_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_5110_22 | ACLineSegment | Line | 0.51338 | 0.0044505 | 0.0044505 | 0.0028949 | 0.8669 | 0 | 0 | 0 | 2024-01-20 15:00 | FALSE | 1 | line_5110_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_623_22 | Transformer | Transformer | 0.07125 | 0.0044505 | 0.0044505 | 0.0028949 | 6.2463 | 0 | 0 | 0 | 2024-01-20 15:00 | FALSE | 1 | tr_623_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_2147_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2147_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_5112_22 | ACLineSegment | Line | 0.51338 | 0.0076385 | 0.0076385 | 0.005484 | 1.4879 | 0 | 0 | 0 | 2024-01-17 15:55 | FALSE | 1 | line_5112_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_624_22 | Transformer | Transformer | 0.07125 | 0.0076385 | 0.0076385 | 0.005484 | 10.7206 | 0 | 0 | 0 | 2024-01-17 15:55 | FALSE | 1 | tr_624_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_2151_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2151_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_5139_22 | ACLineSegment | Line | 0.51338 | 0.0076079 | 0.0076079 | 0.0054375 | 1.4819 | 0 | 0 | 0 | 2024-01-20 17:15 | FALSE | 1 | line_5139_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_639_22 | Transformer | Transformer | 0.285 | 0.0076079 | 0.0076079 | 0.0054375 | 2.6695 | 0 | 0 | 0 | 2024-01-20 17:15 | FALSE | 1 | tr_639_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_2161_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2161_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_5116_22 | ACLineSegment | Line | 0.025406 | 0.023833 | 0.023833 | 0.017708 | 93.8094 | 0 | 0 | 0 | 2024-01-20 19:55 | FALSE | 1 | line_5116_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | tr_627_22 | Transformer | Transformer | 0.02375 | 0.023833 | 0.023833 | 0.017708 | 100.3493 | 1 | 0.083333 | 0.00094923 | 2024-01-20 19:55 | FALSE | 1 | tr_627_22 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_142 | line_2169_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2169_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_5169_22 | ACLineSegment | Line | 0.025406 | 0.0082977 | 0.0082977 | 0.0053818 | 32.6607 | 0 | 0 | 0 | 2024-07-16 03:00 | FALSE | 1 | line_5169_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | tr_652_22 | Transformer | Transformer | 0.02375 | 0.0082977 | 0.0082977 | 0.0053818 | 34.9376 | 0 | 0 | 0 | 2024-07-16 03:00 | FALSE | 1 | tr_652_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_2171_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2171_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_5130_22 | ACLineSegment | Line | 0.034884 | 0.0071625 | 0.0071625 | 0.0037219 | 20.5327 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | line_5130_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | tr_633_22 | Transformer | Transformer | 0.02375 | 0.0071625 | 0.0071625 | 0.0037219 | 30.1579 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | tr_633_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_2172_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2172_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_5118_22 | ACLineSegment | Line | 0.034884 | 0.0077821 | 0.0077821 | 0.0047131 | 22.3087 | 0 | 0 | 0 | 2024-01-20 17:15 | FALSE | 1 | line_5118_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | tr_628_22 | Transformer | Transformer | 0.02375 | 0.0077821 | 0.0077821 | 0.0047131 | 32.7666 | 0 | 0 | 0 | 2024-01-20 17:15 | FALSE | 1 | tr_628_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_218_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_218_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_4998_22 | ACLineSegment | Line | 0.51338 | 0.0070547 | 0.0070547 | 0.0052782 | 1.3742 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | line_4998_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_559_22 | Transformer | Transformer | 0.07125 | 0.0070547 | 0.0070547 | 0.0052782 | 9.9013 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | tr_559_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_219_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_219_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_4795_22 | ACLineSegment | Line | 0.034884 | 0.0065517 | 0.0065517 | 0.0047935 | 18.7817 | 0 | 0 | 0 | 2024-07-15 04:00 | FALSE | 1 | line_4795_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | tr_470_22 | Transformer | Transformer | 0.0475 | 0.0065517 | 0.0065517 | 0.0047935 | 13.7931 | 0 | 0 | 0 | 2024-07-15 04:00 | FALSE | 1 | tr_470_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_220_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_220_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_4822_22 | ACLineSegment | Line | 0.034884 | 0.0012387 | 0.0012387 | 0.00079838 | 3.5508 | 0 | 0 | 0 | 2024-01-20 11:55 | FALSE | 1 | line_4822_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | tr_481_22 | Transformer | Transformer | 0.02375 | 0.0012387 | 0.0012387 | 0.00079838 | 5.2154 | 0 | 0 | 0 | 2024-01-20 11:55 | FALSE | 1 | tr_481_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_221_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_221_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_4847_22 | ACLineSegment | Line | 0.22905 | 0.0047499 | 0.0047499 | 0.003502 | 2.0738 | 0 | 0 | 0 | 2024-01-22 04:00 | FALSE | 1 | line_4847_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_492_22 | Transformer | Transformer | 0.07125 | 0.0047499 | 0.0047499 | 0.003502 | 6.6665 | 0 | 0 | 0 | 2024-01-22 04:00 | FALSE | 1 | tr_492_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_2332_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2332_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_6342_22 | ACLineSegment | Line | 0.034884 | 0.0053033 | 0.0053033 | 0.0039035 | 15.203 | 0 | 0 | 0 | 2024-01-21 18:00 | FALSE | 1 | line_6342_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | tr_1226_22 | Transformer | Transformer | 0.0475 | 0.0053033 | 0.0053033 | 0.0039035 | 11.1649 | 0 | 0 | 0 | 2024-01-21 18:00 | FALSE | 1 | tr_1226_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_2336_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2336_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_6681_22 | ACLineSegment | Line | 0.51338 | 0.0041478 | 0.0041478 | 0.0029123 | 0.80794 | 0 | 0 | 0 | 2024-01-20 05:00 | FALSE | 1 | line_6681_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_1470_22 | Transformer | Transformer | 0.07125 | 0.0041478 | 0.0041478 | 0.0029123 | 5.8215 | 0 | 0 | 0 | 2024-01-20 05:00 | FALSE | 1 | tr_1470_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_2386_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2386_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_3911_22 | ACLineSegment | Line | 0.51338 | 0.0035668 | 0.0035668 | 0.002705 | 0.69476 | 0 | 0 | 0 | 2024-07-05 20:00 | FALSE | 1 | line_3911_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_126_22 | Transformer | Transformer | 0.07125 | 0.0035668 | 0.0035668 | 0.002705 | 5.006 | 0 | 0 | 0 | 2024-07-05 20:00 | FALSE | 1 | tr_126_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_2387_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2387_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_6802_22 | ACLineSegment | Line | 0.034884 | 0.0080222 | 0.0080222 | 0.0055825 | 22.9972 | 0 | 0 | 0 | 2024-01-17 20:00 | FALSE | 1 | line_6802_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | tr_1548_22 | Transformer | Transformer | 0.0475 | 0.0080222 | 0.0080222 | 0.0055825 | 16.8889 | 0 | 0 | 0 | 2024-01-17 20:00 | FALSE | 1 | tr_1548_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_2388_22 | ACLineSegment | Line | 0.034884 | 0.0061257 | 0.0061257 | 0.0043349 | 17.5605 | 0 | 0 | 0 | 2024-06-27 | FALSE | 1 | line_2388_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_2389_22 | ACLineSegment | Line | 0.034884 | 0.0061257 | 0.0061257 | 0.0043349 | 17.5605 | 0 | 0 | 0 | 2024-06-27 | FALSE | 1 | line_2389_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_2390_22 | ACLineSegment | Line | 0.034884 | 0.020581 | 0.020581 | 0.015173 | 58.9987 | 0 | 0 | 0 | 2024-01-20 17:15 | FALSE | 1 | line_2390_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_2391_22 | ACLineSegment | Line | 0.034884 | 0.020581 | 0.020581 | 0.015173 | 58.9987 | 0 | 0 | 0 | 2024-01-20 17:15 | FALSE | 1 | line_2391_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_2429_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2429_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_3750_22 | ACLineSegment | Line | 0.22905 | 0.0087558 | 0.0087558 | 0.0063916 | 3.8227 | 0 | 0 | 0 | 2024-07-10 07:05 | FALSE | 1 | line_3750_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_2431_22 | ACLineSegment | Line | 0.025406 | 0.0054657 | 0.0054657 | 0.0031901 | 21.5137 | 0 | 0 | 0 | 2024-01-20 21:45 | FALSE | 1 | line_2431_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_2432_22 | ACLineSegment | Line | 0.025406 | 0.0054657 | 0.0054657 | 0.0031901 | 21.5137 | 0 | 0 | 0 | 2024-01-20 21:45 | FALSE | 1 | line_2432_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_2433_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2433_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_3689_22 | ACLineSegment | Line | 0.029092 | 0.0072373 | 0.0072373 | 0.0051568 | 24.8778 | 0 | 0 | 0 | 2024-06-26 05:55 | FALSE | 1 | line_3689_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | tr_48_22 | Transformer | Transformer | 0.0475 | 0.010429 | 0.010429 | 0.0075306 | 21.9558 | 0 | 0 | 0 | 2024-07-05 05:55 | FALSE | 1 | tr_48_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_2434_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2434_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_3633_22 | ACLineSegment | Line | 0.51338 | 0.0039418 | 0.0039418 | 0.002626 | 0.7678 | 0 | 0 | 0 | 2024-07-15 08:00 | FALSE | 1 | line_3633_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_2437_22 | ACLineSegment | Line | 0.51338 | 0.0072893 | 0.0072893 | 0.0052341 | 1.4199 | 0 | 0 | 0 | 2024-01-20 23:05 | FALSE | 1 | line_2437_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_2438_22 | ACLineSegment | Line | 0.51338 | 0.0072893 | 0.0072893 | 0.0052341 | 1.4199 | 0 | 0 | 0 | 2024-01-20 23:05 | FALSE | 1 | line_2438_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_2439_22 | ACLineSegment | Line | 0.51338 | 0.0055522 | 0.0055522 | 0.0040447 | 1.0815 | 0 | 0 | 0 | 2024-07-15 05:55 | FALSE | 1 | line_2439_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_159_22 | Transformer | Transformer | 0.095 | 0.011382 | 0.011382 | 0.0085231 | 11.9808 | 0 | 0 | 0 | 2024-01-20 23:05 | FALSE | 1 | tr_159_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_2440_22 | ACLineSegment | Line | 0.51338 | 0.0055522 | 0.0055522 | 0.0040447 | 1.0815 | 0 | 0 | 0 | 2024-07-15 05:55 | FALSE | 1 | line_2440_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_2441_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2441_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_2442_22 | ACLineSegment | Line | 0.029092 | 0.0055117 | 0.0055117 | 0.00397 | 18.9462 | 0 | 0 | 0 | 2024-07-15 20:00 | FALSE | 1 | line_2442_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_6761_22 | ACLineSegment | Line | 0.025406 | 0.0041395 | 0.0041395 | 0.0023208 | 16.2936 | 0 | 0 | 0 | 2024-01-21 03:55 | FALSE | 1 | line_6761_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | tr_1526_22 | Transformer | Transformer | 0.0475 | 0.0084978 | 0.0084978 | 0.005723 | 17.89 | 0 | 0 | 0 | 2024-07-15 20:00 | FALSE | 1 | tr_1526_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_2443_22 | ACLineSegment | Line | 0.029092 | 0.0055117 | 0.0055117 | 0.00397 | 18.9462 | 0 | 0 | 0 | 2024-07-15 20:00 | FALSE | 1 | line_2443_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_2444_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2444_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_6857_22 | ACLineSegment | Line | 0.51338 | 0.0054824 | 0.0054824 | 0.0039981 | 1.0679 | 0 | 0 | 0 | 2024-01-20 18:05 | FALSE | 1 | line_6857_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_1581_22 | Transformer | Transformer | 0.285 | 0.0054824 | 0.0054824 | 0.0039981 | 1.9236 | 0 | 0 | 0 | 2024-01-20 18:05 | FALSE | 1 | tr_1581_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_2446_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2446_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_3817_22 | ACLineSegment | Line | 0.51338 | 0.0097916 | 0.0097916 | 0.0073136 | 1.9073 | 0 | 0 | 0 | 2024-07-15 05:55 | FALSE | 1 | line_3817_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_92_22 | Transformer | Transformer | 0.285 | 0.0097916 | 0.0097916 | 0.0073136 | 3.4357 | 0 | 0 | 0 | 2024-07-15 05:55 | FALSE | 1 | tr_92_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_2464_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2464_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_2465_22 | ACLineSegment | Line | 0.034884 | 0.0087382 | 0.0087382 | 0.0053 | 25.0496 | 0 | 0 | 0 | 2024-01-17 09:10 | FALSE | 1 | line_2465_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_2466_22 | ACLineSegment | Line | 0.034884 | 0.0051231 | 0.0051231 | 0.0029161 | 14.6864 | 0 | 0 | 0 | 2024-01-17 09:10 | FALSE | 1 | line_2466_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_2467_22 | ACLineSegment | Line | 0.034884 | 0.0047943 | 0.0047943 | 0.0026917 | 13.7438 | 0 | 0 | 0 | 2024-01-21 00:55 | FALSE | 1 | line_2467_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_2469_22 | ACLineSegment | Line | 0.034884 | 0.019932 | 0.019932 | 0.012424 | 57.1387 | 0 | 0 | 0 | 2024-01-20 19:55 | FALSE | 1 | line_2469_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_2474_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2474_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_2475_22 | ACLineSegment | Line | 0.034884 | 0.0069543 | 0.0069543 | 0.0037165 | 19.9358 | 0 | 0 | 0 | 2024-01-20 19:55 | FALSE | 1 | line_2475_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_2476_22 | ACLineSegment | Line | 0.034884 | 0.0075479 | 0.0075479 | 0.0040467 | 21.6375 | 0 | 0 | 0 | 2024-01-20 22:55 | FALSE | 1 | line_2476_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_2468_22 | ACLineSegment | Line | 0.034884 | 0.010344 | 0.010344 | 0.006013 | 29.6527 | 0 | 0 | 0 | 2024-01-20 19:55 | FALSE | 1 | line_2468_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_2470_22 | ACLineSegment | Line | 0.034884 | 0.030276 | 0.030276 | 0.017955 | 86.7914 | 0 | 0 | 0 | 2024-01-20 19:55 | FALSE | 1 | line_2470_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_2471_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2471_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_2472_22 | ACLineSegment | Line | 0.034884 | 0.0041911 | 0.0041911 | 0.0024311 | 12.0145 | 0 | 0 | 0 | 2024-07-15 12:00 | FALSE | 1 | line_2472_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_2473_22 | ACLineSegment | Line | 0.034884 | 0.006735 | 0.006735 | 0.0037967 | 19.3071 | 0 | 0 | 0 | 2024-07-06 03:00 | FALSE | 1 | line_2473_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_3594_22 | ACLineSegment | Line | 0.034884 | 0.0032978 | 0.0032978 | 0.0016129 | 9.4537 | 0 | 0 | 0 | 2024-01-20 19:55 | FALSE | 1 | line_3594_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | tr_15_22 | Transformer | Transformer | 0.02375 | 0.033574 | 0.033574 | 0.019446 | 141.3628 | 708 | 59 | 0.67206 | 2024-01-20 19:55 | FALSE | 1 | tr_15_22 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_142 | line_2477_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2477_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_6819_22 | ACLineSegment | Line | 0.51338 | 0.0063571 | 0.0063571 | 0.0045636 | 1.2383 | 0 | 0 | 0 | 2024-01-18 01:55 | FALSE | 1 | line_6819_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_1559_22 | Transformer | Transformer | 0.07125 | 0.0063571 | 0.0063571 | 0.0045636 | 8.9222 | 0 | 0 | 0 | 2024-01-18 01:55 | FALSE | 1 | tr_1559_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_2478_22 | ACLineSegment | Line | 0.034884 | 0.0039107 | 0.0039107 | 0.0022357 | 11.2108 | 0 | 0 | 0 | 2024-07-15 16:00 | FALSE | 1 | line_2478_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_2479_22 | ACLineSegment | Line | 0.025406 | 0.0039107 | 0.0039107 | 0.0022357 | 15.393 | 0 | 0 | 0 | 2024-07-15 16:00 | FALSE | 1 | line_2479_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_2482_22 | ACLineSegment | Line | 0.034884 | 0.0039107 | 0.0039107 | 0.0022357 | 11.2108 | 0 | 0 | 0 | 2024-07-15 16:00 | FALSE | 1 | line_2482_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_2480_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2480_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_3721_22 | ACLineSegment | Line | 0.034884 | 0.003843 | 0.003843 | 0.0021716 | 11.0166 | 0 | 0 | 0 | 2024-07-15 23:55 | FALSE | 1 | line_3721_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_3722_22 | ACLineSegment | Line | 0.034884 | 0.0078503 | 0.0078503 | 0.0044049 | 22.5044 | 0 | 0 | 0 | 2024-07-15 08:00 | FALSE | 1 | line_3722_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | tr_59_22 | Transformer | Transformer | 0.02375 | 0.01263 | 0.01263 | 0.0082942 | 53.1805 | 0 | 0 | 0 | 2024-01-20 09:55 | FALSE | 1 | tr_59_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_2483_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2483_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_3884_22 | ACLineSegment | Line | 0.034884 | 0.0067151 | 0.0067151 | 0.0047782 | 19.25 | 0 | 0 | 0 | 2024-07-09 12:00 | FALSE | 1 | line_3884_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | tr_115_22 | Transformer | Transformer | 0.02375 | 0.0067151 | 0.0067151 | 0.0047782 | 28.274 | 0 | 0 | 0 | 2024-07-09 12:00 | FALSE | 1 | tr_115_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_2484_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2484_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_6737_22 | ACLineSegment | Line | 0.51338 | 0.0058783 | 0.0058783 | 0.0037624 | 1.145 | 0 | 0 | 0 | 2024-01-20 05:00 | FALSE | 1 | line_6737_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_1515_22 | Transformer | Transformer | 0.07125 | 0.0058783 | 0.0058783 | 0.0037624 | 8.2502 | 0 | 0 | 0 | 2024-01-20 05:00 | FALSE | 1 | tr_1515_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_2485_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2485_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_3939_22 | ACLineSegment | Line | 0.034884 | 0.0060033 | 0.0060033 | 0.0027853 | 17.2096 | 0 | 0 | 0 | 2024-01-21 02:00 | FALSE | 1 | line_3939_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | tr_137_22 | Transformer | Transformer | 0.02375 | 0.0060033 | 0.0060033 | 0.0027853 | 25.2771 | 0 | 0 | 0 | 2024-01-21 02:00 | FALSE | 1 | tr_137_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_2486_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2486_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_4013_22 | ACLineSegment | Line | 0.51338 | 0.1172 | 0.1172 | 0.058076 | 22.8296 | 0 | 0 | 0 | 2024-03-19 | FALSE | 1 | line_4013_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_170_22 | Transformer | Transformer | 0.285 | 0.1172 | 0.1172 | 0.058076 | 41.1237 | 0 | 0 | 0 | 2024-03-19 | FALSE | 1 | tr_170_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_2496_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2496_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_4144_22 | ACLineSegment | Line | 0.025406 | 0.0046771 | 0.0046771 | 0.0025091 | 18.4097 | 0 | 0 | 0 | 2024-01-20 05:00 | FALSE | 1 | line_4144_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | tr_226_22 | Transformer | Transformer | 0.02375 | 0.0046771 | 0.0046771 | 0.0025091 | 19.6931 | 0 | 0 | 0 | 2024-01-20 05:00 | FALSE | 1 | tr_226_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_26_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_26_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_4607_22 | ACLineSegment | Line | 0.51338 | 0.0085866 | 0.0085866 | 0.0062604 | 1.6726 | 0 | 0 | 0 | 2024-01-20 23:05 | FALSE | 1 | line_4607_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_392_22 | Transformer | Transformer | 0.07125 | 0.0085866 | 0.0085866 | 0.0062604 | 12.0513 | 0 | 0 | 0 | 2024-01-20 23:05 | FALSE | 1 | tr_392_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_2659_22 | ACLineSegment | Line | 0.034884 | 0.02619 | 0.02619 | 0.01763 | 75.0784 | 0 | 0 | 0 | 2024-01-20 10:00 | FALSE | 1 | line_2659_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_2660_22 | ACLineSegment | Line | 0.034884 | 0.02619 | 0.02619 | 0.01763 | 75.0784 | 0 | 0 | 0 | 2024-01-20 10:00 | FALSE | 1 | line_2660_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | tr_767_22 | Transformer | Transformer | 0.02375 | 0.02619 | 0.02619 | 0.01763 | 110.2736 | 61 | 5.0833 | 0.057903 | 2024-01-20 10:00 | FALSE | 1 | tr_767_22 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_142 | line_2675_22 | ACLineSegment | Line | 0.51338 | 0.0051152 | 0.0051152 | 0.0035837 | 0.99638 | 0 | 0 | 0 | 2024-01-20 14:55 | FALSE | 1 | line_2675_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_2676_22 | ACLineSegment | Line | 0.51338 | 0.0051152 | 0.0051152 | 0.0035837 | 0.99638 | 0 | 0 | 0 | 2024-01-20 14:55 | FALSE | 1 | line_2676_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_766_22 | Transformer | Transformer | 0.285 | 0.0051152 | 0.0051152 | 0.0035837 | 1.7948 | 0 | 0 | 0 | 2024-01-20 14:55 | FALSE | 1 | tr_766_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_2692_22 | ACLineSegment | Line | 0.51338 | 0.0063563 | 0.0063563 | 0.0046703 | 1.2381 | 0 | 0 | 0 | 2024-01-21 00:55 | FALSE | 1 | line_2692_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_2693_22 | ACLineSegment | Line | 0.51338 | 0.0063563 | 0.0063563 | 0.0046703 | 1.2381 | 0 | 0 | 0 | 2024-01-21 00:55 | FALSE | 1 | line_2693_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_778_22 | Transformer | Transformer | 0.07125 | 0.0063563 | 0.0063563 | 0.0046703 | 8.9211 | 0 | 0 | 0 | 2024-01-21 00:55 | FALSE | 1 | tr_778_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_2700_22 | ACLineSegment | Line | 0.51338 | 0.027183 | 0.027183 | 0.018429 | 5.2949 | 0 | 0 | 0 | 2024-01-20 10:00 | FALSE | 1 | line_2700_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_2701_22 | ACLineSegment | Line | 0.51338 | 0.027183 | 0.027183 | 0.018429 | 5.2949 | 0 | 0 | 0 | 2024-01-20 10:00 | FALSE | 1 | line_2701_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_765_22 | Transformer | Transformer | 0.07125 | 0.027183 | 0.027183 | 0.018429 | 38.1516 | 0 | 0 | 0 | 2024-01-20 10:00 | FALSE | 1 | tr_765_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_2710_22 | ACLineSegment | Line | 0.51338 | 0.0048688 | 0.0048688 | 0.0036252 | 0.94839 | 0 | 0 | 0 | 2024-01-21 01:50 | FALSE | 1 | line_2710_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_2711_22 | ACLineSegment | Line | 0.51338 | 0.0048688 | 0.0048688 | 0.0036252 | 0.94839 | 0 | 0 | 0 | 2024-01-21 01:50 | FALSE | 1 | line_2711_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_772_22 | Transformer | Transformer | 0.07125 | 0.0048688 | 0.0048688 | 0.0036252 | 6.8334 | 0 | 0 | 0 | 2024-01-21 01:50 | FALSE | 1 | tr_772_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_2740_22 | ACLineSegment | Line | 0.025406 | 0.013784 | 0.013784 | 0.010714 | 54.2536 | 0 | 0 | 0 | 2024-01-21 00:55 | FALSE | 1 | line_2740_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_2741_22 | ACLineSegment | Line | 0.025406 | 0.013784 | 0.013784 | 0.010714 | 54.2536 | 0 | 0 | 0 | 2024-01-21 00:55 | FALSE | 1 | line_2741_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | tr_789_22 | Transformer | Transformer | 0.02375 | 0.013784 | 0.013784 | 0.010714 | 58.0358 | 0 | 0 | 0 | 2024-01-21 00:55 | FALSE | 1 | tr_789_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_2746_22 | ACLineSegment | Line | 0.51338 | 0.0053974 | 0.0053974 | 0.004099 | 1.0513 | 0 | 0 | 0 | 2024-07-05 03:55 | FALSE | 1 | line_2746_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_2747_22 | ACLineSegment | Line | 0.51338 | 0.0053974 | 0.0053974 | 0.004099 | 1.0513 | 0 | 0 | 0 | 2024-07-05 03:55 | FALSE | 1 | line_2747_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_792_22 | Transformer | Transformer | 0.07125 | 0.0053974 | 0.0053974 | 0.004099 | 7.5753 | 0 | 0 | 0 | 2024-07-05 03:55 | FALSE | 1 | tr_792_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_2865_22 | ACLineSegment | Line | 0.51338 | 0.014848 | 0.014848 | 0.0090822 | 2.8923 | 0 | 0 | 0 | 2024-05-05 17:55 | FALSE | 1 | line_2865_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_2866_22 | ACLineSegment | Line | 0.51338 | 0.014848 | 0.014848 | 0.0090822 | 2.8923 | 0 | 0 | 0 | 2024-05-05 17:55 | FALSE | 1 | line_2866_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_825_22 | Transformer | Transformer | 0.07125 | 0.014848 | 0.014848 | 0.0090822 | 20.8397 | 0 | 0 | 0 | 2024-05-05 17:55 | FALSE | 1 | tr_825_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_2906_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_2906_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_5346_22 | ACLineSegment | Line | 0.51338 | 0.005661 | 0.005661 | 0.0036989 | 1.1027 | 0 | 0 | 0 | 2024-01-21 20:55 | FALSE | 1 | line_5346_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_725_22 | Transformer | Transformer | 0.07125 | 0.005661 | 0.005661 | 0.0036989 | 7.9453 | 0 | 0 | 0 | 2024-01-21 20:55 | FALSE | 1 | tr_725_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_3013_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_3013_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_5411_22 | ACLineSegment | Line | 0.51338 | 0.0083287 | 0.0083287 | 0.0057344 | 1.6223 | 0 | 0 | 0 | 2024-01-20 14:55 | FALSE | 1 | line_5411_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_756_22 | Transformer | Transformer | 0.07125 | 0.0083287 | 0.0083287 | 0.0057344 | 11.6893 | 0 | 0 | 0 | 2024-01-20 14:55 | FALSE | 1 | tr_756_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_3024_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_3024_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_5184_22 | ACLineSegment | Line | 0.51338 | 0.0063107 | 0.0063107 | 0.004566 | 1.2292 | 0 | 0 | 0 | 2024-01-20 20:00 | FALSE | 1 | line_5184_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_647_22 | Transformer | Transformer | 0.07125 | 0.0063107 | 0.0063107 | 0.004566 | 8.8571 | 0 | 0 | 0 | 2024-01-20 20:00 | FALSE | 1 | tr_647_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_3087_22 | ACLineSegment | Line | 0.034884 | 0.005931 | 0.005931 | 0.0042276 | 17.0024 | 0 | 0 | 0 | 2024-01-20 14:55 | FALSE | 1 | line_3087_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_3088_22 | ACLineSegment | Line | 0.034884 | 0.005931 | 0.005931 | 0.0042276 | 17.0024 | 0 | 0 | 0 | 2024-01-20 14:55 | FALSE | 1 | line_3088_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_3089_22 | ACLineSegment | Line | 0.034884 | 0.026422 | 0.026422 | 0.017758 | 75.7436 | 0 | 0 | 0 | 2024-07-10 08:00 | FALSE | 1 | line_3089_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | tr_636_22 | Transformer | Transformer | 0.0475 | 0.029277 | 0.029277 | 0.021453 | 61.6368 | 0 | 0 | 0 | 2024-07-10 08:00 | FALSE | 1 | tr_636_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_3090_22 | ACLineSegment | Line | 0.034884 | 0.026422 | 0.026422 | 0.017758 | 75.7436 | 0 | 0 | 0 | 2024-07-10 08:00 | FALSE | 1 | line_3090_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_3093_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_3093_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_5113_22 | ACLineSegment | Line | 0.029092 | 0.0062772 | 0.0062772 | 0.0046059 | 21.5774 | 0 | 0 | 0 | 2024-07-15 07:55 | FALSE | 1 | line_5113_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | tr_614_22 | Transformer | Transformer | 0.0475 | 0.0062772 | 0.0062772 | 0.0046059 | 13.2151 | 0 | 0 | 0 | 2024-07-15 07:55 | FALSE | 1 | tr_614_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_3096_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_3096_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_5727_22 | ACLineSegment | Line | 0.034884 | 0.0049234 | 0.0049234 | 0.0027755 | 14.1139 | 0 | 0 | 0 | 2024-07-15 11:55 | FALSE | 1 | line_5727_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | tr_933_22 | Transformer | Transformer | 0.02375 | 0.0049234 | 0.0049234 | 0.0027755 | 20.7302 | 0 | 0 | 0 | 2024-07-15 11:55 | FALSE | 1 | tr_933_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_3134_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_3134_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_5726_22 | ACLineSegment | Line | 0.51338 | 0.0056436 | 0.0056436 | 0.0036724 | 1.0993 | 0 | 0 | 0 | 2024-01-17 16:00 | FALSE | 1 | line_5726_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_932_22 | Transformer | Transformer | 0.07125 | 0.0056436 | 0.0056436 | 0.0036724 | 7.9208 | 0 | 0 | 0 | 2024-01-17 16:00 | FALSE | 1 | tr_932_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_3190_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_3190_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_5543_22 | ACLineSegment | Line | 0.51338 | 0.0066615 | 0.0066615 | 0.0046795 | 1.2976 | 0 | 0 | 0 | 2024-07-16 03:00 | FALSE | 1 | line_5543_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_844_22 | Transformer | Transformer | 0.07125 | 0.0066615 | 0.0066615 | 0.0046795 | 9.3495 | 0 | 0 | 0 | 2024-07-16 03:00 | FALSE | 1 | tr_844_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_3203_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_3203_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_5557_22 | ACLineSegment | Line | 0.034884 | 0.0061846 | 0.0061846 | 0.0044629 | 17.7292 | 0 | 0 | 0 | 2024-01-20 12:00 | FALSE | 1 | line_5557_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | tr_853_22 | Transformer | Transformer | 0.02375 | 0.0061846 | 0.0061846 | 0.0044629 | 26.0403 | 0 | 0 | 0 | 2024-01-20 12:00 | FALSE | 1 | tr_853_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_3205_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_3205_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_5519_22 | ACLineSegment | Line | 0.034884 | 0.0028752 | 0.0028752 | 0.0015425 | 8.2422 | 0 | 0 | 0 | 2024-07-15 14:50 | FALSE | 1 | line_5519_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | tr_833_22 | Transformer | Transformer | 0.02375 | 0.0028752 | 0.0028752 | 0.0015425 | 12.1059 | 0 | 0 | 0 | 2024-07-15 14:50 | FALSE | 1 | tr_833_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_3206_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_3206_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_5567_22 | ACLineSegment | Line | 0.51338 | 0.0067399 | 0.0067399 | 0.0050182 | 1.3128 | 0 | 0 | 0 | 2024-07-15 20:00 | FALSE | 1 | line_5567_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_858_22 | Transformer | Transformer | 0.07125 | 0.0067399 | 0.0067399 | 0.0050182 | 9.4595 | 0 | 0 | 0 | 2024-07-15 20:00 | FALSE | 1 | tr_858_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_3207_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_3207_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_5568_22 | ACLineSegment | Line | 0.51338 | 0.0048531 | 0.0048531 | 0.0035113 | 0.94533 | 0 | 0 | 0 | 2024-07-15 17:45 | FALSE | 1 | line_5568_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_859_22 | Transformer | Transformer | 0.07125 | 0.0048531 | 0.0048531 | 0.0035113 | 6.8114 | 0 | 0 | 0 | 2024-07-15 17:45 | FALSE | 1 | tr_859_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_3422_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_3422_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_5749_22 | ACLineSegment | Line | 0.025406 | 0.0061323 | 0.0061323 | 0.0033226 | 24.1376 | 0 | 0 | 0 | 2024-01-20 23:05 | FALSE | 1 | line_5749_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | tr_946_22 | Transformer | Transformer | 0.02375 | 0.0061323 | 0.0061323 | 0.0033226 | 25.8204 | 0 | 0 | 0 | 2024-01-20 23:05 | FALSE | 1 | tr_946_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_3423_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_3423_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_5782_22 | ACLineSegment | Line | 0.025406 | 0.0053523 | 0.0053523 | 0.0026037 | 21.0672 | 0 | 0 | 0 | 2024-01-20 09:55 | FALSE | 1 | line_5782_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | tr_962_22 | Transformer | Transformer | 0.02375 | 0.0053523 | 0.0053523 | 0.0026037 | 22.5359 | 0 | 0 | 0 | 2024-01-20 09:55 | FALSE | 1 | tr_962_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_3430_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_3430_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_5778_22 | ACLineSegment | Line | 0.034884 | 0.0038259 | 0.0038259 | 0.0015378 | 10.9676 | 0 | 0 | 0 | 2024-01-20 22:55 | FALSE | 1 | line_5778_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | tr_959_22 | Transformer | Transformer | 0.02375 | 0.0038259 | 0.0038259 | 0.0015378 | 16.109 | 0 | 0 | 0 | 2024-01-20 22:55 | FALSE | 1 | tr_959_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_3435_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_3435_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_5750_22 | ACLineSegment | Line | 0.51338 | 0.0051956 | 0.0051956 | 0.0035241 | 1.012 | 0 | 0 | 0 | 2024-07-10 19:00 | FALSE | 1 | line_5750_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_947_22 | Transformer | Transformer | 0.07125 | 0.0051956 | 0.0051956 | 0.0035241 | 7.292 | 0 | 0 | 0 | 2024-07-10 19:00 | FALSE | 1 | tr_947_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_3565_22 | ACLineSegment | Line | 13.5424 | 0.0059441 | 0.0059441 | 0.0044 | 0.043892 | 0 | 0 | 0 | 2024-07-05 09:00 | FALSE | 1 | line_3565_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_3566_22 | ACLineSegment | Line | 13.5424 | 0.036773 | 0.036773 | 0.023049 | 0.27154 | 0 | 0 | 0 | 2024-01-20 19:55 | FALSE | 1 | line_3566_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_4608_22 | ACLineSegment | Line | 13.5424 | 0.57571 | 0.57571 | 0.45248 | 4.2512 | 0 | 0 | 0 | 2024-01-21 04:05 | FALSE | 1 | line_4608_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_4889_22 | ACLineSegment | Line | 13.5424 | 0.60243 | 0.60243 | 0.47897 | 4.4485 | 0 | 0 | 0 | 2024-01-21 04:05 | FALSE | 1 | line_4889_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_4464_22 | ACLineSegment | Line | 13.5424 | 0.16895 | 0.16895 | 0.13133 | 1.2476 | 0 | 0 | 0 | 2024-01-17 16:00 | FALSE | 1 | line_4464_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_4919_22 | ACLineSegment | Line | 13.5424 | 0.19182 | 0.19182 | 0.1513 | 1.4165 | 0 | 0 | 0 | 2024-01-17 16:00 | FALSE | 1 | line_4919_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_3662_22 | ACLineSegment | Line | 12.3112 | 0.28113 | 0.28113 | 0.22849 | 2.2835 | 0 | 0 | 0 | 2024-01-17 16:00 | FALSE | 1 | line_3662_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_3663_22 | ACLineSegment | Line | 12.3112 | 0.29065 | 0.29065 | 0.23528 | 2.3609 | 0 | 0 | 0 | 2024-01-21 04:05 | FALSE | 1 | line_3663_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_6503_22 | ACLineSegment | Line | 12.3112 | 0.29438 | 0.29438 | 0.23773 | 2.3911 | 0 | 0 | 0 | 2024-01-21 04:05 | FALSE | 1 | line_6503_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_4823_22 | ACLineSegment | Line | 13.5424 | 0.079508 | 0.079508 | 0.06012 | 0.58711 | 0 | 0 | 0 | 2024-01-17 08:00 | FALSE | 1 | line_4823_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_3782_22 | ACLineSegment | Line | 12.3112 | 0.0097916 | 0.0097916 | 0.0073136 | 0.079534 | 0 | 0 | 0 | 2024-07-15 05:55 | FALSE | 1 | line_3782_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_3857_22 | ACLineSegment | Line | 0.94778 | 0.0067151 | 0.0067151 | 0.0047782 | 0.70851 | 0 | 0 | 0 | 2024-07-09 12:00 | FALSE | 1 | line_3857_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_4921_22 | ACLineSegment | Line | 13.5424 | 0.0048531 | 0.0048531 | 0.0035113 | 0.035837 | 0 | 0 | 0 | 2024-07-15 17:45 | FALSE | 1 | line_4921_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_4549_22 | ACLineSegment | Line | 13.5424 | 0.022747 | 0.022747 | 0.017918 | 0.16797 | 0 | 0 | 0 | 2024-01-20 20:00 | FALSE | 1 | line_4549_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_3885_22 | ACLineSegment | Line | 12.3112 | 0.030493 | 0.030493 | 0.019869 | 0.24769 | 0 | 0 | 0 | 2024-01-22 04:00 | FALSE | 1 | line_3885_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_3886_22 | ACLineSegment | Line | 13.5424 | 0.11942 | 0.11942 | 0.090159 | 0.88183 | 0 | 0 | 0 | 2024-01-21 04:05 | FALSE | 1 | line_3886_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_3983_22 | ACLineSegment | Line | 13.5424 | 0.12916 | 0.12916 | 0.098773 | 0.95376 | 0 | 0 | 0 | 2024-01-21 04:05 | FALSE | 1 | line_3983_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_3887_22 | ACLineSegment | Line | 12.3112 | 0.091999 | 0.091999 | 0.070125 | 0.74728 | 0 | 0 | 0 | 2024-01-20 22:55 | FALSE | 1 | line_3887_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_4582_22 | ACLineSegment | Line | 12.3112 | 0.088495 | 0.088495 | 0.067328 | 0.71882 | 0 | 0 | 0 | 2024-01-17 08:00 | FALSE | 1 | line_4582_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_3912_22 | ACLineSegment | Line | 13.5424 | 0.30373 | 0.30373 | 0.24616 | 2.2428 | 0 | 0 | 0 | 2024-01-21 04:05 | FALSE | 1 | line_3912_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_3913_22 | ACLineSegment | Line | 13.5424 | 0.30651 | 0.30651 | 0.24831 | 2.2634 | 0 | 0 | 0 | 2024-01-21 04:05 | FALSE | 1 | line_3913_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_5156_22 | ACLineSegment | Line | 13.5424 | 0.0028752 | 0.0028752 | 0.0015425 | 0.021231 | 0 | 0 | 0 | 2024-07-15 14:50 | FALSE | 1 | line_5156_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_5157_22 | ACLineSegment | Line | 12.3112 | 0.29791 | 0.29791 | 0.24115 | 2.4198 | 0 | 0 | 0 | 2024-01-21 04:05 | FALSE | 1 | line_5157_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_5463_22 | ACLineSegment | Line | 13.5424 | 0.31016 | 0.31016 | 0.25157 | 2.2903 | 0 | 0 | 0 | 2024-01-21 04:05 | FALSE | 1 | line_5463_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_3966_22 | ACLineSegment | Line | 13.5424 | 0.011382 | 0.011382 | 0.0085231 | 0.084046 | 0 | 0 | 0 | 2024-01-20 23:05 | FALSE | 1 | line_3966_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_4904_22 | ACLineSegment | Line | 13.5424 | 0.1947 | 0.1947 | 0.12193 | 1.4377 | 0 | 0 | 0 | 2024-10-02 08:00 | FALSE | 1 | line_4904_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_4905_22 | ACLineSegment | Line | 13.5424 | 0.18159 | 0.18159 | 0.11099 | 1.3409 | 0 | 0 | 0 | 2024-10-02 08:00 | FALSE | 1 | line_4905_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_3982_22 | ACLineSegment | Line | 2.3694 | 0.0080467 | 0.0080467 | 0.0054382 | 0.3396 | 0 | 0 | 0 | 2024-07-16 | FALSE | 1 | line_3982_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | tr_436_22 | Transformer | Transformer | 0.0475 | 0.0080467 | 0.0080467 | 0.0054382 | 16.9404 | 0 | 0 | 0 | 2024-07-16 | FALSE | 1 | tr_436_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_3984_22 | ACLineSegment | Line | 12.3112 | 0.13755 | 0.13755 | 0.10569 | 1.1172 | 0 | 0 | 0 | 2024-01-21 04:05 | FALSE | 1 | line_3984_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_3988_22 | ACLineSegment | Line | 13.5424 | 0.14852 | 0.14852 | 0.083048 | 1.0967 | 0 | 0 | 0 | 2024-10-02 08:00 | FALSE | 1 | line_3988_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_4440_22 | ACLineSegment | Line | 13.5424 | 0.15152 | 0.15152 | 0.086986 | 1.1188 | 0 | 0 | 0 | 2024-10-02 08:00 | FALSE | 1 | line_4440_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_3989_22 | ACLineSegment | Line | 13.5424 | 0.04196 | 0.04196 | 0.030691 | 0.30984 | 0 | 0 | 0 | 2024-07-15 08:00 | FALSE | 1 | line_3989_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_4560_22 | ACLineSegment | Line | 13.5424 | 0.037788 | 0.037788 | 0.027562 | 0.27904 | 0 | 0 | 0 | 2024-07-15 08:00 | FALSE | 1 | line_4560_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_40_22 | ACLineSegment | Line | 0.029092 | 0.004198 | 0.004198 | 0.0030493 | 14.4303 | 0 | 0 | 0 | 2024-01-20 20:00 | FALSE | 1 | line_40_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_41_22 | ACLineSegment | Line | 0.029092 | 0.004198 | 0.004198 | 0.0030493 | 14.4303 | 0 | 0 | 0 | 2024-01-20 20:00 | FALSE | 1 | line_41_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_42_22 | ACLineSegment | Line | 0.025406 | 0.0048014 | 0.0048014 | 0.0027176 | 18.8991 | 0 | 0 | 0 | 2024-07-15 22:50 | FALSE | 1 | line_42_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_4122_22 | ACLineSegment | Line | 2.3694 | 0.0046771 | 0.0046771 | 0.0025091 | 0.19739 | 0 | 0 | 0 | 2024-01-20 05:00 | FALSE | 1 | line_4122_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_4891_22 | ACLineSegment | Line | 12.3112 | 0.0093285 | 0.0093285 | 0.0062802 | 0.075772 | 0 | 0 | 0 | 2024-01-20 05:00 | FALSE | 1 | line_4891_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_43_22 | ACLineSegment | Line | 0.025406 | 0.0048014 | 0.0048014 | 0.0027176 | 18.8991 | 0 | 0 | 0 | 2024-07-15 22:50 | FALSE | 1 | line_43_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_4262_22 | ACLineSegment | Line | 12.3112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_4262_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_5168_22 | ACLineSegment | Line | 12.3112 | 0.0082977 | 0.0082977 | 0.0053818 | 0.067399 | 0 | 0 | 0 | 2024-07-16 03:00 | FALSE | 1 | line_5168_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_4684_22 | ACLineSegment | Line | 13.5424 | 0.63769 | 0.63769 | 0.51543 | 4.7088 | 0 | 0 | 0 | 2024-01-21 04:05 | FALSE | 1 | line_4684_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_4685_22 | ACLineSegment | Line | 13.5424 | 0.61895 | 0.61895 | 0.49599 | 4.5705 | 0 | 0 | 0 | 2024-01-21 04:05 | FALSE | 1 | line_4685_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_4387_22 | ACLineSegment | Line | 13.5424 | 0.077598 | 0.077598 | 0.059142 | 0.573 | 0 | 0 | 0 | 2024-01-17 16:00 | FALSE | 1 | line_4387_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_4792_22 | ACLineSegment | Line | 13.5424 | 0.072986 | 0.072986 | 0.054283 | 0.53895 | 0 | 0 | 0 | 2024-01-17 16:00 | FALSE | 1 | line_4792_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_4391_22 | ACLineSegment | Line | 12.3112 | 0.2629 | 0.2629 | 0.21429 | 2.1354 | 0 | 0 | 0 | 2024-01-20 10:00 | FALSE | 1 | line_4391_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_4392_22 | ACLineSegment | Line | 12.3112 | 0.25225 | 0.25225 | 0.20412 | 2.0489 | 0 | 0 | 0 | 2024-01-20 10:00 | FALSE | 1 | line_4392_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_4830_22 | ACLineSegment | Line | 12.3112 | 0.248 | 0.248 | 0.20096 | 2.0144 | 0 | 0 | 0 | 2024-01-20 10:00 | FALSE | 1 | line_4830_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_4393_22 | ACLineSegment | Line | 12.3112 | 0.0096125 | 0.0096125 | 0.0068829 | 0.078079 | 0 | 0 | 0 | 2024-01-20 05:00 | FALSE | 1 | line_4393_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_4419_22 | ACLineSegment | Line | 13.5424 | 0.0055171 | 0.0055171 | 0.0038878 | 0.04074 | 0 | 0 | 0 | 2024-01-20 20:00 | FALSE | 1 | line_4419_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_4439_22 | ACLineSegment | Line | 13.5424 | 0.15898 | 0.15898 | 0.093056 | 1.174 | 0 | 0 | 0 | 2024-10-02 08:00 | FALSE | 1 | line_4439_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_44_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_44_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_4581_22 | ACLineSegment | Line | 0.51338 | 0.0047034 | 0.0047034 | 0.0035068 | 0.91616 | 0 | 0 | 0 | 2024-01-20 23:05 | FALSE | 1 | line_4581_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_381_22 | Transformer | Transformer | 0.07125 | 0.0047034 | 0.0047034 | 0.0035068 | 6.6012 | 0 | 0 | 0 | 2024-01-20 23:05 | FALSE | 1 | tr_381_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_4434_22 | ACLineSegment | Line | 12.3112 | 0.21356 | 0.21356 | 0.16925 | 1.7347 | 0 | 0 | 0 | 2024-01-17 16:00 | FALSE | 1 | line_4434_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_4435_22 | ACLineSegment | Line | 13.5424 | 0.19446 | 0.19446 | 0.15384 | 1.4359 | 0 | 0 | 0 | 2024-01-17 16:00 | FALSE | 1 | line_4435_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_4436_22 | ACLineSegment | Line | 12.3112 | 0.02141 | 0.02141 | 0.014874 | 0.17391 | 0 | 0 | 0 | 2024-01-20 23:05 | FALSE | 1 | line_4436_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_337_22 | Transformer | Transformer | 0.02375 | 0.0043123 | 0.0043123 | 0.0021451 | 18.1571 | 0 | 0 | 0 | 2024-01-20 12:00 | FALSE | 1 | tr_337_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_4457_22 | ACLineSegment | Line | 13.5424 | 0.033078 | 0.033078 | 0.023359 | 0.24426 | 0 | 0 | 0 | 2024-01-17 16:00 | FALSE | 1 | line_4457_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_4458_22 | ACLineSegment | Line | 13.5424 | 0.037284 | 0.037284 | 0.027199 | 0.27532 | 0 | 0 | 0 | 2024-01-17 16:00 | FALSE | 1 | line_4458_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_4678_22 | ACLineSegment | Line | 13.5424 | 0.010339 | 0.010339 | 0.0075647 | 0.076348 | 0 | 0 | 0 | 2024-01-21 02:00 | FALSE | 1 | line_4678_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_4548_22 | ACLineSegment | Line | 13.5424 | 0.031694 | 0.031694 | 0.02504 | 0.23404 | 0 | 0 | 0 | 2024-01-20 07:55 | FALSE | 1 | line_4548_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_4462_22 | ACLineSegment | Line | 0.025406 | 0.0043123 | 0.0043123 | 0.0021451 | 16.9738 | 0 | 0 | 0 | 2024-01-20 12:00 | FALSE | 1 | line_4462_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_98_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_98_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_4463_22 | ACLineSegment | Line | 13.5424 | 0.1656 | 0.1656 | 0.12782 | 1.2229 | 0 | 0 | 0 | 2024-01-17 16:00 | FALSE | 1 | line_4463_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_4770_22 | ACLineSegment | Line | 13.5424 | 0.14256 | 0.14256 | 0.11135 | 1.0527 | 0 | 0 | 0 | 2024-01-17 16:00 | FALSE | 1 | line_4770_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_4476_22 | ACLineSegment | Line | 12.3112 | 0.014916 | 0.014916 | 0.010811 | 0.12116 | 0 | 0 | 0 | 2024-07-15 23:55 | FALSE | 1 | line_4476_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_4477_22 | ACLineSegment | Line | 12.3112 | 0.23285 | 0.23285 | 0.18645 | 1.8914 | 0 | 0 | 0 | 2024-01-17 16:00 | FALSE | 1 | line_4477_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_5109_22 | ACLineSegment | Line | 12.3112 | 0.23516 | 0.23516 | 0.18867 | 1.9101 | 0 | 0 | 0 | 2024-01-17 16:00 | FALSE | 1 | line_5109_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_45_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_45_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_4744_22 | ACLineSegment | Line | 0.51338 | 0.0091275 | 0.0091275 | 0.0067774 | 1.7779 | 0 | 0 | 0 | 2024-01-20 13:00 | FALSE | 1 | line_4744_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_448_22 | Transformer | Transformer | 0.095 | 0.0091275 | 0.0091275 | 0.0067774 | 9.6079 | 0 | 0 | 0 | 2024-01-20 13:00 | FALSE | 1 | tr_448_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_4924_22 | ACLineSegment | Line | 13.5424 | 0.1772 | 0.1772 | 0.10698 | 1.3085 | 0 | 0 | 0 | 2024-10-02 08:00 | FALSE | 1 | line_4924_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_4545_22 | ACLineSegment | Line | 12.3112 | 0.18767 | 0.18767 | 0.14267 | 1.5243 | 0 | 0 | 0 | 2024-01-21 04:05 | FALSE | 1 | line_4545_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_4553_22 | ACLineSegment | Line | 12.3112 | 0.010238 | 0.010238 | 0.0072008 | 0.083159 | 0 | 0 | 0 | 2024-01-21 00:55 | FALSE | 1 | line_4553_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_4554_22 | ACLineSegment | Line | 12.3112 | 0.19942 | 0.19942 | 0.15173 | 1.6198 | 0 | 0 | 0 | 2024-01-21 04:05 | FALSE | 1 | line_4554_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_4546_22 | ACLineSegment | Line | 12.3112 | 0.18548 | 0.18548 | 0.14113 | 1.5066 | 0 | 0 | 0 | 2024-01-21 04:05 | FALSE | 1 | line_4546_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_4561_22 | ACLineSegment | Line | 13.5424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_4561_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_4562_22 | ACLineSegment | Line | 13.5424 | 0.032266 | 0.032266 | 0.023685 | 0.23826 | 0 | 0 | 0 | 2024-07-15 08:00 | FALSE | 1 | line_4562_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_4717_22 | ACLineSegment | Line | 13.5424 | 0.028997 | 0.028997 | 0.0206 | 0.21412 | 0 | 0 | 0 | 2024-07-15 08:00 | FALSE | 1 | line_4717_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_4570_22 | ACLineSegment | Line | 13.5424 | 0.0061184 | 0.0061184 | 0.004163 | 0.04518 | 0 | 0 | 0 | 2024-01-20 19:55 | FALSE | 1 | line_4570_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_4929_22 | ACLineSegment | Line | 13.5424 | 0.011355 | 0.011355 | 0.0077546 | 0.08385 | 0 | 0 | 0 | 2024-07-14 08:05 | FALSE | 1 | line_4929_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_4583_22 | ACLineSegment | Line | 12.3112 | 0.082862 | 0.082862 | 0.062194 | 0.67306 | 0 | 0 | 0 | 2024-01-17 08:00 | FALSE | 1 | line_4583_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_4584_22 | ACLineSegment | Line | 12.3112 | 0.17695 | 0.17695 | 0.13459 | 1.4373 | 0 | 0 | 0 | 2024-01-21 04:05 | FALSE | 1 | line_4584_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_4609_22 | ACLineSegment | Line | 13.5424 | 0.56386 | 0.56386 | 0.44288 | 4.1637 | 0 | 0 | 0 | 2024-01-21 04:05 | FALSE | 1 | line_4609_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_4610_22 | ACLineSegment | Line | 13.5424 | 0.0063571 | 0.0063571 | 0.0045636 | 0.046942 | 0 | 0 | 0 | 2024-01-18 01:55 | FALSE | 1 | line_4610_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_4938_22 | ACLineSegment | Line | 13.5424 | 0.23705 | 0.23705 | 0.18117 | 1.7504 | 0 | 0 | 0 | 2024-01-21 04:05 | FALSE | 1 | line_4938_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_5129_22 | ACLineSegment | Line | 13.5424 | 0.32089 | 0.32089 | 0.26004 | 2.3695 | 0 | 0 | 0 | 2024-01-21 04:05 | FALSE | 1 | line_5129_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_4658_22 | ACLineSegment | Line | 12.3112 | 0.26664 | 0.26664 | 0.21744 | 2.1658 | 0 | 0 | 0 | 2024-01-20 10:00 | FALSE | 1 | line_4658_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_4910_22 | ACLineSegment | Line | 13.5424 | 0.0064854 | 0.0064854 | 0.0047814 | 0.04789 | 0 | 0 | 0 | 2024-01-17 11:55 | FALSE | 1 | line_4910_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_4682_22 | ACLineSegment | Line | 12.3112 | 0.016789 | 0.016789 | 0.01227 | 0.13637 | 0 | 0 | 0 | 2024-07-15 05:55 | FALSE | 1 | line_4682_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_5565_22 | ACLineSegment | Line | 13.5424 | 0.6423 | 0.6423 | 0.51863 | 4.7429 | 0 | 0 | 0 | 2024-01-21 04:05 | FALSE | 1 | line_5565_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_5427_22 | ACLineSegment | Line | 13.5424 | 0.61699 | 0.61699 | 0.4933 | 4.556 | 0 | 0 | 0 | 2024-01-21 04:05 | FALSE | 1 | line_5427_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_1404_22 | Transformer | Transformer | 0.07125 | 0.0056396 | 0.0056396 | 0.0033 | 7.9152 | 0 | 0 | 0 | 2024-01-21 14:50 | FALSE | 1 | tr_1404_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_480_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_480_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_6601_22 | ACLineSegment | Line | 0.51338 | 0.0056396 | 0.0056396 | 0.0033 | 1.0985 | 0 | 0 | 0 | 2024-01-21 14:50 | FALSE | 1 | line_6601_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_4864_22 | ACLineSegment | Line | 12.3112 | 0.27456 | 0.27456 | 0.22272 | 2.2302 | 0 | 0 | 0 | 2024-01-20 10:00 | FALSE | 1 | line_4864_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_4875_22 | ACLineSegment | Line | 13.5424 | 0.21249 | 0.21249 | 0.16137 | 1.5691 | 0 | 0 | 0 | 2024-01-21 04:05 | FALSE | 1 | line_4875_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_4876_22 | ACLineSegment | Line | 13.5424 | 0.2063 | 0.2063 | 0.15805 | 1.5234 | 0 | 0 | 0 | 2024-01-21 04:05 | FALSE | 1 | line_4876_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_5117_22 | ACLineSegment | Line | 13.5424 | 0.21523 | 0.21523 | 0.16521 | 1.5893 | 0 | 0 | 0 | 2024-01-21 04:05 | FALSE | 1 | line_5117_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_5777_22 | ACLineSegment | Line | 13.5424 | 0.20475 | 0.20475 | 0.15669 | 1.5119 | 0 | 0 | 0 | 2024-01-21 04:05 | FALSE | 1 | line_5777_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_4913_22 | ACLineSegment | Line | 13.5424 | 0.19652 | 0.19652 | 0.12397 | 1.4512 | 0 | 0 | 0 | 2024-10-02 08:00 | FALSE | 1 | line_4913_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_4907_22 | ACLineSegment | Line | 12.3112 | 0.14039 | 0.14039 | 0.10918 | 1.1403 | 0 | 0 | 0 | 2024-01-20 22:55 | FALSE | 1 | line_4907_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_4908_22 | ACLineSegment | Line | 12.3112 | 0.14603 | 0.14603 | 0.11396 | 1.1861 | 0 | 0 | 0 | 2024-01-21 04:05 | FALSE | 1 | line_4908_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_5428_22 | ACLineSegment | Line | 13.5424 | 0.78857 | 0.78857 | 0.62186 | 5.823 | 0 | 0 | 0 | 2024-07-09 | FALSE | 1 | line_5428_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_5566_22 | ACLineSegment | Line | 13.5424 | 0.0088988 | 0.0088988 | 0.0061734 | 0.065711 | 0 | 0 | 0 | 2024-01-20 22:55 | FALSE | 1 | line_5566_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_4939_22 | ACLineSegment | Line | 13.5424 | 0.2207 | 0.2207 | 0.16954 | 1.6297 | 0 | 0 | 0 | 2024-01-21 04:05 | FALSE | 1 | line_4939_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_547_22 | Transformer | Transformer | 0.02375 | 0.014315 | 0.014315 | 0.0080344 | 60.275 | 0 | 0 | 0 | 2024-01-17 19:05 | FALSE | 1 | tr_547_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_4935_22 | ACLineSegment | Line | 12.3112 | 0.0056313 | 0.0056313 | 0.0037819 | 0.045741 | 0 | 0 | 0 | 2024-07-16 | FALSE | 1 | line_4935_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_4965_22 | ACLineSegment | Line | 0.034884 | 0.01136 | 0.01136 | 0.0064891 | 32.5668 | 0 | 0 | 0 | 2024-07-11 21:55 | FALSE | 1 | line_4965_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_4966_22 | ACLineSegment | Line | 0.034884 | 0.0043419 | 0.0043419 | 0.0026049 | 12.4469 | 0 | 0 | 0 | 2024-01-20 17:15 | FALSE | 1 | line_4966_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_5099_22 | ACLineSegment | Line | 12.3112 | 0.026091 | 0.026091 | 0.019274 | 0.21193 | 0 | 0 | 0 | 2024-01-21 04:05 | FALSE | 1 | line_5099_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_5111_22 | ACLineSegment | Line | 12.3112 | 0.23892 | 0.23892 | 0.19299 | 1.9406 | 0 | 0 | 0 | 2024-01-17 16:00 | FALSE | 1 | line_5111_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_5442_22 | ACLineSegment | Line | 13.5424 | 0.31582 | 0.31582 | 0.25636 | 2.3321 | 0 | 0 | 0 | 2024-01-21 04:05 | FALSE | 1 | line_5442_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_5345_22 | ACLineSegment | Line | 12.3112 | 0.0058783 | 0.0058783 | 0.0037624 | 0.047747 | 0 | 0 | 0 | 2024-01-20 05:00 | FALSE | 1 | line_5345_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_5429_22 | ACLineSegment | Line | 13.5424 | 0.79259 | 0.79259 | 0.62478 | 5.8527 | 0 | 0 | 0 | 2024-07-09 | TRUE | 1 | line_5429_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | tr_1237_22 | Transformer | Transformer | 0.02375 | 0.0077562 | 0.0077562 | 0.0048113 | 32.6578 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | tr_1237_22 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_142 | line_6359_22 | ACLineSegment | Line | 0.034884 | 0.0077562 | 0.0077562 | 0.0048113 | 22.2347 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | line_6359_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_912_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_912_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_142 | line_6639_22 | ACLineSegment | Line | 0.51338 | 0.0069972 | 0.0069972 | 0.0050948 | 1.363 | 0 | 0 | 0 | 2024-01-21 04:05 | FALSE | 1 | line_6639_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_142 | line_667_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_667_22 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_116127_21 | ACLineSegment | Line | 13.5424 | 0.49804 | 0.49804 | 0.38066 | 3.6777 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | line_116127_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | line_128625_21 | ACLineSegment | Line | 13.5424 | 0.46056 | 0.46056 | 0.35756 | 3.4009 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | line_128625_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | tr_10640_21 | Transformer | Transformer | 0.07125 | 0.0048594 | 0.0048594 | 0.0030174 | 6.8202 | 0 | 0 | 0 | 2024-01-17 07:00 | FALSE | 1 | tr_10640_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_126656_21 | ACLineSegment | Line | 0.94778 | 0.035246 | 0.035246 | 0.022835 | 3.7188 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | line_126656_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_107809_21 | ACLineSegment | Line | 13.5424 | 1.8374 | 1.8374 | 1.3719 | 13.5678 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | line_107809_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | line_107810_21 | ACLineSegment | Line | 13.5424 | 1.8959 | 1.8959 | 1.4115 | 13.9998 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | line_107810_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | tr_660_21 | Transformer | Transformer | 0.02375 | 0.0093892 | 0.0093892 | 0.0053915 | 39.5335 | 0 | 0 | 0 | 2024-01-20 07:25 | FALSE | 1 | tr_660_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_107808_21 | ACLineSegment | Line | 0.94778 | 0.050634 | 0.050634 | 0.034461 | 5.3423 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | line_107808_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_106465_21 | ACLineSegment | Line | 13.5424 | 0.034336 | 0.034336 | 0.023226 | 0.25355 | 0 | 0 | 0 | 2024-01-17 20:10 | FALSE | 1 | line_106465_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | line_127115_21 | ACLineSegment | Line | 13.5424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_127115_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | tr_9246_21 | Transformer | Transformer | 0.1425 | 0.0074636 | 0.0074636 | 0.0044177 | 5.2376 | 0 | 0 | 0 | 2024-01-20 13:05 | FALSE | 1 | tr_9246_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_108159_21 | ACLineSegment | Line | 0.94778 | 0.029091 | 0.029091 | 0.01967 | 3.0694 | 0 | 0 | 0 | 2024-01-20 21:15 | FALSE | 1 | line_108159_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_108322_21 | ACLineSegment | Line | 13.5424 | 1.9494 | 1.9494 | 1.4588 | 14.3946 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | line_108322_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | line_108323_21 | ACLineSegment | Line | 13.5424 | 2.2897 | 2.2897 | 1.713 | 16.9078 | 0 | 0 | 0 | 2024-01-21 | TRUE | 1 | line_108323_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | tr_833_21 | Transformer | Transformer | 0.02375 | 0.025146 | 0.025146 | 0.014511 | 105.8766 | 12 | 1 | 0.011391 | 2024-01-20 10:55 | FALSE | 1 | tr_833_21 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_108321_21 | ACLineSegment | Line | 0.94778 | 0.33294 | 0.33294 | 0.23969 | 35.1285 | 0 | 0 | 0 | 2024-01-20 20:20 | FALSE | 1 | line_108321_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_109743_21 | ACLineSegment | Line | 13.5424 | 0.20708 | 0.20708 | 0.15396 | 1.5292 | 0 | 0 | 0 | 2024-01-20 05:00 | FALSE | 1 | line_109743_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | line_110125_21 | ACLineSegment | Line | 13.5424 | 0.084613 | 0.084613 | 0.063536 | 0.6248 | 0 | 0 | 0 | 2024-01-17 23:55 | FALSE | 1 | line_110125_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | tr_1495_21 | Transformer | Transformer | 0.02375 | 0.0054309 | 0.0054309 | 0.0028824 | 22.8671 | 0 | 0 | 0 | 2024-01-20 19:55 | FALSE | 1 | tr_1495_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_110213_21 | ACLineSegment | Line | 0.94778 | 0.062919 | 0.062919 | 0.045891 | 6.6386 | 0 | 0 | 0 | 2024-01-21 01:25 | FALSE | 1 | line_110213_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_108303_21 | ACLineSegment | Line | 13.5424 | 0.96166 | 0.96166 | 0.72974 | 7.1012 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | line_108303_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | line_110281_21 | ACLineSegment | Line | 13.5424 | 1.3291 | 1.3291 | 0.99909 | 9.8144 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | line_110281_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | tr_1520_21 | Transformer | Transformer | 0.02375 | 0.019896 | 0.019896 | 0.013951 | 83.7747 | 0 | 0 | 0 | 2024-01-20 23:55 | FALSE | 1 | tr_1520_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_110282_21 | ACLineSegment | Line | 0.94778 | 0.35507 | 0.35507 | 0.25573 | 37.4635 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_110282_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_111505_21 | ACLineSegment | Line | 0.94778 | 0.0029693 | 0.0029693 | 0.0015123 | 0.31329 | 0 | 0 | 0 | 2024-01-17 22:10 | FALSE | 1 | line_111505_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | tr_1985_21 | Transformer | Transformer | 0.02375 | 0.00671 | 0.00671 | 0.0031629 | 28.2528 | 0 | 0 | 0 | 2024-01-20 23:55 | FALSE | 1 | tr_1985_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_111504_21 | ACLineSegment | Line | 0.94778 | 0.0088065 | 0.0088065 | 0.0045082 | 0.92917 | 0 | 0 | 0 | 2024-01-20 23:55 | FALSE | 1 | line_111504_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | tr_2009_21 | Transformer | Transformer | 0.02375 | 0.0037348 | 0.0037348 | 0.0022713 | 15.7254 | 0 | 0 | 0 | 2024-01-21 01:25 | FALSE | 1 | tr_2009_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_116128_21 | ACLineSegment | Line | 13.5424 | 0.010719 | 0.010719 | 0.0068116 | 0.079152 | 0 | 0 | 0 | 2024-01-22 04:00 | FALSE | 1 | line_116128_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | tr_11870_21 | Transformer | Transformer | 0.475 | 0.0071783 | 0.0071783 | 0.0050335 | 1.5112 | 0 | 0 | 0 | 2024-01-22 04:00 | FALSE | 1 | tr_11870_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_110794_21 | ACLineSegment | Line | 13.5424 | 1.8165 | 1.8165 | 1.3563 | 13.4131 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | line_110794_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | line_111728_21 | ACLineSegment | Line | 13.5424 | 1.7395 | 1.7395 | 1.2996 | 12.8448 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | line_111728_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | tr_2082_21 | Transformer | Transformer | 0.02375 | 0.0047325 | 0.0047325 | 0.0026987 | 19.9263 | 0 | 0 | 0 | 2024-01-17 09:55 | FALSE | 1 | tr_2082_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_111729_21 | ACLineSegment | Line | 0.94778 | 0.078082 | 0.078082 | 0.05397 | 8.2384 | 0 | 0 | 0 | 2024-01-20 07:25 | FALSE | 1 | line_111729_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_108372_21 | ACLineSegment | Line | 13.5424 | 0.015716 | 0.015716 | 0.010035 | 0.11605 | 0 | 0 | 0 | 2024-01-20 23:55 | FALSE | 1 | line_108372_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | line_115816_21 | ACLineSegment | Line | 13.5424 | 0.047419 | 0.047419 | 0.029632 | 0.35015 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_115816_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | tr_3781_21 | Transformer | Transformer | 0.02375 | 0.0085198 | 0.0085198 | 0.0051093 | 35.8729 | 0 | 0 | 0 | 2024-01-17 17:55 | FALSE | 1 | tr_3781_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_112325_21 | ACLineSegment | Line | 0.94778 | 0.025559 | 0.025559 | 0.015005 | 2.6967 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_112325_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_112973_21 | ACLineSegment | Line | 13.5424 | 0.019697 | 0.019697 | 0.014848 | 0.14545 | 0 | 0 | 0 | 2024-01-21 03:05 | FALSE | 1 | line_112973_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | tr_12327_21 | Transformer | Transformer | 0.07125 | 0.0044955 | 0.0044955 | 0.0034699 | 6.3094 | 0 | 0 | 0 | 2024-01-20 21:15 | FALSE | 1 | tr_12327_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_112861_21 | ACLineSegment | Line | 0.94778 | 0.01617 | 0.01617 | 0.011907 | 1.7061 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | line_112861_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | tr_2431_21 | Transformer | Transformer | 0.02375 | 0.010358 | 0.010358 | 0.0055988 | 43.6133 | 0 | 0 | 0 | 2024-01-20 07:25 | FALSE | 1 | tr_2431_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_106667_21 | ACLineSegment | Line | 0.94778 | 0.41123 | 0.41123 | 0.29401 | 43.3889 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_106667_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_112222_21 | ACLineSegment | Line | 13.5424 | 0.36186 | 0.36186 | 0.26896 | 2.672 | 0 | 0 | 0 | 2024-07-15 23:05 | FALSE | 1 | line_112222_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | line_113499_21 | ACLineSegment | Line | 13.5424 | 0.36767 | 0.36767 | 0.27601 | 2.715 | 0 | 0 | 0 | 2024-07-15 23:05 | FALSE | 1 | line_113499_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | tr_10639_21 | Transformer | Transformer | 0.07125 | 0.0077068 | 0.0077068 | 0.0057941 | 10.8165 | 0 | 0 | 0 | 2024-06-26 11:00 | FALSE | 1 | tr_10639_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_106670_21 | ACLineSegment | Line | 0.94778 | 0.0052794 | 0.0052794 | 0.0036446 | 0.55703 | 0 | 0 | 0 | 2024-01-20 14:50 | FALSE | 1 | line_106670_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_129230_21 | ACLineSegment | Line | 13.5424 | 0.027947 | 0.027947 | 0.01818 | 0.20637 | 0 | 0 | 0 | 2024-01-21 01:25 | FALSE | 1 | line_129230_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | tr_10624_21 | Transformer | Transformer | 0.285 | 0.0052162 | 0.0052162 | 0.0041155 | 1.8303 | 0 | 0 | 0 | 2024-07-05 08:35 | FALSE | 1 | tr_10624_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_106690_21 | ACLineSegment | Line | 0.94778 | 0.023736 | 0.023736 | 0.01462 | 2.5044 | 0 | 0 | 0 | 2024-01-21 01:25 | FALSE | 1 | line_106690_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_106801_21 | ACLineSegment | Line | 0.94778 | 0.072335 | 0.072335 | 0.049661 | 7.6321 | 0 | 0 | 0 | 2024-01-21 03:05 | FALSE | 1 | line_106801_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_108246_21 | ACLineSegment | Line | 13.5424 | 0.042677 | 0.042677 | 0.031629 | 0.31514 | 0 | 0 | 0 | 2024-01-20 05:00 | FALSE | 1 | line_108246_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | tr_10002_21 | Transformer | Transformer | 0.07125 | 0.0067475 | 0.0067475 | 0.0045061 | 9.4702 | 0 | 0 | 0 | 2024-01-20 05:00 | FALSE | 1 | tr_10002_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_106886_21 | ACLineSegment | Line | 0.94778 | 0.036365 | 0.036365 | 0.027898 | 3.8369 | 0 | 0 | 0 | 2024-01-20 15:45 | FALSE | 1 | line_106886_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_106064_21 | ACLineSegment | Line | 0.94778 | 0.0047458 | 0.0047458 | 0.0022861 | 0.50073 | 0 | 0 | 0 | 2024-01-20 23:55 | FALSE | 1 | line_106064_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | tr_74_21 | Transformer | Transformer | 0.02375 | 0.0047458 | 0.0047458 | 0.0022861 | 19.9822 | 0 | 0 | 0 | 2024-01-20 23:55 | FALSE | 1 | tr_74_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_106666_21 | ACLineSegment | Line | 0.94778 | 0.3897 | 0.3897 | 0.27784 | 41.1173 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_106666_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_112184_21 | ACLineSegment | Line | 0.94778 | 0.3766 | 0.3766 | 0.26903 | 39.735 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_112184_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | tr_2273_21 | Transformer | Transformer | 0.02375 | 0.011158 | 0.011158 | 0.0067742 | 46.9815 | 0 | 0 | 0 | 2024-01-20 09:00 | FALSE | 1 | tr_2273_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_106065_21 | ACLineSegment | Line | 0.034884 | 0.0047458 | 0.0047458 | 0.0022861 | 13.6046 | 0 | 0 | 0 | 2024-01-20 23:55 | FALSE | 1 | line_106065_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_90187_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_90187_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_106073_21 | ACLineSegment | Line | 0.94778 | 0.1517 | 0.1517 | 0.10135 | 16.0061 | 0 | 0 | 0 | 2024-01-20 15:45 | FALSE | 1 | line_106073_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_106074_21 | ACLineSegment | Line | 0.94778 | 0.13509 | 0.13509 | 0.086349 | 14.2531 | 0 | 0 | 0 | 2024-01-20 15:45 | FALSE | 1 | line_106074_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | tr_77_21 | Transformer | Transformer | 0.02375 | 0.024146 | 0.024146 | 0.014961 | 101.6686 | 12 | 1 | 0.011391 | 2024-01-20 12:00 | FALSE | 1 | tr_77_21 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_109986_21 | ACLineSegment | Line | 0.94778 | 0.35151 | 0.35151 | 0.25193 | 37.088 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_109986_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_109987_21 | ACLineSegment | Line | 0.94778 | 0.065034 | 0.065034 | 0.045173 | 6.8617 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | line_109987_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_109988_21 | ACLineSegment | Line | 0.94778 | 0.1467 | 0.1467 | 0.10123 | 15.4784 | 0 | 0 | 0 | 2024-01-21 01:25 | FALSE | 1 | line_109988_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | tr_1411_21 | Transformer | Transformer | 0.02375 | 0.006113 | 0.006113 | 0.0037033 | 25.7388 | 0 | 0 | 0 | 2024-07-15 05:55 | FALSE | 1 | tr_1411_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_115874_21 | ACLineSegment | Line | 0.94778 | 0.079378 | 0.079378 | 0.051339 | 8.3752 | 0 | 0 | 0 | 2024-01-21 03:05 | FALSE | 1 | line_115874_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | tr_3798_21 | Transformer | Transformer | 0.0475 | 0.057114 | 0.057114 | 0.035029 | 120.2408 | 125 | 10.4167 | 0.11865 | 2024-01-20 15:45 | FALSE | 1 | tr_3798_21 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_106075_21 | ACLineSegment | Line | 0.034884 | 0.0064232 | 0.0064232 | 0.0033941 | 18.4132 | 0 | 0 | 0 | 2024-01-20 18:50 | FALSE | 1 | line_106075_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_106076_21 | ACLineSegment | Line | 0.034884 | 0.009263 | 0.009263 | 0.0037284 | 26.5541 | 0 | 0 | 0 | 2024-01-20 12:00 | FALSE | 1 | line_106076_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_90310_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_90310_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_90311_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_90311_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_90313_21 | ACLineSegment | Line | 0.034884 | 0.010874 | 0.010874 | 0.0059585 | 31.1726 | 0 | 0 | 0 | 2024-01-20 09:00 | FALSE | 1 | line_90313_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_90316_21 | ACLineSegment | Line | 0.034884 | 0.0048181 | 0.0048181 | 0.0026386 | 13.8118 | 0 | 0 | 0 | 2024-07-15 09:15 | FALSE | 1 | line_90316_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_106218_21 | ACLineSegment | Line | 13.5424 | 0.032081 | 0.032081 | 0.025456 | 0.23689 | 0 | 0 | 0 | 2024-07-15 23:05 | FALSE | 1 | line_106218_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | line_106219_21 | ACLineSegment | Line | 13.5424 | 0.036453 | 0.036453 | 0.028848 | 0.26918 | 0 | 0 | 0 | 2024-07-15 23:05 | FALSE | 1 | line_106219_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | tr_125_21 | Transformer | Transformer | 0.07125 | 0.0059732 | 0.0059732 | 0.004289 | 8.3835 | 0 | 0 | 0 | 2024-01-17 14:00 | FALSE | 1 | tr_125_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_107862_21 | ACLineSegment | Line | 13.5424 | 0.0081666 | 0.0081666 | 0.0064363 | 0.060304 | 0 | 0 | 0 | 2024-01-20 12:00 | FALSE | 1 | line_107862_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | line_107863_21 | ACLineSegment | Line | 13.5424 | 0.022684 | 0.022684 | 0.017252 | 0.1675 | 0 | 0 | 0 | 2024-07-15 23:05 | FALSE | 1 | line_107863_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | tr_679_21 | Transformer | Transformer | 0.285 | 0.0052956 | 0.0052956 | 0.0034556 | 1.8581 | 0 | 0 | 0 | 2024-01-20 09:00 | FALSE | 1 | tr_679_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_112666_21 | ACLineSegment | Line | 13.5424 | 0.041826 | 0.041826 | 0.033074 | 0.30885 | 0 | 0 | 0 | 2024-07-15 23:05 | FALSE | 1 | line_112666_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | tr_2496_21 | Transformer | Transformer | 0.1425 | 0.0076477 | 0.0076477 | 0.0050433 | 5.3668 | 0 | 0 | 0 | 2024-01-20 05:00 | FALSE | 1 | tr_2496_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_106220_21 | ACLineSegment | Line | 0.51338 | 0.0059732 | 0.0059732 | 0.004289 | 1.1635 | 0 | 0 | 0 | 2024-01-17 14:00 | FALSE | 1 | line_106220_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | line_91425_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_91425_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_106466_21 | ACLineSegment | Line | 13.5424 | 0.039535 | 0.039535 | 0.027505 | 0.29193 | 0 | 0 | 0 | 2024-01-17 20:10 | FALSE | 1 | line_106466_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | tr_208_21 | Transformer | Transformer | 0.02375 | 0.0077577 | 0.0077577 | 0.0045025 | 32.6641 | 0 | 0 | 0 | 2024-01-20 23:55 | FALSE | 1 | tr_208_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_111484_21 | ACLineSegment | Line | 13.5424 | 0.046273 | 0.046273 | 0.030923 | 0.34169 | 0 | 0 | 0 | 2024-01-20 09:00 | FALSE | 1 | line_111484_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | tr_9257_21 | Transformer | Transformer | 0.02375 | 0.0069008 | 0.0069008 | 0.0042382 | 29.0562 | 0 | 0 | 0 | 2024-01-20 09:00 | FALSE | 1 | tr_9257_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_106467_21 | ACLineSegment | Line | 0.034884 | 0.0035977 | 0.0035977 | 0.0021567 | 10.3135 | 0 | 0 | 0 | 2024-01-17 12:55 | FALSE | 1 | line_106467_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_90823_21 | ACLineSegment | Line | 0.034884 | 0.0047198 | 0.0047198 | 0.002512 | 13.53 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | line_90823_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_106608_21 | ACLineSegment | Line | 0.94778 | 0.051668 | 0.051668 | 0.035518 | 5.4514 | 0 | 0 | 0 | 2024-01-20 06:55 | FALSE | 1 | line_106608_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | tr_256_21 | Transformer | Transformer | 0.0475 | 0.051668 | 0.051668 | 0.035518 | 108.7739 | 144 | 12 | 0.13669 | 2024-01-20 06:55 | FALSE | 1 | tr_256_21 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_109050_21 | ACLineSegment | Line | 0.94778 | 0.12645 | 0.12645 | 0.090905 | 13.3422 | 0 | 0 | 0 | 2024-01-20 20:20 | FALSE | 1 | line_109050_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_109051_21 | ACLineSegment | Line | 0.94778 | 0.18157 | 0.18157 | 0.12846 | 19.1574 | 0 | 0 | 0 | 2024-01-20 20:20 | FALSE | 1 | line_109051_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | tr_1088_21 | Transformer | Transformer | 0.02375 | 0.0043959 | 0.0043959 | 0.0023827 | 18.5092 | 0 | 0 | 0 | 2024-01-20 18:50 | FALSE | 1 | tr_1088_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_106609_21 | ACLineSegment | Line | 0.034884 | 0.0031683 | 0.0031683 | 0.001822 | 9.0826 | 0 | 0 | 0 | 2024-01-20 06:55 | FALSE | 1 | line_106609_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_90897_21 | ACLineSegment | Line | 0.034884 | 0.028189 | 0.028189 | 0.01732 | 80.808 | 0 | 0 | 0 | 2024-01-20 05:00 | FALSE | 1 | line_90897_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_90898_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_90898_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_90903_21 | ACLineSegment | Line | 0.034884 | 0.025919 | 0.025919 | 0.01661 | 74.3004 | 0 | 0 | 0 | 2024-01-21 03:05 | FALSE | 1 | line_90903_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_106648_21 | ACLineSegment | Line | 13.5424 | 0.0091951 | 0.0091951 | 0.0060679 | 0.067899 | 0 | 0 | 0 | 2024-01-20 13:05 | FALSE | 1 | line_106648_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | line_106649_21 | ACLineSegment | Line | 13.5424 | 0.01588 | 0.01588 | 0.010605 | 0.11726 | 0 | 0 | 0 | 2024-01-20 13:05 | FALSE | 1 | line_106649_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | tr_269_21 | Transformer | Transformer | 0.07125 | 0.0067354 | 0.0067354 | 0.0053899 | 9.4532 | 0 | 0 | 0 | 2024-01-20 08:55 | FALSE | 1 | tr_269_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | tr_1655_21 | Transformer | Transformer | 0.07125 | 0.0091951 | 0.0091951 | 0.0060679 | 12.9055 | 0 | 0 | 0 | 2024-01-20 13:05 | FALSE | 1 | tr_1655_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_111342_21 | ACLineSegment | Line | 13.5424 | 0.057334 | 0.057334 | 0.041383 | 0.42337 | 0 | 0 | 0 | 2024-01-20 09:00 | FALSE | 1 | line_111342_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | line_111343_21 | ACLineSegment | Line | 13.5424 | 0.086386 | 0.086386 | 0.06574 | 0.63789 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | line_111343_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | tr_1922_21 | Transformer | Transformer | 0.0475 | 0.024264 | 0.024264 | 0.018126 | 51.0822 | 0 | 0 | 0 | 2024-01-17 17:55 | FALSE | 1 | tr_1922_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_106650_21 | ACLineSegment | Line | 0.51338 | 0.0067354 | 0.0067354 | 0.0053899 | 1.312 | 0 | 0 | 0 | 2024-01-20 08:55 | FALSE | 1 | line_106650_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | line_90966_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_90966_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | tr_274_21 | Transformer | Transformer | 0.02375 | 0.024268 | 0.024268 | 0.016703 | 102.1794 | 19 | 1.5833 | 0.018035 | 2024-01-20 09:00 | FALSE | 1 | tr_274_21 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_106668_21 | ACLineSegment | Line | 0.94778 | 0.041606 | 0.041606 | 0.026925 | 4.3899 | 0 | 0 | 0 | 2024-01-20 21:15 | FALSE | 1 | line_106668_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_106669_21 | ACLineSegment | Line | 0.94778 | 0.036473 | 0.036473 | 0.022729 | 3.8482 | 0 | 0 | 0 | 2024-01-20 21:15 | FALSE | 1 | line_106669_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | tr_275_21 | Transformer | Transformer | 0.02375 | 0.0066479 | 0.0066479 | 0.0041973 | 27.9913 | 0 | 0 | 0 | 2024-01-17 15:40 | FALSE | 1 | tr_275_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_116237_21 | ACLineSegment | Line | 0.94778 | 0.10072 | 0.10072 | 0.068555 | 10.6269 | 0 | 0 | 0 | 2024-01-20 21:15 | FALSE | 1 | line_116237_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | tr_3954_21 | Transformer | Transformer | 0.0475 | 0.060853 | 0.060853 | 0.041897 | 128.1108 | 1352 | 112.6667 | 1.2834 | 2024-01-21 01:25 | FALSE | 1 | tr_3954_21 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | tr_3974_21 | Transformer | Transformer | 0.0475 | 0.036473 | 0.036473 | 0.022729 | 76.7847 | 0 | 0 | 0 | 2024-01-20 21:15 | FALSE | 1 | tr_3974_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | tr_276_21 | Transformer | Transformer | 0.02375 | 0.0052794 | 0.0052794 | 0.0036446 | 22.2292 | 0 | 0 | 0 | 2024-01-20 14:50 | FALSE | 1 | tr_276_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_106671_21 | ACLineSegment | Line | 0.034884 | 0.0052794 | 0.0052794 | 0.0036446 | 15.1345 | 0 | 0 | 0 | 2024-01-20 14:50 | FALSE | 1 | line_106671_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_90951_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_90951_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | tr_284_21 | Transformer | Transformer | 0.02375 | 0.023736 | 0.023736 | 0.01462 | 99.9404 | 0 | 0 | 0 | 2024-01-21 01:25 | FALSE | 1 | tr_284_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_106691_21 | ACLineSegment | Line | 0.034884 | 0.0075149 | 0.0075149 | 0.0043712 | 21.5429 | 0 | 0 | 0 | 2024-01-17 09:55 | FALSE | 1 | line_106691_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_106692_21 | ACLineSegment | Line | 0.034884 | 0.0063622 | 0.0063622 | 0.0035154 | 18.2383 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | line_106692_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_106693_21 | ACLineSegment | Line | 0.034884 | 0.0049145 | 0.0049145 | 0.0027237 | 14.0883 | 0 | 0 | 0 | 2024-01-20 13:05 | FALSE | 1 | line_106693_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_106694_21 | ACLineSegment | Line | 0.034884 | 0.0037669 | 0.0037669 | 0.0021998 | 10.7986 | 0 | 0 | 0 | 2024-07-15 10:55 | FALSE | 1 | line_106694_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_106695_21 | ACLineSegment | Line | 0.034884 | 0.0050894 | 0.0050894 | 0.0027771 | 14.5896 | 0 | 0 | 0 | 2024-01-18 | FALSE | 1 | line_106695_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_106802_21 | ACLineSegment | Line | 0.94778 | 0.041982 | 0.041982 | 0.026938 | 4.4295 | 0 | 0 | 0 | 2024-01-17 08:10 | FALSE | 1 | line_106802_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | tr_316_21 | Transformer | Transformer | 0.02375 | 0.033424 | 0.033424 | 0.022958 | 140.7332 | 4109 | 342.4167 | 3.9004 | 2024-01-21 03:05 | FALSE | 1 | tr_316_21 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | tr_9936_21 | Transformer | Transformer | 0.02375 | 0.041982 | 0.041982 | 0.026938 | 176.7671 | 11154 | 929.5 | 10.5878 | 2024-01-17 08:10 | FALSE | 1 | tr_9936_21 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_106839_21 | ACLineSegment | Line | 2.3694 | 0.0087802 | 0.0087802 | 0.0046469 | 0.37056 | 0 | 0 | 0 | 2024-01-20 19:55 | FALSE | 1 | line_106839_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_107001_21 | ACLineSegment | Line | 0.94778 | 0.023034 | 0.023034 | 0.015367 | 2.4304 | 0 | 0 | 0 | 2024-01-20 19:55 | FALSE | 1 | line_107001_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | tr_384_21 | Transformer | Transformer | 0.02375 | 0.016569 | 0.016569 | 0.010979 | 69.766 | 0 | 0 | 0 | 2024-07-15 20:35 | FALSE | 1 | tr_384_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_106840_21 | ACLineSegment | Line | 0.025406 | 0.0026677 | 0.0026677 | 0.0014999 | 10.5003 | 0 | 0 | 0 | 2024-01-21 22:55 | FALSE | 1 | line_106840_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_91338_21 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_91338_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_91339_21 | ACLineSegment | Line | 0.025406 | 0.0065049 | 0.0065049 | 0.0033231 | 25.6041 | 0 | 0 | 0 | 2024-01-20 19:55 | FALSE | 1 | line_91339_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | tr_329_21 | Transformer | Transformer | 0.02375 | 0.0087802 | 0.0087802 | 0.0046469 | 36.9691 | 0 | 0 | 0 | 2024-01-20 19:55 | FALSE | 1 | tr_329_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_106885_21 | ACLineSegment | Line | 0.94778 | 0.025927 | 0.025927 | 0.019451 | 2.7355 | 0 | 0 | 0 | 2024-07-15 21:45 | FALSE | 1 | line_106885_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | tr_345_21 | Transformer | Transformer | 0.0475 | 0.013755 | 0.013755 | 0.010055 | 28.9585 | 0 | 0 | 0 | 2024-01-17 19:55 | FALSE | 1 | tr_345_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_110709_21 | ACLineSegment | Line | 0.94778 | 0.0068327 | 0.0068327 | 0.0050272 | 0.72092 | 0 | 0 | 0 | 2024-07-15 21:45 | FALSE | 1 | line_110709_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | tr_1677_21 | Transformer | Transformer | 0.02375 | 0.02006 | 0.02006 | 0.015485 | 84.4648 | 0 | 0 | 0 | 2024-07-15 14:00 | FALSE | 1 | tr_1677_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_106887_21 | ACLineSegment | Line | 0.034884 | 0.0034388 | 0.0034388 | 0.0016699 | 9.8581 | 0 | 0 | 0 | 2024-01-20 09:00 | FALSE | 1 | line_106887_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_106888_21 | ACLineSegment | Line | 0.034884 | 0.0075868 | 0.0075868 | 0.0055273 | 21.7491 | 0 | 0 | 0 | 2024-01-20 22:50 | FALSE | 1 | line_106888_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_106889_21 | ACLineSegment | Line | 0.034884 | 0.0051623 | 0.0051623 | 0.0039466 | 14.7986 | 0 | 0 | 0 | 2024-01-21 15:00 | FALSE | 1 | line_106889_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | tr_783_21 | Transformer | Transformer | 0.02375 | 0.0090116 | 0.0090116 | 0.0046088 | 37.9436 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | tr_783_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_107002_21 | ACLineSegment | Line | 0.025406 | 0.0061256 | 0.0061256 | 0.0035505 | 24.1112 | 0 | 0 | 0 | 2024-01-20 07:25 | FALSE | 1 | line_107002_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_91901_21 | ACLineSegment | Line | 0.025406 | 0.011716 | 0.011716 | 0.0076318 | 46.115 | 0 | 0 | 0 | 2024-01-20 22:50 | FALSE | 1 | line_91901_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | tr_9123_21 | Transformer | Transformer | 0.0475 | 0.050634 | 0.050634 | 0.034461 | 106.597 | 34 | 2.8333 | 0.032274 | 2024-01-18 04:00 | FALSE | 1 | tr_9123_21 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_110795_21 | ACLineSegment | Line | 13.5424 | 1.8304 | 1.8304 | 1.3674 | 13.516 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | line_110795_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | tr_10613_21 | Transformer | Transformer | 0.02375 | 0.0089858 | 0.0089858 | 0.006628 | 37.8349 | 0 | 0 | 0 | 2024-01-17 13:10 | FALSE | 1 | tr_10613_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_129223_21 | ACLineSegment | Line | 13.5424 | 1.899 | 1.899 | 1.4202 | 14.023 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | line_129223_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | tr_10616_21 | Transformer | Transformer | 0.285 | 0.03013 | 0.03013 | 0.020922 | 10.5719 | 0 | 0 | 0 | 2024-02-14 22:00 | FALSE | 1 | tr_10616_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_107811_21 | ACLineSegment | Line | 0.034884 | 0.0037278 | 0.0037278 | 0.0020796 | 10.6864 | 0 | 0 | 0 | 2024-01-17 13:10 | FALSE | 1 | line_107811_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_92843_21 | ACLineSegment | Line | 0.034884 | 0.0061986 | 0.0061986 | 0.0035474 | 17.7695 | 0 | 0 | 0 | 2024-01-20 07:25 | FALSE | 1 | line_92843_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_92845_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_92845_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | tr_1034_21 | Transformer | Transformer | 0.285 | 0.0081666 | 0.0081666 | 0.0064363 | 2.8655 | 0 | 0 | 0 | 2024-01-20 12:00 | FALSE | 1 | tr_1034_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_113658_21 | ACLineSegment | Line | 13.5424 | 0.019438 | 0.019438 | 0.013946 | 0.14353 | 0 | 0 | 0 | 2024-07-15 23:05 | FALSE | 1 | line_113658_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | tr_8914_21 | Transformer | Transformer | 0.0475 | 0.0054144 | 0.0054144 | 0.004101 | 11.3988 | 0 | 0 | 0 | 2024-01-18 | FALSE | 1 | tr_8914_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_107864_21 | ACLineSegment | Line | 0.51338 | 0.0052956 | 0.0052956 | 0.0034556 | 1.0315 | 0 | 0 | 0 | 2024-01-20 09:00 | FALSE | 1 | line_107864_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | line_92855_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_92855_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_108116_21 | ACLineSegment | Line | 13.5424 | 0.58818 | 0.58818 | 0.44148 | 4.3432 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | line_108116_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | line_108117_21 | ACLineSegment | Line | 13.5424 | 0.62108 | 0.62108 | 0.46454 | 4.5862 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | line_108117_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | tr_767_21 | Transformer | Transformer | 0.02375 | 0.036561 | 0.036561 | 0.024036 | 153.9425 | 5862 | 488.5 | 5.5644 | 2024-01-21 01:25 | FALSE | 1 | tr_767_21 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | tr_3910_21 | Transformer | Transformer | 0.0475 | 0.08436 | 0.08436 | 0.058206 | 177.601 | 17316 | 1443 | 16.437 | 2024-01-21 03:05 | FALSE | 1 | tr_3910_21 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_108304_21 | ACLineSegment | Line | 13.5424 | 0.63488 | 0.63488 | 0.47264 | 4.6881 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | line_108304_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | tr_9073_21 | Transformer | Transformer | 0.02375 | 0.014108 | 0.014108 | 0.0083749 | 59.4022 | 0 | 0 | 0 | 2024-07-16 03:00 | FALSE | 1 | tr_9073_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_108160_21 | ACLineSegment | Line | 0.034884 | 0.0090116 | 0.0090116 | 0.0046088 | 25.8334 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | line_108160_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_93090_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_93090_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_108245_21 | ACLineSegment | Line | 13.5424 | 0.050294 | 0.050294 | 0.03876 | 0.37138 | 0 | 0 | 0 | 2024-01-20 15:45 | FALSE | 1 | line_108245_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | tr_812_21 | Transformer | Transformer | 0.0475 | 0.010505 | 0.010505 | 0.0078206 | 22.1151 | 0 | 0 | 0 | 2024-07-01 03:00 | FALSE | 1 | tr_812_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_110779_21 | ACLineSegment | Line | 13.5424 | 0.1687 | 0.1687 | 0.13385 | 1.2457 | 0 | 0 | 0 | 2024-01-20 15:45 | FALSE | 1 | line_110779_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | line_110780_21 | ACLineSegment | Line | 13.5424 | 0.12265 | 0.12265 | 0.093207 | 0.90568 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | line_110780_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | tr_1702_21 | Transformer | Transformer | 0.07125 | 0.0068895 | 0.0068895 | 0.0053989 | 9.6695 | 0 | 0 | 0 | 2024-07-16 02:00 | FALSE | 1 | tr_1702_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_108247_21 | ACLineSegment | Line | 0.034884 | 0.0076842 | 0.0076842 | 0.0047053 | 22.0281 | 0 | 0 | 0 | 2024-07-01 03:00 | FALSE | 1 | line_108247_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_108248_21 | ACLineSegment | Line | 0.034884 | 0.0054512 | 0.0054512 | 0.0041779 | 15.6269 | 0 | 0 | 0 | 2024-01-17 23:55 | FALSE | 1 | line_108248_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_108305_21 | ACLineSegment | Line | 13.5424 | 0.29686 | 0.29686 | 0.21781 | 2.1921 | 0 | 0 | 0 | 2024-01-20 13:05 | FALSE | 1 | line_108305_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | tr_828_21 | Transformer | Transformer | 0.0475 | 0.060853 | 0.060853 | 0.039944 | 128.1125 | 959 | 79.9167 | 0.91032 | 2024-01-20 23:55 | FALSE | 1 | tr_828_21 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_109744_21 | ACLineSegment | Line | 13.5424 | 0.2105 | 0.2105 | 0.1566 | 1.5544 | 0 | 0 | 0 | 2024-01-20 05:00 | FALSE | 1 | line_109744_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | tr_9205_21 | Transformer | Transformer | 0.0475 | 0.0885 | 0.0885 | 0.06224 | 186.3155 | 22209 | 1850.75 | 21.0816 | 2024-01-20 13:05 | FALSE | 1 | tr_9205_21 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_108642_21 | ACLineSegment | Line | 0.94778 | 0.30586 | 0.30586 | 0.21933 | 32.2714 | 0 | 0 | 0 | 2024-01-20 20:20 | FALSE | 1 | line_108642_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | tr_946_21 | Transformer | Transformer | 0.0475 | 0.031743 | 0.031743 | 0.020228 | 66.8271 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | tr_946_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_122867_21 | ACLineSegment | Line | 13.5424 | 1.9262 | 1.9262 | 1.4424 | 14.2235 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | line_122867_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | tr_6998_21 | Transformer | Transformer | 0.02375 | 0.024021 | 0.024021 | 0.016282 | 101.1394 | 23 | 1.9167 | 0.021832 | 2024-01-17 20:10 | FALSE | 1 | tr_6998_21 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_108324_21 | ACLineSegment | Line | 0.034884 | 0.0033864 | 0.0033864 | 0.0020187 | 9.7079 | 0 | 0 | 0 | 2024-07-01 03:00 | FALSE | 1 | line_108324_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_93258_21 | ACLineSegment | Line | 0.034884 | 0.013497 | 0.013497 | 0.0071108 | 38.6926 | 0 | 0 | 0 | 2024-01-20 10:55 | FALSE | 1 | line_93258_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_93260_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_93260_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_93261_21 | ACLineSegment | Line | 0.034884 | 0.010105 | 0.010105 | 0.0057107 | 28.9689 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | line_93261_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_108371_21 | ACLineSegment | Line | 13.5424 | 0.013692 | 0.013692 | 0.0091054 | 0.1011 | 0 | 0 | 0 | 2024-01-20 23:55 | FALSE | 1 | line_108371_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | line_108373_21 | ACLineSegment | Line | 13.5424 | 0.015716 | 0.015716 | 0.010035 | 0.11605 | 0 | 0 | 0 | 2024-01-20 23:55 | FALSE | 1 | line_108373_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | tr_850_21 | Transformer | Transformer | 0.0095 | 0.0021956 | 0.0021956 | 0.0011989 | 23.1117 | 0 | 0 | 0 | 2024-01-21 03:05 | FALSE | 1 | tr_850_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_111503_21 | ACLineSegment | Line | 0.94778 | 0.0088065 | 0.0088065 | 0.0045082 | 0.92917 | 0 | 0 | 0 | 2024-01-20 23:55 | FALSE | 1 | line_111503_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | tr_2617_21 | Transformer | Transformer | 0.095 | 0.007373 | 0.007373 | 0.0053142 | 7.761 | 0 | 0 | 0 | 2024-01-21 01:25 | FALSE | 1 | tr_2617_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_108374_21 | ACLineSegment | Line | 0.034884 | 0.0021956 | 0.0021956 | 0.0011989 | 6.2941 | 0 | 0 | 0 | 2024-01-21 03:05 | FALSE | 1 | line_108374_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_108379_21 | ACLineSegment | Line | 0.94778 | 0.037826 | 0.037826 | 0.023315 | 3.991 | 0 | 0 | 0 | 2024-01-20 07:25 | FALSE | 1 | line_108379_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_108380_21 | ACLineSegment | Line | 0.94778 | 0.11527 | 0.11527 | 0.077857 | 12.162 | 0 | 0 | 0 | 2024-01-20 21:15 | FALSE | 1 | line_108380_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_108381_21 | ACLineSegment | Line | 0.94778 | 0.07605 | 0.07605 | 0.04861 | 8.024 | 0 | 0 | 0 | 2024-01-20 21:15 | FALSE | 1 | line_108381_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | tr_853_21 | Transformer | Transformer | 0.02375 | 0.011714 | 0.011714 | 0.0062917 | 49.3227 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | tr_853_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_111444_21 | ACLineSegment | Line | 0.94778 | 0.026098 | 0.026098 | 0.015959 | 2.7536 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | line_111444_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | tr_2699_21 | Transformer | Transformer | 0.02375 | 0.013764 | 0.013764 | 0.0075581 | 57.952 | 0 | 0 | 0 | 2024-01-20 07:25 | FALSE | 1 | tr_2699_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_112251_21 | ACLineSegment | Line | 0.94778 | 0.20984 | 0.20984 | 0.14925 | 22.1397 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_112251_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | tr_3877_21 | Transformer | Transformer | 0.0475 | 0.061222 | 0.061222 | 0.041863 | 128.8889 | 1392 | 116 | 1.3213 | 2024-01-21 01:25 | FALSE | 1 | tr_3877_21 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | tr_10625_21 | Transformer | Transformer | 0.0475 | 0.07605 | 0.07605 | 0.04861 | 160.1053 | 6226 | 518.8333 | 5.9099 | 2024-01-20 21:15 | FALSE | 1 | tr_10625_21 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_108382_21 | ACLineSegment | Line | 0.034884 | 0.0068464 | 0.0068464 | 0.0030279 | 19.6264 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_108382_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_93306_21 | ACLineSegment | Line | 0.034884 | 0.007429 | 0.007429 | 0.0035905 | 21.2967 | 0 | 0 | 0 | 2024-01-20 14:50 | FALSE | 1 | line_93306_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_115810_21 | ACLineSegment | Line | 0.94778 | 0.25554 | 0.25554 | 0.17932 | 26.9623 | 0 | 0 | 0 | 2024-01-20 20:20 | FALSE | 1 | line_115810_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | tr_3780_21 | Transformer | Transformer | 0.0475 | 0.05818 | 0.05818 | 0.039578 | 122.4833 | 675 | 56.25 | 0.64073 | 2024-01-21 03:05 | FALSE | 1 | tr_3780_21 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_108643_21 | ACLineSegment | Line | 0.034884 | 0.0052948 | 0.0052948 | 0.0032612 | 15.1785 | 0 | 0 | 0 | 2024-06-27 01:55 | FALSE | 1 | line_108643_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_92924_21 | ACLineSegment | Line | 0.034884 | 0.014248 | 0.014248 | 0.0084677 | 40.8437 | 0 | 0 | 0 | 2024-01-20 09:00 | FALSE | 1 | line_92924_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_92929_21 | ACLineSegment | Line | 0.034884 | 0.015625 | 0.015625 | 0.0089645 | 44.7919 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_92929_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_108895_21 | ACLineSegment | Line | 0.51338 | 0.0052637 | 0.0052637 | 0.0038832 | 1.0253 | 0 | 0 | 0 | 2024-06-23 | FALSE | 1 | line_108895_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | line_108896_21 | ACLineSegment | Line | 0.51338 | 0.004667 | 0.004667 | 0.0033463 | 0.90907 | 0 | 0 | 0 | 2024-01-17 09:55 | FALSE | 1 | line_108896_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | line_93738_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_93738_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_93739_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_93739_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_108953_21 | ACLineSegment | Line | 0.94778 | 0.0089187 | 0.0089187 | 0.0041243 | 0.94101 | 0 | 0 | 0 | 2024-01-20 05:00 | FALSE | 1 | line_108953_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_108954_21 | ACLineSegment | Line | 0.94778 | 0.10525 | 0.10525 | 0.075338 | 11.1053 | 0 | 0 | 0 | 2024-01-20 09:00 | FALSE | 1 | line_108954_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_108955_21 | ACLineSegment | Line | 0.94778 | 0.09082 | 0.09082 | 0.066745 | 9.5825 | 0 | 0 | 0 | 2024-01-20 20:20 | FALSE | 1 | line_108955_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | tr_1056_21 | Transformer | Transformer | 0.02375 | 0.0098242 | 0.0098242 | 0.0056233 | 41.3652 | 0 | 0 | 0 | 2024-01-20 09:00 | FALSE | 1 | tr_1056_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | tr_1314_21 | Transformer | Transformer | 0.02375 | 0.0089187 | 0.0089187 | 0.0041243 | 37.5522 | 0 | 0 | 0 | 2024-01-20 05:00 | FALSE | 1 | tr_1314_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_109719_21 | ACLineSegment | Line | 0.94778 | 0.11849 | 0.11849 | 0.085427 | 12.5018 | 0 | 0 | 0 | 2024-01-20 09:00 | FALSE | 1 | line_109719_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | tr_1323_21 | Transformer | Transformer | 0.02375 | 0.015829 | 0.015829 | 0.01043 | 66.6504 | 0 | 0 | 0 | 2024-07-15 12:50 | FALSE | 1 | tr_1323_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_126719_21 | ACLineSegment | Line | 0.94778 | 0.0090079 | 0.0090079 | 0.0056338 | 0.95042 | 0 | 0 | 0 | 2024-01-20 09:00 | FALSE | 1 | line_126719_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_127045_21 | ACLineSegment | Line | 0.94778 | 0.042003 | 0.042003 | 0.02917 | 4.4317 | 0 | 0 | 0 | 2024-01-17 07:00 | FALSE | 1 | line_127045_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | tr_12661_21 | Transformer | Transformer | 0.0475 | 0.046603 | 0.046603 | 0.032438 | 98.1112 | 0 | 0 | 0 | 2024-01-20 20:20 | FALSE | 1 | tr_12661_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | tr_1317_21 | Transformer | Transformer | 0.02375 | 0.0099372 | 0.0099372 | 0.0056502 | 41.8407 | 0 | 0 | 0 | 2024-01-20 10:55 | FALSE | 1 | tr_1317_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_116051_21 | ACLineSegment | Line | 0.94778 | 0.23634 | 0.23634 | 0.16676 | 24.9359 | 0 | 0 | 0 | 2024-01-20 20:20 | FALSE | 1 | line_116051_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | tr_3871_21 | Transformer | Transformer | 0.0475 | 0.056751 | 0.056751 | 0.038156 | 119.4765 | 450 | 37.5 | 0.42716 | 2024-01-20 13:05 | FALSE | 1 | tr_3871_21 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_109052_21 | ACLineSegment | Line | 0.034884 | 0.0043959 | 0.0043959 | 0.0023827 | 12.6018 | 0 | 0 | 0 | 2024-01-20 18:50 | FALSE | 1 | line_109052_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_93837_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_93837_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_109710_21 | ACLineSegment | Line | 0.034884 | 0.0089187 | 0.0089187 | 0.0041243 | 25.567 | 0 | 0 | 0 | 2024-01-20 05:00 | FALSE | 1 | line_109710_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_94631_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_94631_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_109720_21 | ACLineSegment | Line | 0.034884 | 0.0043183 | 0.0043183 | 0.0020336 | 12.3792 | 0 | 0 | 0 | 2024-01-17 11:00 | FALSE | 1 | line_109720_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_94634_21 | ACLineSegment | Line | 0.034884 | 0.0076716 | 0.0076716 | 0.003968 | 21.9921 | 0 | 0 | 0 | 2024-01-20 10:55 | FALSE | 1 | line_94634_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_109738_21 | ACLineSegment | Line | 0.034884 | 0.0089283 | 0.0089283 | 0.0049918 | 25.5945 | 0 | 0 | 0 | 2024-01-20 17:05 | FALSE | 1 | line_109738_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_94647_21 | ACLineSegment | Line | 0.034884 | 0.0031558 | 0.0031558 | 0.0019075 | 9.0468 | 0 | 0 | 0 | 2024-07-15 13:05 | FALSE | 1 | line_94647_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_94649_21 | ACLineSegment | Line | 0.034884 | 0.0073232 | 0.0073232 | 0.0039603 | 20.9934 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_94649_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | tr_1325_21 | Transformer | Transformer | 0.02375 | 0.0043056 | 0.0043056 | 0.0027623 | 18.129 | 0 | 0 | 0 | 2024-01-20 20:20 | FALSE | 1 | tr_1325_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_109745_21 | ACLineSegment | Line | 0.034884 | 0.0024878 | 0.0024878 | 0.0014816 | 7.1318 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_109745_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_94101_21 | ACLineSegment | Line | 0.034884 | 0.0024698 | 0.0024698 | 0.0014106 | 7.0801 | 0 | 0 | 0 | 2024-01-20 21:15 | FALSE | 1 | line_94101_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | tr_2800_21 | Transformer | Transformer | 0.02375 | 0.0063597 | 0.0063597 | 0.0039823 | 26.7776 | 0 | 0 | 0 | 2024-07-05 10:15 | FALSE | 1 | tr_2800_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | tr_3794_21 | Transformer | Transformer | 0.0475 | 0.065034 | 0.065034 | 0.045173 | 136.9137 | 3564 | 297 | 3.3831 | 2024-01-21 | FALSE | 1 | tr_3794_21 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | tr_9252_21 | Transformer | Transformer | 0.0475 | 0.048486 | 0.048486 | 0.032591 | 102.0757 | 24 | 2 | 0.022782 | 2024-01-21 01:25 | FALSE | 1 | tr_9252_21 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_110126_21 | ACLineSegment | Line | 13.5424 | 0.082697 | 0.082697 | 0.061905 | 0.61066 | 0 | 0 | 0 | 2024-01-17 23:55 | FALSE | 1 | line_110126_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | tr_1463_21 | Transformer | Transformer | 0.02375 | 0.0047595 | 0.0047595 | 0.0024831 | 20.0401 | 0 | 0 | 0 | 2024-01-17 14:00 | FALSE | 1 | tr_1463_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_113231_21 | ACLineSegment | Line | 13.5424 | 0.048708 | 0.048708 | 0.03783 | 0.35967 | 0 | 0 | 0 | 2024-07-15 23:05 | FALSE | 1 | line_113231_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | tr_8968_21 | Transformer | Transformer | 0.095 | 0.04047 | 0.04047 | 0.02903 | 42.5998 | 0 | 0 | 0 | 2024-07-01 03:00 | FALSE | 1 | tr_8968_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_110127_21 | ACLineSegment | Line | 0.034884 | 0.0047595 | 0.0047595 | 0.0024831 | 13.644 | 0 | 0 | 0 | 2024-01-17 14:00 | FALSE | 1 | line_110127_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_94673_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_94673_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | tr_3831_21 | Transformer | Transformer | 0.0475 | 0.062919 | 0.062919 | 0.045891 | 132.461 | 3891 | 324.25 | 3.6935 | 2024-01-21 01:25 | FALSE | 1 | tr_3831_21 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_110214_21 | ACLineSegment | Line | 0.034884 | 0.0054309 | 0.0054309 | 0.0028824 | 15.5688 | 0 | 0 | 0 | 2024-01-20 19:55 | FALSE | 1 | line_110214_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_94851_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_94851_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_110283_21 | ACLineSegment | Line | 0.034884 | 0.0079018 | 0.0079018 | 0.0045233 | 22.6519 | 0 | 0 | 0 | 2024-01-17 08:10 | FALSE | 1 | line_110283_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_110284_21 | ACLineSegment | Line | 0.034884 | 0.003891 | 0.003891 | 0.002249 | 11.1541 | 0 | 0 | 0 | 2024-01-20 19:55 | FALSE | 1 | line_110284_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_94888_21 | ACLineSegment | Line | 0.034884 | 0.01029 | 0.01029 | 0.0060624 | 29.4985 | 0 | 0 | 0 | 2024-07-05 07:00 | FALSE | 1 | line_94888_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_94889_21 | ACLineSegment | Line | 0.034884 | 0.0026991 | 0.0026991 | 0.0015828 | 7.7374 | 0 | 0 | 0 | 2024-01-20 15:45 | FALSE | 1 | line_94889_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_94892_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_94892_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_110659_21 | ACLineSegment | Line | 0.51338 | 0.0091951 | 0.0091951 | 0.0060679 | 1.7911 | 0 | 0 | 0 | 2024-01-20 13:05 | FALSE | 1 | line_110659_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | line_95746_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_95746_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | tr_12321_21 | Transformer | Transformer | 0.02375 | 0.0068327 | 0.0068327 | 0.0050272 | 28.7694 | 0 | 0 | 0 | 2024-07-15 21:45 | FALSE | 1 | tr_12321_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_110710_21 | ACLineSegment | Line | 0.034884 | 0.02006 | 0.02006 | 0.015485 | 57.5068 | 0 | 0 | 0 | 2024-07-15 14:00 | FALSE | 1 | line_110710_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_112965_21 | ACLineSegment | Line | 13.5424 | 0.17257 | 0.17257 | 0.13757 | 1.2743 | 0 | 0 | 0 | 2024-01-20 15:45 | FALSE | 1 | line_112965_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | tr_2627_21 | Transformer | Transformer | 0.02375 | 0.007805 | 0.007805 | 0.0039401 | 32.8631 | 0 | 0 | 0 | 2024-01-21 02:15 | FALSE | 1 | tr_2627_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_112972_21 | ACLineSegment | Line | 13.5424 | 0.02511 | 0.02511 | 0.019015 | 0.18542 | 0 | 0 | 0 | 2024-01-21 03:05 | FALSE | 1 | line_112972_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | line_131950_21 | ACLineSegment | Line | 13.5424 | 0.075534 | 0.075534 | 0.056249 | 0.55776 | 0 | 0 | 0 | 2024-01-22 04:00 | FALSE | 1 | line_131950_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | tr_12320_21 | Transformer | Transformer | 0.02375 | 0.030329 | 0.030329 | 0.020517 | 127.701 | 761 | 63.4167 | 0.72237 | 2024-01-20 09:00 | FALSE | 1 | tr_12320_21 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_110781_21 | ACLineSegment | Line | 0.51338 | 0.0068895 | 0.0068895 | 0.0053989 | 1.342 | 0 | 0 | 0 | 2024-07-16 02:00 | FALSE | 1 | line_110781_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | tr_1709_21 | Transformer | Transformer | 0.02375 | 0.017531 | 0.017531 | 0.011194 | 73.8127 | 0 | 0 | 0 | 2024-07-15 07:55 | FALSE | 1 | tr_1709_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_110796_21 | ACLineSegment | Line | 0.034884 | 0.0054926 | 0.0054926 | 0.003243 | 15.7455 | 0 | 0 | 0 | 2024-01-20 21:15 | FALSE | 1 | line_110796_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_95209_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_95209_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_95210_21 | ACLineSegment | Line | 0.034884 | 0.0068395 | 0.0068395 | 0.0041282 | 19.6067 | 0 | 0 | 0 | 2024-07-15 07:55 | FALSE | 1 | line_95210_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_95214_21 | ACLineSegment | Line | 0.034884 | 0.0072435 | 0.0072435 | 0.0042195 | 20.7649 | 0 | 0 | 0 | 2024-01-20 18:50 | FALSE | 1 | line_95214_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_129249_21 | ACLineSegment | Line | 13.5424 | 0.052724 | 0.052724 | 0.037761 | 0.38933 | 0 | 0 | 0 | 2024-01-20 09:00 | FALSE | 1 | line_129249_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | tr_10636_21 | Transformer | Transformer | 0.07125 | 0.0059583 | 0.0059583 | 0.0043189 | 8.3625 | 0 | 0 | 0 | 2024-01-21 05:00 | FALSE | 1 | tr_10636_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_112168_21 | ACLineSegment | Line | 13.5424 | 0.093669 | 0.093669 | 0.070491 | 0.69168 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | line_112168_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | tr_10647_21 | Transformer | Transformer | 0.07125 | 0.0076729 | 0.0076729 | 0.0056866 | 10.769 | 0 | 0 | 0 | 2024-01-20 05:00 | FALSE | 1 | tr_10647_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_111344_21 | ACLineSegment | Line | 0.034884 | 0.024264 | 0.024264 | 0.018126 | 69.5573 | 0 | 0 | 0 | 2024-01-17 17:55 | FALSE | 1 | line_111344_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_95859_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_95859_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | tr_1963_21 | Transformer | Transformer | 0.02375 | 0.026098 | 0.026098 | 0.015959 | 109.8869 | 17 | 1.4167 | 0.016137 | 2024-01-18 04:00 | FALSE | 1 | tr_1963_21 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_111445_21 | ACLineSegment | Line | 0.034884 | 0.0041817 | 0.0041817 | 0.0025256 | 11.9875 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | line_111445_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_111446_21 | ACLineSegment | Line | 0.034884 | 0.003881 | 0.003881 | 0.0020966 | 11.1257 | 0 | 0 | 0 | 2024-01-20 16:00 | FALSE | 1 | line_111446_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_95939_21 | ACLineSegment | Line | 0.034884 | 0.0088966 | 0.0088966 | 0.0052034 | 25.5038 | 0 | 0 | 0 | 2024-01-17 17:55 | FALSE | 1 | line_95939_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_95944_21 | ACLineSegment | Line | 0.034884 | 0.011668 | 0.011668 | 0.0066749 | 33.4487 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | line_95944_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_111485_21 | ACLineSegment | Line | 13.5424 | 0.04949 | 0.04949 | 0.033521 | 0.36545 | 0 | 0 | 0 | 2024-01-20 09:00 | FALSE | 1 | line_111485_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | tr_1980_21 | Transformer | Transformer | 0.02375 | 0.0047193 | 0.0047193 | 0.002741 | 19.8709 | 0 | 0 | 0 | 2024-01-20 23:55 | FALSE | 1 | tr_1980_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | tr_10644_21 | Transformer | Transformer | 0.07125 | 0.0072588 | 0.0072588 | 0.005365 | 10.1878 | 0 | 0 | 0 | 2024-12-23 13:05 | FALSE | 1 | tr_10644_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_111486_21 | ACLineSegment | Line | 0.034884 | 0.0047193 | 0.0047193 | 0.002741 | 13.5288 | 0 | 0 | 0 | 2024-01-20 23:55 | FALSE | 1 | line_111486_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_95991_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_95991_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | tr_2654_21 | Transformer | Transformer | 0.02375 | 0.0029693 | 0.0029693 | 0.0015123 | 12.5023 | 0 | 0 | 0 | 2024-01-17 22:10 | FALSE | 1 | tr_2654_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_111506_21 | ACLineSegment | Line | 0.034884 | 0.00671 | 0.00671 | 0.0031629 | 19.2356 | 0 | 0 | 0 | 2024-01-20 23:55 | FALSE | 1 | line_111506_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_95999_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_95999_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_111568_21 | ACLineSegment | Line | 0.034884 | 0.0037348 | 0.0037348 | 0.0022713 | 10.7064 | 0 | 0 | 0 | 2024-01-21 01:25 | FALSE | 1 | line_111568_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_96030_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_96030_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_111623_21 | ACLineSegment | Line | 13.5424 | 0.0064302 | 0.0064302 | 0.0043017 | 0.047482 | 0 | 0 | 0 | 2024-01-20 19:55 | FALSE | 1 | line_111623_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | tr_2035_21 | Transformer | Transformer | 0.285 | 0.0064302 | 0.0064302 | 0.0043017 | 2.2562 | 0 | 0 | 0 | 2024-01-20 19:55 | FALSE | 1 | tr_2035_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_112166_21 | ACLineSegment | Line | 13.5424 | 0.32775 | 0.32775 | 0.24761 | 2.4202 | 0 | 0 | 0 | 2024-07-15 23:05 | FALSE | 1 | line_112166_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | line_112221_21 | ACLineSegment | Line | 13.5424 | 0.33845 | 0.33845 | 0.25516 | 2.4992 | 0 | 0 | 0 | 2024-07-15 23:05 | FALSE | 1 | line_112221_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | tr_5957_21 | Transformer | Transformer | 0.02375 | 0.0067895 | 0.0067895 | 0.0049455 | 28.5874 | 0 | 0 | 0 | 2024-01-21 23:50 | FALSE | 1 | tr_5957_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_111624_21 | ACLineSegment | Line | 0.51338 | 0.0064302 | 0.0064302 | 0.0043017 | 1.2525 | 0 | 0 | 0 | 2024-01-20 19:55 | FALSE | 1 | line_111624_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | line_96107_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_96107_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | tr_9993_21 | Transformer | Transformer | 0.0475 | 0.078082 | 0.078082 | 0.05397 | 164.3832 | 10652 | 887.6667 | 10.1113 | 2024-01-20 07:25 | FALSE | 1 | tr_9993_21 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_111730_21 | ACLineSegment | Line | 0.034884 | 0.0047325 | 0.0047325 | 0.0026987 | 13.5665 | 0 | 0 | 0 | 2024-01-17 09:55 | FALSE | 1 | line_111730_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_96209_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_96209_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_111905_21 | ACLineSegment | Line | 13.5424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_111905_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | tr_2964_21 | Transformer | Transformer | 0.07125 | 0.019438 | 0.019438 | 0.013946 | 27.2809 | 0 | 0 | 0 | 2024-07-15 23:05 | FALSE | 1 | tr_2964_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_111906_21 | ACLineSegment | Line | 13.5424 | 0.39194 | 0.39194 | 0.30067 | 2.8942 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | line_111906_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | line_111907_21 | ACLineSegment | Line | 13.5424 | 0.38684 | 0.38684 | 0.29694 | 2.8565 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | line_111907_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | tr_2156_21 | Transformer | Transformer | 0.095 | 0.0074838 | 0.0074838 | 0.0052782 | 7.8777 | 0 | 0 | 0 | 2024-06-27 03:00 | FALSE | 1 | tr_2156_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_112561_21 | ACLineSegment | Line | 13.5424 | 0.39627 | 0.39627 | 0.3044 | 2.9262 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | line_112561_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | tr_9136_21 | Transformer | Transformer | 0.095 | 0.0067134 | 0.0067134 | 0.0050724 | 7.0667 | 0 | 0 | 0 | 2024-01-17 16:35 | FALSE | 1 | tr_9136_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_113500_21 | ACLineSegment | Line | 13.5424 | 0.37946 | 0.37946 | 0.29199 | 2.802 | 0 | 0 | 0 | 2024-07-15 23:05 | FALSE | 1 | line_113500_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | tr_11868_21 | Transformer | Transformer | 0.285 | 0.0082756 | 0.0082756 | 0.0057773 | 2.9037 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | tr_11868_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_111908_21 | ACLineSegment | Line | 0.51338 | 0.0074838 | 0.0074838 | 0.0052782 | 1.4577 | 0 | 0 | 0 | 2024-06-27 03:00 | FALSE | 1 | line_111908_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | line_96567_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_96567_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_112167_21 | ACLineSegment | Line | 13.5424 | 0.24766 | 0.24766 | 0.18284 | 1.8287 | 0 | 0 | 0 | 2024-12-24 | FALSE | 1 | line_112167_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | tr_2265_21 | Transformer | Transformer | 0.285 | 0.0056505 | 0.0056505 | 0.0039686 | 1.9826 | 0 | 0 | 0 | 2024-01-20 04:55 | FALSE | 1 | tr_2265_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_120823_21 | ACLineSegment | Line | 13.5424 | 0.1862 | 0.1862 | 0.1472 | 1.375 | 0 | 0 | 0 | 2024-01-20 15:45 | FALSE | 1 | line_120823_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | tr_5959_21 | Transformer | Transformer | 0.285 | 0.11009 | 0.11009 | 0.057817 | 38.627 | 0 | 0 | 0 | 2024-10-03 02:00 | FALSE | 1 | tr_5959_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_112169_21 | ACLineSegment | Line | 0.51338 | 0.0056505 | 0.0056505 | 0.0039686 | 1.1007 | 0 | 0 | 0 | 2024-01-20 04:55 | FALSE | 1 | line_112169_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | line_96363_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_96363_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_112171_21 | ACLineSegment | Line | 0.94778 | 0.20232 | 0.20232 | 0.14293 | 21.3463 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_112171_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_112172_21 | ACLineSegment | Line | 0.94778 | 0.20008 | 0.20008 | 0.14127 | 21.1101 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_112172_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | tr_2267_21 | Transformer | Transformer | 0.02375 | 0.0028322 | 0.0028322 | 0.0017187 | 11.925 | 0 | 0 | 0 | 2024-01-20 18:50 | FALSE | 1 | tr_2267_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_112250_21 | ACLineSegment | Line | 0.94778 | 0.20569 | 0.20569 | 0.1455 | 21.7025 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_112250_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | tr_2403_21 | Transformer | Transformer | 0.02375 | 0.0080151 | 0.0080151 | 0.0049574 | 33.7478 | 0 | 0 | 0 | 2024-01-17 21:45 | FALSE | 1 | tr_2403_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_113593_21 | ACLineSegment | Line | 0.94778 | 0.0063515 | 0.0063515 | 0.0032145 | 0.67015 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | line_113593_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_120790_21 | ACLineSegment | Line | 0.94778 | 0.12858 | 0.12858 | 0.087645 | 13.5661 | 0 | 0 | 0 | 2024-01-21 03:05 | FALSE | 1 | line_120790_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | tr_5945_21 | Transformer | Transformer | 0.0475 | 0.079363 | 0.079363 | 0.050983 | 167.0804 | 7941 | 661.75 | 7.5379 | 2024-01-20 15:45 | FALSE | 1 | tr_5945_21 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_112173_21 | ACLineSegment | Line | 0.034884 | 0.0028322 | 0.0028322 | 0.0017187 | 8.119 | 0 | 0 | 0 | 2024-01-20 18:50 | FALSE | 1 | line_112173_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_96371_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_96371_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_112185_21 | ACLineSegment | Line | 0.034884 | 0.0038144 | 0.0038144 | 0.0020791 | 10.9346 | 0 | 0 | 0 | 2024-01-17 23:55 | FALSE | 1 | line_112185_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_112186_21 | ACLineSegment | Line | 0.034884 | 0.0045866 | 0.0045866 | 0.0025576 | 13.1484 | 0 | 0 | 0 | 2024-01-20 22:50 | FALSE | 1 | line_112186_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_96377_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_96377_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_96378_21 | ACLineSegment | Line | 0.034884 | 0.0051893 | 0.0051893 | 0.002521 | 14.8761 | 0 | 0 | 0 | 2024-01-20 09:00 | FALSE | 1 | line_96378_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_96380_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_96380_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | tr_2288_21 | Transformer | Transformer | 0.07125 | 0.026192 | 0.026192 | 0.018371 | 36.7611 | 0 | 0 | 0 | 2024-01-20 14:50 | FALSE | 1 | tr_2288_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_112223_21 | ACLineSegment | Line | 0.51338 | 0.026192 | 0.026192 | 0.018371 | 5.1019 | 0 | 0 | 0 | 2024-01-20 14:50 | FALSE | 1 | line_112223_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | line_96406_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_96406_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | tr_2300_21 | Transformer | Transformer | 0.02375 | 0.0072232 | 0.0072232 | 0.0038941 | 30.4134 | 0 | 0 | 0 | 2024-01-21 03:05 | FALSE | 1 | tr_2300_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_112252_21 | ACLineSegment | Line | 0.034884 | 0.0072232 | 0.0072232 | 0.0038941 | 20.7066 | 0 | 0 | 0 | 2024-01-21 03:05 | FALSE | 1 | line_112252_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_96419_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_96419_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_112326_21 | ACLineSegment | Line | 0.94778 | 0.016378 | 0.016378 | 0.0090636 | 1.728 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_112326_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | tr_2333_21 | Transformer | Transformer | 0.02375 | 0.010113 | 0.010113 | 0.0061895 | 42.5822 | 0 | 0 | 0 | 2024-01-20 15:45 | FALSE | 1 | tr_2333_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | tr_10028_21 | Transformer | Transformer | 0.02375 | 0.016378 | 0.016378 | 0.0090636 | 68.9601 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | tr_10028_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_112479_21 | ACLineSegment | Line | 0.034884 | 0.0080151 | 0.0080151 | 0.0049574 | 22.9768 | 0 | 0 | 0 | 2024-01-17 21:45 | FALSE | 1 | line_112479_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_96820_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_96820_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_112529_21 | ACLineSegment | Line | 0.034884 | 0.0059583 | 0.0059583 | 0.0033576 | 17.0805 | 0 | 0 | 0 | 2024-07-15 07:55 | FALSE | 1 | line_112529_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_96862_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_96862_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_96863_21 | ACLineSegment | Line | 0.034884 | 0.0049637 | 0.0049637 | 0.0025986 | 14.2294 | 0 | 0 | 0 | 2024-01-17 19:55 | FALSE | 1 | line_96863_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_112560_21 | ACLineSegment | Line | 13.5424 | 0.40193 | 0.40193 | 0.30832 | 2.968 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | line_112560_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | tr_2444_21 | Transformer | Transformer | 0.07125 | 0.0082426 | 0.0082426 | 0.0057982 | 11.5686 | 0 | 0 | 0 | 2024-07-15 12:50 | FALSE | 1 | tr_2444_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_116037_21 | ACLineSegment | Line | 13.5424 | 0.40982 | 0.40982 | 0.31553 | 3.0262 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | line_116037_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | tr_3986_21 | Transformer | Transformer | 0.07125 | 0.011765 | 0.011765 | 0.008944 | 16.5118 | 0 | 0 | 0 | 2024-01-17 09:55 | FALSE | 1 | tr_3986_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_112562_21 | ACLineSegment | Line | 0.22905 | 0.0082426 | 0.0082426 | 0.0057982 | 3.5987 | 0 | 0 | 0 | 2024-07-15 12:50 | FALSE | 1 | line_112562_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | line_96873_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_96873_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | tr_2754_21 | Transformer | Transformer | 0.095 | 0.0078299 | 0.0078299 | 0.005669 | 8.2419 | 0 | 0 | 0 | 2024-01-21 15:00 | FALSE | 1 | tr_2754_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_112667_21 | ACLineSegment | Line | 0.51338 | 0.0076477 | 0.0076477 | 0.0050433 | 1.4897 | 0 | 0 | 0 | 2024-01-20 05:00 | FALSE | 1 | line_112667_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | line_96958_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_96958_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | tr_2581_21 | Transformer | Transformer | 0.0475 | 0.01617 | 0.01617 | 0.011907 | 34.0423 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | tr_2581_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_112862_21 | ACLineSegment | Line | 0.034884 | 0.0050846 | 0.0050846 | 0.0038725 | 14.5758 | 0 | 0 | 0 | 2024-07-10 01:55 | FALSE | 1 | line_112862_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_112863_21 | ACLineSegment | Line | 0.034884 | 0.0090608 | 0.0090608 | 0.0065354 | 25.9746 | 0 | 0 | 0 | 2024-01-17 23:55 | FALSE | 1 | line_112863_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_112864_21 | ACLineSegment | Line | 0.034884 | 0.0048779 | 0.0048779 | 0.0029187 | 13.9834 | 0 | 0 | 0 | 2024-01-17 16:35 | FALSE | 1 | line_112864_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_112945_21 | ACLineSegment | Line | 0.51338 | 0.007373 | 0.007373 | 0.0053142 | 1.4362 | 0 | 0 | 0 | 2024-01-21 01:25 | FALSE | 1 | line_112945_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | tr_9112_21 | Transformer | Transformer | 0.07125 | 0.016259 | 0.016259 | 0.012087 | 22.8195 | 0 | 0 | 0 | 2024-07-15 20:35 | FALSE | 1 | tr_9112_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_112966_21 | ACLineSegment | Line | 0.034884 | 0.007805 | 0.007805 | 0.0039401 | 22.3745 | 0 | 0 | 0 | 2024-01-21 02:15 | FALSE | 1 | line_112966_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | tr_2630_21 | Transformer | Transformer | 0.07125 | 0.0061009 | 0.0061009 | 0.0047998 | 8.5626 | 0 | 0 | 0 | 2024-01-21 23:50 | FALSE | 1 | tr_2630_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_112974_21 | ACLineSegment | Line | 0.51338 | 0.0061009 | 0.0061009 | 0.0047998 | 1.1884 | 0 | 0 | 0 | 2024-01-21 23:50 | FALSE | 1 | line_112974_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | line_113029_21 | ACLineSegment | Line | 0.034884 | 0.0029693 | 0.0029693 | 0.0015123 | 8.512 | 0 | 0 | 0 | 2024-01-17 22:10 | FALSE | 1 | line_113029_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_97019_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_97019_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_113115_21 | ACLineSegment | Line | 0.034884 | 0.0056167 | 0.0056167 | 0.0029041 | 16.1014 | 0 | 0 | 0 | 2024-01-20 16:00 | FALSE | 1 | line_113115_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_113116_21 | ACLineSegment | Line | 0.034884 | 0.0093451 | 0.0093451 | 0.0048445 | 26.7895 | 0 | 0 | 0 | 2024-01-20 05:00 | FALSE | 1 | line_113116_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_97056_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_97056_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_97057_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_97057_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_113232_21 | ACLineSegment | Line | 0.51338 | 0.0078299 | 0.0078299 | 0.005669 | 1.5252 | 0 | 0 | 0 | 2024-01-21 15:00 | FALSE | 1 | line_113232_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | line_97421_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_97421_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_113332_21 | ACLineSegment | Line | 0.034884 | 0.0063597 | 0.0063597 | 0.0039823 | 18.2312 | 0 | 0 | 0 | 2024-07-05 10:15 | FALSE | 1 | line_113332_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_97465_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_97465_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_113501_21 | ACLineSegment | Line | 13.5424 | 0.042824 | 0.042824 | 0.027971 | 0.31622 | 0 | 0 | 0 | 2024-06-20 16:55 | FALSE | 1 | line_113501_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | tr_2887_21 | Transformer | Transformer | 0.02375 | 0.0040442 | 0.0040442 | 0.0022215 | 17.0283 | 0 | 0 | 0 | 2024-01-20 18:50 | FALSE | 1 | tr_2887_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_113502_21 | ACLineSegment | Line | 0.034884 | 0.0040442 | 0.0040442 | 0.0022215 | 11.5935 | 0 | 0 | 0 | 2024-01-20 18:50 | FALSE | 1 | line_113502_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_97326_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_97326_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | tr_2932_21 | Transformer | Transformer | 0.02375 | 0.0063515 | 0.0063515 | 0.0032145 | 26.7433 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | tr_2932_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_113594_21 | ACLineSegment | Line | 0.034884 | 0.0063515 | 0.0063515 | 0.0032145 | 18.2078 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | line_113594_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_97397_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_97397_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_113659_21 | ACLineSegment | Line | 0.51338 | 0.019438 | 0.019438 | 0.013946 | 3.7862 | 0 | 0 | 0 | 2024-07-15 23:05 | FALSE | 1 | line_113659_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | line_97377_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_97377_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | tr_9245_21 | Transformer | Transformer | 0.02375 | 0.019778 | 0.019778 | 0.012766 | 83.2764 | 0 | 0 | 0 | 2024-01-20 21:15 | FALSE | 1 | tr_9245_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_115811_21 | ACLineSegment | Line | 0.034884 | 0.0037671 | 0.0037671 | 0.0019838 | 10.799 | 0 | 0 | 0 | 2024-01-20 09:00 | FALSE | 1 | line_115811_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_115812_21 | ACLineSegment | Line | 0.034884 | 0.0044839 | 0.0044839 | 0.0025029 | 12.854 | 0 | 0 | 0 | 2024-01-21 03:05 | FALSE | 1 | line_115812_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_115813_21 | ACLineSegment | Line | 0.034884 | 0.0030517 | 0.0030517 | 0.0017711 | 8.7483 | 0 | 0 | 0 | 2024-07-15 05:55 | FALSE | 1 | line_115813_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_115814_21 | ACLineSegment | Line | 0.034884 | 0.0051323 | 0.0051323 | 0.0028325 | 14.7128 | 0 | 0 | 0 | 2024-01-17 15:40 | FALSE | 1 | line_115814_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_115815_21 | ACLineSegment | Line | 0.034884 | 0.0036556 | 0.0036556 | 0.0019945 | 10.4795 | 0 | 0 | 0 | 2024-01-20 22:50 | FALSE | 1 | line_115815_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_24868_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_24868_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_24870_21 | ACLineSegment | Line | 0.034884 | 0.017838 | 0.017838 | 0.011861 | 51.1354 | 0 | 0 | 0 | 2024-07-15 06:00 | FALSE | 1 | line_24870_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_24883_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_24883_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_24885_21 | ACLineSegment | Line | 0.034884 | 0.027749 | 0.027749 | 0.017748 | 79.5472 | 0 | 0 | 0 | 2024-01-21 01:25 | FALSE | 1 | line_24885_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_24887_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_24887_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_24889_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_24889_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_128347_21 | ACLineSegment | Line | 13.5424 | 0.052226 | 0.052226 | 0.033337 | 0.38565 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_128347_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | tr_10069_21 | Transformer | Transformer | 0.02375 | 0.0064328 | 0.0064328 | 0.0044343 | 27.0854 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | tr_10069_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_115861_21 | ACLineSegment | Line | 0.034884 | 0.0048 | 0.0048 | 0.002361 | 13.7601 | 0 | 0 | 0 | 2024-01-21 03:05 | FALSE | 1 | line_115861_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25057_21 | ACLineSegment | Line | 0.034884 | 0.036523 | 0.036523 | 0.024802 | 104.7001 | 36 | 3 | 0.034172 | 2024-01-20 23:55 | FALSE | 1 | line_25057_21 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_25071_21 | ACLineSegment | Line | 0.034884 | 0.02911 | 0.02911 | 0.018546 | 83.4506 | 0 | 0 | 0 | 2024-01-20 07:25 | FALSE | 1 | line_25071_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_127903_21 | ACLineSegment | Line | 0.94778 | 0.075483 | 0.075483 | 0.048809 | 7.9642 | 0 | 0 | 0 | 2024-01-21 03:05 | FALSE | 1 | line_127903_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | tr_10035_21 | Transformer | Transformer | 0.02375 | 0.0048842 | 0.0048842 | 0.0026881 | 20.5652 | 0 | 0 | 0 | 2024-01-20 09:00 | FALSE | 1 | tr_10035_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_115875_21 | ACLineSegment | Line | 0.034884 | 0.0064848 | 0.0064848 | 0.0030615 | 18.59 | 0 | 0 | 0 | 2024-01-20 15:45 | FALSE | 1 | line_115875_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25135_21 | ACLineSegment | Line | 0.034884 | 0.029455 | 0.029455 | 0.018615 | 84.4387 | 0 | 0 | 0 | 2024-01-20 11:55 | FALSE | 1 | line_25135_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25140_21 | ACLineSegment | Line | 0.034884 | 0.022735 | 0.022735 | 0.013854 | 65.1747 | 0 | 0 | 0 | 2024-01-20 15:45 | FALSE | 1 | line_25140_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_115957_21 | ACLineSegment | Line | 0.034884 | 0.0057836 | 0.0057836 | 0.0034554 | 16.5796 | 0 | 0 | 0 | 2024-07-15 09:15 | FALSE | 1 | line_115957_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25835_21 | ACLineSegment | Line | 0.034884 | 0.03586 | 0.03586 | 0.022969 | 102.8001 | 12 | 1 | 0.011391 | 2024-01-20 11:55 | FALSE | 1 | line_25835_21 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_25856_21 | ACLineSegment | Line | 0.034884 | 0.02992 | 0.02992 | 0.01982 | 85.7704 | 0 | 0 | 0 | 2024-01-20 08:55 | FALSE | 1 | line_25856_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_116038_21 | ACLineSegment | Line | 13.5424 | 0.43492 | 0.43492 | 0.33368 | 3.2116 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | line_116038_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | tr_3864_21 | Transformer | Transformer | 0.0475 | 0.031391 | 0.031391 | 0.020488 | 66.0857 | 0 | 0 | 0 | 2024-01-20 06:55 | FALSE | 1 | tr_3864_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_131276_21 | ACLineSegment | Line | 13.5424 | 0.45477 | 0.45477 | 0.35215 | 3.3581 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | line_131276_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | line_116039_21 | ACLineSegment | Line | 0.034884 | 0.0081587 | 0.0081587 | 0.0042702 | 23.3883 | 0 | 0 | 0 | 2024-01-20 17:05 | FALSE | 1 | line_116039_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_15467_21 | ACLineSegment | Line | 0.034884 | 0.010137 | 0.010137 | 0.0055458 | 29.0605 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | line_15467_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_15469_21 | ACLineSegment | Line | 0.034884 | 0.017366 | 0.017366 | 0.012533 | 49.7815 | 0 | 0 | 0 | 2024-01-20 06:55 | FALSE | 1 | line_15469_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_116059_21 | ACLineSegment | Line | 0.034884 | 0.0071645 | 0.0071645 | 0.0037073 | 20.5382 | 0 | 0 | 0 | 2024-01-20 07:25 | FALSE | 1 | line_116059_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_116060_21 | ACLineSegment | Line | 0.034884 | 0.0027375 | 0.0027375 | 0.0015583 | 7.8475 | 0 | 0 | 0 | 2024-01-18 | FALSE | 1 | line_116060_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_116061_21 | ACLineSegment | Line | 0.034884 | 0.0086025 | 0.0086025 | 0.0044715 | 24.6606 | 0 | 0 | 0 | 2024-01-21 01:25 | FALSE | 1 | line_116061_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_15592_21 | ACLineSegment | Line | 0.034884 | 0.031052 | 0.031052 | 0.021107 | 89.0154 | 0 | 0 | 0 | 2024-01-20 09:00 | FALSE | 1 | line_15592_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_15602_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_15602_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_15610_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_15610_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_15611_21 | ACLineSegment | Line | 0.034884 | 0.018103 | 0.018103 | 0.011912 | 51.8959 | 0 | 0 | 0 | 2024-01-20 19:55 | FALSE | 1 | line_15611_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_116129_21 | ACLineSegment | Line | 0.034884 | 0.0092016 | 0.0092016 | 0.0050038 | 26.3782 | 0 | 0 | 0 | 2024-01-20 22:50 | FALSE | 1 | line_116129_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_116130_21 | ACLineSegment | Line | 0.034884 | 0.0031845 | 0.0031845 | 0.001632 | 9.1288 | 0 | 0 | 0 | 2024-01-20 15:45 | FALSE | 1 | line_116130_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_16390_21 | ACLineSegment | Line | 0.034884 | 0.037463 | 0.037463 | 0.024419 | 107.3934 | 50 | 4.1667 | 0.047462 | 2024-01-18 04:00 | FALSE | 1 | line_16390_21 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_16421_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_16421_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_16422_21 | ACLineSegment | Line | 0.034884 | 0.041322 | 0.041322 | 0.027875 | 118.456 | 334 | 27.8333 | 0.31704 | 2024-01-20 11:55 | FALSE | 1 | line_16422_21 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_116238_21 | ACLineSegment | Line | 0.034884 | 0.0064313 | 0.0064313 | 0.0035616 | 18.4365 | 0 | 0 | 0 | 2024-01-20 10:55 | FALSE | 1 | line_116238_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_17635_21 | ACLineSegment | Line | 0.034884 | 0.030058 | 0.030058 | 0.02083 | 86.1665 | 0 | 0 | 0 | 2024-01-20 18:50 | FALSE | 1 | line_17635_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_17638_21 | ACLineSegment | Line | 0.034884 | 0.028426 | 0.028426 | 0.017844 | 81.4877 | 0 | 0 | 0 | 2024-01-20 11:55 | FALSE | 1 | line_17638_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_116286_21 | ACLineSegment | Line | 0.034884 | 0.004241 | 0.004241 | 0.0023426 | 12.1576 | 0 | 0 | 0 | 2024-07-16 03:00 | FALSE | 1 | line_116286_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_116287_21 | ACLineSegment | Line | 0.034884 | 0.0083443 | 0.0083443 | 0.0043497 | 23.9204 | 0 | 0 | 0 | 2024-01-20 22:50 | FALSE | 1 | line_116287_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_17899_21 | ACLineSegment | Line | 0.034884 | 0.013761 | 0.013761 | 0.0082823 | 39.4498 | 0 | 0 | 0 | 2024-01-20 10:55 | FALSE | 1 | line_17899_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_17902_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_17902_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_17907_21 | ACLineSegment | Line | 0.034884 | 0.014276 | 0.014276 | 0.0086026 | 40.9252 | 0 | 0 | 0 | 2024-01-20 21:15 | FALSE | 1 | line_17907_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_122817_21 | ACLineSegment | Line | 0.94778 | 0.11135 | 0.11135 | 0.074177 | 11.7488 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_122817_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | tr_12338_21 | Transformer | Transformer | 0.02375 | 0.023447 | 0.023447 | 0.01359 | 98.7255 | 0 | 0 | 0 | 2024-01-20 05:00 | FALSE | 1 | tr_12338_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_122816_21 | ACLineSegment | Line | 0.94778 | 0.0302 | 0.0302 | 0.01903 | 3.1864 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_122816_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | tr_6973_21 | Transformer | Transformer | 0.0475 | 0.081895 | 0.081895 | 0.055125 | 172.4098 | 12667 | 1055.5833 | 12.024 | 2024-01-20 11:55 | FALSE | 1 | tr_6973_21 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_122824_21 | ACLineSegment | Line | 0.94778 | 0.0085911 | 0.0085911 | 0.005037 | 0.90645 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | line_122824_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | tr_6975_21 | Transformer | Transformer | 0.02375 | 0.023777 | 0.023777 | 0.014239 | 100.1126 | 2 | 0.16667 | 0.0018985 | 2024-01-18 01:55 | FALSE | 1 | tr_6975_21 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_122818_21 | ACLineSegment | Line | 0.034884 | 0.0048147 | 0.0048147 | 0.0026619 | 13.8023 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | line_122818_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_122819_21 | ACLineSegment | Line | 0.034884 | 0.00403 | 0.00403 | 0.0021591 | 11.5526 | 0 | 0 | 0 | 2024-01-20 11:55 | FALSE | 1 | line_122819_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_122820_21 | ACLineSegment | Line | 0.034884 | 0.0041151 | 0.0041151 | 0.0021681 | 11.7967 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | line_122820_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_55496_21 | ACLineSegment | Line | 0.034884 | 0.048271 | 0.048271 | 0.030517 | 138.3767 | 1526 | 127.1667 | 1.4485 | 2024-01-20 11:55 | FALSE | 1 | line_55496_21 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_55503_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_55503_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_55508_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_55508_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_55523_21 | ACLineSegment | Line | 0.034884 | 0.029565 | 0.029565 | 0.018328 | 84.753 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_55523_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_55531_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_55531_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | tr_6981_21 | Transformer | Transformer | 0.02375 | 0.0085911 | 0.0085911 | 0.005037 | 36.1732 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | tr_6981_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_122825_21 | ACLineSegment | Line | 0.034884 | 0.0039882 | 0.0039882 | 0.0022652 | 11.433 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | line_122825_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_122826_21 | ACLineSegment | Line | 0.034884 | 0.003887 | 0.003887 | 0.0020207 | 11.1428 | 0 | 0 | 0 | 2024-01-20 09:00 | FALSE | 1 | line_122826_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_122827_21 | ACLineSegment | Line | 0.034884 | 0.0035583 | 0.0035583 | 0.0020018 | 10.2005 | 0 | 0 | 0 | 2024-07-15 11:00 | FALSE | 1 | line_122827_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_55342_21 | ACLineSegment | Line | 0.034884 | 0.01492 | 0.01492 | 0.0085367 | 42.7702 | 0 | 0 | 0 | 2024-01-18 01:55 | FALSE | 1 | line_55342_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_55343_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_55343_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_55344_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_55344_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_122834_21 | ACLineSegment | Line | 0.034884 | 0.0053135 | 0.0053135 | 0.003032 | 15.2321 | 0 | 0 | 0 | 2024-01-18 | FALSE | 1 | line_122834_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_122835_21 | ACLineSegment | Line | 0.034884 | 0.0045411 | 0.0045411 | 0.002235 | 13.0179 | 0 | 0 | 0 | 2024-01-20 17:05 | FALSE | 1 | line_122835_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_55651_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_55651_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_55652_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_55652_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | tr_10620_21 | Transformer | Transformer | 0.02375 | 0.0079628 | 0.0079628 | 0.0056751 | 33.5275 | 0 | 0 | 0 | 2024-01-21 03:05 | FALSE | 1 | tr_10620_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_122868_21 | ACLineSegment | Line | 0.034884 | 0.0065263 | 0.0065263 | 0.003848 | 18.7088 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | line_122868_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_122869_21 | ACLineSegment | Line | 0.034884 | 0.0039024 | 0.0039024 | 0.0020725 | 11.187 | 0 | 0 | 0 | 2024-06-27 03:00 | FALSE | 1 | line_122869_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_53932_21 | ACLineSegment | Line | 0.034884 | 0.010595 | 0.010595 | 0.0059782 | 30.3736 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_53932_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_53936_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_53936_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_53937_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_53937_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_53938_21 | ACLineSegment | Line | 0.034884 | 0.0084028 | 0.0084028 | 0.0050359 | 24.0882 | 0 | 0 | 0 | 2024-01-17 20:10 | FALSE | 1 | line_53938_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_126507_21 | ACLineSegment | Line | 0.034884 | 0.0054144 | 0.0054144 | 0.004101 | 15.5214 | 0 | 0 | 0 | 2024-01-18 | FALSE | 1 | line_126507_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_65044_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_65044_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_126596_21 | ACLineSegment | Line | 0.51338 | 0.04047 | 0.04047 | 0.02903 | 7.883 | 0 | 0 | 0 | 2024-07-01 03:00 | FALSE | 1 | line_126596_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | line_65796_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_65796_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | tr_8999_21 | Transformer | Transformer | 0.02375 | 0.035246 | 0.035246 | 0.022835 | 148.4034 | 4043 | 336.9167 | 3.8378 | 2024-01-21 | FALSE | 1 | tr_8999_21 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_126657_21 | ACLineSegment | Line | 0.034884 | 0.0053486 | 0.0053486 | 0.002952 | 15.3327 | 0 | 0 | 0 | 2024-01-20 07:25 | FALSE | 1 | line_126657_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_65976_21 | ACLineSegment | Line | 0.034884 | 0.016008 | 0.016008 | 0.010188 | 45.8913 | 0 | 0 | 0 | 2024-01-20 14:50 | FALSE | 1 | line_65976_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_65983_21 | ACLineSegment | Line | 0.034884 | 0.018782 | 0.018782 | 0.010346 | 53.8429 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | line_65983_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_65985_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_65985_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | tr_9028_21 | Transformer | Transformer | 0.02375 | 0.0090079 | 0.0090079 | 0.0056338 | 37.928 | 0 | 0 | 0 | 2024-01-20 09:00 | FALSE | 1 | tr_9028_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_126883_21 | ACLineSegment | Line | 0.51338 | 0.016259 | 0.016259 | 0.012087 | 3.167 | 0 | 0 | 0 | 2024-07-15 20:35 | FALSE | 1 | line_126883_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | line_126895_21 | ACLineSegment | Line | 0.034884 | 0.0060734 | 0.0060734 | 0.0034077 | 17.4106 | 0 | 0 | 0 | 2024-01-20 06:55 | FALSE | 1 | line_126895_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_126896_21 | ACLineSegment | Line | 0.034884 | 0.0032544 | 0.0032544 | 0.0015672 | 9.3292 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | line_126896_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_67991_21 | ACLineSegment | Line | 0.034884 | 0.031021 | 0.031021 | 0.020279 | 88.9273 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | line_67991_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_68005_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_68005_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_68006_21 | ACLineSegment | Line | 0.034884 | 0.016259 | 0.016259 | 0.009883 | 46.6089 | 0 | 0 | 0 | 2024-01-20 10:55 | FALSE | 1 | line_68006_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_126916_21 | ACLineSegment | Line | 0.51338 | 0.0067134 | 0.0067134 | 0.0050724 | 1.3077 | 0 | 0 | 0 | 2024-01-17 16:35 | FALSE | 1 | line_126916_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | line_67900_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_67900_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_127035_21 | ACLineSegment | Line | 0.034884 | 0.0045392 | 0.0045392 | 0.0026257 | 13.0125 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | line_127035_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_127036_21 | ACLineSegment | Line | 0.034884 | 0.0059283 | 0.0059283 | 0.0032381 | 16.9945 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_127036_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69062_21 | ACLineSegment | Line | 0.034884 | 0.043934 | 0.043934 | 0.029778 | 125.9461 | 1220 | 101.6667 | 1.1581 | 2024-01-21 03:05 | FALSE | 1 | line_69062_21 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_69078_21 | ACLineSegment | Line | 0.034884 | 0.039349 | 0.039349 | 0.026998 | 112.8016 | 204 | 17 | 0.19364 | 2024-01-20 22:50 | FALSE | 1 | line_69078_21 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_69084_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_69084_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | tr_9210_21 | Transformer | Transformer | 0.0475 | 0.042003 | 0.042003 | 0.02917 | 88.4277 | 0 | 0 | 0 | 2024-01-17 07:00 | FALSE | 1 | tr_9210_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_127046_21 | ACLineSegment | Line | 0.034884 | 0.004784 | 0.004784 | 0.0024896 | 13.7143 | 0 | 0 | 0 | 2024-01-20 19:55 | FALSE | 1 | line_127046_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69146_21 | ACLineSegment | Line | 0.034884 | 0.026438 | 0.026438 | 0.017252 | 75.7894 | 0 | 0 | 0 | 2024-01-21 03:05 | FALSE | 1 | line_69146_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69154_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_69154_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69155_21 | ACLineSegment | Line | 0.034884 | 0.015213 | 0.015213 | 0.0096387 | 43.6095 | 0 | 0 | 0 | 2024-07-16 02:00 | FALSE | 1 | line_69155_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_127113_21 | ACLineSegment | Line | 0.034884 | 0.0051383 | 0.0051383 | 0.0029666 | 14.73 | 0 | 0 | 0 | 2024-07-15 19:55 | FALSE | 1 | line_127113_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_127114_21 | ACLineSegment | Line | 0.034884 | 0.0078423 | 0.0078423 | 0.0040481 | 22.4814 | 0 | 0 | 0 | 2024-01-21 01:25 | FALSE | 1 | line_127114_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69299_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_69299_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69302_21 | ACLineSegment | Line | 0.034884 | 0.0078657 | 0.0078657 | 0.0045543 | 22.5485 | 0 | 0 | 0 | 2024-01-20 11:55 | FALSE | 1 | line_69302_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69308_21 | ACLineSegment | Line | 0.034884 | 0.0040328 | 0.0040328 | 0.0023244 | 11.5609 | 0 | 0 | 0 | 2024-01-20 17:05 | FALSE | 1 | line_69308_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_127116_21 | ACLineSegment | Line | 0.51338 | 0.0074636 | 0.0074636 | 0.0044177 | 1.4538 | 0 | 0 | 0 | 2024-01-20 13:05 | FALSE | 1 | line_127116_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | line_69708_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_69708_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_127126_21 | ACLineSegment | Line | 0.034884 | 0.0066597 | 0.0066597 | 0.0034644 | 19.0912 | 0 | 0 | 0 | 2024-01-20 06:55 | FALSE | 1 | line_127126_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69753_21 | ACLineSegment | Line | 0.034884 | 0.023798 | 0.023798 | 0.015181 | 68.2203 | 0 | 0 | 0 | 2024-01-20 06:55 | FALSE | 1 | line_69753_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69760_21 | ACLineSegment | Line | 0.034884 | 0.021261 | 0.021261 | 0.014442 | 60.9487 | 0 | 0 | 0 | 2024-01-21 01:25 | FALSE | 1 | line_69760_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_127131_21 | ACLineSegment | Line | 0.034884 | 0.0044438 | 0.0044438 | 0.0028431 | 12.7391 | 0 | 0 | 0 | 2024-08-08 18:10 | FALSE | 1 | line_127131_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_127132_21 | ACLineSegment | Line | 0.034884 | 0.0039961 | 0.0039961 | 0.0021528 | 11.4557 | 0 | 0 | 0 | 2024-01-21 03:05 | FALSE | 1 | line_127132_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | tr_9773_21 | Transformer | Transformer | 0.0475 | 0.075483 | 0.075483 | 0.048809 | 158.912 | 6577 | 548.0833 | 6.2431 | 2024-01-21 03:05 | FALSE | 1 | tr_9773_21 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_127904_21 | ACLineSegment | Line | 0.034884 | 0.0052775 | 0.0052775 | 0.0030181 | 15.129 | 0 | 0 | 0 | 2024-01-20 23:55 | FALSE | 1 | line_127904_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_73276_21 | ACLineSegment | Line | 0.046073 | 0.072106 | 0.072106 | 0.045966 | 156.5042 | 5170 | 430.8333 | 4.9075 | 2024-01-21 03:05 | FALSE | 1 | line_73276_21 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_128131_21 | ACLineSegment | Line | 0.034884 | 0.0069803 | 0.0069803 | 0.0039278 | 20.0102 | 0 | 0 | 0 | 2024-01-17 14:00 | FALSE | 1 | line_128131_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_72176_21 | ACLineSegment | Line | 0.034884 | 0.037081 | 0.037081 | 0.023251 | 106.2985 | 35 | 2.9167 | 0.033223 | 2024-01-17 08:10 | FALSE | 1 | line_72176_21 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_128234_21 | ACLineSegment | Line | 0.034884 | 0.0033351 | 0.0033351 | 0.0018721 | 9.5607 | 0 | 0 | 0 | 2024-07-15 13:05 | FALSE | 1 | line_128234_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_128235_21 | ACLineSegment | Line | 0.034884 | 0.0034963 | 0.0034963 | 0.0021981 | 10.0227 | 0 | 0 | 0 | 2024-07-15 16:45 | FALSE | 1 | line_128235_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_75359_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_75359_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_75360_21 | ACLineSegment | Line | 0.034884 | 0.033763 | 0.033763 | 0.022431 | 96.7889 | 0 | 0 | 0 | 2024-01-20 07:25 | FALSE | 1 | line_75360_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_75394_21 | ACLineSegment | Line | 0.034884 | 0.042609 | 0.042609 | 0.027758 | 122.1475 | 530 | 44.1667 | 0.50309 | 2024-01-20 23:55 | FALSE | 1 | line_75394_21 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_128249_21 | ACLineSegment | Line | 0.51338 | 0.0067475 | 0.0067475 | 0.0045061 | 1.3143 | 0 | 0 | 0 | 2024-01-20 05:00 | FALSE | 1 | line_128249_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | line_128297_21 | ACLineSegment | Line | 0.034884 | 0.0048842 | 0.0048842 | 0.0026881 | 14.0016 | 0 | 0 | 0 | 2024-01-20 09:00 | FALSE | 1 | line_128297_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_75880_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_75880_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | tr_12314_21 | Transformer | Transformer | 0.0475 | 0.032607 | 0.032607 | 0.02451 | 68.6459 | 0 | 0 | 0 | 2024-01-21 02:15 | FALSE | 1 | tr_12314_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_128348_21 | ACLineSegment | Line | 0.034884 | 0.0064328 | 0.0064328 | 0.0044343 | 18.4408 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | line_128348_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_76172_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_76172_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_128626_21 | ACLineSegment | Line | 13.5424 | 0.45813 | 0.45813 | 0.3561 | 3.383 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | line_128626_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | tr_10235_21 | Transformer | Transformer | 0.02375 | 0.0033635 | 0.0033635 | 0.0018008 | 14.1621 | 0 | 0 | 0 | 2024-01-20 15:45 | FALSE | 1 | tr_10235_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | tr_11876_21 | Transformer | Transformer | 0.475 | 0.0072096 | 0.0072096 | 0.0054025 | 1.5178 | 0 | 0 | 0 | 2024-01-17 13:10 | FALSE | 1 | tr_11876_21 | Transformer_kVA_x_PF | No modeled rating exceedance
GSO_18 | line_128627_21 | ACLineSegment | Line | 0.034884 | 0.0033635 | 0.0033635 | 0.0018008 | 9.6421 | 0 | 0 | 0 | 2024-01-20 15:45 | FALSE | 1 | line_128627_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_78640_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_78640_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_129218_21 | ACLineSegment | Line | 0.034884 | 0.0089858 | 0.0089858 | 0.006628 | 25.7594 | 0 | 0 | 0 | 2024-01-17 13:10 | FALSE | 1 | line_129218_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_79128_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_79128_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_129224_21 | ACLineSegment | Line | 0.51338 | 0.03013 | 0.03013 | 0.020922 | 5.8689 | 0 | 0 | 0 | 2024-02-14 22:00 | FALSE | 1 | line_129224_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | line_79132_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_79132_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_129231_21 | ACLineSegment | Line | 0.034884 | 0.0079628 | 0.0079628 | 0.0056751 | 22.8268 | 0 | 0 | 0 | 2024-01-21 03:05 | FALSE | 1 | line_129231_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_79131_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_79131_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_129234_21 | ACLineSegment | Line | 0.51338 | 0.0052162 | 0.0052162 | 0.0041155 | 1.0161 | 0 | 0 | 0 | 2024-07-05 08:35 | FALSE | 1 | line_129234_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | line_129250_21 | ACLineSegment | Line | 0.51338 | 0.0059583 | 0.0059583 | 0.0043189 | 1.1606 | 0 | 0 | 0 | 2024-01-21 05:00 | FALSE | 1 | line_129250_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | line_79219_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_79219_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_129253_21 | ACLineSegment | Line | 0.51338 | 0.0077068 | 0.0077068 | 0.0057941 | 1.5012 | 0 | 0 | 0 | 2024-06-26 11:00 | FALSE | 1 | line_129253_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | line_79129_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_79129_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_129254_21 | ACLineSegment | Line | 0.51338 | 0.0048594 | 0.0048594 | 0.0030174 | 0.94655 | 0 | 0 | 0 | 2024-01-17 07:00 | FALSE | 1 | line_129254_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | line_79247_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_79247_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_129258_21 | ACLineSegment | Line | 0.22905 | 0.0072588 | 0.0072588 | 0.005365 | 3.1691 | 0 | 0 | 0 | 2024-12-23 13:05 | FALSE | 1 | line_129258_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | line_79222_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_79222_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_129262_21 | ACLineSegment | Line | 0.51338 | 0.0076729 | 0.0076729 | 0.0056866 | 1.4946 | 0 | 0 | 0 | 2024-01-20 05:00 | FALSE | 1 | line_129262_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | line_79227_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_79227_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_131266_21 | ACLineSegment | Line | 0.51338 | 0.0082756 | 0.0082756 | 0.0057773 | 1.612 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | line_131266_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | line_86356_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_86356_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_131268_21 | ACLineSegment | Line | 0.51338 | 0.0071783 | 0.0071783 | 0.0050335 | 1.3982 | 0 | 0 | 0 | 2024-01-22 04:00 | FALSE | 1 | line_131268_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | line_86355_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_86355_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_131277_21 | ACLineSegment | Line | 0.51338 | 0.0072096 | 0.0072096 | 0.0054025 | 1.4043 | 0 | 0 | 0 | 2024-01-17 13:10 | FALSE | 1 | line_131277_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | line_86361_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_86361_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_131951_21 | ACLineSegment | Line | 0.034884 | 0.0038237 | 0.0038237 | 0.0020202 | 10.9613 | 0 | 0 | 0 | 2024-01-20 07:25 | FALSE | 1 | line_131951_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_131952_21 | ACLineSegment | Line | 0.034884 | 0.0026126 | 0.0026126 | 0.0016141 | 7.4894 | 0 | 0 | 0 | 2024-07-15 17:05 | FALSE | 1 | line_131952_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_131953_21 | ACLineSegment | Line | 0.034884 | 0.0092687 | 0.0092687 | 0.00655 | 26.5704 | 0 | 0 | 0 | 2024-01-20 18:50 | FALSE | 1 | line_131953_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_88164_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_88164_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_88166_21 | ACLineSegment | Line | 0.034884 | 0.022565 | 0.022565 | 0.016562 | 64.6869 | 0 | 0 | 0 | 2024-01-20 08:55 | FALSE | 1 | line_88166_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_88173_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_88173_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_131971_21 | ACLineSegment | Line | 0.034884 | 0.0056384 | 0.0056384 | 0.0027649 | 16.1637 | 0 | 0 | 0 | 2024-01-17 13:10 | FALSE | 1 | line_131971_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_131972_21 | ACLineSegment | Line | 0.034884 | 0.0071566 | 0.0071566 | 0.0029099 | 20.5156 | 0 | 0 | 0 | 2024-01-20 20:20 | FALSE | 1 | line_131972_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_131973_21 | ACLineSegment | Line | 0.034884 | 0.021412 | 0.021412 | 0.016287 | 61.3824 | 0 | 0 | 0 | 2024-07-15 20:35 | FALSE | 1 | line_131973_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_131974_21 | ACLineSegment | Line | 0.034884 | 0.0068327 | 0.0068327 | 0.0050272 | 19.5873 | 0 | 0 | 0 | 2024-07-15 21:45 | FALSE | 1 | line_131974_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_131984_21 | ACLineSegment | Line | 0.51338 | 0.0044955 | 0.0044955 | 0.0034699 | 0.87566 | 0 | 0 | 0 | 2024-01-20 21:15 | FALSE | 1 | line_131984_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | line_131998_21 | ACLineSegment | Line | 0.034884 | 0.0096084 | 0.0096084 | 0.0046113 | 27.5444 | 0 | 0 | 0 | 2024-01-21 03:05 | FALSE | 1 | line_131998_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_131999_21 | ACLineSegment | Line | 0.034884 | 0.002878 | 0.002878 | 0.0015394 | 8.2503 | 0 | 0 | 0 | 2024-01-20 05:00 | FALSE | 1 | line_131999_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_132000_21 | ACLineSegment | Line | 0.034884 | 0.0039159 | 0.0039159 | 0.002288 | 11.2255 | 0 | 0 | 0 | 2024-01-20 23:55 | FALSE | 1 | line_132000_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_132001_21 | ACLineSegment | Line | 0.034884 | 0.006381 | 0.006381 | 0.0029244 | 18.2922 | 0 | 0 | 0 | 2024-01-20 05:00 | FALSE | 1 | line_132001_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_132002_21 | ACLineSegment | Line | 0.034884 | 0.0054937 | 0.0054937 | 0.0032228 | 15.7488 | 0 | 0 | 0 | 2024-01-20 10:55 | FALSE | 1 | line_132002_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_88589_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_88589_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_88590_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_88590_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_88591_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_88591_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_88593_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_88593_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_88594_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_88594_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_15464_21 | ACLineSegment | Line | 0.034884 | 0.0065816 | 0.0065816 | 0.003843 | 18.8674 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | line_15464_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_15465_21 | ACLineSegment | Line | 0.034884 | 0.0065816 | 0.0065816 | 0.003843 | 18.8674 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | line_15465_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_15466_21 | ACLineSegment | Line | 0.034884 | 0.010137 | 0.010137 | 0.0055458 | 29.0605 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | line_15466_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_15468_21 | ACLineSegment | Line | 0.034884 | 0.0035557 | 0.0035557 | 0.0019272 | 10.1931 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | line_15468_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_15470_21 | ACLineSegment | Line | 0.034884 | 0.017366 | 0.017366 | 0.012533 | 49.7815 | 0 | 0 | 0 | 2024-01-20 06:55 | FALSE | 1 | line_15470_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_15479_21 | ACLineSegment | Line | 0.034884 | 0.014519 | 0.014519 | 0.0088594 | 41.6213 | 0 | 0 | 0 | 2024-01-20 15:45 | FALSE | 1 | line_15479_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_15480_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_15480_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_15481_21 | ACLineSegment | Line | 0.034884 | 0.0090853 | 0.0090853 | 0.005001 | 26.0446 | 0 | 0 | 0 | 2024-01-20 17:05 | FALSE | 1 | line_15481_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_15482_21 | ACLineSegment | Line | 0.034884 | 0.0066595 | 0.0066595 | 0.0029608 | 19.0906 | 0 | 0 | 0 | 2024-01-20 20:20 | FALSE | 1 | line_15482_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_15483_21 | ACLineSegment | Line | 0.034884 | 0.0026751 | 0.0026751 | 0.0013885 | 7.6686 | 0 | 0 | 0 | 2024-01-20 21:15 | FALSE | 1 | line_15483_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_15497_21 | ACLineSegment | Line | 0.034884 | 0.016503 | 0.016503 | 0.010252 | 47.3077 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | line_15497_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_15498_21 | ACLineSegment | Line | 0.034884 | 0.0030903 | 0.0030903 | 0.0015608 | 8.8588 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | line_15498_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_15508_21 | ACLineSegment | Line | 0.034884 | 0.0090853 | 0.0090853 | 0.005001 | 26.0446 | 0 | 0 | 0 | 2024-01-20 17:05 | FALSE | 1 | line_15508_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_15484_21 | ACLineSegment | Line | 0.034884 | 0.0098666 | 0.0098666 | 0.0060532 | 28.2843 | 0 | 0 | 0 | 2024-01-17 06:55 | FALSE | 1 | line_15484_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_15485_21 | ACLineSegment | Line | 0.034884 | 0.0035611 | 0.0035611 | 0.0019579 | 10.2086 | 0 | 0 | 0 | 2024-01-17 06:55 | FALSE | 1 | line_15485_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_15486_21 | ACLineSegment | Line | 0.034884 | 0.0072904 | 0.0072904 | 0.0043166 | 20.8992 | 0 | 0 | 0 | 2024-01-17 05:55 | FALSE | 1 | line_15486_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_15489_21 | ACLineSegment | Line | 0.034884 | 0.018426 | 0.018426 | 0.01158 | 52.8215 | 0 | 0 | 0 | 2024-01-20 13:05 | FALSE | 1 | line_15489_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_15495_21 | ACLineSegment | Line | 0.034884 | 0.0099621 | 0.0099621 | 0.0059144 | 28.5583 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | line_15495_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_15487_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_15487_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_15488_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_15488_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_15490_21 | ACLineSegment | Line | 0.034884 | 0.028728 | 0.028728 | 0.018184 | 82.3543 | 0 | 0 | 0 | 2024-07-15 06:00 | FALSE | 1 | line_15490_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_15491_21 | ACLineSegment | Line | 0.034884 | 0.0050828 | 0.0050828 | 0.0028583 | 14.5706 | 0 | 0 | 0 | 2024-01-20 19:55 | FALSE | 1 | line_15491_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_15492_21 | ACLineSegment | Line | 0.034884 | 0.0040189 | 0.0040189 | 0.0022493 | 11.5209 | 0 | 0 | 0 | 2024-01-20 21:15 | FALSE | 1 | line_15492_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_15493_21 | ACLineSegment | Line | 0.034884 | 0.0039374 | 0.0039374 | 0.0020598 | 11.2871 | 0 | 0 | 0 | 2024-01-17 06:55 | FALSE | 1 | line_15493_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_15503_21 | ACLineSegment | Line | 0.034884 | 0.030914 | 0.030914 | 0.020228 | 88.6219 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_15503_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_15494_21 | ACLineSegment | Line | 0.034884 | 0.0080128 | 0.0080128 | 0.0040735 | 22.9701 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | line_15494_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_15496_21 | ACLineSegment | Line | 0.034884 | 0.0031913 | 0.0031913 | 0.0020298 | 9.1483 | 0 | 0 | 0 | 2024-01-17 09:55 | FALSE | 1 | line_15496_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_15499_21 | ACLineSegment | Line | 0.034884 | 0.0080128 | 0.0080128 | 0.0040735 | 22.9701 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | line_15499_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_15505_21 | ACLineSegment | Line | 0.034884 | 0.020582 | 0.020582 | 0.012998 | 59.0023 | 0 | 0 | 0 | 2024-01-20 20:20 | FALSE | 1 | line_15505_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_15506_21 | ACLineSegment | Line | 0.034884 | 0.0054403 | 0.0054403 | 0.0029342 | 15.5958 | 0 | 0 | 0 | 2024-01-20 23:55 | FALSE | 1 | line_15506_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_15502_21 | ACLineSegment | Line | 0.034884 | 0.025316 | 0.025316 | 0.016001 | 72.5734 | 0 | 0 | 0 | 2024-01-22 04:00 | FALSE | 1 | line_15502_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_15504_21 | ACLineSegment | Line | 0.034884 | 0.009024 | 0.009024 | 0.0046377 | 25.869 | 0 | 0 | 0 | 2024-01-17 14:00 | FALSE | 1 | line_15504_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_15507_21 | ACLineSegment | Line | 0.034884 | 0.0055021 | 0.0055021 | 0.0033599 | 15.7728 | 0 | 0 | 0 | 2024-07-05 08:35 | FALSE | 1 | line_15507_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_15585_21 | ACLineSegment | Line | 0.034884 | 0.0087099 | 0.0087099 | 0.0059656 | 24.9687 | 0 | 0 | 0 | 2024-07-14 13:55 | FALSE | 1 | line_15585_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_15586_21 | ACLineSegment | Line | 0.034884 | 0.0037846 | 0.0037846 | 0.0020927 | 10.8493 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_15586_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_15587_21 | ACLineSegment | Line | 0.034884 | 0.0063891 | 0.0063891 | 0.0040684 | 18.3157 | 0 | 0 | 0 | 2024-07-14 13:55 | FALSE | 1 | line_15587_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_15596_21 | ACLineSegment | Line | 0.034884 | 0.012543 | 0.012543 | 0.0086726 | 35.9564 | 0 | 0 | 0 | 2024-06-23 13:55 | FALSE | 1 | line_15596_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_15599_21 | ACLineSegment | Line | 0.034884 | 0.0056505 | 0.0056505 | 0.0030309 | 16.1981 | 0 | 0 | 0 | 2024-01-17 09:55 | FALSE | 1 | line_15599_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_15603_21 | ACLineSegment | Line | 0.034884 | 0.0037846 | 0.0037846 | 0.0020927 | 10.8493 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_15603_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_15606_21 | ACLineSegment | Line | 0.034884 | 0.0043694 | 0.0043694 | 0.002512 | 12.5258 | 0 | 0 | 0 | 2024-07-16 00:30 | FALSE | 1 | line_15606_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_15607_21 | ACLineSegment | Line | 0.034884 | 0.0031704 | 0.0031704 | 0.0017562 | 9.0886 | 0 | 0 | 0 | 2024-01-20 16:00 | FALSE | 1 | line_15607_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_15588_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_15588_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_15589_21 | ACLineSegment | Line | 0.034884 | 0.009291 | 0.009291 | 0.0058177 | 26.6345 | 0 | 0 | 0 | 2024-01-20 06:55 | FALSE | 1 | line_15589_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_15590_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_15590_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_15591_21 | ACLineSegment | Line | 0.034884 | 0.016222 | 0.016222 | 0.0095865 | 46.504 | 0 | 0 | 0 | 2024-01-20 09:00 | FALSE | 1 | line_15591_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_15593_21 | ACLineSegment | Line | 0.034884 | 0.0043466 | 0.0043466 | 0.0024611 | 12.4605 | 0 | 0 | 0 | 2024-01-20 12:00 | FALSE | 1 | line_15593_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_15594_21 | ACLineSegment | Line | 0.034884 | 0.0047551 | 0.0047551 | 0.0026735 | 13.6314 | 0 | 0 | 0 | 2024-01-20 16:00 | FALSE | 1 | line_15594_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_15595_21 | ACLineSegment | Line | 0.034884 | 0.0024159 | 0.0024159 | 0.0012203 | 6.9255 | 0 | 0 | 0 | 2024-01-20 18:50 | FALSE | 1 | line_15595_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_15604_21 | ACLineSegment | Line | 0.034884 | 0.0036938 | 0.0036938 | 0.0021743 | 10.5889 | 0 | 0 | 0 | 2024-01-20 06:55 | FALSE | 1 | line_15604_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_15605_21 | ACLineSegment | Line | 0.034884 | 0.00667 | 0.00667 | 0.003858 | 19.1208 | 0 | 0 | 0 | 2024-01-18 | FALSE | 1 | line_15605_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_15612_21 | ACLineSegment | Line | 0.034884 | 0.010714 | 0.010714 | 0.005887 | 30.7142 | 0 | 0 | 0 | 2024-01-20 09:00 | FALSE | 1 | line_15612_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_15614_21 | ACLineSegment | Line | 0.034884 | 0.0071816 | 0.0071816 | 0.0040161 | 20.5872 | 0 | 0 | 0 | 2024-01-20 23:55 | FALSE | 1 | line_15614_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_15597_21 | ACLineSegment | Line | 0.034884 | 0.018103 | 0.018103 | 0.011912 | 51.8959 | 0 | 0 | 0 | 2024-01-20 19:55 | FALSE | 1 | line_15597_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_15598_21 | ACLineSegment | Line | 0.034884 | 0.0066432 | 0.0066432 | 0.0035157 | 19.044 | 0 | 0 | 0 | 2024-01-21 01:25 | FALSE | 1 | line_15598_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_15600_21 | ACLineSegment | Line | 0.034884 | 0.0068272 | 0.0068272 | 0.0037448 | 19.5714 | 0 | 0 | 0 | 2024-01-20 09:00 | FALSE | 1 | line_15600_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_15601_21 | ACLineSegment | Line | 0.034884 | 0.0068272 | 0.0068272 | 0.0037448 | 19.5714 | 0 | 0 | 0 | 2024-01-20 09:00 | FALSE | 1 | line_15601_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_15613_21 | ACLineSegment | Line | 0.034884 | 0.0042149 | 0.0042149 | 0.0024128 | 12.0829 | 0 | 0 | 0 | 2024-01-20 19:55 | FALSE | 1 | line_15613_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_15609_21 | ACLineSegment | Line | 0.034884 | 0.0036938 | 0.0036938 | 0.0021743 | 10.5889 | 0 | 0 | 0 | 2024-01-20 06:55 | FALSE | 1 | line_15609_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_16381_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_16381_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_16382_21 | ACLineSegment | Line | 0.034884 | 0.0096368 | 0.0096368 | 0.006085 | 27.6256 | 0 | 0 | 0 | 2024-01-20 20:20 | FALSE | 1 | line_16382_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_16383_21 | ACLineSegment | Line | 0.034884 | 0.004856 | 0.004856 | 0.002326 | 13.9207 | 0 | 0 | 0 | 2024-01-20 14:50 | FALSE | 1 | line_16383_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_16384_21 | ACLineSegment | Line | 0.034884 | 0.0040517 | 0.0040517 | 0.0022812 | 11.615 | 0 | 0 | 0 | 2024-01-20 15:45 | FALSE | 1 | line_16384_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_16385_21 | ACLineSegment | Line | 0.034884 | 0.00348 | 0.00348 | 0.0020024 | 9.976 | 0 | 0 | 0 | 2024-01-17 06:55 | FALSE | 1 | line_16385_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_16407_21 | ACLineSegment | Line | 0.034884 | 0.024698 | 0.024698 | 0.015516 | 70.8008 | 0 | 0 | 0 | 2024-01-20 21:15 | FALSE | 1 | line_16407_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_16413_21 | ACLineSegment | Line | 0.034884 | 0.017251 | 0.017251 | 0.0097702 | 49.4525 | 0 | 0 | 0 | 2024-01-20 21:15 | FALSE | 1 | line_16413_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_16388_21 | ACLineSegment | Line | 0.034884 | 0.0313 | 0.0313 | 0.019654 | 89.7264 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | line_16388_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_16389_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_16389_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_16391_21 | ACLineSegment | Line | 0.034884 | 0.0033376 | 0.0033376 | 0.0019178 | 9.568 | 0 | 0 | 0 | 2024-01-20 07:25 | FALSE | 1 | line_16391_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_16392_21 | ACLineSegment | Line | 0.034884 | 0.0058416 | 0.0058416 | 0.0033143 | 16.7459 | 0 | 0 | 0 | 2024-01-22 04:00 | FALSE | 1 | line_16392_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_16403_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_16403_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_16404_21 | ACLineSegment | Line | 0.034884 | 0.022266 | 0.022266 | 0.013339 | 63.8291 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | line_16404_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_16405_21 | ACLineSegment | Line | 0.034884 | 0.0063925 | 0.0063925 | 0.0037802 | 18.3252 | 0 | 0 | 0 | 2024-01-17 16:35 | FALSE | 1 | line_16405_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_16406_21 | ACLineSegment | Line | 0.034884 | 0.0056618 | 0.0056618 | 0.0030133 | 16.2305 | 0 | 0 | 0 | 2024-01-20 11:55 | FALSE | 1 | line_16406_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_16393_21 | ACLineSegment | Line | 0.034884 | 0.0072058 | 0.0072058 | 0.0044715 | 20.6569 | 0 | 0 | 0 | 2024-06-27 03:00 | FALSE | 1 | line_16393_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_16394_21 | ACLineSegment | Line | 0.034884 | 0.01071 | 0.01071 | 0.0063808 | 30.7032 | 0 | 0 | 0 | 2024-01-20 08:55 | FALSE | 1 | line_16394_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_16395_21 | ACLineSegment | Line | 0.034884 | 0.0041548 | 0.0041548 | 0.0020917 | 11.9106 | 0 | 0 | 0 | 2024-01-20 08:55 | FALSE | 1 | line_16395_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_16401_21 | ACLineSegment | Line | 0.034884 | 0.0050153 | 0.0050153 | 0.0030162 | 14.3772 | 0 | 0 | 0 | 2024-06-27 03:00 | FALSE | 1 | line_16401_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_16402_21 | ACLineSegment | Line | 0.034884 | 0.0029267 | 0.0029267 | 0.0016216 | 8.3899 | 0 | 0 | 0 | 2024-01-20 07:25 | FALSE | 1 | line_16402_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_16418_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_16418_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_16420_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_16420_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_16425_21 | ACLineSegment | Line | 0.034884 | 0.0069614 | 0.0069614 | 0.003739 | 19.956 | 0 | 0 | 0 | 2024-01-21 01:25 | FALSE | 1 | line_16425_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_16426_21 | ACLineSegment | Line | 0.034884 | 0.0035209 | 0.0035209 | 0.0015736 | 10.0933 | 0 | 0 | 0 | 2024-01-20 09:00 | FALSE | 1 | line_16426_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_16427_21 | ACLineSegment | Line | 0.034884 | 0.0045427 | 0.0045427 | 0.0022571 | 13.0226 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | line_16427_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_16396_21 | ACLineSegment | Line | 0.034884 | 0.032294 | 0.032294 | 0.022098 | 92.5761 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | line_16396_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_16397_21 | ACLineSegment | Line | 0.034884 | 0.041322 | 0.041322 | 0.027875 | 118.456 | 334 | 27.8333 | 0.31704 | 2024-01-20 11:55 | FALSE | 1 | line_16397_21 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_16398_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_16398_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_16399_21 | ACLineSegment | Line | 0.034884 | 0.011462 | 0.011462 | 0.007272 | 32.8588 | 0 | 0 | 0 | 2024-05-14 18:05 | FALSE | 1 | line_16399_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_16400_21 | ACLineSegment | Line | 0.034884 | 0.00356 | 0.00356 | 0.0018888 | 10.2054 | 0 | 0 | 0 | 2024-01-20 20:20 | FALSE | 1 | line_16400_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_16408_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_16408_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_16409_21 | ACLineSegment | Line | 0.034884 | 0.0075427 | 0.0075427 | 0.0038077 | 21.6225 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | line_16409_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_16410_21 | ACLineSegment | Line | 0.034884 | 0.0060558 | 0.0060558 | 0.0035842 | 17.36 | 0 | 0 | 0 | 2024-06-25 00:55 | FALSE | 1 | line_16410_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_16419_21 | ACLineSegment | Line | 0.034884 | 0.0050153 | 0.0050153 | 0.0030162 | 14.3772 | 0 | 0 | 0 | 2024-06-27 03:00 | FALSE | 1 | line_16419_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_16411_21 | ACLineSegment | Line | 0.034884 | 0.0104 | 0.0104 | 0.0054556 | 29.8126 | 0 | 0 | 0 | 2024-01-21 03:05 | FALSE | 1 | line_16411_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_16412_21 | ACLineSegment | Line | 0.034884 | 0.0104 | 0.0104 | 0.0054556 | 29.8126 | 0 | 0 | 0 | 2024-01-21 03:05 | FALSE | 1 | line_16412_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_16415_21 | ACLineSegment | Line | 0.034884 | 0.0085657 | 0.0085657 | 0.0046291 | 24.5551 | 0 | 0 | 0 | 2024-01-20 21:15 | FALSE | 1 | line_16415_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_16416_21 | ACLineSegment | Line | 0.034884 | 0.0047084 | 0.0047084 | 0.0023253 | 13.4974 | 0 | 0 | 0 | 2024-01-21 03:05 | FALSE | 1 | line_16416_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_16417_21 | ACLineSegment | Line | 0.034884 | 0.005728 | 0.005728 | 0.0033596 | 16.4205 | 0 | 0 | 0 | 2024-01-20 14:50 | FALSE | 1 | line_16417_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_17429_21 | ACLineSegment | Line | 0.22905 | 0.0071769 | 0.0071769 | 0.0053061 | 3.1334 | 0 | 0 | 0 | 2024-01-17 09:55 | FALSE | 1 | line_17429_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | line_17430_21 | ACLineSegment | Line | 0.22905 | 0.0071769 | 0.0071769 | 0.0053061 | 3.1334 | 0 | 0 | 0 | 2024-01-17 09:55 | FALSE | 1 | line_17430_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | line_17431_21 | ACLineSegment | Line | 0.22905 | 0.0062651 | 0.0062651 | 0.0046645 | 2.7353 | 0 | 0 | 0 | 2024-01-20 13:05 | FALSE | 1 | line_17431_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | line_17432_21 | ACLineSegment | Line | 0.22905 | 0.0062651 | 0.0062651 | 0.0046645 | 2.7353 | 0 | 0 | 0 | 2024-01-20 13:05 | FALSE | 1 | line_17432_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | line_17634_21 | ACLineSegment | Line | 0.034884 | 0.030058 | 0.030058 | 0.02083 | 86.1665 | 0 | 0 | 0 | 2024-01-20 18:50 | FALSE | 1 | line_17634_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_17653_21 | ACLineSegment | Line | 0.034884 | 0.027129 | 0.027129 | 0.019079 | 77.7696 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_17653_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_17654_21 | ACLineSegment | Line | 0.034884 | 0.0036825 | 0.0036825 | 0.0019185 | 10.5565 | 0 | 0 | 0 | 2024-01-20 13:05 | FALSE | 1 | line_17654_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_17636_21 | ACLineSegment | Line | 0.034884 | 0.021432 | 0.021432 | 0.012549 | 61.4383 | 0 | 0 | 0 | 2024-01-20 11:55 | FALSE | 1 | line_17636_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_17637_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_17637_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_17639_21 | ACLineSegment | Line | 0.034884 | 0.005705 | 0.005705 | 0.0033431 | 16.3544 | 0 | 0 | 0 | 2024-01-20 20:20 | FALSE | 1 | line_17639_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_17640_21 | ACLineSegment | Line | 0.034884 | 0.0040195 | 0.0040195 | 0.0023351 | 11.5226 | 0 | 0 | 0 | 2024-01-17 08:10 | FALSE | 1 | line_17640_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_17644_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_17644_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_17645_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_17645_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_17646_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_17646_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_17647_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_17647_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_17648_21 | ACLineSegment | Line | 0.034884 | 0.0032116 | 0.0032116 | 0.0017235 | 9.2067 | 0 | 0 | 0 | 2024-01-20 09:00 | FALSE | 1 | line_17648_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_17649_21 | ACLineSegment | Line | 0.034884 | 0.0070796 | 0.0070796 | 0.0035263 | 20.2949 | 0 | 0 | 0 | 2024-01-20 11:55 | FALSE | 1 | line_17649_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_17650_21 | ACLineSegment | Line | 0.034884 | 0.006408 | 0.006408 | 0.0035364 | 18.3697 | 0 | 0 | 0 | 2024-07-15 12:50 | FALSE | 1 | line_17650_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_17651_21 | ACLineSegment | Line | 0.034884 | 0.0035748 | 0.0035748 | 0.0020831 | 10.2477 | 0 | 0 | 0 | 2024-01-20 11:55 | FALSE | 1 | line_17651_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_17652_21 | ACLineSegment | Line | 0.034884 | 0.0052292 | 0.0052292 | 0.0026636 | 14.9904 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_17652_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_17641_21 | ACLineSegment | Line | 0.034884 | 0.011006 | 0.011006 | 0.0067956 | 31.55 | 0 | 0 | 0 | 2024-01-20 18:50 | FALSE | 1 | line_17641_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_17642_21 | ACLineSegment | Line | 0.034884 | 0.0090418 | 0.0090418 | 0.0054218 | 25.9201 | 0 | 0 | 0 | 2024-07-15 21:45 | FALSE | 1 | line_17642_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_17643_21 | ACLineSegment | Line | 0.034884 | 0.002472 | 0.002472 | 0.0014649 | 7.0865 | 0 | 0 | 0 | 2024-01-17 19:55 | FALSE | 1 | line_17643_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_17655_21 | ACLineSegment | Line | 0.034884 | 0.017131 | 0.017131 | 0.010465 | 49.1078 | 0 | 0 | 0 | 2024-01-20 18:50 | FALSE | 1 | line_17655_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_17656_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_17656_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_17657_21 | ACLineSegment | Line | 0.034884 | 0.0035397 | 0.0035397 | 0.001956 | 10.1472 | 0 | 0 | 0 | 2024-01-17 11:00 | FALSE | 1 | line_17657_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_17658_21 | ACLineSegment | Line | 0.034884 | 0.0033962 | 0.0033962 | 0.0020562 | 9.7358 | 0 | 0 | 0 | 2024-01-17 11:00 | FALSE | 1 | line_17658_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_17667_21 | ACLineSegment | Line | 0.034884 | 0.0049435 | 0.0049435 | 0.002683 | 14.1715 | 0 | 0 | 0 | 2024-01-20 18:50 | FALSE | 1 | line_17667_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_17669_21 | ACLineSegment | Line | 0.034884 | 0.0051455 | 0.0051455 | 0.0029188 | 14.7504 | 0 | 0 | 0 | 2024-01-17 21:45 | FALSE | 1 | line_17669_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_17663_21 | ACLineSegment | Line | 0.034884 | 0.025304 | 0.025304 | 0.017346 | 72.5393 | 0 | 0 | 0 | 2024-01-20 21:15 | FALSE | 1 | line_17663_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_17671_21 | ACLineSegment | Line | 0.034884 | 0.003872 | 0.003872 | 0.0018104 | 11.0999 | 0 | 0 | 0 | 2024-01-20 19:55 | FALSE | 1 | line_17671_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_17661_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_17661_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_17662_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_17662_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_17664_21 | ACLineSegment | Line | 0.034884 | 0.003257 | 0.003257 | 0.0017815 | 9.3369 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_17664_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_17665_21 | ACLineSegment | Line | 0.034884 | 0.005334 | 0.005334 | 0.0029817 | 15.291 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | line_17665_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_17666_21 | ACLineSegment | Line | 0.034884 | 0.0053385 | 0.0053385 | 0.002638 | 15.3038 | 0 | 0 | 0 | 2024-01-20 16:00 | FALSE | 1 | line_17666_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_17668_21 | ACLineSegment | Line | 0.034884 | 0.0049435 | 0.0049435 | 0.002683 | 14.1715 | 0 | 0 | 0 | 2024-01-20 18:50 | FALSE | 1 | line_17668_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_17889_21 | ACLineSegment | Line | 0.034884 | 0.0073957 | 0.0073957 | 0.0044606 | 21.2012 | 0 | 0 | 0 | 2024-01-20 21:15 | FALSE | 1 | line_17889_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_17890_21 | ACLineSegment | Line | 0.034884 | 0.0047971 | 0.0047971 | 0.0028717 | 13.7518 | 0 | 0 | 0 | 2024-01-20 21:15 | FALSE | 1 | line_17890_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_17891_21 | ACLineSegment | Line | 0.034884 | 0.0031057 | 0.0031057 | 0.0017753 | 8.903 | 0 | 0 | 0 | 2024-01-20 14:50 | FALSE | 1 | line_17891_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_17892_21 | ACLineSegment | Line | 0.034884 | 0.014276 | 0.014276 | 0.0086026 | 40.9252 | 0 | 0 | 0 | 2024-01-20 21:15 | FALSE | 1 | line_17892_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_17893_21 | ACLineSegment | Line | 0.034884 | 0.0050876 | 0.0050876 | 0.0028864 | 14.5846 | 0 | 0 | 0 | 2024-01-21 03:05 | FALSE | 1 | line_17893_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_17894_21 | ACLineSegment | Line | 0.034884 | 0.0032906 | 0.0032906 | 0.0017236 | 9.4331 | 0 | 0 | 0 | 2024-07-15 10:55 | FALSE | 1 | line_17894_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_17900_21 | ACLineSegment | Line | 0.034884 | 0.0047971 | 0.0047971 | 0.0028717 | 13.7518 | 0 | 0 | 0 | 2024-01-20 21:15 | FALSE | 1 | line_17900_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_17895_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_17895_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_17897_21 | ACLineSegment | Line | 0.034884 | 0.011489 | 0.011489 | 0.0068345 | 32.9342 | 0 | 0 | 0 | 2024-01-20 10:55 | FALSE | 1 | line_17897_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_17903_21 | ACLineSegment | Line | 0.034884 | 0.0042649 | 0.0042649 | 0.0021136 | 12.2262 | 0 | 0 | 0 | 2024-01-20 20:20 | FALSE | 1 | line_17903_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_17904_21 | ACLineSegment | Line | 0.034884 | 0.0055074 | 0.0055074 | 0.0029011 | 15.7879 | 0 | 0 | 0 | 2024-01-20 08:55 | FALSE | 1 | line_17904_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_17905_21 | ACLineSegment | Line | 0.034884 | 0.0039653 | 0.0039653 | 0.0023319 | 11.3672 | 0 | 0 | 0 | 2024-01-20 18:50 | FALSE | 1 | line_17905_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_17896_21 | ACLineSegment | Line | 0.034884 | 0.013761 | 0.013761 | 0.0082823 | 39.4498 | 0 | 0 | 0 | 2024-01-20 10:55 | FALSE | 1 | line_17896_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_17898_21 | ACLineSegment | Line | 0.034884 | 0.0027786 | 0.0027786 | 0.0015835 | 7.9652 | 0 | 0 | 0 | 2024-07-16 01:45 | FALSE | 1 | line_17898_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_17906_21 | ACLineSegment | Line | 0.034884 | 0.0042649 | 0.0042649 | 0.0021136 | 12.2262 | 0 | 0 | 0 | 2024-01-20 20:20 | FALSE | 1 | line_17906_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_24661_21 | ACLineSegment | Line | 0.034884 | 0.0027268 | 0.0027268 | 0.0014658 | 7.8169 | 0 | 0 | 0 | 2024-01-21 01:25 | FALSE | 1 | line_24661_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_24662_21 | ACLineSegment | Line | 0.034884 | 0.0027268 | 0.0027268 | 0.0014658 | 7.8169 | 0 | 0 | 0 | 2024-01-21 01:25 | FALSE | 1 | line_24662_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_24663_21 | ACLineSegment | Line | 0.034884 | 0.006149 | 0.006149 | 0.0037748 | 17.6274 | 0 | 0 | 0 | 2024-01-17 17:55 | FALSE | 1 | line_24663_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_24664_21 | ACLineSegment | Line | 0.034884 | 0.006149 | 0.006149 | 0.0037748 | 17.6274 | 0 | 0 | 0 | 2024-01-17 17:55 | FALSE | 1 | line_24664_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_24864_21 | ACLineSegment | Line | 0.034884 | 0.004919 | 0.004919 | 0.0029238 | 14.1012 | 0 | 0 | 0 | 2024-01-20 15:45 | FALSE | 1 | line_24864_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_24865_21 | ACLineSegment | Line | 0.034884 | 0.0091979 | 0.0091979 | 0.005627 | 26.3676 | 0 | 0 | 0 | 2024-01-20 12:00 | FALSE | 1 | line_24865_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_24866_21 | ACLineSegment | Line | 0.034884 | 0.0059728 | 0.0059728 | 0.0029236 | 17.1222 | 0 | 0 | 0 | 2024-01-20 17:05 | FALSE | 1 | line_24866_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_24867_21 | ACLineSegment | Line | 0.034884 | 0.004919 | 0.004919 | 0.0029238 | 14.1012 | 0 | 0 | 0 | 2024-01-20 15:45 | FALSE | 1 | line_24867_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_24873_21 | ACLineSegment | Line | 0.034884 | 0.017679 | 0.017679 | 0.010432 | 50.6793 | 0 | 0 | 0 | 2024-01-21 03:05 | FALSE | 1 | line_24873_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_24886_21 | ACLineSegment | Line | 0.034884 | 0.0041909 | 0.0041909 | 0.0022829 | 12.0139 | 0 | 0 | 0 | 2024-01-20 06:55 | FALSE | 1 | line_24886_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_24869_21 | ACLineSegment | Line | 0.034884 | 0.017838 | 0.017838 | 0.011861 | 51.1354 | 0 | 0 | 0 | 2024-07-15 06:00 | FALSE | 1 | line_24869_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_24876_21 | ACLineSegment | Line | 0.034884 | 0.014001 | 0.014001 | 0.0088449 | 40.1361 | 0 | 0 | 0 | 2024-07-15 13:05 | FALSE | 1 | line_24876_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_24882_21 | ACLineSegment | Line | 0.034884 | 0.0056797 | 0.0056797 | 0.003295 | 16.282 | 0 | 0 | 0 | 2024-01-21 03:05 | FALSE | 1 | line_24882_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_24872_21 | ACLineSegment | Line | 0.034884 | 0.01574 | 0.01574 | 0.0087208 | 45.1221 | 0 | 0 | 0 | 2024-01-21 03:05 | FALSE | 1 | line_24872_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_24874_21 | ACLineSegment | Line | 0.034884 | 0.0030556 | 0.0030556 | 0.0018712 | 8.7594 | 0 | 0 | 0 | 2024-01-20 16:00 | FALSE | 1 | line_24874_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_24880_21 | ACLineSegment | Line | 0.034884 | 0.01574 | 0.01574 | 0.0087208 | 45.1221 | 0 | 0 | 0 | 2024-01-21 03:05 | FALSE | 1 | line_24880_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_24875_21 | ACLineSegment | Line | 0.034884 | 0.008463 | 0.008463 | 0.0050992 | 24.2607 | 0 | 0 | 0 | 2024-07-15 13:05 | FALSE | 1 | line_24875_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_24877_21 | ACLineSegment | Line | 0.034884 | 0.0067629 | 0.0067629 | 0.0040583 | 19.3871 | 0 | 0 | 0 | 2024-01-20 07:25 | FALSE | 1 | line_24877_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_24878_21 | ACLineSegment | Line | 0.034884 | 0.0054861 | 0.0054861 | 0.003082 | 15.7268 | 0 | 0 | 0 | 2024-01-20 22:50 | FALSE | 1 | line_24878_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_24879_21 | ACLineSegment | Line | 0.034884 | 0.0035309 | 0.0035309 | 0.0022772 | 10.122 | 0 | 0 | 0 | 2024-07-15 05:55 | FALSE | 1 | line_24879_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_24884_21 | ACLineSegment | Line | 0.034884 | 0.0054861 | 0.0054861 | 0.003082 | 15.7268 | 0 | 0 | 0 | 2024-01-20 22:50 | FALSE | 1 | line_24884_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_24881_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_24881_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_24890_21 | ACLineSegment | Line | 0.034884 | 0.0048959 | 0.0048959 | 0.0024829 | 14.035 | 0 | 0 | 0 | 2024-01-21 03:05 | FALSE | 1 | line_24890_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_24891_21 | ACLineSegment | Line | 0.034884 | 0.0046449 | 0.0046449 | 0.0028686 | 13.3156 | 0 | 0 | 0 | 2024-01-20 10:55 | FALSE | 1 | line_24891_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_24892_21 | ACLineSegment | Line | 0.034884 | 0.00773 | 0.00773 | 0.0038176 | 22.1593 | 0 | 0 | 0 | 2024-01-21 03:05 | FALSE | 1 | line_24892_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25042_21 | ACLineSegment | Line | 0.034884 | 0.017971 | 0.017971 | 0.011539 | 51.5171 | 0 | 0 | 0 | 2024-01-20 12:00 | FALSE | 1 | line_25042_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25043_21 | ACLineSegment | Line | 0.034884 | 0.012918 | 0.012918 | 0.0080536 | 37.0313 | 0 | 0 | 0 | 2024-01-21 02:15 | FALSE | 1 | line_25043_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25044_21 | ACLineSegment | Line | 0.034884 | 0.0072734 | 0.0072734 | 0.0038368 | 20.8505 | 0 | 0 | 0 | 2024-01-20 17:05 | FALSE | 1 | line_25044_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25056_21 | ACLineSegment | Line | 0.034884 | 0.026229 | 0.026229 | 0.017598 | 75.1912 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | line_25056_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25063_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_25063_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25064_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_25064_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25065_21 | ACLineSegment | Line | 0.034884 | 0.0046234 | 0.0046234 | 0.0020447 | 13.2539 | 0 | 0 | 0 | 2024-01-20 22:50 | FALSE | 1 | line_25065_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25066_21 | ACLineSegment | Line | 0.034884 | 0.0043631 | 0.0043631 | 0.0021387 | 12.5077 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | line_25066_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25067_21 | ACLineSegment | Line | 0.034884 | 0.0043313 | 0.0043313 | 0.0024189 | 12.4164 | 0 | 0 | 0 | 2024-01-17 20:10 | FALSE | 1 | line_25067_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25069_21 | ACLineSegment | Line | 0.034884 | 0.0099938 | 0.0099938 | 0.0058397 | 28.6491 | 0 | 0 | 0 | 2024-01-21 02:15 | FALSE | 1 | line_25069_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25072_21 | ACLineSegment | Line | 0.034884 | 0.0050842 | 0.0050842 | 0.0025049 | 14.5748 | 0 | 0 | 0 | 2024-01-20 12:00 | FALSE | 1 | line_25072_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25045_21 | ACLineSegment | Line | 0.034884 | 0.003628 | 0.003628 | 0.0019576 | 10.4003 | 0 | 0 | 0 | 2024-07-15 10:55 | FALSE | 1 | line_25045_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25046_21 | ACLineSegment | Line | 0.034884 | 0.003628 | 0.003628 | 0.0019576 | 10.4003 | 0 | 0 | 0 | 2024-07-15 10:55 | FALSE | 1 | line_25046_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25070_21 | ACLineSegment | Line | 0.034884 | 0.0071393 | 0.0071393 | 0.0041157 | 20.4662 | 0 | 0 | 0 | 2024-01-20 05:00 | FALSE | 1 | line_25070_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25047_21 | ACLineSegment | Line | 0.034884 | 0.0034891 | 0.0034891 | 0.0021541 | 10.0023 | 0 | 0 | 0 | 2024-01-20 11:55 | FALSE | 1 | line_25047_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25048_21 | ACLineSegment | Line | 0.034884 | 0.0034891 | 0.0034891 | 0.0021541 | 10.0023 | 0 | 0 | 0 | 2024-01-20 11:55 | FALSE | 1 | line_25048_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25061_21 | ACLineSegment | Line | 0.034884 | 0.0085224 | 0.0085224 | 0.0048463 | 24.431 | 0 | 0 | 0 | 2024-01-20 11:55 | FALSE | 1 | line_25061_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25062_21 | ACLineSegment | Line | 0.034884 | 0.0050749 | 0.0050749 | 0.0028807 | 14.5482 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_25062_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25049_21 | ACLineSegment | Line | 0.034884 | 0.026013 | 0.026013 | 0.016494 | 74.5703 | 0 | 0 | 0 | 2024-01-20 07:25 | FALSE | 1 | line_25049_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25050_21 | ACLineSegment | Line | 0.034884 | 0.02911 | 0.02911 | 0.018546 | 83.4506 | 0 | 0 | 0 | 2024-01-20 07:25 | FALSE | 1 | line_25050_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25051_21 | ACLineSegment | Line | 0.034884 | 0.0043204 | 0.0043204 | 0.0023304 | 12.3853 | 0 | 0 | 0 | 2024-01-17 12:55 | FALSE | 1 | line_25051_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25052_21 | ACLineSegment | Line | 0.034884 | 0.0067921 | 0.0067921 | 0.0037451 | 19.4708 | 0 | 0 | 0 | 2024-01-20 20:20 | FALSE | 1 | line_25052_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25053_21 | ACLineSegment | Line | 0.034884 | 0.018394 | 0.018394 | 0.011568 | 52.7285 | 0 | 0 | 0 | 2024-01-20 07:25 | FALSE | 1 | line_25053_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25054_21 | ACLineSegment | Line | 0.034884 | 0.0036022 | 0.0036022 | 0.0018149 | 10.3262 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | line_25054_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25060_21 | ACLineSegment | Line | 0.034884 | 0.0067921 | 0.0067921 | 0.0037451 | 19.4708 | 0 | 0 | 0 | 2024-01-20 20:20 | FALSE | 1 | line_25060_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25073_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_25073_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25074_21 | ACLineSegment | Line | 0.034884 | 0.0062291 | 0.0062291 | 0.0036252 | 17.8569 | 0 | 0 | 0 | 2024-01-20 16:00 | FALSE | 1 | line_25074_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25075_21 | ACLineSegment | Line | 0.034884 | 0.007128 | 0.007128 | 0.003634 | 20.4336 | 0 | 0 | 0 | 2024-01-20 07:25 | FALSE | 1 | line_25075_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25055_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_25055_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25058_21 | ACLineSegment | Line | 0.034884 | 0.0067326 | 0.0067326 | 0.0035102 | 19.3002 | 0 | 0 | 0 | 2024-06-27 02:00 | FALSE | 1 | line_25058_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25059_21 | ACLineSegment | Line | 0.034884 | 0.0085242 | 0.0085242 | 0.0043556 | 24.4362 | 0 | 0 | 0 | 2024-01-20 23:55 | FALSE | 1 | line_25059_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25120_21 | ACLineSegment | Line | 0.034884 | 0.004167 | 0.004167 | 0.0022519 | 11.9454 | 0 | 0 | 0 | 2024-07-15 21:45 | FALSE | 1 | line_25120_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25121_21 | ACLineSegment | Line | 0.034884 | 0.004167 | 0.004167 | 0.0022519 | 11.9454 | 0 | 0 | 0 | 2024-07-15 21:45 | FALSE | 1 | line_25121_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25122_21 | ACLineSegment | Line | 0.034884 | 0.029455 | 0.029455 | 0.018615 | 84.4387 | 0 | 0 | 0 | 2024-01-20 11:55 | FALSE | 1 | line_25122_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25123_21 | ACLineSegment | Line | 0.034884 | 0.021047 | 0.021047 | 0.013962 | 60.3338 | 0 | 0 | 0 | 2024-01-21 02:15 | FALSE | 1 | line_25123_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25124_21 | ACLineSegment | Line | 0.034884 | 0.004957 | 0.004957 | 0.0026458 | 14.2103 | 0 | 0 | 0 | 2024-01-20 11:55 | FALSE | 1 | line_25124_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25132_21 | ACLineSegment | Line | 0.034884 | 0.021047 | 0.021047 | 0.013962 | 60.3338 | 0 | 0 | 0 | 2024-01-21 02:15 | FALSE | 1 | line_25132_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25125_21 | ACLineSegment | Line | 0.034884 | 0.0048196 | 0.0048196 | 0.002251 | 13.8164 | 0 | 0 | 0 | 2024-01-20 15:45 | FALSE | 1 | line_25125_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25126_21 | ACLineSegment | Line | 0.034884 | 0.0048196 | 0.0048196 | 0.002251 | 13.8164 | 0 | 0 | 0 | 2024-01-20 15:45 | FALSE | 1 | line_25126_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25143_21 | ACLineSegment | Line | 0.034884 | 0.0072941 | 0.0072941 | 0.0042178 | 20.91 | 0 | 0 | 0 | 2024-01-20 15:45 | FALSE | 1 | line_25143_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25150_21 | ACLineSegment | Line | 0.034884 | 0.0035612 | 0.0035612 | 0.0021255 | 10.2089 | 0 | 0 | 0 | 2024-01-17 15:40 | FALSE | 1 | line_25150_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25127_21 | ACLineSegment | Line | 0.034884 | 0.0034978 | 0.0034978 | 0.0018741 | 10.027 | 0 | 0 | 0 | 2024-01-20 13:05 | FALSE | 1 | line_25127_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25128_21 | ACLineSegment | Line | 0.034884 | 0.0034978 | 0.0034978 | 0.0018741 | 10.027 | 0 | 0 | 0 | 2024-01-20 13:05 | FALSE | 1 | line_25128_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25129_21 | ACLineSegment | Line | 0.034884 | 0.0077438 | 0.0077438 | 0.0046422 | 22.199 | 0 | 0 | 0 | 2024-01-20 13:05 | FALSE | 1 | line_25129_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25130_21 | ACLineSegment | Line | 0.034884 | 0.0047846 | 0.0047846 | 0.0029264 | 13.716 | 0 | 0 | 0 | 2024-07-05 21:50 | FALSE | 1 | line_25130_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25136_21 | ACLineSegment | Line | 0.034884 | 0.0077438 | 0.0077438 | 0.0046422 | 22.199 | 0 | 0 | 0 | 2024-01-20 13:05 | FALSE | 1 | line_25136_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25131_21 | ACLineSegment | Line | 0.034884 | 0.014709 | 0.014709 | 0.0089335 | 42.1657 | 0 | 0 | 0 | 2024-01-20 13:05 | FALSE | 1 | line_25131_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25133_21 | ACLineSegment | Line | 0.034884 | 0.0065927 | 0.0065927 | 0.0035983 | 18.8993 | 0 | 0 | 0 | 2024-01-20 22:50 | FALSE | 1 | line_25133_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25134_21 | ACLineSegment | Line | 0.034884 | 0.003206 | 0.003206 | 0.0018366 | 9.1905 | 0 | 0 | 0 | 2024-01-21 02:15 | FALSE | 1 | line_25134_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25137_21 | ACLineSegment | Line | 0.034884 | 0.0030757 | 0.0030757 | 0.0016446 | 8.8171 | 0 | 0 | 0 | 2024-01-20 11:55 | FALSE | 1 | line_25137_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25138_21 | ACLineSegment | Line | 0.034884 | 0.0061648 | 0.0061648 | 0.0029921 | 17.6725 | 0 | 0 | 0 | 2024-01-20 18:50 | FALSE | 1 | line_25138_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25139_21 | ACLineSegment | Line | 0.034884 | 0.022735 | 0.022735 | 0.013854 | 65.1747 | 0 | 0 | 0 | 2024-01-20 15:45 | FALSE | 1 | line_25139_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25142_21 | ACLineSegment | Line | 0.034884 | 0.0092615 | 0.0092615 | 0.0058468 | 26.5499 | 0 | 0 | 0 | 2024-01-20 15:45 | FALSE | 1 | line_25142_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25145_21 | ACLineSegment | Line | 0.034884 | 0.0067837 | 0.0067837 | 0.0039414 | 19.4466 | 0 | 0 | 0 | 2024-01-20 19:55 | FALSE | 1 | line_25145_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25146_21 | ACLineSegment | Line | 0.034884 | 0.0033198 | 0.0033198 | 0.0019638 | 9.5169 | 0 | 0 | 0 | 2024-07-15 20:35 | FALSE | 1 | line_25146_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25147_21 | ACLineSegment | Line | 0.034884 | 0.0052026 | 0.0052026 | 0.0027634 | 14.9141 | 0 | 0 | 0 | 2024-01-20 15:45 | FALSE | 1 | line_25147_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25144_21 | ACLineSegment | Line | 0.034884 | 0.0035524 | 0.0035524 | 0.0017962 | 10.1836 | 0 | 0 | 0 | 2024-01-17 16:35 | FALSE | 1 | line_25144_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25148_21 | ACLineSegment | Line | 0.034884 | 0.0041814 | 0.0041814 | 0.0021158 | 11.9867 | 0 | 0 | 0 | 2024-01-20 20:20 | FALSE | 1 | line_25148_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25151_21 | ACLineSegment | Line | 0.034884 | 0.0038513 | 0.0038513 | 0.0021386 | 11.0406 | 0 | 0 | 0 | 2024-01-17 15:40 | FALSE | 1 | line_25151_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25149_21 | ACLineSegment | Line | 0.034884 | 0.0041814 | 0.0041814 | 0.0021158 | 11.9867 | 0 | 0 | 0 | 2024-01-20 20:20 | FALSE | 1 | line_25149_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25818_21 | ACLineSegment | Line | 0.034884 | 0.015014 | 0.015014 | 0.0095491 | 43.0396 | 0 | 0 | 0 | 2024-01-20 08:55 | FALSE | 1 | line_25818_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25819_21 | ACLineSegment | Line | 0.034884 | 0.015966 | 0.015966 | 0.010789 | 45.7684 | 0 | 0 | 0 | 2024-01-20 08:55 | FALSE | 1 | line_25819_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25820_21 | ACLineSegment | Line | 0.034884 | 0.0023775 | 0.0023775 | 0.0013961 | 6.8155 | 0 | 0 | 0 | 2024-07-14 13:55 | FALSE | 1 | line_25820_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25821_21 | ACLineSegment | Line | 0.034884 | 0.011365 | 0.011365 | 0.00722 | 32.5797 | 0 | 0 | 0 | 2024-01-20 05:00 | FALSE | 1 | line_25821_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25822_21 | ACLineSegment | Line | 0.034884 | 0.0045861 | 0.0045861 | 0.002494 | 13.147 | 0 | 0 | 0 | 2024-01-20 23:55 | FALSE | 1 | line_25822_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25849_21 | ACLineSegment | Line | 0.034884 | 0.006522 | 0.006522 | 0.0036846 | 18.6966 | 0 | 0 | 0 | 2024-01-20 08:55 | FALSE | 1 | line_25849_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25854_21 | ACLineSegment | Line | 0.034884 | 0.022488 | 0.022488 | 0.014342 | 64.465 | 0 | 0 | 0 | 2024-01-20 08:55 | FALSE | 1 | line_25854_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25836_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_25836_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25837_21 | ACLineSegment | Line | 0.034884 | 0.0039253 | 0.0039253 | 0.0022496 | 11.2525 | 0 | 0 | 0 | 2024-01-20 18:50 | FALSE | 1 | line_25837_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25838_21 | ACLineSegment | Line | 0.034884 | 0.0055946 | 0.0055946 | 0.0030812 | 16.0379 | 0 | 0 | 0 | 2024-01-17 07:00 | FALSE | 1 | line_25838_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25839_21 | ACLineSegment | Line | 0.034884 | 0.00456 | 0.00456 | 0.0024421 | 13.0722 | 0 | 0 | 0 | 2024-01-20 06:55 | FALSE | 1 | line_25839_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25859_21 | ACLineSegment | Line | 0.034884 | 0.0045861 | 0.0045861 | 0.002494 | 13.147 | 0 | 0 | 0 | 2024-01-20 23:55 | FALSE | 1 | line_25859_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25823_21 | ACLineSegment | Line | 0.034884 | 0.01454 | 0.01454 | 0.0090829 | 41.682 | 0 | 0 | 0 | 2024-01-17 17:55 | FALSE | 1 | line_25823_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25824_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_25824_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25825_21 | ACLineSegment | Line | 0.034884 | 0.0084804 | 0.0084804 | 0.0052691 | 24.3106 | 0 | 0 | 0 | 2024-01-17 17:55 | FALSE | 1 | line_25825_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25826_21 | ACLineSegment | Line | 0.034884 | 0.0050021 | 0.0050021 | 0.0027707 | 14.3395 | 0 | 0 | 0 | 2024-07-16 00:30 | FALSE | 1 | line_25826_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25827_21 | ACLineSegment | Line | 0.034884 | 0.0023756 | 0.0023756 | 0.0013288 | 6.8102 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_25827_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25833_21 | ACLineSegment | Line | 0.034884 | 0.02024 | 0.02024 | 0.012606 | 58.0204 | 0 | 0 | 0 | 2024-01-20 11:55 | FALSE | 1 | line_25833_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25834_21 | ACLineSegment | Line | 0.034884 | 0.0068785 | 0.0068785 | 0.0037529 | 19.7185 | 0 | 0 | 0 | 2024-01-20 14:50 | FALSE | 1 | line_25834_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25852_21 | ACLineSegment | Line | 0.034884 | 0.0047086 | 0.0047086 | 0.0029476 | 13.4982 | 0 | 0 | 0 | 2024-07-15 20:35 | FALSE | 1 | line_25852_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25860_21 | ACLineSegment | Line | 0.034884 | 0.004399 | 0.004399 | 0.0024373 | 12.6105 | 0 | 0 | 0 | 2024-01-17 17:55 | FALSE | 1 | line_25860_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25828_21 | ACLineSegment | Line | 0.034884 | 0.03586 | 0.03586 | 0.022969 | 102.8001 | 12 | 1 | 0.011391 | 2024-01-20 11:55 | FALSE | 1 | line_25828_21 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_25829_21 | ACLineSegment | Line | 0.034884 | 0.026939 | 0.026939 | 0.017272 | 77.2258 | 0 | 0 | 0 | 2024-01-20 11:55 | FALSE | 1 | line_25829_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25830_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_25830_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25831_21 | ACLineSegment | Line | 0.034884 | 0.0057446 | 0.0057446 | 0.0027967 | 16.468 | 0 | 0 | 0 | 2024-01-21 02:15 | FALSE | 1 | line_25831_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25832_21 | ACLineSegment | Line | 0.034884 | 0.0059129 | 0.0059129 | 0.00347 | 16.9504 | 0 | 0 | 0 | 2024-07-15 06:00 | FALSE | 1 | line_25832_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25846_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_25846_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25847_21 | ACLineSegment | Line | 0.034884 | 0.0051563 | 0.0051563 | 0.0030901 | 14.7814 | 0 | 0 | 0 | 2024-01-18 | FALSE | 1 | line_25847_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25848_21 | ACLineSegment | Line | 0.034884 | 0.0037037 | 0.0037037 | 0.0019082 | 10.6173 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_25848_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25850_21 | ACLineSegment | Line | 0.034884 | 0.0031114 | 0.0031114 | 0.0018354 | 8.9195 | 0 | 0 | 0 | 2024-07-15 22:50 | FALSE | 1 | line_25850_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25851_21 | ACLineSegment | Line | 0.034884 | 0.0036779 | 0.0036779 | 0.001979 | 10.5433 | 0 | 0 | 0 | 2024-01-20 08:55 | FALSE | 1 | line_25851_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25853_21 | ACLineSegment | Line | 0.034884 | 0.0047086 | 0.0047086 | 0.0029476 | 13.4982 | 0 | 0 | 0 | 2024-07-15 20:35 | FALSE | 1 | line_25853_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25855_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_25855_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25857_21 | ACLineSegment | Line | 0.034884 | 0.0071204 | 0.0071204 | 0.0036571 | 20.412 | 0 | 0 | 0 | 2024-01-20 13:05 | FALSE | 1 | line_25857_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_25858_21 | ACLineSegment | Line | 0.034884 | 0.0043946 | 0.0043946 | 0.0023223 | 12.598 | 0 | 0 | 0 | 2024-07-15 16:45 | FALSE | 1 | line_25858_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_45221_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_45221_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_45231_21 | ACLineSegment | Line | 0.034884 | 0.025045 | 0.025045 | 0.015501 | 71.7967 | 0 | 0 | 0 | 2024-01-20 11:55 | FALSE | 1 | line_45231_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_45232_21 | ACLineSegment | Line | 0.034884 | 0.013219 | 0.013219 | 0.0087936 | 37.895 | 0 | 0 | 0 | 2024-01-20 15:45 | FALSE | 1 | line_45232_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_45233_21 | ACLineSegment | Line | 0.034884 | 0.0090307 | 0.0090307 | 0.0044469 | 25.8882 | 0 | 0 | 0 | 2024-01-20 21:15 | FALSE | 1 | line_45233_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_45234_21 | ACLineSegment | Line | 0.034884 | 0.0053156 | 0.0053156 | 0.0028118 | 15.2381 | 0 | 0 | 0 | 2024-01-17 09:55 | FALSE | 1 | line_45234_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_45222_21 | ACLineSegment | Line | 0.034884 | 0.0079004 | 0.0079004 | 0.0043684 | 22.648 | 0 | 0 | 0 | 2024-07-15 13:05 | FALSE | 1 | line_45222_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_45223_21 | ACLineSegment | Line | 0.034884 | 0.0044293 | 0.0044293 | 0.0023058 | 12.6974 | 0 | 0 | 0 | 2024-07-15 13:05 | FALSE | 1 | line_45223_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_45224_21 | ACLineSegment | Line | 0.034884 | 0.0048485 | 0.0048485 | 0.0024243 | 13.899 | 0 | 0 | 0 | 2024-01-20 11:55 | FALSE | 1 | line_45224_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_45235_21 | ACLineSegment | Line | 0.034884 | 0.0079004 | 0.0079004 | 0.0043684 | 22.648 | 0 | 0 | 0 | 2024-07-15 13:05 | FALSE | 1 | line_45235_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_45225_21 | ACLineSegment | Line | 0.046073 | 0.066782 | 0.066782 | 0.044115 | 144.9488 | 3415 | 284.5833 | 3.2416 | 2024-01-20 15:45 | FALSE | 1 | line_45225_21 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_45226_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_45226_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_45227_21 | ACLineSegment | Line | 0.046073 | 0.079363 | 0.079363 | 0.050983 | 172.2569 | 9264 | 772 | 8.7937 | 2024-01-20 15:45 | FALSE | 1 | line_45227_21 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_45228_21 | ACLineSegment | Line | 0.034884 | 0.0065707 | 0.0065707 | 0.0034545 | 18.8362 | 0 | 0 | 0 | 2024-01-20 15:45 | FALSE | 1 | line_45228_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_45229_21 | ACLineSegment | Line | 0.034884 | 0.0047927 | 0.0047927 | 0.0026202 | 13.7393 | 0 | 0 | 0 | 2024-01-20 15:45 | FALSE | 1 | line_45229_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_45230_21 | ACLineSegment | Line | 0.034884 | 0.0021865 | 0.0021865 | 0.001293 | 6.2679 | 0 | 0 | 0 | 2024-07-15 05:55 | FALSE | 1 | line_45230_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_45240_21 | ACLineSegment | Line | 0.034884 | 0.039657 | 0.039657 | 0.025168 | 113.6849 | 97 | 8.0833 | 0.092076 | 2024-01-20 15:45 | FALSE | 1 | line_45240_21 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_45258_21 | ACLineSegment | Line | 0.034884 | 0.029908 | 0.029908 | 0.018997 | 85.7358 | 0 | 0 | 0 | 2024-01-20 20:20 | FALSE | 1 | line_45258_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_45242_21 | ACLineSegment | Line | 0.034884 | 0.03052 | 0.03052 | 0.019213 | 87.4909 | 0 | 0 | 0 | 2024-01-20 12:00 | FALSE | 1 | line_45242_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_45243_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_45243_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_45244_21 | ACLineSegment | Line | 0.034884 | 0.0039032 | 0.0039032 | 0.0021497 | 11.1893 | 0 | 0 | 0 | 2024-07-15 21:45 | FALSE | 1 | line_45244_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_45245_21 | ACLineSegment | Line | 0.034884 | 0.0033254 | 0.0033254 | 0.0019967 | 9.5328 | 0 | 0 | 0 | 2024-07-16 00:30 | FALSE | 1 | line_45245_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_45236_21 | ACLineSegment | Line | 0.034884 | 0.013219 | 0.013219 | 0.0087936 | 37.895 | 0 | 0 | 0 | 2024-01-20 15:45 | FALSE | 1 | line_45236_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_45237_21 | ACLineSegment | Line | 0.034884 | 0.0038765 | 0.0038765 | 0.002011 | 11.1126 | 0 | 0 | 0 | 2024-01-20 09:00 | FALSE | 1 | line_45237_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_45238_21 | ACLineSegment | Line | 0.034884 | 0.0052695 | 0.0052695 | 0.0027907 | 15.1059 | 0 | 0 | 0 | 2024-01-21 02:15 | FALSE | 1 | line_45238_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_45239_21 | ACLineSegment | Line | 0.034884 | 0.036541 | 0.036541 | 0.022901 | 104.7518 | 18 | 1.5 | 0.017086 | 2024-01-20 15:45 | FALSE | 1 | line_45239_21 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_45241_21 | ACLineSegment | Line | 0.034884 | 0.0041934 | 0.0041934 | 0.0023707 | 12.0211 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | line_45241_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_45257_21 | ACLineSegment | Line | 0.034884 | 0.0087001 | 0.0087001 | 0.0043763 | 24.9405 | 0 | 0 | 0 | 2024-01-21 01:25 | FALSE | 1 | line_45257_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_45246_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_45246_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_45247_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_45247_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_45248_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_45248_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_45249_21 | ACLineSegment | Line | 0.034884 | 0.023443 | 0.023443 | 0.01489 | 67.203 | 0 | 0 | 0 | 2024-01-20 07:25 | FALSE | 1 | line_45249_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_45250_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_45250_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_45251_21 | ACLineSegment | Line | 0.034884 | 0.0041127 | 0.0041127 | 0.002454 | 11.7898 | 0 | 0 | 0 | 2024-07-15 05:55 | FALSE | 1 | line_45251_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_45252_21 | ACLineSegment | Line | 0.034884 | 0.0032927 | 0.0032927 | 0.0019722 | 9.4391 | 0 | 0 | 0 | 2024-01-20 22:50 | FALSE | 1 | line_45252_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_45253_21 | ACLineSegment | Line | 0.034884 | 0.0082982 | 0.0082982 | 0.0043472 | 23.7884 | 0 | 0 | 0 | 2024-01-20 07:25 | FALSE | 1 | line_45253_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_45254_21 | ACLineSegment | Line | 0.034884 | 0.0061593 | 0.0061593 | 0.0032524 | 17.6567 | 0 | 0 | 0 | 2024-01-20 20:20 | FALSE | 1 | line_45254_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_45255_21 | ACLineSegment | Line | 0.034884 | 0.0030895 | 0.0030895 | 0.0017949 | 8.8567 | 0 | 0 | 0 | 2024-01-20 13:05 | FALSE | 1 | line_45255_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_45256_21 | ACLineSegment | Line | 0.034884 | 0.0038785 | 0.0038785 | 0.0021554 | 11.1183 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_45256_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_45259_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_45259_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_45260_21 | ACLineSegment | Line | 0.034884 | 0.0037793 | 0.0037793 | 0.0021344 | 10.8341 | 0 | 0 | 0 | 2024-01-20 20:20 | FALSE | 1 | line_45260_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_45261_21 | ACLineSegment | Line | 0.034884 | 0.003562 | 0.003562 | 0.0022163 | 10.2111 | 0 | 0 | 0 | 2024-01-20 22:50 | FALSE | 1 | line_45261_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_45267_21 | ACLineSegment | Line | 0.034884 | 0.0041127 | 0.0041127 | 0.002454 | 11.7898 | 0 | 0 | 0 | 2024-07-15 05:55 | FALSE | 1 | line_45267_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_45289_21 | ACLineSegment | Line | 0.034884 | 0.0067895 | 0.0067895 | 0.0049455 | 19.4634 | 0 | 0 | 0 | 2024-01-21 23:50 | FALSE | 1 | line_45289_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_45290_21 | ACLineSegment | Line | 0.034884 | 0.0067895 | 0.0067895 | 0.0049455 | 19.4634 | 0 | 0 | 0 | 2024-01-21 23:50 | FALSE | 1 | line_45290_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_45310_21 | ACLineSegment | Line | 0.51338 | 0.11009 | 0.11009 | 0.057817 | 21.4436 | 0 | 0 | 0 | 2024-10-03 02:00 | FALSE | 1 | line_45310_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | line_45311_21 | ACLineSegment | Line | 0.51338 | 0.11009 | 0.11009 | 0.057817 | 21.4436 | 0 | 0 | 0 | 2024-10-03 02:00 | FALSE | 1 | line_45311_21 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance
GSO_18 | line_53930_21 | ACLineSegment | Line | 0.034884 | 0.004939 | 0.004939 | 0.0025238 | 14.1585 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_53930_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_53931_21 | ACLineSegment | Line | 0.034884 | 0.004939 | 0.004939 | 0.0025238 | 14.1585 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_53931_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_53933_21 | ACLineSegment | Line | 0.034884 | 0.0062823 | 0.0062823 | 0.0036876 | 18.0093 | 0 | 0 | 0 | 2024-01-20 09:00 | FALSE | 1 | line_53933_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_53934_21 | ACLineSegment | Line | 0.034884 | 0.0039658 | 0.0039658 | 0.0023418 | 11.3687 | 0 | 0 | 0 | 2024-01-20 13:05 | FALSE | 1 | line_53934_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_53935_21 | ACLineSegment | Line | 0.034884 | 0.0039658 | 0.0039658 | 0.0023418 | 11.3687 | 0 | 0 | 0 | 2024-01-20 13:05 | FALSE | 1 | line_53935_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_53939_21 | ACLineSegment | Line | 0.034884 | 0.0052176 | 0.0052176 | 0.0028853 | 14.9573 | 0 | 0 | 0 | 2024-01-20 08:55 | FALSE | 1 | line_53939_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_55339_21 | ACLineSegment | Line | 0.034884 | 0.0033431 | 0.0033431 | 0.0019958 | 9.5837 | 0 | 0 | 0 | 2024-01-20 09:00 | FALSE | 1 | line_55339_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_55340_21 | ACLineSegment | Line | 0.034884 | 0.0033431 | 0.0033431 | 0.0019958 | 9.5837 | 0 | 0 | 0 | 2024-01-20 09:00 | FALSE | 1 | line_55340_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_55341_21 | ACLineSegment | Line | 0.034884 | 0.012203 | 0.012203 | 0.0066785 | 34.9817 | 0 | 0 | 0 | 2024-01-18 01:55 | FALSE | 1 | line_55341_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_55345_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_55345_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_55346_21 | ACLineSegment | Line | 0.034884 | 0.0060236 | 0.0060236 | 0.0033447 | 17.2677 | 0 | 0 | 0 | 2024-01-18 01:55 | FALSE | 1 | line_55346_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_55347_21 | ACLineSegment | Line | 0.034884 | 0.0062921 | 0.0062921 | 0.003552 | 18.0375 | 0 | 0 | 0 | 2024-07-16 01:45 | FALSE | 1 | line_55347_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_55488_21 | ACLineSegment | Line | 0.034884 | 0.048271 | 0.048271 | 0.030517 | 138.3767 | 1526 | 127.1667 | 1.4485 | 2024-01-20 11:55 | FALSE | 1 | line_55488_21 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_55489_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_55489_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_55490_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_55490_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_55491_21 | ACLineSegment | Line | 0.034884 | 0.030344 | 0.030344 | 0.018895 | 86.9853 | 0 | 0 | 0 | 2024-01-21 03:05 | FALSE | 1 | line_55491_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_55492_21 | ACLineSegment | Line | 0.034884 | 0.0028133 | 0.0028133 | 0.0015951 | 8.065 | 0 | 0 | 0 | 2024-01-20 20:20 | FALSE | 1 | line_55492_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_55493_21 | ACLineSegment | Line | 0.034884 | 0.0060543 | 0.0060543 | 0.0034726 | 17.3558 | 0 | 0 | 0 | 2024-01-20 11:55 | FALSE | 1 | line_55493_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_55494_21 | ACLineSegment | Line | 0.034884 | 0.0083167 | 0.0083167 | 0.0043538 | 23.8414 | 0 | 0 | 0 | 2024-01-20 11:55 | FALSE | 1 | line_55494_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_55495_21 | ACLineSegment | Line | 0.034884 | 0.0056775 | 0.0056775 | 0.0031303 | 16.2756 | 0 | 0 | 0 | 2024-01-20 10:55 | FALSE | 1 | line_55495_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_55513_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_55513_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_55514_21 | ACLineSegment | Line | 0.034884 | 0.012198 | 0.012198 | 0.0071839 | 34.9681 | 0 | 0 | 0 | 2024-01-21 03:05 | FALSE | 1 | line_55514_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_55515_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_55515_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_55516_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_55516_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_55517_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_55517_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_55518_21 | ACLineSegment | Line | 0.034884 | 0.0036283 | 0.0036283 | 0.0020653 | 10.4013 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | line_55518_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_55519_21 | ACLineSegment | Line | 0.034884 | 0.0053034 | 0.0053034 | 0.003092 | 15.2033 | 0 | 0 | 0 | 2024-01-20 18:50 | FALSE | 1 | line_55519_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_55520_21 | ACLineSegment | Line | 0.034884 | 0.0062297 | 0.0062297 | 0.0033247 | 17.8586 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | line_55520_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_55521_21 | ACLineSegment | Line | 0.034884 | 0.0034161 | 0.0034161 | 0.0019453 | 9.7927 | 0 | 0 | 0 | 2024-07-16 01:45 | FALSE | 1 | line_55521_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_55522_21 | ACLineSegment | Line | 0.034884 | 0.0048114 | 0.0048114 | 0.0025573 | 13.7928 | 0 | 0 | 0 | 2024-01-20 07:25 | FALSE | 1 | line_55522_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_55497_21 | ACLineSegment | Line | 0.034884 | 0.011153 | 0.011153 | 0.0059762 | 31.9728 | 0 | 0 | 0 | 2024-01-20 19:55 | FALSE | 1 | line_55497_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_55498_21 | ACLineSegment | Line | 0.034884 | 0.018485 | 0.018485 | 0.010418 | 52.9905 | 0 | 0 | 0 | 2024-01-20 19:55 | FALSE | 1 | line_55498_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_55499_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_55499_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_55500_21 | ACLineSegment | Line | 0.034884 | 0.0039563 | 0.0039563 | 0.0022032 | 11.3415 | 0 | 0 | 0 | 2024-01-17 06:55 | FALSE | 1 | line_55500_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_55501_21 | ACLineSegment | Line | 0.034884 | 0.0055743 | 0.0055743 | 0.0027277 | 15.9799 | 0 | 0 | 0 | 2024-01-20 16:00 | FALSE | 1 | line_55501_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_55502_21 | ACLineSegment | Line | 0.034884 | 0.011153 | 0.011153 | 0.0059762 | 31.9728 | 0 | 0 | 0 | 2024-01-20 19:55 | FALSE | 1 | line_55502_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_55506_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_55506_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_55509_21 | ACLineSegment | Line | 0.034884 | 0.029565 | 0.029565 | 0.018328 | 84.753 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_55509_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_55510_21 | ACLineSegment | Line | 0.034884 | 0.0042239 | 0.0042239 | 0.0024505 | 12.1086 | 0 | 0 | 0 | 2024-01-20 08:55 | FALSE | 1 | line_55510_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_55511_21 | ACLineSegment | Line | 0.034884 | 0.0031149 | 0.0031149 | 0.0017058 | 8.9295 | 0 | 0 | 0 | 2024-01-20 12:00 | FALSE | 1 | line_55511_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_55512_21 | ACLineSegment | Line | 0.034884 | 0.0084449 | 0.0084449 | 0.0044341 | 24.2089 | 0 | 0 | 0 | 2024-01-20 23:55 | FALSE | 1 | line_55512_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_55504_21 | ACLineSegment | Line | 0.034884 | 0.0072412 | 0.0072412 | 0.0029455 | 20.7583 | 0 | 0 | 0 | 2024-01-20 19:55 | FALSE | 1 | line_55504_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_55505_21 | ACLineSegment | Line | 0.034884 | 0.0053672 | 0.0053672 | 0.0031972 | 15.3861 | 0 | 0 | 0 | 2024-01-20 08:55 | FALSE | 1 | line_55505_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_55524_21 | ACLineSegment | Line | 0.034884 | 0.012198 | 0.012198 | 0.0071839 | 34.9681 | 0 | 0 | 0 | 2024-01-21 03:05 | FALSE | 1 | line_55524_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_55525_21 | ACLineSegment | Line | 0.034884 | 0.012198 | 0.012198 | 0.0071839 | 34.9681 | 0 | 0 | 0 | 2024-01-21 03:05 | FALSE | 1 | line_55525_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_55526_21 | ACLineSegment | Line | 0.034884 | 0.0041054 | 0.0041054 | 0.0021317 | 11.7689 | 0 | 0 | 0 | 2024-01-21 01:25 | FALSE | 1 | line_55526_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_55527_21 | ACLineSegment | Line | 0.034884 | 0.0068624 | 0.0068624 | 0.0037452 | 19.6723 | 0 | 0 | 0 | 2024-01-20 11:55 | FALSE | 1 | line_55527_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_55528_21 | ACLineSegment | Line | 0.034884 | 0.0032341 | 0.0032341 | 0.0018373 | 9.2713 | 0 | 0 | 0 | 2024-01-20 15:45 | FALSE | 1 | line_55528_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_65974_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_65974_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_65975_21 | ACLineSegment | Line | 0.034884 | 0.0066732 | 0.0066732 | 0.0039782 | 19.13 | 0 | 0 | 0 | 2024-01-20 17:05 | FALSE | 1 | line_65975_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_65977_21 | ACLineSegment | Line | 0.034884 | 0.0059612 | 0.0059612 | 0.0032531 | 17.0889 | 0 | 0 | 0 | 2024-01-20 06:55 | FALSE | 1 | line_65977_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_65978_21 | ACLineSegment | Line | 0.034884 | 0.0067694 | 0.0067694 | 0.0034504 | 19.4057 | 0 | 0 | 0 | 2024-06-26 22:45 | FALSE | 1 | line_65978_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_65988_21 | ACLineSegment | Line | 0.034884 | 0.0066732 | 0.0066732 | 0.0039782 | 19.13 | 0 | 0 | 0 | 2024-01-20 17:05 | FALSE | 1 | line_65988_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_65979_21 | ACLineSegment | Line | 0.034884 | 0.0082545 | 0.0082545 | 0.0044819 | 23.6629 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | line_65979_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_65980_21 | ACLineSegment | Line | 0.034884 | 0.0082545 | 0.0082545 | 0.0044819 | 23.6629 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | line_65980_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_65981_21 | ACLineSegment | Line | 0.034884 | 0.014682 | 0.014682 | 0.0067865 | 42.0886 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | line_65981_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_65984_21 | ACLineSegment | Line | 0.034884 | 0.0064275 | 0.0064275 | 0.0026363 | 18.4257 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | line_65984_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_65982_21 | ACLineSegment | Line | 0.034884 | 0.0059676 | 0.0059676 | 0.0037683 | 17.1073 | 0 | 0 | 0 | 2024-07-05 10:15 | FALSE | 1 | line_65982_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_65989_21 | ACLineSegment | Line | 0.034884 | 0.0030857 | 0.0030857 | 0.0017571 | 8.8457 | 0 | 0 | 0 | 2024-01-17 15:40 | FALSE | 1 | line_65989_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_65990_21 | ACLineSegment | Line | 0.034884 | 0.0039927 | 0.0039927 | 0.0022192 | 11.4458 | 0 | 0 | 0 | 2024-07-05 10:15 | FALSE | 1 | line_65990_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_66567_21 | ACLineSegment | Line | 0.034884 | 0.0069471 | 0.0069471 | 0.0040102 | 19.9152 | 0 | 0 | 0 | 2024-01-20 09:00 | FALSE | 1 | line_66567_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_66568_21 | ACLineSegment | Line | 0.034884 | 0.0069471 | 0.0069471 | 0.0040102 | 19.9152 | 0 | 0 | 0 | 2024-01-20 09:00 | FALSE | 1 | line_66568_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_66569_21 | ACLineSegment | Line | 0.034884 | 0.0034628 | 0.0034628 | 0.0018942 | 9.9268 | 0 | 0 | 0 | 2024-01-20 18:50 | FALSE | 1 | line_66569_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_66570_21 | ACLineSegment | Line | 0.034884 | 0.0034628 | 0.0034628 | 0.0018942 | 9.9268 | 0 | 0 | 0 | 2024-01-20 18:50 | FALSE | 1 | line_66570_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_67374_21 | ACLineSegment | Line | 0.034884 | 0.0088163 | 0.0088163 | 0.0044781 | 25.2735 | 0 | 0 | 0 | 2024-07-16 03:00 | FALSE | 1 | line_67374_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_67375_21 | ACLineSegment | Line | 0.034884 | 0.0088163 | 0.0088163 | 0.0044781 | 25.2735 | 0 | 0 | 0 | 2024-07-16 03:00 | FALSE | 1 | line_67375_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_67377_21 | ACLineSegment | Line | 0.034884 | 0.006365 | 0.006365 | 0.004286 | 18.2464 | 0 | 0 | 0 | 2024-01-17 08:10 | FALSE | 1 | line_67377_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_67376_21 | ACLineSegment | Line | 0.034884 | 0.006365 | 0.006365 | 0.004286 | 18.2464 | 0 | 0 | 0 | 2024-01-17 08:10 | FALSE | 1 | line_67376_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_67378_21 | ACLineSegment | Line | 0.034884 | 0.0034166 | 0.0034166 | 0.0019978 | 9.7942 | 0 | 0 | 0 | 2024-07-15 09:15 | FALSE | 1 | line_67378_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_67379_21 | ACLineSegment | Line | 0.034884 | 0.0042871 | 0.0042871 | 0.002534 | 12.2899 | 0 | 0 | 0 | 2024-01-18 01:55 | FALSE | 1 | line_67379_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_67979_21 | ACLineSegment | Line | 0.034884 | 0.0044739 | 0.0044739 | 0.0020507 | 12.8252 | 0 | 0 | 0 | 2024-01-20 18:50 | FALSE | 1 | line_67979_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_67980_21 | ACLineSegment | Line | 0.034884 | 0.0044739 | 0.0044739 | 0.0020507 | 12.8252 | 0 | 0 | 0 | 2024-01-20 18:50 | FALSE | 1 | line_67980_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_67984_21 | ACLineSegment | Line | 0.034884 | 0.0078745 | 0.0078745 | 0.0046556 | 22.5736 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | line_67984_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_67985_21 | ACLineSegment | Line | 0.034884 | 0.005454 | 0.005454 | 0.0027749 | 15.6349 | 0 | 0 | 0 | 2024-01-20 11:55 | FALSE | 1 | line_67985_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_67981_21 | ACLineSegment | Line | 0.034884 | 0.023729 | 0.023729 | 0.015122 | 68.0244 | 0 | 0 | 0 | 2024-01-20 08:55 | FALSE | 1 | line_67981_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_67982_21 | ACLineSegment | Line | 0.034884 | 0.026212 | 0.026212 | 0.017034 | 75.1402 | 0 | 0 | 0 | 2024-01-20 08:55 | FALSE | 1 | line_67982_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_67983_21 | ACLineSegment | Line | 0.034884 | 0.0040117 | 0.0040117 | 0.0020875 | 11.5002 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | line_67983_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_67990_21 | ACLineSegment | Line | 0.034884 | 0.023729 | 0.023729 | 0.015122 | 68.0244 | 0 | 0 | 0 | 2024-01-20 08:55 | FALSE | 1 | line_67990_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_67992_21 | ACLineSegment | Line | 0.034884 | 0.0064033 | 0.0064033 | 0.0035253 | 18.3561 | 0 | 0 | 0 | 2024-01-20 09:00 | FALSE | 1 | line_67992_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_67998_21 | ACLineSegment | Line | 0.034884 | 0.0078745 | 0.0078745 | 0.0046556 | 22.5736 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | line_67998_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_67986_21 | ACLineSegment | Line | 0.034884 | 0.0044674 | 0.0044674 | 0.0024067 | 12.8068 | 0 | 0 | 0 | 2024-01-20 10:55 | FALSE | 1 | line_67986_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_67987_21 | ACLineSegment | Line | 0.034884 | 0.0044674 | 0.0044674 | 0.0024067 | 12.8068 | 0 | 0 | 0 | 2024-01-20 10:55 | FALSE | 1 | line_67987_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_67993_21 | ACLineSegment | Line | 0.034884 | 0.0085402 | 0.0085402 | 0.0045722 | 24.4822 | 0 | 0 | 0 | 2024-01-20 10:55 | FALSE | 1 | line_67993_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_67994_21 | ACLineSegment | Line | 0.034884 | 0.0043587 | 0.0043587 | 0.0023442 | 12.495 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | line_67994_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_67997_21 | ACLineSegment | Line | 0.034884 | 0.017676 | 0.017676 | 0.010798 | 50.6712 | 0 | 0 | 0 | 2024-01-20 08:55 | FALSE | 1 | line_67997_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_68001_21 | ACLineSegment | Line | 0.034884 | 0.0038063 | 0.0038063 | 0.0019915 | 10.9115 | 0 | 0 | 0 | 2024-01-20 18:50 | FALSE | 1 | line_68001_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_68002_21 | ACLineSegment | Line | 0.034884 | 0.0045646 | 0.0045646 | 0.0026871 | 13.0853 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_68002_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_67995_21 | ACLineSegment | Line | 0.034884 | 0.013372 | 0.013372 | 0.0078013 | 38.3335 | 0 | 0 | 0 | 2024-01-20 10:55 | FALSE | 1 | line_67995_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_67996_21 | ACLineSegment | Line | 0.034884 | 0.0054643 | 0.0054643 | 0.003398 | 15.6645 | 0 | 0 | 0 | 2024-07-16 03:00 | FALSE | 1 | line_67996_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_68003_21 | ACLineSegment | Line | 0.034884 | 0.016259 | 0.016259 | 0.009883 | 46.6089 | 0 | 0 | 0 | 2024-01-20 10:55 | FALSE | 1 | line_68003_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_68004_21 | ACLineSegment | Line | 0.034884 | 0.0046437 | 0.0046437 | 0.0023151 | 13.3119 | 0 | 0 | 0 | 2024-01-20 05:00 | FALSE | 1 | line_68004_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_67999_21 | ACLineSegment | Line | 0.034884 | 0.0074096 | 0.0074096 | 0.0040063 | 21.241 | 0 | 0 | 0 | 2024-01-17 11:00 | FALSE | 1 | line_67999_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_68000_21 | ACLineSegment | Line | 0.034884 | 0.0048703 | 0.0048703 | 0.002646 | 13.9617 | 0 | 0 | 0 | 2024-01-20 08:55 | FALSE | 1 | line_68000_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69053_21 | ACLineSegment | Line | 0.034884 | 0.022664 | 0.022664 | 0.014878 | 64.9699 | 0 | 0 | 0 | 2024-01-20 22:50 | FALSE | 1 | line_69053_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69054_21 | ACLineSegment | Line | 0.034884 | 0.024992 | 0.024992 | 0.016586 | 71.6436 | 0 | 0 | 0 | 2024-01-20 22:50 | FALSE | 1 | line_69054_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69055_21 | ACLineSegment | Line | 0.034884 | 0.0036318 | 0.0036318 | 0.0019207 | 10.4113 | 0 | 0 | 0 | 2024-01-20 08:55 | FALSE | 1 | line_69055_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69074_21 | ACLineSegment | Line | 0.034884 | 0.0073554 | 0.0073554 | 0.0045205 | 21.0857 | 0 | 0 | 0 | 2024-01-17 09:55 | FALSE | 1 | line_69074_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69079_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_69079_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69080_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_69080_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69081_21 | ACLineSegment | Line | 0.034884 | 0.0069296 | 0.0069296 | 0.0035777 | 19.8651 | 0 | 0 | 0 | 2024-01-20 21:15 | FALSE | 1 | line_69081_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69082_21 | ACLineSegment | Line | 0.034884 | 0.0065033 | 0.0065033 | 0.0035111 | 18.6429 | 0 | 0 | 0 | 2024-01-20 22:50 | FALSE | 1 | line_69082_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69083_21 | ACLineSegment | Line | 0.034884 | 0.006649 | 0.006649 | 0.0039983 | 19.0606 | 0 | 0 | 0 | 2024-01-20 19:55 | FALSE | 1 | line_69083_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69091_21 | ACLineSegment | Line | 0.034884 | 0.030344 | 0.030344 | 0.020543 | 86.9874 | 0 | 0 | 0 | 2024-01-20 22:50 | FALSE | 1 | line_69091_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69092_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_69092_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69093_21 | ACLineSegment | Line | 0.034884 | 0.0045329 | 0.0045329 | 0.0024123 | 12.9945 | 0 | 0 | 0 | 2024-01-20 07:25 | FALSE | 1 | line_69093_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69094_21 | ACLineSegment | Line | 0.034884 | 0.0034575 | 0.0034575 | 0.0019092 | 9.9115 | 0 | 0 | 0 | 2024-01-20 17:05 | FALSE | 1 | line_69094_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69056_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_69056_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69057_21 | ACLineSegment | Line | 0.034884 | 0.038618 | 0.038618 | 0.025481 | 110.7044 | 147 | 12.25 | 0.13954 | 2024-01-20 07:25 | FALSE | 1 | line_69057_21 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_69063_21 | ACLineSegment | Line | 0.034884 | 0.0047841 | 0.0047841 | 0.002524 | 13.7146 | 0 | 0 | 0 | 2024-01-20 12:00 | FALSE | 1 | line_69063_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69064_21 | ACLineSegment | Line | 0.034884 | 0.0037575 | 0.0037575 | 0.0021671 | 10.7716 | 0 | 0 | 0 | 2024-01-17 10:00 | FALSE | 1 | line_69064_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69058_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_69058_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69059_21 | ACLineSegment | Line | 0.034884 | 0.029776 | 0.029776 | 0.018877 | 85.3582 | 0 | 0 | 0 | 2024-01-20 07:25 | FALSE | 1 | line_69059_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69060_21 | ACLineSegment | Line | 0.034884 | 0.0067725 | 0.0067725 | 0.0038593 | 19.4146 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | line_69060_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69061_21 | ACLineSegment | Line | 0.034884 | 0.0054442 | 0.0054442 | 0.0033087 | 15.6067 | 0 | 0 | 0 | 2024-01-20 06:55 | FALSE | 1 | line_69061_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69072_21 | ACLineSegment | Line | 0.034884 | 0.027159 | 0.027159 | 0.01669 | 77.8563 | 0 | 0 | 0 | 2024-01-20 07:25 | FALSE | 1 | line_69072_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69100_21 | ACLineSegment | Line | 0.034884 | 0.0038695 | 0.0038695 | 0.0023156 | 11.0926 | 0 | 0 | 0 | 2024-01-20 14:50 | FALSE | 1 | line_69100_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69071_21 | ACLineSegment | Line | 0.034884 | 0.023284 | 0.023284 | 0.014318 | 66.7485 | 0 | 0 | 0 | 2024-01-20 07:25 | FALSE | 1 | line_69071_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69073_21 | ACLineSegment | Line | 0.034884 | 0.0043867 | 0.0043867 | 0.0025613 | 12.5753 | 0 | 0 | 0 | 2024-01-20 18:50 | FALSE | 1 | line_69073_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69085_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_69085_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69086_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_69086_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69087_21 | ACLineSegment | Line | 0.034884 | 0.0075361 | 0.0075361 | 0.0039284 | 21.6036 | 0 | 0 | 0 | 2024-01-20 21:15 | FALSE | 1 | line_69087_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69088_21 | ACLineSegment | Line | 0.034884 | 0.0085465 | 0.0085465 | 0.0045543 | 24.5 | 0 | 0 | 0 | 2024-01-21 03:05 | FALSE | 1 | line_69088_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69089_21 | ACLineSegment | Line | 0.034884 | 0.0047917 | 0.0047917 | 0.0023685 | 13.7362 | 0 | 0 | 0 | 2024-01-20 09:00 | FALSE | 1 | line_69089_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69090_21 | ACLineSegment | Line | 0.034884 | 0.0097211 | 0.0097211 | 0.0044774 | 27.8674 | 0 | 0 | 0 | 2024-01-17 06:55 | FALSE | 1 | line_69090_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69075_21 | ACLineSegment | Line | 0.034884 | 0.0055358 | 0.0055358 | 0.0033163 | 15.8695 | 0 | 0 | 0 | 2024-01-17 11:00 | FALSE | 1 | line_69075_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69076_21 | ACLineSegment | Line | 0.034884 | 0.0027856 | 0.0027856 | 0.0013571 | 7.9855 | 0 | 0 | 0 | 2024-01-20 22:50 | FALSE | 1 | line_69076_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69096_21 | ACLineSegment | Line | 0.034884 | 0.0055358 | 0.0055358 | 0.0033163 | 15.8695 | 0 | 0 | 0 | 2024-01-17 11:00 | FALSE | 1 | line_69096_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69077_21 | ACLineSegment | Line | 0.034884 | 0.039349 | 0.039349 | 0.026998 | 112.8016 | 204 | 17 | 0.19364 | 2024-01-20 22:50 | FALSE | 1 | line_69077_21 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_69097_21 | ACLineSegment | Line | 0.034884 | 0.03673 | 0.03673 | 0.02473 | 105.2926 | 28 | 2.3333 | 0.026579 | 2024-01-20 22:50 | FALSE | 1 | line_69097_21 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_69099_21 | ACLineSegment | Line | 0.034884 | 0.0049162 | 0.0049162 | 0.0024302 | 14.0931 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | line_69099_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69095_21 | ACLineSegment | Line | 0.034884 | 0.0075361 | 0.0075361 | 0.0039284 | 21.6036 | 0 | 0 | 0 | 2024-01-20 21:15 | FALSE | 1 | line_69095_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69098_21 | ACLineSegment | Line | 0.034884 | 0.0080756 | 0.0080756 | 0.0045641 | 23.1501 | 0 | 0 | 0 | 2024-01-20 20:20 | FALSE | 1 | line_69098_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69130_21 | ACLineSegment | Line | 0.034884 | 0.01341 | 0.01341 | 0.0083269 | 38.4409 | 0 | 0 | 0 | 2024-01-20 22:50 | FALSE | 1 | line_69130_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69131_21 | ACLineSegment | Line | 0.034884 | 0.01341 | 0.01341 | 0.0083269 | 38.4409 | 0 | 0 | 0 | 2024-01-20 22:50 | FALSE | 1 | line_69131_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69132_21 | ACLineSegment | Line | 0.034884 | 0.0095811 | 0.0095811 | 0.005778 | 27.4659 | 0 | 0 | 0 | 2024-01-21 03:05 | FALSE | 1 | line_69132_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69133_21 | ACLineSegment | Line | 0.034884 | 0.0047423 | 0.0047423 | 0.0027094 | 13.5947 | 0 | 0 | 0 | 2024-01-20 22:50 | FALSE | 1 | line_69133_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69134_21 | ACLineSegment | Line | 0.034884 | 0.020951 | 0.020951 | 0.013651 | 60.0589 | 0 | 0 | 0 | 2024-01-20 14:50 | FALSE | 1 | line_69134_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69135_21 | ACLineSegment | Line | 0.034884 | 0.0073394 | 0.0073394 | 0.0036959 | 21.0397 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | line_69135_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69136_21 | ACLineSegment | Line | 0.034884 | 0.0049338 | 0.0049338 | 0.0021219 | 14.1436 | 0 | 0 | 0 | 2024-01-20 14:50 | FALSE | 1 | line_69136_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69138_21 | ACLineSegment | Line | 0.034884 | 0.0063175 | 0.0063175 | 0.0036481 | 18.1104 | 0 | 0 | 0 | 2024-01-20 07:25 | FALSE | 1 | line_69138_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69148_21 | ACLineSegment | Line | 0.034884 | 0.0040849 | 0.0040849 | 0.0022997 | 11.7101 | 0 | 0 | 0 | 2024-01-17 06:55 | FALSE | 1 | line_69148_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69143_21 | ACLineSegment | Line | 0.034884 | 0.02427 | 0.02427 | 0.015793 | 69.5737 | 0 | 0 | 0 | 2024-01-21 03:05 | FALSE | 1 | line_69143_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69144_21 | ACLineSegment | Line | 0.034884 | 0.0052299 | 0.0052299 | 0.0024559 | 14.9924 | 0 | 0 | 0 | 2024-01-20 16:00 | FALSE | 1 | line_69144_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69137_21 | ACLineSegment | Line | 0.034884 | 0.0035111 | 0.0035111 | 0.0019624 | 10.0651 | 0 | 0 | 0 | 2024-01-20 11:55 | FALSE | 1 | line_69137_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69139_21 | ACLineSegment | Line | 0.034884 | 0.0035273 | 0.0035273 | 0.0018487 | 10.1117 | 0 | 0 | 0 | 2024-01-21 03:05 | FALSE | 1 | line_69139_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69141_21 | ACLineSegment | Line | 0.034884 | 0.0035111 | 0.0035111 | 0.0019624 | 10.0651 | 0 | 0 | 0 | 2024-01-20 11:55 | FALSE | 1 | line_69141_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69140_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_69140_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69145_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_69145_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69149_21 | ACLineSegment | Line | 0.034884 | 0.015213 | 0.015213 | 0.0096387 | 43.6095 | 0 | 0 | 0 | 2024-07-16 02:00 | FALSE | 1 | line_69149_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69150_21 | ACLineSegment | Line | 0.034884 | 0.0052671 | 0.0052671 | 0.0031129 | 15.0992 | 0 | 0 | 0 | 2024-06-27 03:00 | FALSE | 1 | line_69150_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69151_21 | ACLineSegment | Line | 0.034884 | 0.0059747 | 0.0059747 | 0.0029665 | 17.1277 | 0 | 0 | 0 | 2024-07-15 21:45 | FALSE | 1 | line_69151_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69152_21 | ACLineSegment | Line | 0.034884 | 0.004319 | 0.004319 | 0.0021086 | 12.3812 | 0 | 0 | 0 | 2024-01-20 17:05 | FALSE | 1 | line_69152_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69153_21 | ACLineSegment | Line | 0.034884 | 0.0034025 | 0.0034025 | 0.0020489 | 9.754 | 0 | 0 | 0 | 2024-01-17 17:55 | FALSE | 1 | line_69153_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69147_21 | ACLineSegment | Line | 0.034884 | 0.0030712 | 0.0030712 | 0.0016114 | 8.8043 | 0 | 0 | 0 | 2024-01-21 02:15 | FALSE | 1 | line_69147_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69300_21 | ACLineSegment | Line | 0.034884 | 0.0040328 | 0.0040328 | 0.0023244 | 11.5609 | 0 | 0 | 0 | 2024-01-20 17:05 | FALSE | 1 | line_69300_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69301_21 | ACLineSegment | Line | 0.034884 | 0.0040328 | 0.0040328 | 0.0023244 | 11.5609 | 0 | 0 | 0 | 2024-01-20 17:05 | FALSE | 1 | line_69301_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69303_21 | ACLineSegment | Line | 0.034884 | 0.0078657 | 0.0078657 | 0.0045543 | 22.5485 | 0 | 0 | 0 | 2024-01-20 11:55 | FALSE | 1 | line_69303_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69742_21 | ACLineSegment | Line | 0.034884 | 0.0054222 | 0.0054222 | 0.003154 | 15.5437 | 0 | 0 | 0 | 2024-01-18 01:55 | FALSE | 1 | line_69742_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69743_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_69743_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69744_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_69744_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69745_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_69745_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69746_21 | ACLineSegment | Line | 0.034884 | 0.019918 | 0.019918 | 0.012666 | 57.0989 | 0 | 0 | 0 | 2024-01-21 01:25 | FALSE | 1 | line_69746_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69747_21 | ACLineSegment | Line | 0.034884 | 0.0058959 | 0.0058959 | 0.002809 | 16.9017 | 0 | 0 | 0 | 2024-07-15 10:55 | FALSE | 1 | line_69747_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69748_21 | ACLineSegment | Line | 0.034884 | 0.0048326 | 0.0048326 | 0.0025979 | 13.8536 | 0 | 0 | 0 | 2024-07-16 02:00 | FALSE | 1 | line_69748_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69749_21 | ACLineSegment | Line | 0.034884 | 0.0060562 | 0.0060562 | 0.003469 | 17.3613 | 0 | 0 | 0 | 2024-07-15 08:55 | FALSE | 1 | line_69749_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69750_21 | ACLineSegment | Line | 0.034884 | 0.003614 | 0.003614 | 0.0018677 | 10.3603 | 0 | 0 | 0 | 2024-01-20 08:55 | FALSE | 1 | line_69750_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69751_21 | ACLineSegment | Line | 0.034884 | 0.0054222 | 0.0054222 | 0.003154 | 15.5437 | 0 | 0 | 0 | 2024-01-18 01:55 | FALSE | 1 | line_69751_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69752_21 | ACLineSegment | Line | 0.034884 | 0.023798 | 0.023798 | 0.015181 | 68.2203 | 0 | 0 | 0 | 2024-01-20 06:55 | FALSE | 1 | line_69752_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69766_21 | ACLineSegment | Line | 0.034884 | 0.0052743 | 0.0052743 | 0.0027356 | 15.1196 | 0 | 0 | 0 | 2024-01-20 06:55 | FALSE | 1 | line_69766_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69754_21 | ACLineSegment | Line | 0.034884 | 0.015955 | 0.015955 | 0.010477 | 45.7394 | 0 | 0 | 0 | 2024-01-21 01:25 | FALSE | 1 | line_69754_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69755_21 | ACLineSegment | Line | 0.034884 | 0.011175 | 0.011175 | 0.0069314 | 32.0346 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | line_69755_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69756_21 | ACLineSegment | Line | 0.034884 | 0.0069039 | 0.0069039 | 0.0037937 | 19.7914 | 0 | 0 | 0 | 2024-01-18 02:00 | FALSE | 1 | line_69756_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69757_21 | ACLineSegment | Line | 0.034884 | 0.021261 | 0.021261 | 0.014442 | 60.9487 | 0 | 0 | 0 | 2024-01-21 01:25 | FALSE | 1 | line_69757_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69758_21 | ACLineSegment | Line | 0.034884 | 0.0031191 | 0.0031191 | 0.0017055 | 8.9416 | 0 | 0 | 0 | 2024-01-20 12:00 | FALSE | 1 | line_69758_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69759_21 | ACLineSegment | Line | 0.034884 | 0.0050417 | 0.0050417 | 0.0026641 | 14.453 | 0 | 0 | 0 | 2024-01-20 19:55 | FALSE | 1 | line_69759_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69761_21 | ACLineSegment | Line | 0.034884 | 0.0071853 | 0.0071853 | 0.004326 | 20.598 | 0 | 0 | 0 | 2024-01-20 07:25 | FALSE | 1 | line_69761_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69762_21 | ACLineSegment | Line | 0.034884 | 0.0050502 | 0.0050502 | 0.0027535 | 14.4773 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | line_69762_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69763_21 | ACLineSegment | Line | 0.034884 | 0.0071853 | 0.0071853 | 0.004326 | 20.598 | 0 | 0 | 0 | 2024-01-20 07:25 | FALSE | 1 | line_69763_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69764_21 | ACLineSegment | Line | 0.034884 | 0.0049042 | 0.0049042 | 0.00282 | 14.0589 | 0 | 0 | 0 | 2024-01-20 07:25 | FALSE | 1 | line_69764_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_69765_21 | ACLineSegment | Line | 0.034884 | 0.0031684 | 0.0031684 | 0.0017045 | 9.0828 | 0 | 0 | 0 | 2024-01-20 20:20 | FALSE | 1 | line_69765_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_72162_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_72162_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_72163_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_72163_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_72164_21 | ACLineSegment | Line | 0.034884 | 0.016418 | 0.016418 | 0.010619 | 47.0641 | 0 | 0 | 0 | 2024-01-21 03:05 | FALSE | 1 | line_72164_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_72165_21 | ACLineSegment | Line | 0.034884 | 0.0045236 | 0.0045236 | 0.0027419 | 12.9677 | 0 | 0 | 0 | 2024-01-21 10:55 | FALSE | 1 | line_72165_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_72166_21 | ACLineSegment | Line | 0.034884 | 0.0066069 | 0.0066069 | 0.0037449 | 18.94 | 0 | 0 | 0 | 2024-01-20 19:55 | FALSE | 1 | line_72166_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_72167_21 | ACLineSegment | Line | 0.034884 | 0.0082338 | 0.0082338 | 0.0045907 | 23.6037 | 0 | 0 | 0 | 2024-01-20 22:50 | FALSE | 1 | line_72167_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_72175_21 | ACLineSegment | Line | 0.034884 | 0.020697 | 0.020697 | 0.012933 | 59.331 | 0 | 0 | 0 | 2024-01-17 08:10 | FALSE | 1 | line_72175_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_72173_21 | ACLineSegment | Line | 0.034884 | 0.0058449 | 0.0058449 | 0.0034957 | 16.7554 | 0 | 0 | 0 | 2024-01-21 02:15 | FALSE | 1 | line_72173_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_72174_21 | ACLineSegment | Line | 0.034884 | 0.0058449 | 0.0058449 | 0.0034957 | 16.7554 | 0 | 0 | 0 | 2024-01-21 02:15 | FALSE | 1 | line_72174_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_72179_21 | ACLineSegment | Line | 0.034884 | 0.01104 | 0.01104 | 0.0067833 | 31.6485 | 0 | 0 | 0 | 2024-07-15 19:55 | FALSE | 1 | line_72179_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_72180_21 | ACLineSegment | Line | 0.034884 | 0.0061118 | 0.0061118 | 0.0034995 | 17.5206 | 0 | 0 | 0 | 2024-01-20 10:55 | FALSE | 1 | line_72180_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_72177_21 | ACLineSegment | Line | 0.034884 | 0.015101 | 0.015101 | 0.0093087 | 43.2885 | 0 | 0 | 0 | 2024-01-20 08:55 | FALSE | 1 | line_72177_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_72178_21 | ACLineSegment | Line | 0.034884 | 0.0080265 | 0.0080265 | 0.0039515 | 23.0094 | 0 | 0 | 0 | 2024-01-20 11:55 | FALSE | 1 | line_72178_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_72181_21 | ACLineSegment | Line | 0.034884 | 0.0049392 | 0.0049392 | 0.0027891 | 14.1591 | 0 | 0 | 0 | 2024-07-15 08:55 | FALSE | 1 | line_72181_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_73244_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_73244_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_73245_21 | ACLineSegment | Line | 0.034884 | 0.030011 | 0.030011 | 0.019773 | 86.0309 | 0 | 0 | 0 | 2024-01-21 03:05 | FALSE | 1 | line_73245_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_73246_21 | ACLineSegment | Line | 0.034884 | 0.0096879 | 0.0096879 | 0.005674 | 27.7722 | 0 | 0 | 0 | 2024-01-20 15:45 | FALSE | 1 | line_73246_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_73247_21 | ACLineSegment | Line | 0.034884 | 0.050399 | 0.050399 | 0.032142 | 144.4782 | 2455 | 204.5833 | 2.3304 | 2024-01-21 03:05 | FALSE | 1 | line_73247_21 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_73248_21 | ACLineSegment | Line | 0.034884 | 0.0055291 | 0.0055291 | 0.0028817 | 15.8502 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_73248_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_73249_21 | ACLineSegment | Line | 0.034884 | 0.0090451 | 0.0090451 | 0.0046392 | 25.9294 | 0 | 0 | 0 | 2024-01-20 13:05 | FALSE | 1 | line_73249_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_73255_21 | ACLineSegment | Line | 0.034884 | 0.022677 | 0.022677 | 0.01456 | 65.009 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_73255_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_73256_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_73256_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_73257_21 | ACLineSegment | Line | 0.034884 | 0.0071767 | 0.0071767 | 0.0035164 | 20.5734 | 0 | 0 | 0 | 2024-01-20 10:55 | FALSE | 1 | line_73257_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_73258_21 | ACLineSegment | Line | 0.034884 | 0.0032742 | 0.0032742 | 0.0019204 | 9.3862 | 0 | 0 | 0 | 2024-01-20 13:05 | FALSE | 1 | line_73258_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_73262_21 | ACLineSegment | Line | 0.034884 | 0.0048107 | 0.0048107 | 0.0029048 | 13.7906 | 0 | 0 | 0 | 2024-01-17 09:55 | FALSE | 1 | line_73262_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_73271_21 | ACLineSegment | Line | 0.034884 | 0.0056693 | 0.0056693 | 0.0031367 | 16.2521 | 0 | 0 | 0 | 2024-01-20 15:45 | FALSE | 1 | line_73271_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_73275_21 | ACLineSegment | Line | 0.034884 | 0.024076 | 0.024076 | 0.014181 | 69.018 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | line_73275_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_73250_21 | ACLineSegment | Line | 0.034884 | 0.015834 | 0.015834 | 0.009062 | 45.3901 | 0 | 0 | 0 | 2024-01-20 23:55 | FALSE | 1 | line_73250_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_73251_21 | ACLineSegment | Line | 0.034884 | 0.013347 | 0.013347 | 0.0072766 | 38.2612 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | line_73251_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_73252_21 | ACLineSegment | Line | 0.034884 | 0.0042066 | 0.0042066 | 0.0020093 | 12.059 | 0 | 0 | 0 | 2024-01-20 23:55 | FALSE | 1 | line_73252_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_73253_21 | ACLineSegment | Line | 0.034884 | 0.01953 | 0.01953 | 0.011559 | 55.9853 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | line_73253_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_73254_21 | ACLineSegment | Line | 0.034884 | 0.0049689 | 0.0049689 | 0.0027828 | 14.2443 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | line_73254_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_73272_21 | ACLineSegment | Line | 0.034884 | 0.0082136 | 0.0082136 | 0.0043292 | 23.5459 | 0 | 0 | 0 | 2024-01-17 16:35 | FALSE | 1 | line_73272_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_73282_21 | ACLineSegment | Line | 0.034884 | 0.0068844 | 0.0068844 | 0.0034375 | 19.7354 | 0 | 0 | 0 | 2024-01-18 01:55 | FALSE | 1 | line_73282_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_73281_21 | ACLineSegment | Line | 0.034884 | 0.0050056 | 0.0050056 | 0.0029022 | 14.3495 | 0 | 0 | 0 | 2024-01-21 08:45 | FALSE | 1 | line_73281_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_73264_21 | ACLineSegment | Line | 0.034884 | 0.019803 | 0.019803 | 0.012093 | 56.768 | 0 | 0 | 0 | 2024-01-21 03:05 | FALSE | 1 | line_73264_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_73265_21 | ACLineSegment | Line | 0.034884 | 0.0053329 | 0.0053329 | 0.0027188 | 15.2876 | 0 | 0 | 0 | 2024-01-20 12:00 | FALSE | 1 | line_73265_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_73263_21 | ACLineSegment | Line | 0.034884 | 0.0048107 | 0.0048107 | 0.0029048 | 13.7906 | 0 | 0 | 0 | 2024-01-17 09:55 | FALSE | 1 | line_73263_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_73268_21 | ACLineSegment | Line | 0.034884 | 0.013665 | 0.013665 | 0.007566 | 39.1722 | 0 | 0 | 0 | 2024-01-21 03:05 | FALSE | 1 | line_73268_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_73277_21 | ACLineSegment | Line | 0.034884 | 0.0096816 | 0.0096816 | 0.0050229 | 27.7541 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_73277_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_73266_21 | ACLineSegment | Line | 0.034884 | 0.0048738 | 0.0048738 | 0.0024547 | 13.9715 | 0 | 0 | 0 | 2024-01-21 03:05 | FALSE | 1 | line_73266_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_73267_21 | ACLineSegment | Line | 0.034884 | 0.0048738 | 0.0048738 | 0.0024547 | 13.9715 | 0 | 0 | 0 | 2024-01-21 03:05 | FALSE | 1 | line_73267_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_73273_21 | ACLineSegment | Line | 0.034884 | 0.0048453 | 0.0048453 | 0.0022328 | 13.89 | 0 | 0 | 0 | 2024-07-15 16:45 | FALSE | 1 | line_73273_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_73269_21 | ACLineSegment | Line | 0.034884 | 0.0085665 | 0.0085665 | 0.0044007 | 24.5574 | 0 | 0 | 0 | 2024-01-21 03:05 | FALSE | 1 | line_73269_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_73270_21 | ACLineSegment | Line | 0.034884 | 0.0069174 | 0.0069174 | 0.003512 | 19.8301 | 0 | 0 | 0 | 2024-01-20 18:50 | FALSE | 1 | line_73270_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_73274_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_73274_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_73278_21 | ACLineSegment | Line | 0.034884 | 0.002905 | 0.002905 | 0.0016597 | 8.3278 | 0 | 0 | 0 | 2024-01-20 15:45 | FALSE | 1 | line_73278_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_73279_21 | ACLineSegment | Line | 0.034884 | 0.0069025 | 0.0069025 | 0.0035821 | 19.7872 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_73279_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_75356_21 | ACLineSegment | Line | 0.034884 | 0.033763 | 0.033763 | 0.022431 | 96.7889 | 0 | 0 | 0 | 2024-01-20 07:25 | FALSE | 1 | line_75356_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_75357_21 | ACLineSegment | Line | 0.034884 | 0.032293 | 0.032293 | 0.020702 | 92.5731 | 0 | 0 | 0 | 2024-01-20 07:25 | FALSE | 1 | line_75357_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_75358_21 | ACLineSegment | Line | 0.034884 | 0.0031321 | 0.0031321 | 0.0018657 | 8.9787 | 0 | 0 | 0 | 2024-01-20 11:55 | FALSE | 1 | line_75358_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_75376_21 | ACLineSegment | Line | 0.034884 | 0.024799 | 0.024799 | 0.015943 | 71.0919 | 0 | 0 | 0 | 2024-01-20 17:05 | FALSE | 1 | line_75376_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_75377_21 | ACLineSegment | Line | 0.034884 | 0.0052393 | 0.0052393 | 0.0026872 | 15.0195 | 0 | 0 | 0 | 2024-07-15 09:15 | FALSE | 1 | line_75377_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_75378_21 | ACLineSegment | Line | 0.034884 | 0.0045159 | 0.0045159 | 0.0026012 | 12.9458 | 0 | 0 | 0 | 2024-07-16 01:45 | FALSE | 1 | line_75378_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_75361_21 | ACLineSegment | Line | 0.034884 | 0.0056198 | 0.0056198 | 0.0031696 | 16.1101 | 0 | 0 | 0 | 2024-01-20 07:25 | FALSE | 1 | line_75361_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_75362_21 | ACLineSegment | Line | 0.034884 | 0.011637 | 0.011637 | 0.0064703 | 33.359 | 0 | 0 | 0 | 2024-01-20 17:05 | FALSE | 1 | line_75362_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_75363_21 | ACLineSegment | Line | 0.034884 | 0.0064377 | 0.0064377 | 0.0035881 | 18.4548 | 0 | 0 | 0 | 2024-01-20 17:05 | FALSE | 1 | line_75363_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_75373_21 | ACLineSegment | Line | 0.034884 | 0.0056198 | 0.0056198 | 0.0031696 | 16.1101 | 0 | 0 | 0 | 2024-01-20 07:25 | FALSE | 1 | line_75373_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_75382_21 | ACLineSegment | Line | 0.034884 | 0.016061 | 0.016061 | 0.0093964 | 46.0422 | 0 | 0 | 0 | 2024-01-20 17:05 | FALSE | 1 | line_75382_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_75391_21 | ACLineSegment | Line | 0.034884 | 0.0056586 | 0.0056586 | 0.0031527 | 16.2215 | 0 | 0 | 0 | 2024-07-16 03:00 | FALSE | 1 | line_75391_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_75364_21 | ACLineSegment | Line | 0.034884 | 0.020376 | 0.020376 | 0.011733 | 58.4111 | 0 | 0 | 0 | 2024-01-20 13:05 | FALSE | 1 | line_75364_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_75365_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_75365_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_75366_21 | ACLineSegment | Line | 0.034884 | 0.028755 | 0.028755 | 0.017559 | 82.4301 | 0 | 0 | 0 | 2024-01-20 13:05 | FALSE | 1 | line_75366_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_75367_21 | ACLineSegment | Line | 0.034884 | 0.0037805 | 0.0037805 | 0.0021053 | 10.8374 | 0 | 0 | 0 | 2024-01-20 10:55 | FALSE | 1 | line_75367_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_75368_21 | ACLineSegment | Line | 0.034884 | 0.0081755 | 0.0081755 | 0.0043456 | 23.4366 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_75368_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_75369_21 | ACLineSegment | Line | 0.034884 | 0.020376 | 0.020376 | 0.011733 | 58.4111 | 0 | 0 | 0 | 2024-01-20 13:05 | FALSE | 1 | line_75369_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_75384_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_75384_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_75385_21 | ACLineSegment | Line | 0.034884 | 0.035452 | 0.035452 | 0.022061 | 101.6297 | 9 | 0.75 | 0.0085431 | 2024-01-20 13:05 | FALSE | 1 | line_75385_21 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_75386_21 | ACLineSegment | Line | 0.034884 | 0.0045995 | 0.0045995 | 0.0026825 | 13.1854 | 0 | 0 | 0 | 2024-07-15 12:50 | FALSE | 1 | line_75386_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_75387_21 | ACLineSegment | Line | 0.034884 | 0.0037696 | 0.0037696 | 0.0022578 | 10.8062 | 0 | 0 | 0 | 2024-01-20 13:05 | FALSE | 1 | line_75387_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_75379_21 | ACLineSegment | Line | 0.034884 | 0.010844 | 0.010844 | 0.0063062 | 31.0854 | 0 | 0 | 0 | 2024-01-20 23:55 | FALSE | 1 | line_75379_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_75380_21 | ACLineSegment | Line | 0.034884 | 0.0078865 | 0.0078865 | 0.0037654 | 22.6081 | 0 | 0 | 0 | 2024-01-20 13:05 | FALSE | 1 | line_75380_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_75381_21 | ACLineSegment | Line | 0.034884 | 0.0039708 | 0.0039708 | 0.0021877 | 11.3831 | 0 | 0 | 0 | 2024-01-20 23:55 | FALSE | 1 | line_75381_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_75370_21 | ACLineSegment | Line | 0.034884 | 0.020024 | 0.020024 | 0.012835 | 57.4018 | 0 | 0 | 0 | 2024-01-20 17:05 | FALSE | 1 | line_75370_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_75371_21 | ACLineSegment | Line | 0.034884 | 0.024799 | 0.024799 | 0.015943 | 71.0919 | 0 | 0 | 0 | 2024-01-20 17:05 | FALSE | 1 | line_75371_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_75372_21 | ACLineSegment | Line | 0.034884 | 0.0056646 | 0.0056646 | 0.003285 | 16.2386 | 0 | 0 | 0 | 2024-01-20 07:25 | FALSE | 1 | line_75372_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_75383_21 | ACLineSegment | Line | 0.034884 | 0.0061916 | 0.0061916 | 0.0037024 | 17.7495 | 0 | 0 | 0 | 2024-01-18 02:00 | FALSE | 1 | line_75383_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_75374_21 | ACLineSegment | Line | 0.034884 | 0.0068653 | 0.0068653 | 0.0036769 | 19.6808 | 0 | 0 | 0 | 2024-01-20 17:05 | FALSE | 1 | line_75374_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_75375_21 | ACLineSegment | Line | 0.034884 | 0.0068653 | 0.0068653 | 0.0036769 | 19.6808 | 0 | 0 | 0 | 2024-01-20 17:05 | FALSE | 1 | line_75375_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_75390_21 | ACLineSegment | Line | 0.034884 | 0.0050935 | 0.0050935 | 0.002934 | 14.6014 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | line_75390_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_75392_21 | ACLineSegment | Line | 0.034884 | 0.040228 | 0.040228 | 0.025511 | 115.3209 | 181 | 15.0833 | 0.17181 | 2024-01-20 13:05 | FALSE | 1 | line_75392_21 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_75393_21 | ACLineSegment | Line | 0.034884 | 0.0063463 | 0.0063463 | 0.0035283 | 18.1928 | 0 | 0 | 0 | 2024-01-20 18:50 | FALSE | 1 | line_75393_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_75395_21 | ACLineSegment | Line | 0.034884 | 0.0053647 | 0.0053647 | 0.0025463 | 15.3788 | 0 | 0 | 0 | 2024-01-20 19:55 | FALSE | 1 | line_75395_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_75872_21 | ACLineSegment | Line | 0.034884 | 0.010962 | 0.010962 | 0.0055978 | 31.4251 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_75872_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_75873_21 | ACLineSegment | Line | 0.034884 | 0.010962 | 0.010962 | 0.0055978 | 31.4251 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_75873_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_75874_21 | ACLineSegment | Line | 0.034884 | 0.0067544 | 0.0067544 | 0.0035391 | 19.3626 | 0 | 0 | 0 | 2024-01-17 09:55 | FALSE | 1 | line_75874_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_75875_21 | ACLineSegment | Line | 0.034884 | 0.0049077 | 0.0049077 | 0.0024085 | 14.0688 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_75875_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_75876_21 | ACLineSegment | Line | 0.034884 | 0.0074139 | 0.0074139 | 0.0037986 | 21.2533 | 0 | 0 | 0 | 2024-01-21 01:25 | FALSE | 1 | line_75876_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_75877_21 | ACLineSegment | Line | 0.034884 | 0.0074139 | 0.0074139 | 0.0037986 | 21.2533 | 0 | 0 | 0 | 2024-01-21 01:25 | FALSE | 1 | line_75877_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_79141_21 | ACLineSegment | Line | 0.034884 | 0.0085325 | 0.0085325 | 0.0040796 | 24.46 | 0 | 0 | 0 | 2024-07-06 02:45 | FALSE | 1 | line_79141_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_79142_21 | ACLineSegment | Line | 0.034884 | 0.0085325 | 0.0085325 | 0.0040796 | 24.46 | 0 | 0 | 0 | 2024-07-06 02:45 | FALSE | 1 | line_79142_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_79166_21 | ACLineSegment | Line | 0.034884 | 0.013174 | 0.013174 | 0.0072097 | 37.7671 | 0 | 0 | 0 | 2024-07-16 02:00 | FALSE | 1 | line_79166_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_79167_21 | ACLineSegment | Line | 0.034884 | 0.0060286 | 0.0060286 | 0.0034431 | 17.2822 | 0 | 0 | 0 | 2024-01-17 05:55 | FALSE | 1 | line_79167_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_79145_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_79145_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_79146_21 | ACLineSegment | Line | 0.034884 | 0.018392 | 0.018392 | 0.010434 | 52.724 | 0 | 0 | 0 | 2024-01-21 02:15 | FALSE | 1 | line_79146_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_79147_21 | ACLineSegment | Line | 0.034884 | 0.0075554 | 0.0075554 | 0.0038336 | 21.659 | 0 | 0 | 0 | 2024-01-21 02:15 | FALSE | 1 | line_79147_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_79148_21 | ACLineSegment | Line | 0.034884 | 0.0083674 | 0.0083674 | 0.0038376 | 23.9867 | 0 | 0 | 0 | 2024-01-20 22:50 | FALSE | 1 | line_79148_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_79149_21 | ACLineSegment | Line | 0.034884 | 0.0065008 | 0.0065008 | 0.0035414 | 18.6358 | 0 | 0 | 0 | 2024-01-17 09:55 | FALSE | 1 | line_79149_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_79155_21 | ACLineSegment | Line | 0.034884 | 0.021964 | 0.021964 | 0.01271 | 62.9649 | 0 | 0 | 0 | 2024-01-20 06:55 | FALSE | 1 | line_79155_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_79177_21 | ACLineSegment | Line | 0.034884 | 0.036887 | 0.036887 | 0.0228 | 105.7434 | 43 | 3.5833 | 0.040817 | 2024-01-17 09:55 | FALSE | 1 | line_79177_21 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_79150_21 | ACLineSegment | Line | 0.034884 | 0.012213 | 0.012213 | 0.0065063 | 35.0106 | 0 | 0 | 0 | 2024-01-20 06:55 | FALSE | 1 | line_79150_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_79151_21 | ACLineSegment | Line | 0.034884 | 0.0073571 | 0.0073571 | 0.0039899 | 21.0905 | 0 | 0 | 0 | 2024-01-20 06:55 | FALSE | 1 | line_79151_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_79152_21 | ACLineSegment | Line | 0.034884 | 0.0053428 | 0.0053428 | 0.0027136 | 15.3162 | 0 | 0 | 0 | 2024-01-20 21:15 | FALSE | 1 | line_79152_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_79153_21 | ACLineSegment | Line | 0.034884 | 0.012213 | 0.012213 | 0.0065063 | 35.0106 | 0 | 0 | 0 | 2024-01-20 06:55 | FALSE | 1 | line_79153_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_79168_21 | ACLineSegment | Line | 0.034884 | 0.015932 | 0.015932 | 0.0083912 | 45.6716 | 0 | 0 | 0 | 2024-01-20 06:55 | FALSE | 1 | line_79168_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_79178_21 | ACLineSegment | Line | 0.034884 | 0.0037189 | 0.0037189 | 0.002137 | 10.661 | 0 | 0 | 0 | 2024-01-20 06:55 | FALSE | 1 | line_79178_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_79154_21 | ACLineSegment | Line | 0.034884 | 0.019352 | 0.019352 | 0.010699 | 55.4757 | 0 | 0 | 0 | 2024-01-20 06:55 | FALSE | 1 | line_79154_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_79156_21 | ACLineSegment | Line | 0.034884 | 0.0039162 | 0.0039162 | 0.0021789 | 11.2265 | 0 | 0 | 0 | 2024-01-20 10:55 | FALSE | 1 | line_79156_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_79169_21 | ACLineSegment | Line | 0.034884 | 0.0053932 | 0.0053932 | 0.002568 | 15.4605 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_79169_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_79157_21 | ACLineSegment | Line | 0.034884 | 0.0050573 | 0.0050573 | 0.0030278 | 14.4976 | 0 | 0 | 0 | 2024-01-17 13:10 | FALSE | 1 | line_79157_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_79158_21 | ACLineSegment | Line | 0.034884 | 0.0050573 | 0.0050573 | 0.0030278 | 14.4976 | 0 | 0 | 0 | 2024-01-17 13:10 | FALSE | 1 | line_79158_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_79160_21 | ACLineSegment | Line | 0.034884 | 0.029618 | 0.029618 | 0.019307 | 84.9061 | 0 | 0 | 0 | 2024-07-16 02:00 | FALSE | 1 | line_79160_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_79171_21 | ACLineSegment | Line | 0.034884 | 0.020832 | 0.020832 | 0.013609 | 59.7191 | 0 | 0 | 0 | 2024-07-16 02:00 | FALSE | 1 | line_79171_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_79176_21 | ACLineSegment | Line | 0.034884 | 0.0057624 | 0.0057624 | 0.0031964 | 16.5189 | 0 | 0 | 0 | 2024-01-21 02:15 | FALSE | 1 | line_79176_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_79159_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_79159_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_79161_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_79161_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_79162_21 | ACLineSegment | Line | 0.034884 | 0.039728 | 0.039728 | 0.026104 | 113.887 | 261 | 21.75 | 0.24775 | 2024-07-16 02:00 | FALSE | 1 | line_79162_21 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_79163_21 | ACLineSegment | Line | 0.034884 | 0.0029912 | 0.0029912 | 0.0016072 | 8.5747 | 0 | 0 | 0 | 2024-01-20 14:50 | FALSE | 1 | line_79163_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_79164_21 | ACLineSegment | Line | 0.034884 | 0.0039508 | 0.0039508 | 0.002335 | 11.3256 | 0 | 0 | 0 | 2024-01-20 23:55 | FALSE | 1 | line_79164_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_79165_21 | ACLineSegment | Line | 0.034884 | 0.0061675 | 0.0061675 | 0.003624 | 17.6804 | 0 | 0 | 0 | 2024-01-20 13:05 | FALSE | 1 | line_79165_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_79173_21 | ACLineSegment | Line | 0.034884 | 0.013174 | 0.013174 | 0.0072097 | 37.7671 | 0 | 0 | 0 | 2024-07-16 02:00 | FALSE | 1 | line_79173_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_79170_21 | ACLineSegment | Line | 0.034884 | 0.018877 | 0.018877 | 0.012015 | 54.1141 | 0 | 0 | 0 | 2024-01-18 02:00 | FALSE | 1 | line_79170_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_79172_21 | ACLineSegment | Line | 0.034884 | 0.0042025 | 0.0042025 | 0.0017567 | 12.0473 | 0 | 0 | 0 | 2024-01-20 05:00 | FALSE | 1 | line_79172_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_79174_21 | ACLineSegment | Line | 0.034884 | 0.0038995 | 0.0038995 | 0.0023162 | 11.1786 | 0 | 0 | 0 | 2024-01-20 21:15 | FALSE | 1 | line_79174_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_79175_21 | ACLineSegment | Line | 0.034884 | 0.0056644 | 0.0056644 | 0.0030404 | 16.2382 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | line_79175_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_88165_21 | ACLineSegment | Line | 0.034884 | 0.022565 | 0.022565 | 0.016562 | 64.6869 | 0 | 0 | 0 | 2024-01-20 08:55 | FALSE | 1 | line_88165_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_88172_21 | ACLineSegment | Line | 0.034884 | 0.022565 | 0.022565 | 0.016562 | 64.6869 | 0 | 0 | 0 | 2024-01-20 08:55 | FALSE | 1 | line_88172_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_89679_21 | ACLineSegment | Line | 0.034884 | 0.018732 | 0.018732 | 0.011476 | 53.6986 | 0 | 0 | 0 | 2024-01-17 15:40 | FALSE | 1 | line_89679_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_89680_21 | ACLineSegment | Line | 0.034884 | 0.013152 | 0.013152 | 0.0082878 | 37.7012 | 0 | 0 | 0 | 2024-01-20 13:05 | FALSE | 1 | line_89680_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_89681_21 | ACLineSegment | Line | 0.034884 | 0.0062593 | 0.0062593 | 0.0034822 | 17.9435 | 0 | 0 | 0 | 2024-07-15 15:50 | FALSE | 1 | line_89681_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_89682_21 | ACLineSegment | Line | 0.034884 | 0.012509 | 0.012509 | 0.0074903 | 35.8595 | 0 | 0 | 0 | 2024-01-20 22:50 | FALSE | 1 | line_89682_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_89683_21 | ACLineSegment | Line | 0.034884 | 0.02838 | 0.02838 | 0.018721 | 81.3579 | 0 | 0 | 0 | 2024-01-20 21:15 | FALSE | 1 | line_89683_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_89693_21 | ACLineSegment | Line | 0.034884 | 0.0085089 | 0.0085089 | 0.0048995 | 24.3923 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_89693_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_89694_21 | ACLineSegment | Line | 0.034884 | 0.0066584 | 0.0066584 | 0.0037631 | 19.0876 | 0 | 0 | 0 | 2024-01-17 15:40 | FALSE | 1 | line_89694_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_89684_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_89684_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_89696_21 | ACLineSegment | Line | 0.034884 | 0.0058768 | 0.0058768 | 0.0029449 | 16.8468 | 0 | 0 | 0 | 2024-01-20 17:05 | FALSE | 1 | line_89696_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_89697_21 | ACLineSegment | Line | 0.034884 | 0.0054921 | 0.0054921 | 0.0025252 | 15.7443 | 0 | 0 | 0 | 2024-01-20 23:55 | FALSE | 1 | line_89697_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_89698_21 | ACLineSegment | Line | 0.034884 | 0.0046558 | 0.0046558 | 0.0025183 | 13.3467 | 0 | 0 | 0 | 2024-01-17 13:10 | FALSE | 1 | line_89698_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_89687_21 | ACLineSegment | Line | 0.034884 | 0.019952 | 0.019952 | 0.013694 | 57.1954 | 0 | 0 | 0 | 2024-01-20 12:00 | FALSE | 1 | line_89687_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_89685_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_89685_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_89686_21 | ACLineSegment | Line | 0.034884 | 0.013312 | 0.013312 | 0.008419 | 38.1604 | 0 | 0 | 0 | 2024-01-20 12:00 | FALSE | 1 | line_89686_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_89688_21 | ACLineSegment | Line | 0.034884 | 0.0054263 | 0.0054263 | 0.0031238 | 15.5554 | 0 | 0 | 0 | 2024-01-17 14:00 | FALSE | 1 | line_89688_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_89689_21 | ACLineSegment | Line | 0.034884 | 0.0045503 | 0.0045503 | 0.0026957 | 13.0442 | 0 | 0 | 0 | 2024-07-15 01:10 | FALSE | 1 | line_89689_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_89691_21 | ACLineSegment | Line | 0.034884 | 0.0080903 | 0.0080903 | 0.0046607 | 23.1923 | 0 | 0 | 0 | 2024-01-21 03:05 | FALSE | 1 | line_89691_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_89702_21 | ACLineSegment | Line | 0.034884 | 0.0064264 | 0.0064264 | 0.0039498 | 18.4225 | 0 | 0 | 0 | 2024-01-20 09:00 | FALSE | 1 | line_89702_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_89690_21 | ACLineSegment | Line | 0.034884 | 0.0060685 | 0.0060685 | 0.0029153 | 17.3965 | 0 | 0 | 0 | 2024-01-21 03:05 | FALSE | 1 | line_89690_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_89692_21 | ACLineSegment | Line | 0.034884 | 0.0038017 | 0.0038017 | 0.0019841 | 10.8982 | 0 | 0 | 0 | 2024-01-20 23:55 | FALSE | 1 | line_89692_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_89695_21 | ACLineSegment | Line | 0.034884 | 0.0060685 | 0.0060685 | 0.0029153 | 17.3965 | 0 | 0 | 0 | 2024-01-21 03:05 | FALSE | 1 | line_89695_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_89699_21 | ACLineSegment | Line | 0.034884 | 0.0061904 | 0.0061904 | 0.003065 | 17.7459 | 0 | 0 | 0 | 2024-01-20 19:55 | FALSE | 1 | line_89699_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_89700_21 | ACLineSegment | Line | 0.034884 | 0.0037274 | 0.0037274 | 0.0021665 | 10.6854 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_89700_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_89701_21 | ACLineSegment | Line | 0.034884 | 0.0066584 | 0.0066584 | 0.0037631 | 19.0876 | 0 | 0 | 0 | 2024-01-17 15:40 | FALSE | 1 | line_89701_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_90312_21 | ACLineSegment | Line | 0.034884 | 0.0066957 | 0.0066957 | 0.0033968 | 19.1945 | 0 | 0 | 0 | 2024-01-20 12:00 | FALSE | 1 | line_90312_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_90314_21 | ACLineSegment | Line | 0.034884 | 0.0049989 | 0.0049989 | 0.0028113 | 14.3303 | 0 | 0 | 0 | 2024-01-20 09:00 | FALSE | 1 | line_90314_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_90315_21 | ACLineSegment | Line | 0.034884 | 0.0066957 | 0.0066957 | 0.0033968 | 19.1945 | 0 | 0 | 0 | 2024-01-20 12:00 | FALSE | 1 | line_90315_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_90317_21 | ACLineSegment | Line | 0.034884 | 0.0048181 | 0.0048181 | 0.0026386 | 13.8118 | 0 | 0 | 0 | 2024-07-15 09:15 | FALSE | 1 | line_90317_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_90820_21 | ACLineSegment | Line | 0.034884 | 0.0047198 | 0.0047198 | 0.002512 | 13.53 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | line_90820_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_90821_21 | ACLineSegment | Line | 0.034884 | 0.0047198 | 0.0047198 | 0.002512 | 13.53 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | line_90821_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_90886_21 | ACLineSegment | Line | 0.034884 | 0.010216 | 0.010216 | 0.0063463 | 29.2848 | 0 | 0 | 0 | 2024-01-20 09:00 | FALSE | 1 | line_90886_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_90887_21 | ACLineSegment | Line | 0.034884 | 0.016988 | 0.016988 | 0.010146 | 48.6994 | 0 | 0 | 0 | 2024-01-20 09:00 | FALSE | 1 | line_90887_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_90888_21 | ACLineSegment | Line | 0.034884 | 0.0047623 | 0.0047623 | 0.0023007 | 13.6521 | 0 | 0 | 0 | 2024-01-20 13:05 | FALSE | 1 | line_90888_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_90889_21 | ACLineSegment | Line | 0.034884 | 0.0035469 | 0.0035469 | 0.0019699 | 10.1679 | 0 | 0 | 0 | 2024-07-16 02:00 | FALSE | 1 | line_90889_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_90899_21 | ACLineSegment | Line | 0.034884 | 0.010216 | 0.010216 | 0.0063463 | 29.2848 | 0 | 0 | 0 | 2024-01-20 09:00 | FALSE | 1 | line_90899_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_90902_21 | ACLineSegment | Line | 0.034884 | 0.019102 | 0.019102 | 0.012324 | 54.7608 | 0 | 0 | 0 | 2024-01-20 09:00 | FALSE | 1 | line_90902_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_90911_21 | ACLineSegment | Line | 0.034884 | 0.004171 | 0.004171 | 0.0023517 | 11.957 | 0 | 0 | 0 | 2024-01-21 03:05 | FALSE | 1 | line_90911_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_90890_21 | ACLineSegment | Line | 0.034884 | 0.010009 | 0.010009 | 0.0051792 | 28.6925 | 0 | 0 | 0 | 2024-01-20 05:00 | FALSE | 1 | line_90890_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_90891_21 | ACLineSegment | Line | 0.034884 | 0.016684 | 0.016684 | 0.0097245 | 47.8278 | 0 | 0 | 0 | 2024-01-20 05:00 | FALSE | 1 | line_90891_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_90892_21 | ACLineSegment | Line | 0.034884 | 0.0084351 | 0.0084351 | 0.0050258 | 24.1809 | 0 | 0 | 0 | 2024-01-20 19:55 | FALSE | 1 | line_90892_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_90901_21 | ACLineSegment | Line | 0.034884 | 0.010009 | 0.010009 | 0.0051792 | 28.6925 | 0 | 0 | 0 | 2024-01-20 05:00 | FALSE | 1 | line_90901_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_90906_21 | ACLineSegment | Line | 0.034884 | 0.021927 | 0.021927 | 0.012531 | 62.859 | 0 | 0 | 0 | 2024-01-20 05:00 | FALSE | 1 | line_90906_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_90907_21 | ACLineSegment | Line | 0.034884 | 0.0056181 | 0.0056181 | 0.0030618 | 16.1054 | 0 | 0 | 0 | 2024-01-17 11:00 | FALSE | 1 | line_90907_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_90896_21 | ACLineSegment | Line | 0.034884 | 0.028189 | 0.028189 | 0.01732 | 80.808 | 0 | 0 | 0 | 2024-01-20 05:00 | FALSE | 1 | line_90896_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_90913_21 | ACLineSegment | Line | 0.034884 | 0.0078312 | 0.0078312 | 0.0036719 | 22.4495 | 0 | 0 | 0 | 2024-01-20 20:20 | FALSE | 1 | line_90913_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_90914_21 | ACLineSegment | Line | 0.034884 | 0.0039432 | 0.0039432 | 0.0019964 | 11.3039 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_90914_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_90908_21 | ACLineSegment | Line | 0.034884 | 0.010216 | 0.010216 | 0.0063463 | 29.2848 | 0 | 0 | 0 | 2024-01-20 09:00 | FALSE | 1 | line_90908_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_90900_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_90900_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_90904_21 | ACLineSegment | Line | 0.034884 | 0.0053927 | 0.0053927 | 0.0028474 | 15.4591 | 0 | 0 | 0 | 2024-01-21 02:15 | FALSE | 1 | line_90904_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_90905_21 | ACLineSegment | Line | 0.034884 | 0.0027956 | 0.0027956 | 0.0017076 | 8.0141 | 0 | 0 | 0 | 2024-01-20 20:20 | FALSE | 1 | line_90905_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_90909_21 | ACLineSegment | Line | 0.034884 | 0.0061703 | 0.0061703 | 0.0036727 | 17.6882 | 0 | 0 | 0 | 2024-01-20 10:55 | FALSE | 1 | line_90909_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_90910_21 | ACLineSegment | Line | 0.034884 | 0.0050495 | 0.0050495 | 0.0029898 | 14.4753 | 0 | 0 | 0 | 2024-01-18 01:55 | FALSE | 1 | line_90910_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_90946_21 | ACLineSegment | Line | 0.034884 | 0.0036429 | 0.0036429 | 0.0020037 | 10.4431 | 0 | 0 | 0 | 2024-01-20 09:00 | FALSE | 1 | line_90946_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_90947_21 | ACLineSegment | Line | 0.034884 | 0.0036429 | 0.0036429 | 0.0020037 | 10.4431 | 0 | 0 | 0 | 2024-01-20 09:00 | FALSE | 1 | line_90947_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_90948_21 | ACLineSegment | Line | 0.034884 | 0.0038617 | 0.0038617 | 0.0023456 | 11.0702 | 0 | 0 | 0 | 2024-01-17 14:00 | FALSE | 1 | line_90948_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_90949_21 | ACLineSegment | Line | 0.034884 | 0.0038617 | 0.0038617 | 0.0023456 | 11.0702 | 0 | 0 | 0 | 2024-01-17 14:00 | FALSE | 1 | line_90949_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_91037_21 | ACLineSegment | Line | 0.034884 | 0.0058819 | 0.0058819 | 0.003293 | 16.8616 | 0 | 0 | 0 | 2024-01-20 17:05 | FALSE | 1 | line_91037_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_91038_21 | ACLineSegment | Line | 0.034884 | 0.0058819 | 0.0058819 | 0.003293 | 16.8616 | 0 | 0 | 0 | 2024-01-20 17:05 | FALSE | 1 | line_91038_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_91043_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_91043_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_91046_21 | ACLineSegment | Line | 0.034884 | 0.012564 | 0.012564 | 0.008133 | 36.0184 | 0 | 0 | 0 | 2024-01-20 05:00 | FALSE | 1 | line_91046_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_91047_21 | ACLineSegment | Line | 0.034884 | 0.0034454 | 0.0034454 | 0.0019794 | 9.8768 | 0 | 0 | 0 | 2024-01-18 01:55 | FALSE | 1 | line_91047_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_91048_21 | ACLineSegment | Line | 0.034884 | 0.0065662 | 0.0065662 | 0.0032885 | 18.8231 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | line_91048_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_91039_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_91039_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_91040_21 | ACLineSegment | Line | 0.034884 | 0.010653 | 0.010653 | 0.0075632 | 30.5389 | 0 | 0 | 0 | 2024-06-29 17:00 | FALSE | 1 | line_91040_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_91041_21 | ACLineSegment | Line | 0.034884 | 0.0055421 | 0.0055421 | 0.0031122 | 15.8874 | 0 | 0 | 0 | 2024-01-20 20:20 | FALSE | 1 | line_91041_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_91042_21 | ACLineSegment | Line | 0.034884 | 0.0091104 | 0.0091104 | 0.0056184 | 26.1167 | 0 | 0 | 0 | 2024-07-07 17:50 | FALSE | 1 | line_91042_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_91044_21 | ACLineSegment | Line | 0.034884 | 0.014003 | 0.014003 | 0.0093624 | 40.141 | 0 | 0 | 0 | 2024-01-20 09:00 | FALSE | 1 | line_91044_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_91045_21 | ACLineSegment | Line | 0.034884 | 0.0048832 | 0.0048832 | 0.002533 | 13.9985 | 0 | 0 | 0 | 2024-01-20 05:00 | FALSE | 1 | line_91045_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_91229_21 | ACLineSegment | Line | 0.034884 | 0.0046054 | 0.0046054 | 0.0027078 | 13.2022 | 0 | 0 | 0 | 2024-01-21 12:20 | FALSE | 1 | line_91229_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_91230_21 | ACLineSegment | Line | 0.034884 | 0.0046054 | 0.0046054 | 0.0027078 | 13.2022 | 0 | 0 | 0 | 2024-01-21 12:20 | FALSE | 1 | line_91230_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_91231_21 | ACLineSegment | Line | 0.034884 | 0.0095802 | 0.0095802 | 0.0060266 | 27.4634 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_91231_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_91232_21 | ACLineSegment | Line | 0.034884 | 0.0066561 | 0.0066561 | 0.0035999 | 19.081 | 0 | 0 | 0 | 2024-01-20 23:55 | FALSE | 1 | line_91232_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_91233_21 | ACLineSegment | Line | 0.034884 | 0.012631 | 0.012631 | 0.0087935 | 36.2096 | 0 | 0 | 0 | 2024-07-14 21:55 | FALSE | 1 | line_91233_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_91234_21 | ACLineSegment | Line | 0.034884 | 0.0045659 | 0.0045659 | 0.0028928 | 13.0891 | 0 | 0 | 0 | 2024-07-14 21:55 | FALSE | 1 | line_91234_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_91247_21 | ACLineSegment | Line | 0.034884 | 0.018188 | 0.018188 | 0.012608 | 52.1402 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_91247_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_91248_21 | ACLineSegment | Line | 0.034884 | 0.0072953 | 0.0072953 | 0.0040368 | 20.9132 | 0 | 0 | 0 | 2024-01-21 01:25 | FALSE | 1 | line_91248_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_91235_21 | ACLineSegment | Line | 0.034884 | 0.0063931 | 0.0063931 | 0.0034713 | 18.327 | 0 | 0 | 0 | 2024-01-17 09:55 | FALSE | 1 | line_91235_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_91236_21 | ACLineSegment | Line | 0.034884 | 0.015776 | 0.015776 | 0.0084385 | 45.2247 | 0 | 0 | 0 | 2024-01-21 03:05 | FALSE | 1 | line_91236_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_91237_21 | ACLineSegment | Line | 0.034884 | 0.0082715 | 0.0082715 | 0.0035375 | 23.7117 | 0 | 0 | 0 | 2024-01-21 03:05 | FALSE | 1 | line_91237_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_91238_21 | ACLineSegment | Line | 0.034884 | 0.0042838 | 0.0042838 | 0.002192 | 12.2803 | 0 | 0 | 0 | 2024-07-16 00:30 | FALSE | 1 | line_91238_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_91246_21 | ACLineSegment | Line | 0.034884 | 0.0063931 | 0.0063931 | 0.0034713 | 18.327 | 0 | 0 | 0 | 2024-01-17 09:55 | FALSE | 1 | line_91246_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_91239_21 | ACLineSegment | Line | 0.034884 | 0.015776 | 0.015776 | 0.0084385 | 45.2247 | 0 | 0 | 0 | 2024-01-21 03:05 | FALSE | 1 | line_91239_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_91240_21 | ACLineSegment | Line | 0.034884 | 0.018463 | 0.018463 | 0.010821 | 52.9265 | 0 | 0 | 0 | 2024-01-20 11:55 | FALSE | 1 | line_91240_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_91241_21 | ACLineSegment | Line | 0.034884 | 0.0047348 | 0.0047348 | 0.0027427 | 13.5731 | 0 | 0 | 0 | 2024-01-20 15:45 | FALSE | 1 | line_91241_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_91340_21 | ACLineSegment | Line | 0.025406 | 0.0065049 | 0.0065049 | 0.0033231 | 25.6041 | 0 | 0 | 0 | 2024-01-20 19:55 | FALSE | 1 | line_91340_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_91895_21 | ACLineSegment | Line | 0.025406 | 0.0042689 | 0.0042689 | 0.0025919 | 16.8029 | 0 | 0 | 0 | 2024-06-26 20:00 | FALSE | 1 | line_91895_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_91896_21 | ACLineSegment | Line | 0.025406 | 0.0071165 | 0.0071165 | 0.0045201 | 28.0115 | 0 | 0 | 0 | 2024-01-17 20:10 | FALSE | 1 | line_91896_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_91897_21 | ACLineSegment | Line | 0.025406 | 0.0038399 | 0.0038399 | 0.0020771 | 15.1142 | 0 | 0 | 0 | 2024-01-20 20:20 | FALSE | 1 | line_91897_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_91898_21 | ACLineSegment | Line | 0.025406 | 0.0042689 | 0.0042689 | 0.0025919 | 16.8029 | 0 | 0 | 0 | 2024-06-26 20:00 | FALSE | 1 | line_91898_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_91899_21 | ACLineSegment | Line | 0.034884 | 0.0064114 | 0.0064114 | 0.0034415 | 18.3794 | 0 | 0 | 0 | 2024-01-17 10:00 | FALSE | 1 | line_91899_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_91900_21 | ACLineSegment | Line | 0.034884 | 0.0064114 | 0.0064114 | 0.0034415 | 18.3794 | 0 | 0 | 0 | 2024-01-17 10:00 | FALSE | 1 | line_91900_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_92680_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_92680_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_92682_21 | ACLineSegment | Line | 0.034884 | 0.015507 | 0.015507 | 0.0093143 | 44.4549 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | line_92682_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_92689_21 | ACLineSegment | Line | 0.034884 | 0.0058584 | 0.0058584 | 0.0032499 | 16.7943 | 0 | 0 | 0 | 2024-01-21 02:15 | FALSE | 1 | line_92689_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_92694_21 | ACLineSegment | Line | 0.034884 | 0.0037392 | 0.0037392 | 0.0021064 | 10.7191 | 0 | 0 | 0 | 2024-01-20 07:25 | FALSE | 1 | line_92694_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_92695_21 | ACLineSegment | Line | 0.034884 | 0.0058121 | 0.0058121 | 0.0030178 | 16.6613 | 0 | 0 | 0 | 2024-01-20 21:15 | FALSE | 1 | line_92695_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_92696_21 | ACLineSegment | Line | 0.034884 | 0.0032897 | 0.0032897 | 0.0015893 | 9.4306 | 0 | 0 | 0 | 2024-07-15 05:55 | FALSE | 1 | line_92696_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_92681_21 | ACLineSegment | Line | 0.034884 | 0.015507 | 0.015507 | 0.0093143 | 44.4549 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | line_92681_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_92692_21 | ACLineSegment | Line | 0.034884 | 0.021136 | 0.021136 | 0.013528 | 60.5897 | 0 | 0 | 0 | 2024-01-20 18:50 | FALSE | 1 | line_92692_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_92693_21 | ACLineSegment | Line | 0.034884 | 0.0087772 | 0.0087772 | 0.0047024 | 25.1616 | 0 | 0 | 0 | 2024-01-17 17:55 | FALSE | 1 | line_92693_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_92683_21 | ACLineSegment | Line | 0.034884 | 0.00729 | 0.00729 | 0.0040876 | 20.8982 | 0 | 0 | 0 | 2024-01-21 01:25 | FALSE | 1 | line_92683_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_92684_21 | ACLineSegment | Line | 0.034884 | 0.017582 | 0.017582 | 0.010781 | 50.4012 | 0 | 0 | 0 | 2024-01-18 | FALSE | 1 | line_92684_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_92685_21 | ACLineSegment | Line | 0.034884 | 0.0066214 | 0.0066214 | 0.0035422 | 18.9816 | 0 | 0 | 0 | 2024-07-16 03:00 | FALSE | 1 | line_92685_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_92686_21 | ACLineSegment | Line | 0.034884 | 0.0086343 | 0.0086343 | 0.0037738 | 24.7517 | 0 | 0 | 0 | 2024-01-20 20:20 | FALSE | 1 | line_92686_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_92687_21 | ACLineSegment | Line | 0.034884 | 0.0040897 | 0.0040897 | 0.0021237 | 11.7238 | 0 | 0 | 0 | 2024-01-21 01:25 | FALSE | 1 | line_92687_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_92688_21 | ACLineSegment | Line | 0.034884 | 0.0038593 | 0.0038593 | 0.0021761 | 11.0634 | 0 | 0 | 0 | 2024-01-20 16:00 | FALSE | 1 | line_92688_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_92691_21 | ACLineSegment | Line | 0.034884 | 0.017582 | 0.017582 | 0.010781 | 50.4012 | 0 | 0 | 0 | 2024-01-18 | FALSE | 1 | line_92691_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_92697_21 | ACLineSegment | Line | 0.034884 | 0.0040897 | 0.0040897 | 0.0021237 | 11.7238 | 0 | 0 | 0 | 2024-01-21 01:25 | FALSE | 1 | line_92697_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_92690_21 | ACLineSegment | Line | 0.034884 | 0.0058584 | 0.0058584 | 0.0032499 | 16.7943 | 0 | 0 | 0 | 2024-01-21 02:15 | FALSE | 1 | line_92690_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_92844_21 | ACLineSegment | Line | 0.034884 | 0.0061986 | 0.0061986 | 0.0035474 | 17.7695 | 0 | 0 | 0 | 2024-01-20 07:25 | FALSE | 1 | line_92844_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_92916_21 | ACLineSegment | Line | 0.034884 | 0.0083973 | 0.0083973 | 0.0052661 | 24.0723 | 0 | 0 | 0 | 2024-01-20 19:55 | FALSE | 1 | line_92916_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_92917_21 | ACLineSegment | Line | 0.034884 | 0.0054909 | 0.0054909 | 0.0033333 | 15.7406 | 0 | 0 | 0 | 2024-01-20 19:55 | FALSE | 1 | line_92917_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_92918_21 | ACLineSegment | Line | 0.034884 | 0.0040216 | 0.0040216 | 0.002079 | 11.5287 | 0 | 0 | 0 | 2024-01-20 11:55 | FALSE | 1 | line_92918_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_92925_21 | ACLineSegment | Line | 0.034884 | 0.0074594 | 0.0074594 | 0.0034245 | 21.3838 | 0 | 0 | 0 | 2024-01-20 09:00 | FALSE | 1 | line_92925_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_92927_21 | ACLineSegment | Line | 0.034884 | 0.0026118 | 0.0026118 | 0.0012851 | 7.4873 | 0 | 0 | 0 | 2024-01-20 16:00 | FALSE | 1 | line_92927_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_92935_21 | ACLineSegment | Line | 0.034884 | 0.0038927 | 0.0038927 | 0.0022023 | 11.1592 | 0 | 0 | 0 | 2024-01-17 10:00 | FALSE | 1 | line_92935_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_92919_21 | ACLineSegment | Line | 0.034884 | 0.009521 | 0.009521 | 0.0053129 | 27.2937 | 0 | 0 | 0 | 2024-01-20 08:55 | FALSE | 1 | line_92919_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_92920_21 | ACLineSegment | Line | 0.034884 | 0.015625 | 0.015625 | 0.0089645 | 44.7919 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_92920_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_92921_21 | ACLineSegment | Line | 0.034884 | 0.0067118 | 0.0067118 | 0.0039699 | 19.2405 | 0 | 0 | 0 | 2024-01-20 21:15 | FALSE | 1 | line_92921_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_92922_21 | ACLineSegment | Line | 0.034884 | 0.0034279 | 0.0034279 | 0.0021327 | 9.8266 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | line_92922_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_92926_21 | ACLineSegment | Line | 0.034884 | 0.0075433 | 0.0075433 | 0.0034006 | 21.6243 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_92926_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_92923_21 | ACLineSegment | Line | 0.034884 | 0.0034279 | 0.0034279 | 0.0021327 | 9.8266 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | line_92923_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_92928_21 | ACLineSegment | Line | 0.034884 | 0.0026118 | 0.0026118 | 0.0012851 | 7.4873 | 0 | 0 | 0 | 2024-01-20 16:00 | FALSE | 1 | line_92928_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_93145_21 | ACLineSegment | Line | 0.034884 | 0.020022 | 0.020022 | 0.011562 | 57.3955 | 0 | 0 | 0 | 2024-01-20 10:55 | FALSE | 1 | line_93145_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_93146_21 | ACLineSegment | Line | 0.034884 | 0.016862 | 0.016862 | 0.0099199 | 48.3375 | 0 | 0 | 0 | 2024-01-17 14:00 | FALSE | 1 | line_93146_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_93147_21 | ACLineSegment | Line | 0.034884 | 0.037831 | 0.037831 | 0.023966 | 108.4489 | 49 | 4.0833 | 0.046513 | 2024-01-20 10:55 | FALSE | 1 | line_93147_21 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_93148_21 | ACLineSegment | Line | 0.034884 | 0.0055397 | 0.0055397 | 0.0031235 | 15.8805 | 0 | 0 | 0 | 2024-01-20 10:55 | FALSE | 1 | line_93148_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_93161_21 | ACLineSegment | Line | 0.034884 | 0.012744 | 0.012744 | 0.0077723 | 36.5317 | 0 | 0 | 0 | 2024-01-20 10:55 | FALSE | 1 | line_93161_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_93171_21 | ACLineSegment | Line | 0.034884 | 0.007278 | 0.007278 | 0.0040581 | 20.8637 | 0 | 0 | 0 | 2024-01-20 10:55 | FALSE | 1 | line_93171_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_93158_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_93158_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_93164_21 | ACLineSegment | Line | 0.034884 | 0.0060718 | 0.0060718 | 0.0033311 | 17.406 | 0 | 0 | 0 | 2024-01-17 14:00 | FALSE | 1 | line_93164_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_93172_21 | ACLineSegment | Line | 0.034884 | 0.0043183 | 0.0043183 | 0.0022697 | 12.3792 | 0 | 0 | 0 | 2024-01-20 09:00 | FALSE | 1 | line_93172_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_93173_21 | ACLineSegment | Line | 0.034884 | 0.0086622 | 0.0086622 | 0.0047556 | 24.8317 | 0 | 0 | 0 | 2024-07-16 03:00 | FALSE | 1 | line_93173_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_93155_21 | ACLineSegment | Line | 0.034884 | 0.025288 | 0.025288 | 0.016066 | 72.494 | 0 | 0 | 0 | 2024-01-21 02:15 | FALSE | 1 | line_93155_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_93149_21 | ACLineSegment | Line | 0.034884 | 0.020836 | 0.020836 | 0.012593 | 59.7291 | 0 | 0 | 0 | 2024-01-21 02:15 | FALSE | 1 | line_93149_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_93150_21 | ACLineSegment | Line | 0.034884 | 0.015678 | 0.015678 | 0.009817 | 44.9435 | 0 | 0 | 0 | 2024-01-21 02:15 | FALSE | 1 | line_93150_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_93151_21 | ACLineSegment | Line | 0.034884 | 0.0053398 | 0.0053398 | 0.0030556 | 15.3076 | 0 | 0 | 0 | 2024-01-17 16:35 | FALSE | 1 | line_93151_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_93156_21 | ACLineSegment | Line | 0.034884 | 0.0059849 | 0.0059849 | 0.0036044 | 17.1567 | 0 | 0 | 0 | 2024-01-18 | FALSE | 1 | line_93156_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_93167_21 | ACLineSegment | Line | 0.034884 | 0.0071679 | 0.0071679 | 0.0041548 | 20.548 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_93167_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_93168_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2024-01-01 05:00 | FALSE | 1 | line_93168_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_93169_21 | ACLineSegment | Line | 0.034884 | 0.006095 | 0.006095 | 0.0026983 | 17.4726 | 0 | 0 | 0 | 2024-01-20 09:00 | FALSE | 1 | line_93169_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_93170_21 | ACLineSegment | Line | 0.034884 | 0.0066487 | 0.0066487 | 0.0033582 | 19.0598 | 0 | 0 | 0 | 2024-01-20 23:55 | FALSE | 1 | line_93170_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_93152_21 | ACLineSegment | Line | 0.034884 | 0.0071679 | 0.0071679 | 0.0041548 | 20.548 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_93152_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_93153_21 | ACLineSegment | Line | 0.034884 | 0.0055787 | 0.0055787 | 0.0026325 | 15.9925 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_93153_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_93154_21 | ACLineSegment | Line | 0.034884 | 0.0029255 | 0.0029255 | 0.0016944 | 8.3865 | 0 | 0 | 0 | 2024-01-20 09:00 | FALSE | 1 | line_93154_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_93159_21 | ACLineSegment | Line | 0.034884 | 0.0048767 | 0.0048767 | 0.0026348 | 13.98 | 0 | 0 | 0 | 2024-01-20 10:55 | FALSE | 1 | line_93159_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_93160_21 | ACLineSegment | Line | 0.034884 | 0.0048767 | 0.0048767 | 0.0026348 | 13.98 | 0 | 0 | 0 | 2024-01-20 10:55 | FALSE | 1 | line_93160_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_93162_21 | ACLineSegment | Line | 0.034884 | 0.0061732 | 0.0061732 | 0.0032991 | 17.6965 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | line_93162_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_93163_21 | ACLineSegment | Line | 0.034884 | 0.0039717 | 0.0039717 | 0.0022285 | 11.3856 | 0 | 0 | 0 | 2024-07-15 18:40 | FALSE | 1 | line_93163_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_93166_21 | ACLineSegment | Line | 0.034884 | 0.0048767 | 0.0048767 | 0.0026348 | 13.98 | 0 | 0 | 0 | 2024-01-20 10:55 | FALSE | 1 | line_93166_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_93165_21 | ACLineSegment | Line | 0.034884 | 0.0060718 | 0.0060718 | 0.0033311 | 17.406 | 0 | 0 | 0 | 2024-01-17 14:00 | FALSE | 1 | line_93165_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_93250_21 | ACLineSegment | Line | 0.034884 | 0.0031107 | 0.0031107 | 0.0017802 | 8.9175 | 0 | 0 | 0 | 2024-01-20 12:00 | FALSE | 1 | line_93250_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_93251_21 | ACLineSegment | Line | 0.034884 | 0.0060998 | 0.0060998 | 0.0037582 | 17.4862 | 0 | 0 | 0 | 2024-01-20 12:00 | FALSE | 1 | line_93251_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_93252_21 | ACLineSegment | Line | 0.034884 | 0.003759 | 0.003759 | 0.0021403 | 10.7758 | 0 | 0 | 0 | 2024-07-15 12:50 | FALSE | 1 | line_93252_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_93257_21 | ACLineSegment | Line | 0.034884 | 0.0031107 | 0.0031107 | 0.0017802 | 8.9175 | 0 | 0 | 0 | 2024-01-20 12:00 | FALSE | 1 | line_93257_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_93262_21 | ACLineSegment | Line | 0.034884 | 0.0047303 | 0.0047303 | 0.0021073 | 13.5603 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | line_93262_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_93253_21 | ACLineSegment | Line | 0.034884 | 0.0062862 | 0.0062862 | 0.003366 | 18.0204 | 0 | 0 | 0 | 2024-01-20 10:55 | FALSE | 1 | line_93253_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_93254_21 | ACLineSegment | Line | 0.034884 | 0.0062862 | 0.0062862 | 0.003366 | 18.0204 | 0 | 0 | 0 | 2024-01-20 10:55 | FALSE | 1 | line_93254_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_93255_21 | ACLineSegment | Line | 0.034884 | 0.0081174 | 0.0081174 | 0.0043314 | 23.27 | 0 | 0 | 0 | 2024-01-20 10:55 | FALSE | 1 | line_93255_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_93256_21 | ACLineSegment | Line | 0.034884 | 0.0022413 | 0.0022413 | 0.0011838 | 6.425 | 0 | 0 | 0 | 2024-01-20 23:55 | FALSE | 1 | line_93256_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_93259_21 | ACLineSegment | Line | 0.034884 | 0.0056164 | 0.0056164 | 0.0031812 | 16.1006 | 0 | 0 | 0 | 2024-01-20 17:05 | FALSE | 1 | line_93259_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_93304_21 | ACLineSegment | Line | 0.034884 | 0.007429 | 0.007429 | 0.0035905 | 21.2967 | 0 | 0 | 0 | 2024-01-20 14:50 | FALSE | 1 | line_93304_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_93305_21 | ACLineSegment | Line | 0.034884 | 0.007429 | 0.007429 | 0.0035905 | 21.2967 | 0 | 0 | 0 | 2024-01-20 14:50 | FALSE | 1 | line_93305_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_93815_21 | ACLineSegment | Line | 0.034884 | 0.0042917 | 0.0042917 | 0.0022555 | 12.303 | 0 | 0 | 0 | 2024-01-20 19:55 | FALSE | 1 | line_93815_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_93816_21 | ACLineSegment | Line | 0.034884 | 0.0042917 | 0.0042917 | 0.0022555 | 12.303 | 0 | 0 | 0 | 2024-01-20 19:55 | FALSE | 1 | line_93816_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_93818_21 | ACLineSegment | Line | 0.034884 | 0.0064769 | 0.0064769 | 0.0036288 | 18.5672 | 0 | 0 | 0 | 2024-01-20 09:00 | FALSE | 1 | line_93818_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_93819_21 | ACLineSegment | Line | 0.034884 | 0.0064769 | 0.0064769 | 0.0036288 | 18.5672 | 0 | 0 | 0 | 2024-01-20 09:00 | FALSE | 1 | line_93819_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_94099_21 | ACLineSegment | Line | 0.034884 | 0.0024698 | 0.0024698 | 0.0014106 | 7.0801 | 0 | 0 | 0 | 2024-01-20 21:15 | FALSE | 1 | line_94099_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_94100_21 | ACLineSegment | Line | 0.034884 | 0.0024698 | 0.0024698 | 0.0014106 | 7.0801 | 0 | 0 | 0 | 2024-01-20 21:15 | FALSE | 1 | line_94100_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_94246_21 | ACLineSegment | Line | 0.034884 | 0.0039715 | 0.0039715 | 0.002124 | 11.385 | 0 | 0 | 0 | 2024-01-20 11:55 | FALSE | 1 | line_94246_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_94247_21 | ACLineSegment | Line | 0.034884 | 0.0039715 | 0.0039715 | 0.002124 | 11.385 | 0 | 0 | 0 | 2024-01-20 11:55 | FALSE | 1 | line_94247_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_94250_21 | ACLineSegment | Line | 0.034884 | 0.0028741 | 0.0028741 | 0.001761 | 8.2391 | 0 | 0 | 0 | 2024-07-14 14:00 | FALSE | 1 | line_94250_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_94251_21 | ACLineSegment | Line | 0.034884 | 0.0028741 | 0.0028741 | 0.001761 | 8.2391 | 0 | 0 | 0 | 2024-07-14 14:00 | FALSE | 1 | line_94251_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_94633_21 | ACLineSegment | Line | 0.034884 | 0.0076716 | 0.0076716 | 0.003968 | 21.9921 | 0 | 0 | 0 | 2024-01-20 10:55 | FALSE | 1 | line_94633_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_94636_21 | ACLineSegment | Line | 0.034884 | 0.0034453 | 0.0034453 | 0.0018088 | 9.8767 | 0 | 0 | 0 | 2024-01-20 10:55 | FALSE | 1 | line_94636_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_94637_21 | ACLineSegment | Line | 0.034884 | 0.0042263 | 0.0042263 | 0.0022679 | 12.1154 | 0 | 0 | 0 | 2024-01-20 10:55 | FALSE | 1 | line_94637_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_94638_21 | ACLineSegment | Line | 0.034884 | 0.0034453 | 0.0034453 | 0.0018088 | 9.8767 | 0 | 0 | 0 | 2024-01-20 10:55 | FALSE | 1 | line_94638_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_94645_21 | ACLineSegment | Line | 0.034884 | 0.0073232 | 0.0073232 | 0.0039603 | 20.9934 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_94645_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_94646_21 | ACLineSegment | Line | 0.034884 | 0.0073232 | 0.0073232 | 0.0039603 | 20.9934 | 0 | 0 | 0 | 2024-01-21 04:00 | FALSE | 1 | line_94646_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_94648_21 | ACLineSegment | Line | 0.034884 | 0.0031558 | 0.0031558 | 0.0019075 | 9.0468 | 0 | 0 | 0 | 2024-07-15 13:05 | FALSE | 1 | line_94648_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_94885_21 | ACLineSegment | Line | 0.034884 | 0.01029 | 0.01029 | 0.0060624 | 29.4985 | 0 | 0 | 0 | 2024-07-05 07:00 | FALSE | 1 | line_94885_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_94886_21 | ACLineSegment | Line | 0.034884 | 0.0044874 | 0.0044874 | 0.0026448 | 12.8641 | 0 | 0 | 0 | 2024-07-05 07:00 | FALSE | 1 | line_94886_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_94887_21 | ACLineSegment | Line | 0.034884 | 0.0058537 | 0.0058537 | 0.003657 | 16.7808 | 0 | 0 | 0 | 2024-01-17 07:00 | FALSE | 1 | line_94887_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_94891_21 | ACLineSegment | Line | 0.034884 | 0.0044874 | 0.0044874 | 0.0026448 | 12.8641 | 0 | 0 | 0 | 2024-07-05 07:00 | FALSE | 1 | line_94891_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_94890_21 | ACLineSegment | Line | 0.034884 | 0.0026991 | 0.0026991 | 0.0015828 | 7.7374 | 0 | 0 | 0 | 2024-01-20 15:45 | FALSE | 1 | line_94890_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_95211_21 | ACLineSegment | Line | 0.034884 | 0.0068395 | 0.0068395 | 0.0041282 | 19.6067 | 0 | 0 | 0 | 2024-07-15 07:55 | FALSE | 1 | line_95211_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_95212_21 | ACLineSegment | Line | 0.034884 | 0.0033002 | 0.0033002 | 0.0018979 | 9.4608 | 0 | 0 | 0 | 2024-01-20 05:00 | FALSE | 1 | line_95212_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_95213_21 | ACLineSegment | Line | 0.034884 | 0.0033002 | 0.0033002 | 0.0018979 | 9.4608 | 0 | 0 | 0 | 2024-01-20 05:00 | FALSE | 1 | line_95213_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_95215_21 | ACLineSegment | Line | 0.034884 | 0.0043734 | 0.0043734 | 0.0024365 | 12.5371 | 0 | 0 | 0 | 2024-01-20 18:50 | FALSE | 1 | line_95215_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_95935_21 | ACLineSegment | Line | 0.034884 | 0.011668 | 0.011668 | 0.0066749 | 33.4487 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | line_95935_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_95936_21 | ACLineSegment | Line | 0.034884 | 0.011668 | 0.011668 | 0.0066749 | 33.4487 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | line_95936_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_95941_21 | ACLineSegment | Line | 0.034884 | 0.0061299 | 0.0061299 | 0.0037371 | 17.5725 | 0 | 0 | 0 | 2024-01-21 19:00 | FALSE | 1 | line_95941_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_95942_21 | ACLineSegment | Line | 0.034884 | 0.0061828 | 0.0061828 | 0.0032998 | 17.7241 | 0 | 0 | 0 | 2024-01-18 04:00 | FALSE | 1 | line_95942_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_95937_21 | ACLineSegment | Line | 0.034884 | 0.0041758 | 0.0041758 | 0.002255 | 11.9706 | 0 | 0 | 0 | 2024-01-20 08:55 | FALSE | 1 | line_95937_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_95938_21 | ACLineSegment | Line | 0.034884 | 0.0041758 | 0.0041758 | 0.002255 | 11.9706 | 0 | 0 | 0 | 2024-01-20 08:55 | FALSE | 1 | line_95938_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_95940_21 | ACLineSegment | Line | 0.034884 | 0.0058335 | 0.0058335 | 0.0031869 | 16.7228 | 0 | 0 | 0 | 2024-01-17 17:55 | FALSE | 1 | line_95940_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_95943_21 | ACLineSegment | Line | 0.034884 | 0.0061299 | 0.0061299 | 0.0037371 | 17.5725 | 0 | 0 | 0 | 2024-01-21 19:00 | FALSE | 1 | line_95943_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_96379_21 | ACLineSegment | Line | 0.034884 | 0.0051893 | 0.0051893 | 0.002521 | 14.8761 | 0 | 0 | 0 | 2024-01-20 09:00 | FALSE | 1 | line_96379_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_96700_21 | ACLineSegment | Line | 0.034884 | 0.0062342 | 0.0062342 | 0.0034173 | 17.8714 | 0 | 0 | 0 | 2024-01-17 17:55 | FALSE | 1 | line_96700_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_96701_21 | ACLineSegment | Line | 0.034884 | 0.0062342 | 0.0062342 | 0.0034173 | 17.8714 | 0 | 0 | 0 | 2024-01-17 17:55 | FALSE | 1 | line_96701_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_96702_21 | ACLineSegment | Line | 0.034884 | 0.0057341 | 0.0057341 | 0.0030354 | 16.4379 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | line_96702_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_96703_21 | ACLineSegment | Line | 0.034884 | 0.0057341 | 0.0057341 | 0.0030354 | 16.4379 | 0 | 0 | 0 | 2024-01-21 | FALSE | 1 | line_96703_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_18 | line_96864_21 | ACLineSegment | Line | 0.034884 | 0.0049637 | 0.0049637 | 0.0025986 | 14.2294 | 0 | 0 | 0 | 2024-01-17 19:55 | FALSE | 1 | line_96864_21 | 1Phase_VLN_I_x_PF | No modeled rating exceedance
GSO_127 | line_6871_22 | ACLineSegment | Line | 13.5424 | 0.025212 | 0.025212 | 0.016656 | 0.18617 | 0 | 0 | 0 | 2024-01-20 21:00 | TRUE | 1 | line_6871_22 | 3Phase_sqrt3_VLL_I_x_PF | No modeled rating exceedance

## Baseline_Exceedances
GridID | GridElementID | ElementType | ElementClass | CapacityMW_BasePF | PeakExistingAbsMW | PeakExistingSignedMW | P95ExistingAbsMW | PeakUtilizationPct | RatingExceedanceIntervals | RatingExceedanceHoursEquivalent | RatingExceedancePctIntervals | PeakTimestampUTC | OnSelectedCandidatePath | ParallelElementCount | ParallelElementIDs | CapacityMethod | AuditInterpretation
GSO_123 | tr_1402_22 | Transformer | Transformer | 0.02375 | 0.026622 | 0.026622 | 0.021056 | 112.0922 | 863 | 71.9167 | 0.81919 | 2024-01-17 22:25 | FALSE | 1 | tr_1402_22 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_121 | line_6053_22 | ACLineSegment | Line | 0.025406 | 0.036599 | 0.036599 | 0.022557 | 144.0575 | 3054 | 254.5 | 2.899 | 2024-07-05 23:05 | FALSE | 1 | line_6053_22 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_121 | tr_1094_22 | Transformer | Transformer | 0.02375 | 0.036599 | 0.036599 | 0.022557 | 154.1004 | 4046 | 337.1667 | 3.8406 | 2024-07-05 23:05 | FALSE | 1 | tr_1094_22 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_144 | line_283_22 | ACLineSegment | Line | 0.025406 | 0.031335 | 0.031335 | 0.019196 | 123.3377 | 184 | 15.3333 | 0.17466 | 2024-01-20 06:05 | FALSE | 1 | line_283_22 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_144 | line_289_22 | ACLineSegment | Line | 0.038174 | 0.041391 | 0.041391 | 0.02691 | 108.4263 | 11 | 0.91667 | 0.010442 | 2024-01-20 06:05 | FALSE | 1 | line_289_22 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_141 | line_2644_22 | ACLineSegment | Line | 0.034884 | 0.039198 | 0.039198 | 0.025568 | 112.3694 | 106 | 8.8333 | 0.10062 | 2024-01-20 14:00 | FALSE | 1 | line_2644_22 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_141 | line_2822_22 | ACLineSegment | Line | 0.034884 | 0.069344 | 0.069344 | 0.046454 | 198.7868 | 24088 | 2007.3333 | 22.8652 | 2024-01-20 14:00 | FALSE | 1 | line_2822_22 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_141 | tr_815_22 | Transformer | Transformer | 0.0475 | 0.072525 | 0.072525 | 0.049025 | 152.6847 | 6385 | 532.0833 | 6.0609 | 2024-01-20 19:05 | FALSE | 1 | tr_815_22 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_145 | line_5274_22 | ACLineSegment | Line | 0.034884 | 0.035834 | 0.035834 | 0.022146 | 102.7257 | 6 | 0.5 | 0.0056954 | 2024-01-17 23:00 | FALSE | 1 | line_5274_22 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_145 | line_2887_22 | ACLineSegment | Line | 0.046073 | 0.056556 | 0.056556 | 0.037052 | 122.7542 | 553 | 46.0833 | 0.52493 | 2024-01-20 11:05 | FALSE | 1 | line_2887_22 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_145 | tr_724_22 | Transformer | Transformer | 0.0475 | 0.056556 | 0.056556 | 0.037052 | 119.0653 | 302 | 25.1667 | 0.28667 | 2024-01-20 11:05 | FALSE | 1 | tr_724_22 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_145 | tr_751_22 | Transformer | Transformer | 0.0475 | 0.0546 | 0.0546 | 0.035167 | 114.9464 | 104 | 8.6667 | 0.09872 | 2024-01-21 03:55 | FALSE | 1 | tr_751_22 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_142 | line_1699_22 | ACLineSegment | Line | 0.025406 | 0.02849 | 0.02849 | 0.018583 | 112.1413 | 98 | 8.1667 | 0.093025 | 2024-01-22 04:00 | FALSE | 1 | line_1699_22 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_142 | line_1700_22 | ACLineSegment | Line | 0.025406 | 0.02849 | 0.02849 | 0.018583 | 112.1413 | 98 | 8.1667 | 0.093025 | 2024-01-22 04:00 | FALSE | 1 | line_1700_22 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_142 | line_1701_22 | ACLineSegment | Line | 0.025406 | 0.02849 | 0.02849 | 0.018583 | 112.1413 | 98 | 8.1667 | 0.093025 | 2024-01-22 04:00 | FALSE | 1 | line_1701_22 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_142 | tr_273_22 | Transformer | Transformer | 0.02375 | 0.030493 | 0.030493 | 0.019869 | 128.3925 | 678 | 56.5 | 0.64358 | 2024-01-22 04:00 | FALSE | 1 | tr_273_22 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_142 | tr_627_22 | Transformer | Transformer | 0.02375 | 0.023833 | 0.023833 | 0.017708 | 100.3493 | 1 | 0.083333 | 0.00094923 | 2024-01-20 19:55 | FALSE | 1 | tr_627_22 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_142 | tr_15_22 | Transformer | Transformer | 0.02375 | 0.033574 | 0.033574 | 0.019446 | 141.3628 | 708 | 59 | 0.67206 | 2024-01-20 19:55 | FALSE | 1 | tr_15_22 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_142 | tr_767_22 | Transformer | Transformer | 0.02375 | 0.02619 | 0.02619 | 0.01763 | 110.2736 | 61 | 5.0833 | 0.057903 | 2024-01-20 10:00 | FALSE | 1 | tr_767_22 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | tr_833_21 | Transformer | Transformer | 0.02375 | 0.025146 | 0.025146 | 0.014511 | 105.8766 | 12 | 1 | 0.011391 | 2024-01-20 10:55 | FALSE | 1 | tr_833_21 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | tr_77_21 | Transformer | Transformer | 0.02375 | 0.024146 | 0.024146 | 0.014961 | 101.6686 | 12 | 1 | 0.011391 | 2024-01-20 12:00 | FALSE | 1 | tr_77_21 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | tr_3798_21 | Transformer | Transformer | 0.0475 | 0.057114 | 0.057114 | 0.035029 | 120.2408 | 125 | 10.4167 | 0.11865 | 2024-01-20 15:45 | FALSE | 1 | tr_3798_21 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | tr_256_21 | Transformer | Transformer | 0.0475 | 0.051668 | 0.051668 | 0.035518 | 108.7739 | 144 | 12 | 0.13669 | 2024-01-20 06:55 | FALSE | 1 | tr_256_21 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | tr_274_21 | Transformer | Transformer | 0.02375 | 0.024268 | 0.024268 | 0.016703 | 102.1794 | 19 | 1.5833 | 0.018035 | 2024-01-20 09:00 | FALSE | 1 | tr_274_21 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | tr_3954_21 | Transformer | Transformer | 0.0475 | 0.060853 | 0.060853 | 0.041897 | 128.1108 | 1352 | 112.6667 | 1.2834 | 2024-01-21 01:25 | FALSE | 1 | tr_3954_21 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | tr_316_21 | Transformer | Transformer | 0.02375 | 0.033424 | 0.033424 | 0.022958 | 140.7332 | 4109 | 342.4167 | 3.9004 | 2024-01-21 03:05 | FALSE | 1 | tr_316_21 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | tr_9936_21 | Transformer | Transformer | 0.02375 | 0.041982 | 0.041982 | 0.026938 | 176.7671 | 11154 | 929.5 | 10.5878 | 2024-01-17 08:10 | FALSE | 1 | tr_9936_21 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | tr_9123_21 | Transformer | Transformer | 0.0475 | 0.050634 | 0.050634 | 0.034461 | 106.597 | 34 | 2.8333 | 0.032274 | 2024-01-18 04:00 | FALSE | 1 | tr_9123_21 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | tr_767_21 | Transformer | Transformer | 0.02375 | 0.036561 | 0.036561 | 0.024036 | 153.9425 | 5862 | 488.5 | 5.5644 | 2024-01-21 01:25 | FALSE | 1 | tr_767_21 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | tr_3910_21 | Transformer | Transformer | 0.0475 | 0.08436 | 0.08436 | 0.058206 | 177.601 | 17316 | 1443 | 16.437 | 2024-01-21 03:05 | FALSE | 1 | tr_3910_21 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | tr_828_21 | Transformer | Transformer | 0.0475 | 0.060853 | 0.060853 | 0.039944 | 128.1125 | 959 | 79.9167 | 0.91032 | 2024-01-20 23:55 | FALSE | 1 | tr_828_21 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | tr_9205_21 | Transformer | Transformer | 0.0475 | 0.0885 | 0.0885 | 0.06224 | 186.3155 | 22209 | 1850.75 | 21.0816 | 2024-01-20 13:05 | FALSE | 1 | tr_9205_21 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | tr_6998_21 | Transformer | Transformer | 0.02375 | 0.024021 | 0.024021 | 0.016282 | 101.1394 | 23 | 1.9167 | 0.021832 | 2024-01-17 20:10 | FALSE | 1 | tr_6998_21 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | tr_3877_21 | Transformer | Transformer | 0.0475 | 0.061222 | 0.061222 | 0.041863 | 128.8889 | 1392 | 116 | 1.3213 | 2024-01-21 01:25 | FALSE | 1 | tr_3877_21 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | tr_10625_21 | Transformer | Transformer | 0.0475 | 0.07605 | 0.07605 | 0.04861 | 160.1053 | 6226 | 518.8333 | 5.9099 | 2024-01-20 21:15 | FALSE | 1 | tr_10625_21 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | tr_3780_21 | Transformer | Transformer | 0.0475 | 0.05818 | 0.05818 | 0.039578 | 122.4833 | 675 | 56.25 | 0.64073 | 2024-01-21 03:05 | FALSE | 1 | tr_3780_21 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | tr_3871_21 | Transformer | Transformer | 0.0475 | 0.056751 | 0.056751 | 0.038156 | 119.4765 | 450 | 37.5 | 0.42716 | 2024-01-20 13:05 | FALSE | 1 | tr_3871_21 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | tr_3794_21 | Transformer | Transformer | 0.0475 | 0.065034 | 0.065034 | 0.045173 | 136.9137 | 3564 | 297 | 3.3831 | 2024-01-21 | FALSE | 1 | tr_3794_21 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | tr_9252_21 | Transformer | Transformer | 0.0475 | 0.048486 | 0.048486 | 0.032591 | 102.0757 | 24 | 2 | 0.022782 | 2024-01-21 01:25 | FALSE | 1 | tr_9252_21 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | tr_3831_21 | Transformer | Transformer | 0.0475 | 0.062919 | 0.062919 | 0.045891 | 132.461 | 3891 | 324.25 | 3.6935 | 2024-01-21 01:25 | FALSE | 1 | tr_3831_21 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | tr_12320_21 | Transformer | Transformer | 0.02375 | 0.030329 | 0.030329 | 0.020517 | 127.701 | 761 | 63.4167 | 0.72237 | 2024-01-20 09:00 | FALSE | 1 | tr_12320_21 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | tr_1963_21 | Transformer | Transformer | 0.02375 | 0.026098 | 0.026098 | 0.015959 | 109.8869 | 17 | 1.4167 | 0.016137 | 2024-01-18 04:00 | FALSE | 1 | tr_1963_21 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | tr_9993_21 | Transformer | Transformer | 0.0475 | 0.078082 | 0.078082 | 0.05397 | 164.3832 | 10652 | 887.6667 | 10.1113 | 2024-01-20 07:25 | FALSE | 1 | tr_9993_21 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | tr_5945_21 | Transformer | Transformer | 0.0475 | 0.079363 | 0.079363 | 0.050983 | 167.0804 | 7941 | 661.75 | 7.5379 | 2024-01-20 15:45 | FALSE | 1 | tr_5945_21 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_25057_21 | ACLineSegment | Line | 0.034884 | 0.036523 | 0.036523 | 0.024802 | 104.7001 | 36 | 3 | 0.034172 | 2024-01-20 23:55 | FALSE | 1 | line_25057_21 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_25835_21 | ACLineSegment | Line | 0.034884 | 0.03586 | 0.03586 | 0.022969 | 102.8001 | 12 | 1 | 0.011391 | 2024-01-20 11:55 | FALSE | 1 | line_25835_21 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_16390_21 | ACLineSegment | Line | 0.034884 | 0.037463 | 0.037463 | 0.024419 | 107.3934 | 50 | 4.1667 | 0.047462 | 2024-01-18 04:00 | FALSE | 1 | line_16390_21 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_16422_21 | ACLineSegment | Line | 0.034884 | 0.041322 | 0.041322 | 0.027875 | 118.456 | 334 | 27.8333 | 0.31704 | 2024-01-20 11:55 | FALSE | 1 | line_16422_21 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | tr_6973_21 | Transformer | Transformer | 0.0475 | 0.081895 | 0.081895 | 0.055125 | 172.4098 | 12667 | 1055.5833 | 12.024 | 2024-01-20 11:55 | FALSE | 1 | tr_6973_21 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | tr_6975_21 | Transformer | Transformer | 0.02375 | 0.023777 | 0.023777 | 0.014239 | 100.1126 | 2 | 0.16667 | 0.0018985 | 2024-01-18 01:55 | FALSE | 1 | tr_6975_21 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_55496_21 | ACLineSegment | Line | 0.034884 | 0.048271 | 0.048271 | 0.030517 | 138.3767 | 1526 | 127.1667 | 1.4485 | 2024-01-20 11:55 | FALSE | 1 | line_55496_21 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | tr_8999_21 | Transformer | Transformer | 0.02375 | 0.035246 | 0.035246 | 0.022835 | 148.4034 | 4043 | 336.9167 | 3.8378 | 2024-01-21 | FALSE | 1 | tr_8999_21 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_69062_21 | ACLineSegment | Line | 0.034884 | 0.043934 | 0.043934 | 0.029778 | 125.9461 | 1220 | 101.6667 | 1.1581 | 2024-01-21 03:05 | FALSE | 1 | line_69062_21 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_69078_21 | ACLineSegment | Line | 0.034884 | 0.039349 | 0.039349 | 0.026998 | 112.8016 | 204 | 17 | 0.19364 | 2024-01-20 22:50 | FALSE | 1 | line_69078_21 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | tr_9773_21 | Transformer | Transformer | 0.0475 | 0.075483 | 0.075483 | 0.048809 | 158.912 | 6577 | 548.0833 | 6.2431 | 2024-01-21 03:05 | FALSE | 1 | tr_9773_21 | Transformer_kVA_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_73276_21 | ACLineSegment | Line | 0.046073 | 0.072106 | 0.072106 | 0.045966 | 156.5042 | 5170 | 430.8333 | 4.9075 | 2024-01-21 03:05 | FALSE | 1 | line_73276_21 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_72176_21 | ACLineSegment | Line | 0.034884 | 0.037081 | 0.037081 | 0.023251 | 106.2985 | 35 | 2.9167 | 0.033223 | 2024-01-17 08:10 | FALSE | 1 | line_72176_21 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_75394_21 | ACLineSegment | Line | 0.034884 | 0.042609 | 0.042609 | 0.027758 | 122.1475 | 530 | 44.1667 | 0.50309 | 2024-01-20 23:55 | FALSE | 1 | line_75394_21 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_16397_21 | ACLineSegment | Line | 0.034884 | 0.041322 | 0.041322 | 0.027875 | 118.456 | 334 | 27.8333 | 0.31704 | 2024-01-20 11:55 | FALSE | 1 | line_16397_21 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_25828_21 | ACLineSegment | Line | 0.034884 | 0.03586 | 0.03586 | 0.022969 | 102.8001 | 12 | 1 | 0.011391 | 2024-01-20 11:55 | FALSE | 1 | line_25828_21 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_45225_21 | ACLineSegment | Line | 0.046073 | 0.066782 | 0.066782 | 0.044115 | 144.9488 | 3415 | 284.5833 | 3.2416 | 2024-01-20 15:45 | FALSE | 1 | line_45225_21 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_45227_21 | ACLineSegment | Line | 0.046073 | 0.079363 | 0.079363 | 0.050983 | 172.2569 | 9264 | 772 | 8.7937 | 2024-01-20 15:45 | FALSE | 1 | line_45227_21 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_45240_21 | ACLineSegment | Line | 0.034884 | 0.039657 | 0.039657 | 0.025168 | 113.6849 | 97 | 8.0833 | 0.092076 | 2024-01-20 15:45 | FALSE | 1 | line_45240_21 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_45239_21 | ACLineSegment | Line | 0.034884 | 0.036541 | 0.036541 | 0.022901 | 104.7518 | 18 | 1.5 | 0.017086 | 2024-01-20 15:45 | FALSE | 1 | line_45239_21 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_55488_21 | ACLineSegment | Line | 0.034884 | 0.048271 | 0.048271 | 0.030517 | 138.3767 | 1526 | 127.1667 | 1.4485 | 2024-01-20 11:55 | FALSE | 1 | line_55488_21 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_69057_21 | ACLineSegment | Line | 0.034884 | 0.038618 | 0.038618 | 0.025481 | 110.7044 | 147 | 12.25 | 0.13954 | 2024-01-20 07:25 | FALSE | 1 | line_69057_21 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_69077_21 | ACLineSegment | Line | 0.034884 | 0.039349 | 0.039349 | 0.026998 | 112.8016 | 204 | 17 | 0.19364 | 2024-01-20 22:50 | FALSE | 1 | line_69077_21 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_69097_21 | ACLineSegment | Line | 0.034884 | 0.03673 | 0.03673 | 0.02473 | 105.2926 | 28 | 2.3333 | 0.026579 | 2024-01-20 22:50 | FALSE | 1 | line_69097_21 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_73247_21 | ACLineSegment | Line | 0.034884 | 0.050399 | 0.050399 | 0.032142 | 144.4782 | 2455 | 204.5833 | 2.3304 | 2024-01-21 03:05 | FALSE | 1 | line_73247_21 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_75385_21 | ACLineSegment | Line | 0.034884 | 0.035452 | 0.035452 | 0.022061 | 101.6297 | 9 | 0.75 | 0.0085431 | 2024-01-20 13:05 | FALSE | 1 | line_75385_21 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_75392_21 | ACLineSegment | Line | 0.034884 | 0.040228 | 0.040228 | 0.025511 | 115.3209 | 181 | 15.0833 | 0.17181 | 2024-01-20 13:05 | FALSE | 1 | line_75392_21 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_79177_21 | ACLineSegment | Line | 0.034884 | 0.036887 | 0.036887 | 0.0228 | 105.7434 | 43 | 3.5833 | 0.040817 | 2024-01-17 09:55 | FALSE | 1 | line_79177_21 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_79162_21 | ACLineSegment | Line | 0.034884 | 0.039728 | 0.039728 | 0.026104 | 113.887 | 261 | 21.75 | 0.24775 | 2024-07-16 02:00 | FALSE | 1 | line_79162_21 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating
GSO_18 | line_93147_21 | ACLineSegment | Line | 0.034884 | 0.037831 | 0.037831 | 0.023966 | 108.4489 | 49 | 4.0833 | 0.046513 | 2024-01-20 10:55 | FALSE | 1 | line_93147_21 | 1Phase_VLN_I_x_PF | Modeled existing absolute flow exceeds PF-adjusted equipment rating

## Meter_Mapping
MeterID | LoadNode | MappingMethod | Resolved | Depth | GridID
m_1106_22 | UCLV3658 | DirectTerminal | TRUE | 4 | GSO_122
m_1367_22 | UCLV41356 | DirectTerminal | TRUE | 5 | GSO_122
m_2721_22 | UCMV107 | DirectTerminal | TRUE | 4 | GSO_122
m_1116_22 | UCLV3664 | DirectTerminal | TRUE | 8 | GSO_124
m_1211_22 | UCLV38205 | DirectTerminal | TRUE | 8 | GSO_124
m_1381_22 | UCLV41634 | DirectTerminal | TRUE | 10 | GSO_124
m_1526_22 | UCLV45022 | DirectTerminal | TRUE | 10 | GSO_124
m_2747_22 | UCMV3 | DirectTerminal | TRUE | 5 | GSO_124
m_2752_22 | UCMV4 | DirectTerminal | TRUE | 7 | GSO_124
m_366_22 | UCLV15395 | DirectTerminal | TRUE | 7 | GSO_124
m_398_22 | UCLV16891 | DirectTerminal | TRUE | 8 | GSO_124
m_402_22 | UCLV17000 | DirectTerminal | TRUE | 7 | GSO_124
m_424_22 | UCLV18505 | DirectTerminal | TRUE | 5 | GSO_124
m_601_22 | UCLV22029 | DirectTerminal | TRUE | 9 | GSO_124
m_604_22 | UCLV22140 | DirectTerminal | TRUE | 6 | GSO_124
m_665_22 | UCLV25683 | DirectTerminal | TRUE | 4 | GSO_124
m_703_22 | UCLV27473 | DirectTerminal | TRUE | 6 | GSO_124
m_750_22 | UCLV28844 | DirectTerminal | TRUE | 10 | GSO_124
m_876_22 | UCLV31459 | DirectTerminal | TRUE | 11 | GSO_124
m_1012_22 | UCLV34590 | DirectTerminal | TRUE | 33 | GSO_123
m_1015_22 | UCLV34767 | DirectTerminal | TRUE | 16 | GSO_123
m_1084_22 | UCLV36123 | DirectTerminal | TRUE | 29 | GSO_123
m_1208_22 | UCLV38132 | DirectTerminal | TRUE | 30 | GSO_123
m_1267_22 | UCLV39302 | DirectTerminal | TRUE | 11 | GSO_123
m_1277_22 | UCLV39521 | DirectTerminal | TRUE | 30 | GSO_123
m_1356_22 | UCLV41172 | DirectTerminal | TRUE | 6 | GSO_123
m_1426_22 | UCLV42881 | DirectTerminal | TRUE | 13 | GSO_123
m_1480_22 | UCLV43729 | DirectTerminal | TRUE | 18 | GSO_123
m_15_22 | UCLV10014 | DirectTerminal | TRUE | 19 | GSO_123
m_1522_22 | UCLV44974 | DirectTerminal | TRUE | 10 | GSO_123
m_1546_22 | UCLV45381 | DirectTerminal | TRUE | 7 | GSO_123
m_1607_22 | UCLV46893 | DirectTerminal | TRUE | 8 | GSO_123
m_1617_22 | UCLV47101 | DirectTerminal | TRUE | 15 | GSO_123
m_1656_22 | UCLV48193 | DirectTerminal | TRUE | 17 | GSO_123
m_17_22 | UCLV10016 | DirectTerminal | TRUE | 32 | GSO_123
m_1740_22 | UCLV50250 | DirectTerminal | TRUE | 8 | GSO_123
m_1794_22 | UCLV51732 | DirectTerminal | TRUE | 5 | GSO_123
m_2_22 | UCLV10001 | DirectTerminal | TRUE | 5 | GSO_123
m_2746_22 | UCMV29 | DirectTerminal | TRUE | 32 | GSO_123
m_2756_22 | UCMV44 | DirectTerminal | TRUE | 18 | GSO_123
m_3_22 | UCLV10002 | DirectTerminal | TRUE | 20 | GSO_123
m_333_22 | UCLV14278 | DirectTerminal | TRUE | 25 | GSO_123
m_352_22 | UCLV14935 | DirectTerminal | TRUE | 22 | GSO_123
m_356_22 | UCLV15061 | DirectTerminal | TRUE | 14 | GSO_123
m_378_22 | UCLV16140 | DirectTerminal | TRUE | 13 | GSO_123
m_387_22 | UCLV16433 | DirectTerminal | TRUE | 25 | GSO_123
m_400_22 | UCLV16952 | DirectTerminal | TRUE | 30 | GSO_123
m_413_22 | UCLV17927 | DirectTerminal | TRUE | 28 | GSO_123
m_490_22 | UCLV19534 | DirectTerminal | TRUE | 24 | GSO_123
m_492_22 | UCLV19668 | DirectTerminal | TRUE | 18 | GSO_123
m_513_22 | UCLV20406 | DirectTerminal | TRUE | 34 | GSO_123
m_591_22 | UCLV21679 | DirectTerminal | TRUE | 21 | GSO_123
m_607_22 | UCLV22235 | DirectTerminal | TRUE | 22 | GSO_123
m_613_22 | UCLV23074 | DirectTerminal | TRUE | 27 | GSO_123
m_617_22 | UCLV23193 | DirectTerminal | TRUE | 26 | GSO_123
m_651_22 | UCLV25207 | DirectTerminal | TRUE | 24 | GSO_123
m_680_22 | UCLV26611 | DirectTerminal | TRUE | 23 | GSO_123
m_687_22 | UCLV26786 | DirectTerminal | TRUE | 31 | GSO_123
m_698_22 | UCLV27349 | DirectTerminal | TRUE | 33 | GSO_123
m_777_22 | UCLV29355 | DirectTerminal | TRUE | 32 | GSO_123
m_786_22 | UCLV29520 | DirectTerminal | TRUE | 19 | GSO_123
m_845_22 | UCLV30689 | DirectTerminal | TRUE | 9 | GSO_123
m_855_22 | UCLV30966 | DirectTerminal | TRUE | 30 | GSO_123
m_862_22 | UCLV31179 | DirectTerminal | TRUE | 4 | GSO_123
m_933_22 | UCLV33018 | DirectTerminal | TRUE | 28 | GSO_123
m_941_22 | UCLV33278 | DirectTerminal | TRUE | 18 | GSO_123
m_1021_22 | UCLV34991 | DirectTerminal | TRUE | 16 | GSO_121
m_1040_22 | UCLV35370 | DirectTerminal | TRUE | 10 | GSO_121
m_1064_22 | UCLV35751 | DirectTerminal | TRUE | 8 | GSO_121
m_1075_22 | UCLV35980 | DirectTerminal | TRUE | 21 | GSO_121
m_1096_22 | UCLV36504 | DirectTerminal | TRUE | 14 | GSO_121
m_1103_22 | UCLV3657 | DirectTerminal | TRUE | 4 | GSO_121
m_1107_22 | UCLV3659 | DirectTerminal | TRUE | 25 | GSO_121
m_1108_22 | UCLV3660 | DirectTerminal | TRUE | 10 | GSO_121
m_1110_22 | UCLV3661 | DirectTerminal | TRUE | 10 | GSO_121
m_1111_22 | UCLV3662 | DirectTerminal | TRUE | 14 | GSO_121
m_1114_22 | UCLV3663 | DirectTerminal | TRUE | 18 | GSO_121
m_1118_22 | UCLV3665 | DirectTerminal | TRUE | 22 | GSO_121
m_1119_22 | UCLV3666 | DirectTerminal | TRUE | 22 | GSO_121
m_1120_22 | UCLV3667 | DirectTerminal | TRUE | 25 | GSO_121
m_1121_22 | UCLV3668 | DirectTerminal | TRUE | 22 | GSO_121
m_1122_22 | UCLV3669 | DirectTerminal | TRUE | 23 | GSO_121
m_1170_22 | UCLV37219 | DirectTerminal | TRUE | 39 | GSO_121
m_1174_22 | UCLV37292 | DirectTerminal | TRUE | 16 | GSO_121
m_1195_22 | UCLV37615 | DirectTerminal | TRUE | 5 | GSO_121
m_1199_22 | UCLV37686 | DirectTerminal | TRUE | 12 | GSO_121
m_1215_22 | UCLV38319 | DirectTerminal | TRUE | 30 | GSO_121
m_1_22 | UCLV10000 | DirectTerminal | TRUE | 10 | GSO_121
m_1234_22 | UCLV38703 | DirectTerminal | TRUE | 10 | GSO_121
m_1256_22 | UCLV39080 | DirectTerminal | TRUE | 8 | GSO_121
m_1258_22 | UCLV39144 | DirectTerminal | TRUE | 13 | GSO_121
m_1297_22 | UCLV39995 | DirectTerminal | TRUE | 13 | GSO_121
m_1317_22 | UCLV40371 | DirectTerminal | TRUE | 27 | GSO_121
m_1335_22 | UCLV40839 | DirectTerminal | TRUE | 18 | GSO_121
m_1347_22 | UCLV41019 | DirectTerminal | TRUE | 23 | GSO_121
m_1449_22 | UCLV43242 | DirectTerminal | TRUE | 38 | GSO_121
m_1464_22 | UCLV43504 | DirectTerminal | TRUE | 20 | GSO_121
m_1466_22 | UCLV43514 | DirectTerminal | TRUE | 12 | GSO_121
m_1544_22 | UCLV45368 | DirectTerminal | TRUE | 27 | GSO_121
m_1582_22 | UCLV46490 | DirectTerminal | TRUE | 27 | GSO_121
m_1590_22 | UCLV46632 | DirectTerminal | TRUE | 35 | GSO_121
m_1605_22 | UCLV46875 | DirectTerminal | TRUE | 25 | GSO_121
m_1652_22 | UCLV48119 | DirectTerminal | TRUE | 29 | GSO_121
m_1665_22 | UCLV48349 | DirectTerminal | TRUE | 16 | GSO_121
m_1686_22 | UCLV48743 | DirectTerminal | TRUE | 26 | GSO_121
m_1715_22 | UCLV49838 | DirectTerminal | TRUE | 17 | GSO_121
m_1724_22 | UCLV49986 | DirectTerminal | TRUE | 33 | GSO_121
m_1731_22 | UCLV50132 | DirectTerminal | TRUE | 25 | GSO_121
m_1738_22 | UCLV50231 | DirectTerminal | TRUE | 27 | GSO_121
m_1784_22 | UCLV51585 | DirectTerminal | TRUE | 15 | GSO_121
m_1813_22 | UCLV52061 | DirectTerminal | TRUE | 20 | GSO_121
m_1818_22 | UCLV52142 | DirectTerminal | TRUE | 29 | GSO_121
m_1820_22 | UCLV52158 | DirectTerminal | TRUE | 15 | GSO_121
m_1867_22 | UCLV53393 | DirectTerminal | TRUE | 27 | GSO_121
m_1869_22 | UCLV53413 | DirectTerminal | TRUE | 25 | GSO_121
m_1881_22 | UCLV53727 | DirectTerminal | TRUE | 20 | GSO_121
m_2785_22 | UCMV81 | DirectTerminal | TRUE | 9 | GSO_121
m_2793_22 | UCMV95 | DirectTerminal | TRUE | 5 | GSO_121
m_708_22 | UCLV27653 | DirectTerminal | TRUE | 18 | GSO_121
m_716_22 | UCLV27775 | DirectTerminal | TRUE | 29 | GSO_121
m_719_22 | UCLV27999 | DirectTerminal | TRUE | 24 | GSO_121
m_727_22 | UCLV28153 | DirectTerminal | TRUE | 11 | GSO_121
m_730_22 | UCLV28224 | DirectTerminal | TRUE | 11 | GSO_121
m_761_22 | UCLV28962 | DirectTerminal | TRUE | 10 | GSO_121
m_766_22 | UCLV29029 | DirectTerminal | TRUE | 15 | GSO_121
m_794_22 | UCLV29668 | DirectTerminal | TRUE | 31 | GSO_121
m_798_22 | UCLV29740 | DirectTerminal | TRUE | 17 | GSO_121
m_805_22 | UCLV29897 | DirectTerminal | TRUE | 23 | GSO_121
m_815_22 | UCLV30065 | DirectTerminal | TRUE | 27 | GSO_121
m_832_22 | UCLV30508 | DirectTerminal | TRUE | 13 | GSO_121
m_860_22 | UCLV31162 | DirectTerminal | TRUE | 30 | GSO_121
m_865_22 | UCLV31246 | DirectTerminal | TRUE | 15 | GSO_121
m_878_22 | UCLV31546 | DirectTerminal | TRUE | 9 | GSO_121
m_894_22 | UCLV32007 | DirectTerminal | TRUE | 13 | GSO_121
m_912_22 | UCLV32424 | DirectTerminal | TRUE | 12 | GSO_121
m_971_22 | UCLV33842 | DirectTerminal | TRUE | 39 | GSO_121
m_973_22 | UCLV33864 | DirectTerminal | TRUE | 12 | GSO_121
m_998_22 | UCLV34244 | DirectTerminal | TRUE | 6 | GSO_121
m_2321_22 | UCLV7876 | DirectTerminal | TRUE | 10 | GSO_144
m_2324_22 | UCLV7879 | DirectTerminal | TRUE | 11 | GSO_144
m_2333_22 | UCLV7888 | DirectTerminal | TRUE | 4 | GSO_144
m_2334_22 | UCLV7889 | DirectTerminal | TRUE | 4 | GSO_144
m_2335_22 | UCLV7890 | DirectTerminal | TRUE | 4 | GSO_144
m_2336_22 | UCLV7891 | DirectTerminal | TRUE | 6 | GSO_144
m_2337_22 | UCLV7892 | DirectTerminal | TRUE | 8 | GSO_144
m_2338_22 | UCLV7893 | DirectTerminal | TRUE | 6 | GSO_144
m_2340_22 | UCLV7895 | DirectTerminal | TRUE | 9 | GSO_144
m_2341_22 | UCLV7896 | DirectTerminal | TRUE | 8 | GSO_144
m_2342_22 | UCLV7898 | DirectTerminal | TRUE | 8 | GSO_144
m_2343_22 | UCLV7899 | DirectTerminal | TRUE | 9 | GSO_144
m_2344_22 | UCLV7901 | DirectTerminal | TRUE | 8 | GSO_144
m_2345_22 | UCLV7902 | DirectTerminal | TRUE | 9 | GSO_144
m_2346_22 | UCLV7904 | DirectTerminal | TRUE | 10 | GSO_144
m_2347_22 | UCLV7905 | DirectTerminal | TRUE | 10 | GSO_144
m_2348_22 | UCLV7906 | DirectTerminal | TRUE | 8 | GSO_144
m_2349_22 | UCLV7907 | DirectTerminal | TRUE | 8 | GSO_144
m_2350_22 | UCLV7908 | DirectTerminal | TRUE | 14 | GSO_144
m_2351_22 | UCLV7909 | DirectTerminal | TRUE | 10 | GSO_144
m_2352_22 | UCLV7910 | DirectTerminal | TRUE | 10 | GSO_144
m_2353_22 | UCLV7912 | DirectTerminal | TRUE | 12 | GSO_144
m_2354_22 | UCLV7913 | DirectTerminal | TRUE | 12 | GSO_144
m_2355_22 | UCLV7914 | DirectTerminal | TRUE | 12 | GSO_144
m_2356_22 | UCLV7916 | DirectTerminal | TRUE | 14 | GSO_144
m_2357_22 | UCLV7917 | DirectTerminal | TRUE | 14 | GSO_144
m_2358_22 | UCLV7918 | DirectTerminal | TRUE | 14 | GSO_144
m_2359_22 | UCLV7919 | DirectTerminal | TRUE | 14 | GSO_144
m_2360_22 | UCLV7920 | DirectTerminal | TRUE | 14 | GSO_144
m_2361_22 | UCLV7921 | DirectTerminal | TRUE | 12 | GSO_144
m_2362_22 | UCLV7922 | DirectTerminal | TRUE | 14 | GSO_144
m_2363_22 | UCLV7923 | DirectTerminal | TRUE | 10 | GSO_144
m_1030_22 | UCLV35176 | DirectTerminal | TRUE | 40 | GSO_141
m_1065_22 | UCLV35764 | DirectTerminal | TRUE | 6 | GSO_141
m_1172_22 | UCLV37231 | DirectTerminal | TRUE | 10 | GSO_141
m_1188_22 | UCLV37468 | DirectTerminal | TRUE | 32 | GSO_141
m_1226_22 | UCLV38560 | DirectTerminal | TRUE | 46 | GSO_141
m_1247_22 | UCLV38938 | DirectTerminal | TRUE | 38 | GSO_141
m_1325_22 | UCLV40616 | DirectTerminal | TRUE | 40 | GSO_141
m_1407_22 | UCLV42234 | DirectTerminal | TRUE | 21 | GSO_141
m_1410_22 | UCLV42348 | DirectTerminal | TRUE | 7 | GSO_141
m_1429_22 | UCLV42899 | DirectTerminal | TRUE | 52 | GSO_141
m_1552_22 | UCLV45525 | DirectTerminal | TRUE | 15 | GSO_141
m_1596_22 | UCLV46722 | DirectTerminal | TRUE | 51 | GSO_141
m_1609_22 | UCLV46905 | DirectTerminal | TRUE | 32 | GSO_141
m_1624_22 | UCLV47256 | DirectTerminal | TRUE | 22 | GSO_141
m_1681_22 | UCLV48620 | DirectTerminal | TRUE | 48 | GSO_141
m_1705_22 | UCLV49486 | DirectTerminal | TRUE | 4 | GSO_141
m_1757_22 | UCLV50662 | DirectTerminal | TRUE | 28 | GSO_141
m_1766_22 | UCLV50980 | DirectTerminal | TRUE | 22 | GSO_141
m_1810_22 | UCLV52000 | DirectTerminal | TRUE | 48 | GSO_141
m_1831_22 | UCLV52337 | DirectTerminal | TRUE | 16 | GSO_141
m_1843_22 | UCLV52800 | DirectTerminal | TRUE | 19 | GSO_141
m_1859_22 | UCLV53264 | DirectTerminal | TRUE | 52 | GSO_141
m_1879_22 | UCLV53673 | DirectTerminal | TRUE | 46 | GSO_141
m_1890_22 | UCLV53872 | DirectTerminal | TRUE | 24 | GSO_141
m_1901_22 | UCLV54181 | DirectTerminal | TRUE | 12 | GSO_141
m_1949_22 | UCLV55799 | DirectTerminal | TRUE | 26 | GSO_141
m_1977_22 | UCLV56776 | DirectTerminal | TRUE | 28 | GSO_141
m_2025_22 | UCLV58897 | DirectTerminal | TRUE | 30 | GSO_141
m_2033_22 | UCLV59245 | DirectTerminal | TRUE | 17 | GSO_141
m_2059_22 | UCLV60252 | DirectTerminal | TRUE | 26 | GSO_141
m_2070_22 | UCLV60571 | DirectTerminal | TRUE | 27 | GSO_141
m_2096_22 | UCLV61808 | DirectTerminal | TRUE | 18 | GSO_141
m_2124_22 | UCLV63121 | DirectTerminal | TRUE | 29 | GSO_141
m_2149_22 | UCLV6874 | DirectTerminal | TRUE | 28 | GSO_141
m_2150_22 | UCLV6875 | DirectTerminal | TRUE | 28 | GSO_141
m_2151_22 | UCLV6876 | DirectTerminal | TRUE | 27 | GSO_141
m_2152_22 | UCLV6877 | DirectTerminal | TRUE | 27 | GSO_141
m_2153_22 | UCLV6878 | DirectTerminal | TRUE | 27 | GSO_141
m_2154_22 | UCLV6879 | DirectTerminal | TRUE | 27 | GSO_141
m_2155_22 | UCLV6880 | DirectTerminal | TRUE | 25 | GSO_141
m_2156_22 | UCLV6881 | DirectTerminal | TRUE | 25 | GSO_141
m_2157_22 | UCLV6882 | DirectTerminal | TRUE | 23 | GSO_141
m_2158_22 | UCLV6884 | DirectTerminal | TRUE | 21 | GSO_141
m_2159_22 | UCLV6885 | DirectTerminal | TRUE | 23 | GSO_141
m_2160_22 | UCLV6886 | DirectTerminal | TRUE | 23 | GSO_141
m_2161_22 | UCLV6889 | DirectTerminal | TRUE | 23 | GSO_141
m_2162_22 | UCLV6890 | DirectTerminal | TRUE | 26 | GSO_141
m_2163_22 | UCLV6891 | DirectTerminal | TRUE | 24 | GSO_141
m_2164_22 | UCLV6892 | DirectTerminal | TRUE | 26 | GSO_141
m_2165_22 | UCLV6893 | DirectTerminal | TRUE | 26 | GSO_141
m_2166_22 | UCLV6894 | DirectTerminal | TRUE | 27 | GSO_141
m_2167_22 | UCLV6895 | DirectTerminal | TRUE | 27 | GSO_141
m_2385_22 | UCLV8160 | DirectTerminal | TRUE | 28 | GSO_141
m_2386_22 | UCLV8161 | DirectTerminal | TRUE | 20 | GSO_141
m_2389_22 | UCLV8164 | DirectTerminal | TRUE | 50 | GSO_141
m_2390_22 | UCLV8165 | DirectTerminal | TRUE | 52 | GSO_141
m_2734_22 | UCMV128 | DirectTerminal | TRUE | 5 | GSO_141
m_2781_22 | UCMV77 | DirectTerminal | TRUE | 11 | GSO_141
m_2786_22 | UCMV84 | DirectTerminal | TRUE | 6 | GSO_141
m_2791_22 | UCMV93 | DirectTerminal | TRUE | 8 | GSO_141
m_2794_22 | UCMV96 | DirectTerminal | TRUE | 3 | GSO_141
m_738_22 | UCLV28401 | DirectTerminal | TRUE | 36 | GSO_141
m_808_22 | UCLV29912 | DirectTerminal | TRUE | 44 | GSO_141
m_826_22 | UCLV30309 | DirectTerminal | TRUE | 34 | GSO_141
m_880_22 | UCLV31560 | DirectTerminal | TRUE | 30 | GSO_141
m_886_22 | UCLV31806 | DirectTerminal | TRUE | 38 | GSO_141
m_944_22 | UCLV33291 | DirectTerminal | TRUE | 42 | GSO_141
m_962_22 | UCLV33648 | DirectTerminal | TRUE | 28 | GSO_141
m_1025_22 | UCLV35123 | DirectTerminal | TRUE | 44 | GSO_145
m_1027_22 | UCLV35140 | DirectTerminal | TRUE | 51 | GSO_145
m_1034_22 | UCLV35294 | DirectTerminal | TRUE | 8 | GSO_145
m_1039_22 | UCLV35360 | DirectTerminal | TRUE | 36 | GSO_145
m_1043_22 | UCLV35432 | DirectTerminal | TRUE | 11 | GSO_145
m_1050_22 | UCLV35498 | DirectTerminal | TRUE | 50 | GSO_145
m_1052_22 | UCLV35513 | DirectTerminal | TRUE | 50 | GSO_145
m_1063_22 | UCLV35740 | DirectTerminal | TRUE | 45 | GSO_145
m_1066_22 | UCLV35835 | DirectTerminal | TRUE | 7 | GSO_145
m_1071_22 | UCLV35903 | DirectTerminal | TRUE | 9 | GSO_145
m_1102_22 | S_nSSEE4_12.47 | RootFallback | FALSE | 0 | GSO_145
m_1113_22 | UCLV36627 | DirectTerminal | TRUE | 16 | GSO_145
m_1162_22 | UCLV36999 | DirectTerminal | TRUE | 16 | GSO_145
m_1165_22 | UCLV37149 | DirectTerminal | TRUE | 9 | GSO_145
m_1169_22 | UCLV37208 | DirectTerminal | TRUE | 40 | GSO_145
m_1173_22 | UCLV37284 | DirectTerminal | TRUE | 52 | GSO_145
m_1175_22 | UCLV37306 | DirectTerminal | TRUE | 10 | GSO_145
m_1182_22 | UCLV37378 | DirectTerminal | TRUE | 44 | GSO_145
m_1183_22 | UCLV37392 | DirectTerminal | TRUE | 49 | GSO_145
m_1190_22 | UCLV37536 | DirectTerminal | TRUE | 8 | GSO_145
m_1221_22 | UCLV38475 | DirectTerminal | TRUE | 52 | GSO_145
m_1233_22 | UCLV38694 | DirectTerminal | TRUE | 30 | GSO_145
m_1241_22 | UCLV38847 | DirectTerminal | TRUE | 18 | GSO_145
m_1255_22 | UCLV39070 | DirectTerminal | TRUE | 33 | GSO_145
m_1261_22 | UCLV39218 | DirectTerminal | TRUE | 11 | GSO_145
m_1263_22 | UCLV39236 | DirectTerminal | TRUE | 50 | GSO_145
m_1287_22 | UCLV39769 | DirectTerminal | TRUE | 20 | GSO_145
m_1293_22 | UCLV39921 | DirectTerminal | TRUE | 8 | GSO_145
m_1299_22 | UCLV40054 | DirectTerminal | TRUE | 47 | GSO_145
m_1306_22 | UCLV40125 | DirectTerminal | TRUE | 44 | GSO_145
m_1311_22 | UCLV40292 | DirectTerminal | TRUE | 7 | GSO_145
m_1316_22 | UCLV40360 | DirectTerminal | TRUE | 28 | GSO_145
m_1319_22 | UCLV40432 | DirectTerminal | TRUE | 50 | GSO_145
m_1327_22 | UCLV40679 | DirectTerminal | TRUE | 40 | GSO_145
m_1332_22 | UCLV40761 | DirectTerminal | TRUE | 26 | GSO_145
m_1341_22 | UCLV40938 | DirectTerminal | TRUE | 18 | GSO_145
m_1352_22 | UCLV41088 | DirectTerminal | TRUE | 37 | GSO_145
m_1361_22 | UCLV41246 | DirectTerminal | TRUE | 34 | GSO_145
m_1363_22 | UCLV41296 | DirectTerminal | TRUE | 8 | GSO_145
m_1374_22 | UCLV41529 | DirectTerminal | TRUE | 8 | GSO_145
m_1376_22 | UCLV41541 | DirectTerminal | TRUE | 48 | GSO_145
m_1380_22 | UCLV41625 | DirectTerminal | TRUE | 47 | GSO_145
m_1388_22 | UCLV41767 | DirectTerminal | TRUE | 18 | GSO_145
m_1439_22 | UCLV43026 | DirectTerminal | TRUE | 52 | GSO_145
m_1441_22 | UCLV43098 | DirectTerminal | TRUE | 45 | GSO_145
m_1442_22 | UCLV43107 | DirectTerminal | TRUE | 31 | GSO_145
m_1448_22 | UCLV43231 | DirectTerminal | TRUE | 25 | GSO_145
m_1455_22 | UCLV43348 | DirectTerminal | TRUE | 47 | GSO_145
m_1460_22 | UCLV43425 | DirectTerminal | TRUE | 8 | GSO_145
m_1476_22 | UCLV43647 | DirectTerminal | TRUE | 49 | GSO_145
m_1504_22 | UCLV44609 | DirectTerminal | TRUE | 46 | GSO_145
m_1506_22 | UCLV44622 | DirectTerminal | TRUE | 49 | GSO_145
m_1525_22 | UCLV45013 | DirectTerminal | TRUE | 47 | GSO_145
m_1540_22 | UCLV45302 | DirectTerminal | TRUE | 12 | GSO_145
m_1548_22 | UCLV45439 | DirectTerminal | TRUE | 48 | GSO_145
m_1579_22 | UCLV46426 | DirectTerminal | TRUE | 49 | GSO_145
m_1589_22 | UCLV46622 | DirectTerminal | TRUE | 20 | GSO_145
m_1597_22 | UCLV46749 | DirectTerminal | TRUE | 42 | GSO_145
m_1601_22 | UCLV46813 | DirectTerminal | TRUE | 10 | GSO_145
m_1615_22 | UCLV47020 | DirectTerminal | TRUE | 52 | GSO_145
m_1633_22 | S_nSSEE4_12.47 | RootFallback | FALSE | 0 | GSO_145
m_1651_22 | UCLV48110 | DirectTerminal | TRUE | 24 | GSO_145
m_1668_22 | UCLV48415 | DirectTerminal | TRUE | 47 | GSO_145
m_1670_22 | UCLV48431 | DirectTerminal | TRUE | 35 | GSO_145
m_1684_22 | UCLV48697 | DirectTerminal | TRUE | 50 | GSO_145
m_1713_22 | UCLV49773 | DirectTerminal | TRUE | 51 | GSO_145
m_1719_22 | UCLV49905 | DirectTerminal | TRUE | 51 | GSO_145
m_1730_22 | UCLV50122 | DirectTerminal | TRUE | 12 | GSO_145
m_1747_22 | UCLV50402 | DirectTerminal | TRUE | 11 | GSO_145
m_1755_22 | S_nSSEE4_12.47 | RootFallback | FALSE | 0 | GSO_145
m_1765_22 | S_nSSEE4_12.47 | RootFallback | FALSE | 0 | GSO_145
m_1781_22 | UCLV51504 | DirectTerminal | TRUE | 42 | GSO_145
m_1792_22 | UCLV51671 | DirectTerminal | TRUE | 49 | GSO_145
m_1804_22 | UCLV51904 | DirectTerminal | TRUE | 14 | GSO_145
m_1812_22 | UCLV52052 | DirectTerminal | TRUE | 47 | GSO_145
m_1822_22 | UCLV52215 | DirectTerminal | TRUE | 46 | GSO_145
m_1825_22 | UCLV52280 | DirectTerminal | TRUE | 10 | GSO_145
m_1854_22 | UCLV53175 | DirectTerminal | TRUE | 41 | GSO_145
m_1871_22 | UCLV53479 | DirectTerminal | TRUE | 46 | GSO_145
m_1880_22 | UCLV53717 | DirectTerminal | TRUE | 46 | GSO_145
m_1885_22 | UCLV53789 | DirectTerminal | TRUE | 9 | GSO_145
m_1888_22 | S_nSSEE4_12.47 | RootFallback | FALSE | 0 | GSO_145
m_1975_22 | S_nSSEE4_12.47 | RootFallback | FALSE | 0 | GSO_145
m_1991_22 | S_nSSEE4_12.47 | RootFallback | FALSE | 0 | GSO_145
m_2030_22 | UCLV59161 | DirectTerminal | TRUE | 5 | GSO_145
m_2089_22 | S_nSSEE4_12.47 | RootFallback | FALSE | 0 | GSO_145
m_2094_22 | UCLV61724 | DirectTerminal | TRUE | 5 | GSO_145
m_2123_22 | S_nSSEE4_12.47 | RootFallback | FALSE | 0 | GSO_145
m_2138_22 | UCLV63744 | DirectTerminal | TRUE | 6 | GSO_145
m_2240_22 | UCLV7769 | DirectTerminal | TRUE | 6 | GSO_145
m_2241_22 | UCLV7771 | DirectTerminal | TRUE | 8 | GSO_145
m_2242_22 | UCLV7773 | DirectTerminal | TRUE | 8 | GSO_145
m_2243_22 | UCLV7774 | DirectTerminal | TRUE | 7 | GSO_145
m_2244_22 | UCLV7775 | DirectTerminal | TRUE | 6 | GSO_145
m_2245_22 | UCLV7777 | DirectTerminal | TRUE | 5 | GSO_145
m_2252_22 | UCLV7786 | DirectTerminal | TRUE | 8 | GSO_145
m_2391_22 | UCLV8166 | DirectTerminal | TRUE | 9 | GSO_145
m_2392_22 | S_nSSEE4_12.47 | RootFallback | FALSE | 0 | GSO_145
m_2393_22 | UCLV8168 | DirectTerminal | TRUE | 10 | GSO_145
m_2394_22 | UCLV8169 | DirectTerminal | TRUE | 19 | GSO_145
m_2395_22 | UCLV8170 | DirectTerminal | TRUE | 8 | GSO_145
m_2396_22 | UCLV8171 | DirectTerminal | TRUE | 17 | GSO_145
m_2397_22 | UCLV8172 | DirectTerminal | TRUE | 9 | GSO_145
m_2398_22 | UCLV8173 | DirectTerminal | TRUE | 8 | GSO_145
m_2399_22 | UCLV8174 | DirectTerminal | TRUE | 14 | GSO_145
m_2400_22 | UCLV8175 | DirectTerminal | TRUE | 15 | GSO_145
m_2401_22 | UCLV8176 | DirectTerminal | TRUE | 41 | GSO_145
m_2402_22 | UCLV8177 | DirectTerminal | TRUE | 49 | GSO_145
m_2403_22 | UCLV8178 | DirectTerminal | TRUE | 50 | GSO_145
m_2407_22 | UCLV8182 | DirectTerminal | TRUE | 48 | GSO_145
m_2411_22 | UCLV8186 | DirectTerminal | TRUE | 49 | GSO_145
m_2418_22 | UCLV8197 | DirectTerminal | TRUE | 37 | GSO_145
m_2419_22 | UCLV8198 | DirectTerminal | TRUE | 33 | GSO_145
m_2420_22 | UCLV8199 | DirectTerminal | TRUE | 39 | GSO_145
m_2421_22 | UCLV8200 | DirectTerminal | TRUE | 52 | GSO_145
m_2422_22 | UCLV8201 | DirectTerminal | TRUE | 39 | GSO_145
m_2423_22 | S_nSSEE4_12.47 | RootFallback | FALSE | 0 | GSO_145
m_2424_22 | S_nSSEE4_12.47 | RootFallback | FALSE | 0 | GSO_145
m_2425_22 | UCLV8204 | DirectTerminal | TRUE | 51 | GSO_145
m_2426_22 | UCLV8205 | DirectTerminal | TRUE | 40 | GSO_145
m_2444_22 | UCLV8223 | DirectTerminal | TRUE | 47 | GSO_145
m_2732_22 | UCMV122 | DirectTerminal | TRUE | 32 | GSO_145
m_52_22 | UCLV10074 | DirectTerminal | TRUE | 5 | GSO_145
m_53_22 | S_nSSEE4_12.47 | RootFallback | FALSE | 0 | GSO_145
m_54_22 | UCLV10076 | DirectTerminal | TRUE | 10 | GSO_145
m_712_22 | UCLV27716 | DirectTerminal | TRUE | 12 | GSO_145
m_724_22 | UCLV28089 | DirectTerminal | TRUE | 47 | GSO_145
m_729_22 | UCLV28216 | DirectTerminal | TRUE | 48 | GSO_145
m_733_22 | UCLV28315 | DirectTerminal | TRUE | 12 | GSO_145
m_744_22 | UCLV28541 | DirectTerminal | TRUE | 39 | GSO_145
m_752_22 | UCLV28850 | DirectTerminal | TRUE | 50 | GSO_145
m_755_22 | UCLV28908 | DirectTerminal | TRUE | 7 | GSO_145
m_760_22 | UCLV28951 | DirectTerminal | TRUE | 44 | GSO_145
m_779_22 | UCLV29375 | DirectTerminal | TRUE | 9 | GSO_145
m_797_22 | UCLV29732 | DirectTerminal | TRUE | 51 | GSO_145
m_801_22 | UCLV29804 | DirectTerminal | TRUE | 10 | GSO_145
m_803_22 | UCLV29817 | DirectTerminal | TRUE | 51 | GSO_145
m_804_22 | UCLV29831 | DirectTerminal | TRUE | 51 | GSO_145
m_814_22 | UCLV30056 | DirectTerminal | TRUE | 39 | GSO_145
m_835_22 | S_nSSEE4_12.47 | RootFallback | FALSE | 0 | GSO_145
m_841_22 | UCLV30634 | DirectTerminal | TRUE | 10 | GSO_145
m_849_22 | UCLV30761 | DirectTerminal | TRUE | 38 | GSO_145
m_864_22 | UCLV31237 | DirectTerminal | TRUE | 49 | GSO_145
m_868_22 | UCLV31305 | DirectTerminal | TRUE | 49 | GSO_145
m_875_22 | UCLV31451 | DirectTerminal | TRUE | 43 | GSO_145
m_888_22 | UCLV31848 | DirectTerminal | TRUE | 43 | GSO_145
m_900_22 | UCLV32144 | DirectTerminal | TRUE | 12 | GSO_145
m_903_22 | UCLV32231 | DirectTerminal | TRUE | 45 | GSO_145
m_910_22 | UCLV32370 | DirectTerminal | TRUE | 44 | GSO_145
m_919_22 | UCLV32553 | DirectTerminal | TRUE | 18 | GSO_145
m_948_22 | UCLV33406 | DirectTerminal | TRUE | 9 | GSO_145
m_952_22 | UCLV33500 | DirectTerminal | TRUE | 49 | GSO_145
m_959_22 | UCLV33626 | DirectTerminal | TRUE | 45 | GSO_145
m_990_22 | UCLV34160 | DirectTerminal | TRUE | 9 | GSO_145
m_997_22 | UCLV34233 | DirectTerminal | TRUE | 22 | GSO_145
m_1399_22 | UCLV41975 | DirectTerminal | TRUE | 14 | GSO_142
m_1400_22 | UCLV41992 | DirectTerminal | TRUE | 51 | GSO_142
m_1402_22 | UCLV42030 | DirectTerminal | TRUE | 26 | GSO_142
m_1405_22 | UCLV42093 | DirectTerminal | TRUE | 5 | GSO_142
m_1413_22 | UCLV42416 | DirectTerminal | TRUE | 10 | GSO_142
m_1416_22 | UCLV42483 | DirectTerminal | TRUE | 33 | GSO_142
m_1417_22 | UCLV42489 | DirectTerminal | TRUE | 17 | GSO_142
m_1422_22 | UCLV42788 | DirectTerminal | TRUE | 46 | GSO_142
m_1423_22 | UCLV42795 | DirectTerminal | TRUE | 16 | GSO_142
m_1483_22 | UCLV43791 | DirectTerminal | TRUE | 15 | GSO_142
m_1489_22 | UCLV44096 | DirectTerminal | TRUE | 35 | GSO_142
m_1490_22 | UCLV44102 | DirectTerminal | TRUE | 18 | GSO_142
m_1494_22 | UCLV44238 | DirectTerminal | TRUE | 10 | GSO_142
m_1497_22 | UCLV44447 | DirectTerminal | TRUE | 57 | GSO_142
m_1502_22 | UCLV44555 | DirectTerminal | TRUE | 5 | GSO_142
m_1549_22 | UCLV45457 | DirectTerminal | TRUE | 37 | GSO_142
m_1556_22 | UCLV45734 | DirectTerminal | TRUE | 54 | GSO_142
m_1558_22 | UCLV45773 | DirectTerminal | TRUE | 41 | GSO_142
m_1561_22 | UCLV45837 | DirectTerminal | TRUE | 13 | GSO_142
m_1563_22 | UCLV45894 | DirectTerminal | TRUE | 45 | GSO_142
m_1564_22 | UCLV45901 | DirectTerminal | TRUE | 17 | GSO_142
m_1567_22 | UCLV46061 | DirectTerminal | TRUE | 55 | GSO_142
m_1571_22 | UCLV46234 | DirectTerminal | TRUE | 19 | GSO_142
m_1622_22 | UCLV47171 | DirectTerminal | TRUE | 37 | GSO_142
m_1626_22 | UCLV47328 | DirectTerminal | TRUE | 50 | GSO_142
m_1629_22 | UCLV47425 | DirectTerminal | TRUE | 13 | GSO_142
m_1631_22 | UCLV47486 | DirectTerminal | TRUE | 31 | GSO_142
m_1632_22 | UCLV47495 | DirectTerminal | TRUE | 12 | GSO_142
m_1634_22 | UCLV47622 | DirectTerminal | TRUE | 11 | GSO_142
m_1638_22 | UCLV47848 | DirectTerminal | TRUE | 53 | GSO_142
m_1642_22 | UCLV47952 | DirectTerminal | TRUE | 8 | GSO_142
m_1693_22 | UCLV48912 | DirectTerminal | TRUE | 15 | GSO_142
m_1695_22 | UCLV49042 | DirectTerminal | TRUE | 11 | GSO_142
m_1696_22 | UCLV49116 | DirectTerminal | TRUE | 53 | GSO_142
m_1698_22 | UCLV49161 | DirectTerminal | TRUE | 10 | GSO_142
m_1701_22 | UCLV49288 | DirectTerminal | TRUE | 22 | GSO_142
m_1703_22 | UCLV49444 | DirectTerminal | TRUE | 53 | GSO_142
m_1709_22 | UCLV49603 | DirectTerminal | TRUE | 41 | GSO_142
m_1710_22 | UCLV49609 | DirectTerminal | TRUE | 17 | GSO_142
m_1754_22 | UCLV50585 | DirectTerminal | TRUE | 24 | GSO_142
m_1759_22 | UCLV50785 | DirectTerminal | TRUE | 29 | GSO_142
m_1763_22 | UCLV50888 | DirectTerminal | TRUE | 47 | GSO_142
m_1764_22 | UCLV50897 | DirectTerminal | TRUE | 25 | GSO_142
m_1767_22 | UCLV51036 | DirectTerminal | TRUE | 13 | GSO_142
m_1769_22 | UCLV51253 | DirectTerminal | TRUE | 54 | GSO_142
m_1773_22 | UCLV51366 | DirectTerminal | TRUE | 7 | GSO_142
m_1835_22 | UCLV52543 | DirectTerminal | TRUE | 52 | GSO_142
m_1837_22 | UCLV52584 | DirectTerminal | TRUE | 28 | GSO_142
m_1840_22 | UCLV52651 | DirectTerminal | TRUE | 12 | GSO_142
m_1844_22 | UCLV52869 | DirectTerminal | TRUE | 56 | GSO_142
m_1846_22 | UCLV52911 | DirectTerminal | TRUE | 11 | GSO_142
m_1851_22 | UCLV53047 | DirectTerminal | TRUE | 33 | GSO_142
m_1852_22 | UCLV53055 | DirectTerminal | TRUE | 25 | GSO_142
m_1892_22 | UCLV53943 | DirectTerminal | TRUE | 49 | GSO_142
m_1894_22 | UCLV53987 | DirectTerminal | TRUE | 28 | GSO_142
m_1899_22 | UCLV54104 | DirectTerminal | TRUE | 16 | GSO_142
m_1904_22 | UCLV54426 | DirectTerminal | TRUE | 22 | GSO_142
m_1905_22 | UCLV54462 | DirectTerminal | TRUE | 56 | GSO_142
m_1910_22 | UCLV54567 | DirectTerminal | TRUE | 13 | GSO_142
m_1916_22 | UCLV54878 | DirectTerminal | TRUE | 13 | GSO_142
m_1918_22 | UCLV54948 | DirectTerminal | TRUE | 6 | GSO_142
m_1922_22 | UCLV55260 | DirectTerminal | TRUE | 10 | GSO_142
m_1923_22 | UCLV55363 | DirectTerminal | TRUE | 45 | GSO_142
m_1927_22 | UCLV55556 | DirectTerminal | TRUE | 47 | GSO_142
m_1929_22 | UCLV55599 | DirectTerminal | TRUE | 20 | GSO_142
m_1934_22 | UCLV55661 | DirectTerminal | TRUE | 45 | GSO_142
m_1953_22 | UCLV55873 | DirectTerminal | TRUE | 48 | GSO_142
m_1955_22 | UCLV55914 | DirectTerminal | TRUE | 22 | GSO_142
m_1956_22 | UCLV55975 | DirectTerminal | TRUE | 44 | GSO_142
m_1957_22 | UCLV55982 | DirectTerminal | TRUE | 28 | GSO_142
m_1963_22 | UCLV56279 | DirectTerminal | TRUE | 45 | GSO_142
m_1964_22 | UCLV56393 | DirectTerminal | TRUE | 7 | GSO_142
m_1968_22 | UCLV56578 | DirectTerminal | TRUE | 56 | GSO_142
m_1969_22 | UCLV56586 | DirectTerminal | TRUE | 35 | GSO_142
m_1974_22 | UCLV56696 | DirectTerminal | TRUE | 9 | GSO_142
m_1978_22 | UCLV56946 | DirectTerminal | TRUE | 9 | GSO_142
m_1981_22 | UCLV57009 | DirectTerminal | TRUE | 14 | GSO_142
m_1985_22 | UCLV57080 | DirectTerminal | TRUE | 30 | GSO_142
m_1990_22 | UCLV57389 | DirectTerminal | TRUE | 14 | GSO_142
m_1993_22 | UCLV57510 | DirectTerminal | TRUE | 45 | GSO_142
m_1997_22 | UCLV57742 | DirectTerminal | TRUE | 19 | GSO_142
m_1999_22 | UCLV57810 | DirectTerminal | TRUE | 45 | GSO_142
m_2003_22 | UCLV58006 | DirectTerminal | TRUE | 46 | GSO_142
m_2006_22 | UCLV58050 | DirectTerminal | TRUE | 21 | GSO_142
m_2009_22 | UCLV58116 | DirectTerminal | TRUE | 35 | GSO_142
m_2010_22 | UCLV58124 | DirectTerminal | TRUE | 18 | GSO_142
m_2016_22 | UCLV58398 | DirectTerminal | TRUE | 50 | GSO_142
m_2017_22 | UCLV58403 | DirectTerminal | TRUE | 18 | GSO_142
m_2020_22 | UCLV58709 | DirectTerminal | TRUE | 37 | GSO_142
m_2024_22 | UCLV58815 | DirectTerminal | TRUE | 8 | GSO_142
m_2026_22 | UCLV59060 | DirectTerminal | TRUE | 8 | GSO_142
m_2029_22 | UCLV59126 | DirectTerminal | TRUE | 12 | GSO_142
m_2031_22 | UCLV59180 | DirectTerminal | TRUE | 24 | GSO_142
m_2037_22 | UCLV59401 | DirectTerminal | TRUE | 14 | GSO_142
m_2045_22 | UCLV59704 | DirectTerminal | TRUE | 6 | GSO_142
m_2047_22 | UCLV59824 | DirectTerminal | TRUE | 47 | GSO_142
m_2051_22 | UCLV60017 | DirectTerminal | TRUE | 6 | GSO_142
m_2053_22 | UCLV60053 | DirectTerminal | TRUE | 35 | GSO_142
m_2056_22 | UCLV60122 | DirectTerminal | TRUE | 43 | GSO_142
m_2061_22 | UCLV60326 | DirectTerminal | TRUE | 49 | GSO_142
m_2063_22 | UCLV60367 | DirectTerminal | TRUE | 35 | GSO_142
m_2065_22 | UCLV60434 | DirectTerminal | TRUE | 47 | GSO_142
m_2068_22 | UCLV60482 | DirectTerminal | TRUE | 39 | GSO_142
m_2072_22 | UCLV60644 | DirectTerminal | TRUE | 48 | GSO_142
m_2080_22 | UCLV60948 | DirectTerminal | TRUE | 46 | GSO_142
m_2081_22 | UCLV60957 | DirectTerminal | TRUE | 16 | GSO_142
m_2085_22 | UCLV61262 | DirectTerminal | TRUE | 47 | GSO_142
m_2086_22 | UCLV61270 | DirectTerminal | TRUE | 35 | GSO_142
m_2088_22 | UCLV61374 | DirectTerminal | TRUE | 9 | GSO_142
m_2093_22 | UCLV61685 | DirectTerminal | TRUE | 11 | GSO_142
m_2100_22 | UCLV62151 | DirectTerminal | TRUE | 43 | GSO_142
m_2101_22 | UCLV62160 | DirectTerminal | TRUE | 20 | GSO_142
m_2104_22 | UCLV62266 | DirectTerminal | TRUE | 14 | GSO_142
m_2110_22 | UCLV62581 | DirectTerminal | TRUE | 13 | GSO_142
m_2111_22 | UCLV62621 | DirectTerminal | TRUE | 19 | GSO_142
m_2113_22 | UCLV62689 | DirectTerminal | TRUE | 45 | GSO_142
m_2117_22 | UCLV62873 | DirectTerminal | TRUE | 47 | GSO_142
m_2119_22 | UCLV62919 | DirectTerminal | TRUE | 34 | GSO_142
m_2120_22 | UCLV62984 | DirectTerminal | TRUE | 42 | GSO_142
m_2122_22 | UCLV63036 | DirectTerminal | TRUE | 14 | GSO_142
m_2126_22 | UCLV63192 | DirectTerminal | TRUE | 47 | GSO_142
m_2128_22 | UCLV63236 | DirectTerminal | TRUE | 23 | GSO_142
m_2129_22 | UCLV63281 | DirectTerminal | TRUE | 43 | GSO_142
m_2130_22 | UCLV63289 | DirectTerminal | TRUE | 30 | GSO_142
m_2134_22 | UCLV63606 | DirectTerminal | TRUE | 17 | GSO_142
m_2137_22 | UCLV63707 | DirectTerminal | TRUE | 13 | GSO_142
m_2383_22 | UCLV8158 | DirectTerminal | TRUE | 39 | GSO_142
m_2744_22 | UCMV27 | DirectTerminal | TRUE | 26 | GSO_142
m_327_22 | UCLV13216 | DirectTerminal | TRUE | 55 | GSO_142
m_328_22 | UCLV13217 | DirectTerminal | TRUE | 51 | GSO_142
m_370_22 | UCLV15913 | DirectTerminal | TRUE | 32 | GSO_142
m_38_22 | UCLV10060 | DirectTerminal | TRUE | 13 | GSO_142
m_39_22 | UCLV10061 | DirectTerminal | TRUE | 26 | GSO_142
m_40_22 | UCLV10062 | DirectTerminal | TRUE | 15 | GSO_142
m_41_22 | UCLV10063 | DirectTerminal | TRUE | 12 | GSO_142
m_55_22 | UCLV10077 | DirectTerminal | TRUE | 39 | GSO_142
m_56_22 | UCLV10078 | DirectTerminal | TRUE | 37 | GSO_142
m_57_22 | UCLV10079 | DirectTerminal | TRUE | 52 | GSO_142
m_58_22 | UCLV10080 | DirectTerminal | TRUE | 41 | GSO_142
m_59_22 | UCLV10081 | DirectTerminal | TRUE | 37 | GSO_142
m_2027_21 | UCLV12119 | DirectTerminal | TRUE | 33 | GSO_18
m_2029_21 | UCLV12120 | DirectTerminal | TRUE | 35 | GSO_18
m_2049_21 | UCLV12139 | DirectTerminal | TRUE | 30 | GSO_18
m_2051_21 | UCLV12140 | DirectTerminal | TRUE | 28 | GSO_18
m_2052_21 | UCLV12141 | DirectTerminal | TRUE | 28 | GSO_18
m_2053_21 | UCLV12142 | DirectTerminal | TRUE | 30 | GSO_18
m_2056_21 | UCLV12145 | DirectTerminal | TRUE | 26 | GSO_18
m_2057_21 | UCLV12147 | DirectTerminal | TRUE | 26 | GSO_18
m_2058_21 | UCLV12148 | DirectTerminal | TRUE | 25 | GSO_18
m_2059_21 | UCLV12149 | DirectTerminal | TRUE | 25 | GSO_18
m_2061_21 | UCLV12150 | DirectTerminal | TRUE | 24 | GSO_18
m_2062_21 | UCLV12151 | DirectTerminal | TRUE | 21 | GSO_18
m_2063_21 | UCLV12152 | DirectTerminal | TRUE | 21 | GSO_18
m_2064_21 | UCLV12153 | DirectTerminal | TRUE | 21 | GSO_18
m_2065_21 | UCLV12155 | DirectTerminal | TRUE | 23 | GSO_18
m_2066_21 | UCLV12157 | DirectTerminal | TRUE | 24 | GSO_18
m_2067_21 | UCLV12158 | DirectTerminal | TRUE | 24 | GSO_18
m_2068_21 | UCLV12159 | DirectTerminal | TRUE | 24 | GSO_18
m_2070_21 | UCLV12160 | DirectTerminal | TRUE | 24 | GSO_18
m_2071_21 | UCLV12161 | DirectTerminal | TRUE | 23 | GSO_18
m_2072_21 | UCLV12162 | DirectTerminal | TRUE | 23 | GSO_18
m_2073_21 | UCLV12163 | DirectTerminal | TRUE | 28 | GSO_18
m_2074_21 | UCLV12164 | DirectTerminal | TRUE | 28 | GSO_18
m_2075_21 | UCLV12165 | DirectTerminal | TRUE | 28 | GSO_18
m_2076_21 | UCLV12166 | DirectTerminal | TRUE | 25 | GSO_18
m_2077_21 | UCLV12167 | DirectTerminal | TRUE | 25 | GSO_18
m_2078_21 | UCLV12168 | DirectTerminal | TRUE | 25 | GSO_18
m_2079_21 | UCLV12169 | DirectTerminal | TRUE | 21 | GSO_18
m_2081_21 | UCLV12170 | DirectTerminal | TRUE | 21 | GSO_18
m_2082_21 | UCLV12171 | DirectTerminal | TRUE | 21 | GSO_18
m_2083_21 | UCLV12172 | DirectTerminal | TRUE | 21 | GSO_18
m_2084_21 | UCLV12173 | DirectTerminal | TRUE | 21 | GSO_18
m_2085_21 | UCLV12174 | DirectTerminal | TRUE | 22 | GSO_18
m_2086_21 | UCLV12175 | DirectTerminal | TRUE | 25 | GSO_18
m_2087_21 | UCLV12176 | DirectTerminal | TRUE | 25 | GSO_18
m_2088_21 | UCLV12177 | DirectTerminal | TRUE | 23 | GSO_18
m_2089_21 | UCLV12178 | DirectTerminal | TRUE | 23 | GSO_18
m_2090_21 | UCLV12179 | DirectTerminal | TRUE | 23 | GSO_18
m_2092_21 | UCLV12180 | DirectTerminal | TRUE | 25 | GSO_18
m_2093_21 | UCLV12181 | DirectTerminal | TRUE | 24 | GSO_18
m_2094_21 | UCLV12182 | DirectTerminal | TRUE | 24 | GSO_18
m_2095_21 | UCLV12183 | DirectTerminal | TRUE | 27 | GSO_18
m_2096_21 | UCLV12184 | DirectTerminal | TRUE | 27 | GSO_18
m_2097_21 | UCLV12185 | DirectTerminal | TRUE | 25 | GSO_18
m_2098_21 | UCLV12186 | DirectTerminal | TRUE | 25 | GSO_18
m_2099_21 | UCLV12187 | DirectTerminal | TRUE | 24 | GSO_18
m_2100_21 | UCLV12188 | DirectTerminal | TRUE | 24 | GSO_18
m_2101_21 | UCLV12189 | DirectTerminal | TRUE | 24 | GSO_18
m_2103_21 | UCLV12190 | DirectTerminal | TRUE | 22 | GSO_18
m_2104_21 | UCLV12191 | DirectTerminal | TRUE | 22 | GSO_18
m_2105_21 | UCLV12192 | DirectTerminal | TRUE | 25 | GSO_18
m_2106_21 | UCLV12193 | DirectTerminal | TRUE | 25 | GSO_18
m_2107_21 | UCLV12194 | DirectTerminal | TRUE | 24 | GSO_18
m_2108_21 | UCLV12195 | DirectTerminal | TRUE | 24 | GSO_18
m_2109_21 | UCLV12196 | DirectTerminal | TRUE | 24 | GSO_18
m_2110_21 | UCLV12197 | DirectTerminal | TRUE | 24 | GSO_18
m_2111_21 | UCLV12198 | DirectTerminal | TRUE | 7 | GSO_18
m_2931_21 | UCLV13122 | DirectTerminal | TRUE | 39 | GSO_18
m_2932_21 | UCLV13123 | DirectTerminal | TRUE | 39 | GSO_18
m_2933_21 | UCLV13124 | DirectTerminal | TRUE | 38 | GSO_18
m_2934_21 | UCLV13125 | DirectTerminal | TRUE | 38 | GSO_18
m_2935_21 | UCLV13126 | DirectTerminal | TRUE | 40 | GSO_18
m_2936_21 | UCLV13127 | DirectTerminal | TRUE | 38 | GSO_18
m_2937_21 | UCLV13128 | DirectTerminal | TRUE | 43 | GSO_18
m_33157_21 | UCLV41945 | DirectTerminal | TRUE | 24 | GSO_18
m_33160_21 | UCLV41948 | DirectTerminal | TRUE | 10 | GSO_18
m_33218_21 | UCLV42002 | DirectTerminal | TRUE | 20 | GSO_18
m_33220_21 | UCLV42004 | DirectTerminal | TRUE | 18 | GSO_18
m_33282_21 | UCLV42063 | DirectTerminal | TRUE | 20 | GSO_18
m_33284_21 | UCLV42065 | DirectTerminal | TRUE | 39 | GSO_18
m_33350_21 | UCLV42126 | DirectTerminal | TRUE | 19 | GSO_18
m_33352_21 | UCLV42128 | DirectTerminal | TRUE | 21 | GSO_18
m_33426_21 | UCLV42195 | DirectTerminal | TRUE | 16 | GSO_18
m_33433_21 | UCLV42200 | DirectTerminal | TRUE | 18 | GSO_18
m_33478_21 | UCLV42243 | DirectTerminal | TRUE | 35 | GSO_18
m_33489_21 | UCLV42253 | DirectTerminal | TRUE | 22 | GSO_18
m_33491_21 | UCLV42255 | DirectTerminal | TRUE | 25 | GSO_18
m_33559_21 | UCLV42317 | DirectTerminal | TRUE | 23 | GSO_18
m_33628_21 | UCLV42382 | DirectTerminal | TRUE | 21 | GSO_18
m_33631_21 | UCLV42385 | DirectTerminal | TRUE | 41 | GSO_18
m_33633_21 | UCLV42387 | DirectTerminal | TRUE | 8 | GSO_18
m_33675_21 | UCLV42426 | DirectTerminal | TRUE | 6 | GSO_18
m_33716_21 | UCLV42463 | DirectTerminal | TRUE | 16 | GSO_18
m_33776_21 | UCLV42520 | DirectTerminal | TRUE | 22 | GSO_18
m_33779_21 | UCLV42523 | DirectTerminal | TRUE | 21 | GSO_18
m_33782_21 | UCLV42526 | DirectTerminal | TRUE | 14 | GSO_18
m_33844_21 | UCLV42583 | DirectTerminal | TRUE | 23 | GSO_18
m_33846_21 | UCLV42585 | DirectTerminal | TRUE | 22 | GSO_18
m_33897_21 | UCLV42630 | DirectTerminal | TRUE | 18 | GSO_18
m_33898_21 | UCLV42631 | DirectTerminal | TRUE | 24 | GSO_18
m_33969_21 | UCLV42697 | DirectTerminal | TRUE | 18 | GSO_18
m_34045_21 | UCLV42766 | DirectTerminal | TRUE | 20 | GSO_18
m_34048_21 | UCLV42769 | DirectTerminal | TRUE | 9 | GSO_18
m_34099_21 | UCLV42817 | DirectTerminal | TRUE | 42 | GSO_18
m_34111_21 | UCLV42828 | DirectTerminal | TRUE | 21 | GSO_18
m_34115_21 | UCLV42831 | DirectTerminal | TRUE | 25 | GSO_18
m_35086_21 | UCLV43763 | DirectTerminal | TRUE | 17 | GSO_18
m_35149_21 | UCLV43822 | DirectTerminal | TRUE | 22 | GSO_18
m_35153_21 | UCLV43826 | DirectTerminal | TRUE | 12 | GSO_18
m_35206_21 | UCLV43877 | DirectTerminal | TRUE | 39 | GSO_18
m_35216_21 | UCLV43886 | DirectTerminal | TRUE | 15 | GSO_18
m_35276_21 | UCLV43940 | DirectTerminal | TRUE | 23 | GSO_18
m_35353_21 | UCLV44009 | DirectTerminal | TRUE | 12 | GSO_18
m_35419_21 | UCLV44070 | DirectTerminal | TRUE | 16 | GSO_18
m_35475_21 | UCLV44125 | DirectTerminal | TRUE | 46 | GSO_18
m_35487_21 | UCLV44136 | DirectTerminal | TRUE | 19 | GSO_18
m_35489_21 | UCLV44138 | DirectTerminal | TRUE | 17 | GSO_18
m_35562_21 | UCLV44205 | DirectTerminal | TRUE | 20 | GSO_18
m_35564_21 | UCLV44207 | DirectTerminal | TRUE | 40 | GSO_18
m_35566_21 | UCLV44209 | DirectTerminal | TRUE | 7 | GSO_18
m_35629_21 | UCLV44268 | DirectTerminal | TRUE | 19 | GSO_18
m_35632_21 | UCLV44270 | DirectTerminal | TRUE | 19 | GSO_18
m_35715_21 | UCLV44346 | DirectTerminal | TRUE | 17 | GSO_18
m_35766_21 | UCLV44393 | DirectTerminal | TRUE | 13 | GSO_18
m_35835_21 | UCLV44458 | DirectTerminal | TRUE | 21 | GSO_18
m_35906_21 | UCLV44524 | DirectTerminal | TRUE | 19 | GSO_18
m_36913_21 | UCLV45492 | DirectTerminal | TRUE | 19 | GSO_18
m_36915_21 | UCLV45494 | DirectTerminal | TRUE | 39 | GSO_18
m_36917_21 | UCLV45496 | DirectTerminal | TRUE | 14 | GSO_18
m_36982_21 | UCLV45556 | DirectTerminal | TRUE | 22 | GSO_18
m_37021_21 | UCLV45592 | DirectTerminal | TRUE | 9 | GSO_18
m_37056_21 | UCLV45623 | DirectTerminal | TRUE | 19 | GSO_18
m_37094_21 | UCLV45659 | DirectTerminal | TRUE | 14 | GSO_18
m_37113_21 | UCLV45676 | DirectTerminal | TRUE | 19 | GSO_18
m_37183_21 | UCLV45743 | DirectTerminal | TRUE | 15 | GSO_18
m_37186_21 | UCLV45746 | DirectTerminal | TRUE | 6 | GSO_18
m_37250_21 | UCLV45806 | DirectTerminal | TRUE | 20 | GSO_18
m_37252_21 | UCLV45808 | DirectTerminal | TRUE | 43 | GSO_18
m_37317_21 | UCLV45869 | DirectTerminal | TRUE | 24 | GSO_18
m_37374_21 | UCLV45922 | DirectTerminal | TRUE | 47 | GSO_18
m_37386_21 | UCLV45933 | DirectTerminal | TRUE | 22 | GSO_18
m_37388_21 | UCLV45935 | DirectTerminal | TRUE | 19 | GSO_18
m_37391_21 | UCLV45938 | DirectTerminal | TRUE | 12 | GSO_18
m_37451_21 | UCLV45993 | DirectTerminal | TRUE | 38 | GSO_18
m_37462_21 | UCLV46001 | DirectTerminal | TRUE | 22 | GSO_18
m_37465_21 | UCLV46004 | DirectTerminal | TRUE | 19 | GSO_18
m_37538_21 | UCLV46072 | DirectTerminal | TRUE | 16 | GSO_18
m_37541_21 | UCLV46075 | DirectTerminal | TRUE | 23 | GSO_18
m_37542_21 | UCLV46076 | DirectTerminal | TRUE | 8 | GSO_18
m_37608_21 | UCLV46136 | DirectTerminal | TRUE | 18 | GSO_18
m_37610_21 | UCLV46138 | DirectTerminal | TRUE | 17 | GSO_18
m_37646_21 | UCLV46171 | DirectTerminal | TRUE | 5 | GSO_18
m_37682_21 | UCLV46203 | DirectTerminal | TRUE | 19 | GSO_18
m_37739_21 | UCLV46257 | DirectTerminal | TRUE | 43 | GSO_18
m_37750_21 | UCLV46267 | DirectTerminal | TRUE | 24 | GSO_18
m_37752_21 | UCLV46269 | DirectTerminal | TRUE | 19 | GSO_18
m_38662_21 | UCLV47149 | DirectTerminal | TRUE | 23 | GSO_18
m_38666_21 | UCLV47152 | DirectTerminal | TRUE | 15 | GSO_18
m_38723_21 | UCLV47206 | DirectTerminal | TRUE | 23 | GSO_18
m_38725_21 | UCLV47208 | DirectTerminal | TRUE | 21 | GSO_18
m_38728_21 | UCLV47210 | DirectTerminal | TRUE | 11 | GSO_18
m_38783_21 | UCLV47262 | DirectTerminal | TRUE | 41 | GSO_18
m_38795_21 | UCLV47273 | DirectTerminal | TRUE | 16 | GSO_18
m_38864_21 | UCLV47338 | DirectTerminal | TRUE | 22 | GSO_18
m_38867_21 | UCLV47340 | DirectTerminal | TRUE | 22 | GSO_18
m_38868_21 | UCLV47341 | DirectTerminal | TRUE | 10 | GSO_18
m_38924_21 | UCLV47393 | DirectTerminal | TRUE | 16 | GSO_18
m_38960_21 | UCLV47427 | DirectTerminal | TRUE | 9 | GSO_18
m_39057_21 | UCLV47517 | DirectTerminal | TRUE | 46 | GSO_18
m_39069_21 | UCLV47528 | DirectTerminal | TRUE | 24 | GSO_18
m_39072_21 | UCLV47530 | DirectTerminal | TRUE | 13 | GSO_18
m_39137_21 | UCLV47590 | DirectTerminal | TRUE | 23 | GSO_18
m_39139_21 | UCLV47592 | DirectTerminal | TRUE | 46 | GSO_18
m_39207_21 | UCLV47656 | DirectTerminal | TRUE | 23 | GSO_18
m_39209_21 | UCLV47658 | DirectTerminal | TRUE | 19 | GSO_18
m_39287_21 | UCLV47729 | DirectTerminal | TRUE | 18 | GSO_18
m_39356_21 | UCLV47792 | DirectTerminal | TRUE | 24 | GSO_18
m_39427_21 | UCLV47858 | DirectTerminal | TRUE | 23 | GSO_18
m_39494_21 | UCLV47920 | DirectTerminal | TRUE | 21 | GSO_18
m_39559_21 | UCLV47981 | DirectTerminal | TRUE | 24 | GSO_18
m_39563_21 | UCLV47985 | DirectTerminal | TRUE | 10 | GSO_18
m_40495_21 | UCLV48882 | DirectTerminal | TRUE | 20 | GSO_18
m_40498_21 | UCLV48885 | DirectTerminal | TRUE | 36 | GSO_18
m_40500_21 | UCLV48887 | DirectTerminal | TRUE | 14 | GSO_18
m_40548_21 | UCLV48931 | DirectTerminal | TRUE | 32 | GSO_18
m_40559_21 | UCLV48941 | DirectTerminal | TRUE | 20 | GSO_18
m_40562_21 | UCLV48944 | DirectTerminal | TRUE | 16 | GSO_18
m_40564_21 | UCLV48946 | DirectTerminal | TRUE | 15 | GSO_18
m_40599_21 | UCLV48978 | DirectTerminal | TRUE | 9 | GSO_18
m_40637_21 | UCLV49010 | DirectTerminal | TRUE | 24 | GSO_18
m_40763_21 | UCLV49127 | DirectTerminal | TRUE | 21 | GSO_18
m_40765_21 | UCLV49129 | DirectTerminal | TRUE | 20 | GSO_18
m_40767_21 | UCLV49130 | DirectTerminal | TRUE | 9 | GSO_18
m_40834_21 | UCLV49194 | DirectTerminal | TRUE | 17 | GSO_18
m_40836_21 | UCLV49196 | DirectTerminal | TRUE | 42 | GSO_18
m_40899_21 | UCLV49253 | DirectTerminal | TRUE | 23 | GSO_18
m_40901_21 | UCLV49255 | DirectTerminal | TRUE | 17 | GSO_18
m_40963_21 | UCLV49311 | DirectTerminal | TRUE | 46 | GSO_18
m_40976_21 | UCLV49323 | DirectTerminal | TRUE | 23 | GSO_18
m_40978_21 | UCLV49325 | DirectTerminal | TRUE | 18 | GSO_18
m_41035_21 | UCLV49378 | DirectTerminal | TRUE | 41 | GSO_18
m_41049_21 | UCLV49390 | DirectTerminal | TRUE | 20 | GSO_18
m_41120_21 | UCLV49455 | DirectTerminal | TRUE | 22 | GSO_18
m_41122_21 | UCLV49457 | DirectTerminal | TRUE | 18 | GSO_18
m_41184_21 | UCLV49514 | DirectTerminal | TRUE | 24 | GSO_18
m_41186_21 | UCLV49516 | DirectTerminal | TRUE | 16 | GSO_18
m_41257_21 | UCLV49581 | DirectTerminal | TRUE | 17 | GSO_18
m_41260_21 | UCLV49584 | DirectTerminal | TRUE | 7 | GSO_18
m_41323_21 | UCLV49644 | DirectTerminal | TRUE | 24 | GSO_18
m_41325_21 | UCLV49646 | DirectTerminal | TRUE | 16 | GSO_18
m_41392_21 | UCLV49707 | DirectTerminal | TRUE | 22 | GSO_18
m_421_21 | UCLV10440 | DirectTerminal | TRUE | 7 | GSO_18
m_423_21 | UCLV10442 | DirectTerminal | TRUE | 9 | GSO_18
m_42346_21 | UCLV50618 | DirectTerminal | TRUE | 22 | GSO_18
m_42413_21 | UCLV50681 | DirectTerminal | TRUE | 19 | GSO_18
m_424_21 | UCLV10443 | DirectTerminal | TRUE | 7 | GSO_18
m_42494_21 | UCLV50755 | DirectTerminal | TRUE | 14 | GSO_18
m_425_21 | UCLV10444 | DirectTerminal | TRUE | 6 | GSO_18
m_42542_21 | UCLV50800 | DirectTerminal | TRUE | 19 | GSO_18
m_42544_21 | UCLV50802 | DirectTerminal | TRUE | 11 | GSO_18
m_42610_21 | UCLV50864 | DirectTerminal | TRUE | 20 | GSO_18
m_426_21 | UCLV10445 | DirectTerminal | TRUE | 7 | GSO_18
m_42676_21 | UCLV50928 | DirectTerminal | TRUE | 24 | GSO_18
m_42680_21 | UCLV50931 | DirectTerminal | TRUE | 20 | GSO_18
m_42682_21 | UCLV50933 | DirectTerminal | TRUE | 10 | GSO_18
m_42740_21 | UCLV50989 | DirectTerminal | TRUE | 41 | GSO_18
m_42751_21 | UCLV50999 | DirectTerminal | TRUE | 20 | GSO_18
m_42825_21 | UCLV51066 | DirectTerminal | TRUE | 22 | GSO_18
m_42827_21 | UCLV51068 | DirectTerminal | TRUE | 24 | GSO_18
m_42830_21 | UCLV51070 | DirectTerminal | TRUE | 10 | GSO_18
m_42906_21 | UCLV51139 | DirectTerminal | TRUE | 17 | GSO_18
m_42937_21 | UCLV51167 | DirectTerminal | TRUE | 5 | GSO_18
m_42975_21 | UCLV51200 | DirectTerminal | TRUE | 15 | GSO_18
m_43042_21 | UCLV51264 | DirectTerminal | TRUE | 24 | GSO_18
m_43115_21 | UCLV51333 | DirectTerminal | TRUE | 27 | GSO_18
m_43117_21 | UCLV51335 | DirectTerminal | TRUE | 47 | GSO_18
m_43183_21 | UCLV51397 | DirectTerminal | TRUE | 23 | GSO_18
m_43185_21 | UCLV51399 | DirectTerminal | TRUE | 17 | GSO_18
m_43189_21 | UCLV51401 | DirectTerminal | TRUE | 12 | GSO_18
m_44154_21 | UCLV52359 | DirectTerminal | TRUE | 41 | GSO_18
m_44165_21 | UCLV52369 | DirectTerminal | TRUE | 26 | GSO_18
m_44169_21 | UCLV52372 | DirectTerminal | TRUE | 19 | GSO_18
m_44203_21 | UCLV52404 | DirectTerminal | TRUE | 9 | GSO_18
m_44239_21 | UCLV52438 | DirectTerminal | TRUE | 19 | GSO_18
m_44242_21 | UCLV52440 | DirectTerminal | TRUE | 16 | GSO_18
m_44244_21 | UCLV52442 | DirectTerminal | TRUE | 15 | GSO_18
m_44310_21 | UCLV52503 | DirectTerminal | TRUE | 17 | GSO_18
m_44363_21 | UCLV52555 | DirectTerminal | TRUE | 15 | GSO_18
m_44364_21 | UCLV52556 | DirectTerminal | TRUE | 15 | GSO_18
m_44427_21 | UCLV52616 | DirectTerminal | TRUE | 20 | GSO_18
m_44430_21 | UCLV52619 | DirectTerminal | TRUE | 40 | GSO_18
m_44493_21 | UCLV52679 | DirectTerminal | TRUE | 20 | GSO_18
m_44495_21 | UCLV52680 | DirectTerminal | TRUE | 22 | GSO_18
m_44497_21 | UCLV52682 | DirectTerminal | TRUE | 13 | GSO_18
m_44569_21 | UCLV52751 | DirectTerminal | TRUE | 18 | GSO_18
m_44571_21 | UCLV52753 | DirectTerminal | TRUE | 16 | GSO_18
m_44628_21 | UCLV52808 | DirectTerminal | TRUE | 38 | GSO_18
m_44638_21 | UCLV52817 | DirectTerminal | TRUE | 20 | GSO_18
m_44705_21 | UCLV52880 | DirectTerminal | TRUE | 15 | GSO_18
m_44708_21 | UCLV52883 | DirectTerminal | TRUE | 11 | GSO_18
m_44776_21 | UCLV52948 | DirectTerminal | TRUE | 25 | GSO_18
m_44779_21 | UCLV52950 | DirectTerminal | TRUE | 46 | GSO_18
m_44861_21 | UCLV53026 | DirectTerminal | TRUE | 21 | GSO_18
m_44863_21 | UCLV53028 | DirectTerminal | TRUE | 16 | GSO_18
m_44925_21 | UCLV53088 | DirectTerminal | TRUE | 17 | GSO_18
m_44928_21 | UCLV53090 | DirectTerminal | TRUE | 21 | GSO_18
m_44989_21 | UCLV53146 | DirectTerminal | TRUE | 16 | GSO_18
m_45680_21 | UCLV53824 | DirectTerminal | TRUE | 20 | GSO_18
m_45683_21 | UCLV53827 | DirectTerminal | TRUE | 21 | GSO_18
m_45818_21 | UCLV53954 | DirectTerminal | TRUE | 16 | GSO_18
m_45821_21 | UCLV53957 | DirectTerminal | TRUE | 7 | GSO_18
m_45886_21 | UCLV54019 | DirectTerminal | TRUE | 20 | GSO_18
m_45890_21 | UCLV54022 | DirectTerminal | TRUE | 37 | GSO_18
m_45911_21 | UCLV54042 | DirectTerminal | TRUE | 14 | GSO_18
m_45945_21 | UCLV54074 | DirectTerminal | TRUE | 24 | GSO_18
m_45948_21 | UCLV54077 | DirectTerminal | TRUE | 9 | GSO_18
m_46009_21 | UCLV54134 | DirectTerminal | TRUE | 22 | GSO_18
m_46011_21 | UCLV54136 | DirectTerminal | TRUE | 17 | GSO_18
m_46013_21 | UCLV54138 | DirectTerminal | TRUE | 10 | GSO_18
m_46066_21 | UCLV54189 | DirectTerminal | TRUE | 42 | GSO_18
m_46076_21 | UCLV54198 | DirectTerminal | TRUE | 22 | GSO_18
m_46146_21 | UCLV54260 | DirectTerminal | TRUE | 23 | GSO_18
m_46219_21 | UCLV54328 | DirectTerminal | TRUE | 10 | GSO_18
m_46291_21 | UCLV54397 | DirectTerminal | TRUE | 17 | GSO_18
m_46350_21 | UCLV54451 | DirectTerminal | TRUE | 45 | GSO_18
m_46440_21 | UCLV54536 | DirectTerminal | TRUE | 22 | GSO_18
m_46443_21 | UCLV54539 | DirectTerminal | TRUE | 44 | GSO_18
m_46506_21 | UCLV54599 | DirectTerminal | TRUE | 21 | GSO_18
m_46510_21 | UCLV54601 | DirectTerminal | TRUE | 24 | GSO_18
m_46513_21 | UCLV54604 | DirectTerminal | TRUE | 12 | GSO_18
m_46579_21 | UCLV54667 | DirectTerminal | TRUE | 19 | GSO_18
m_46622_21 | UCLV54705 | DirectTerminal | TRUE | 37 | GSO_18
m_46632_21 | UCLV54714 | DirectTerminal | TRUE | 24 | GSO_18
m_46635_21 | UCLV54717 | DirectTerminal | TRUE | 22 | GSO_18
m_46702_21 | UCLV54779 | DirectTerminal | TRUE | 13 | GSO_18
m_46705_21 | UCLV54781 | DirectTerminal | TRUE | 15 | GSO_18
m_46775_21 | UCLV54847 | DirectTerminal | TRUE | 22 | GSO_18
m_46848_21 | UCLV54916 | DirectTerminal | TRUE | 18 | GSO_18
m_46912_21 | UCLV54977 | DirectTerminal | TRUE | 23 | GSO_18
m_46989_21 | UCLV55046 | DirectTerminal | TRUE | 11 | GSO_18
m_47052_21 | UCLV55102 | DirectTerminal | TRUE | 20 | GSO_18
m_47054_21 | UCLV55104 | DirectTerminal | TRUE | 20 | GSO_18
m_47119_21 | UCLV55163 | DirectTerminal | TRUE | 17 | GSO_18
m_47122_21 | UCLV55166 | DirectTerminal | TRUE | 11 | GSO_18
m_47189_21 | UCLV55227 | DirectTerminal | TRUE | 22 | GSO_18
m_47257_21 | UCLV55291 | DirectTerminal | TRUE | 24 | GSO_18
m_47304_21 | UCLV55333 | DirectTerminal | TRUE | 22 | GSO_18
m_47306_21 | UCLV55335 | DirectTerminal | TRUE | 18 | GSO_18
m_47309_21 | UCLV55338 | DirectTerminal | TRUE | 10 | GSO_18
m_47366_21 | UCLV55390 | DirectTerminal | TRUE | 23 | GSO_18
m_47368_21 | UCLV55392 | DirectTerminal | TRUE | 24 | GSO_18
m_47440_21 | UCLV55459 | DirectTerminal | TRUE | 17 | GSO_18
m_47558_21 | UCLV55569 | DirectTerminal | TRUE | 19 | GSO_18
m_47561_21 | UCLV55571 | DirectTerminal | TRUE | 17 | GSO_18
m_47562_21 | UCLV55572 | DirectTerminal | TRUE | 7 | GSO_18
m_47625_21 | UCLV55631 | DirectTerminal | TRUE | 21 | GSO_18
m_47627_21 | UCLV55633 | DirectTerminal | TRUE | 35 | GSO_18
m_47683_21 | UCLV55691 | DirectTerminal | TRUE | 20 | GSO_18
m_47741_21 | UCLV55749 | DirectTerminal | TRUE | 20 | GSO_18
m_47809_21 | UCLV55817 | DirectTerminal | TRUE | 21 | GSO_18
m_47811_21 | UCLV55819 | DirectTerminal | TRUE | 18 | GSO_18
m_47880_21 | UCLV55885 | DirectTerminal | TRUE | 26 | GSO_18
m_47950_21 | UCLV55950 | DirectTerminal | TRUE | 26 | GSO_18
m_47953_21 | UCLV55953 | DirectTerminal | TRUE | 38 | GSO_18
m_48006_21 | UCLV56002 | DirectTerminal | TRUE | 47 | GSO_18
m_48017_21 | UCLV56012 | DirectTerminal | TRUE | 20 | GSO_18
m_48019_21 | UCLV56014 | DirectTerminal | TRUE | 21 | GSO_18
m_48085_21 | UCLV56075 | DirectTerminal | TRUE | 20 | GSO_18
m_481_21 | UCLV10495 | DirectTerminal | TRUE | 34 | GSO_18
m_48156_21 | UCLV56140 | DirectTerminal | TRUE | 19 | GSO_18
m_48159_21 | UCLV56143 | DirectTerminal | TRUE | 11 | GSO_18
m_48203_21 | UCLV56184 | DirectTerminal | TRUE | 16 | GSO_18
m_482_21 | UCLV10496 | DirectTerminal | TRUE | 25 | GSO_18
m_48278_21 | UCLV56254 | DirectTerminal | TRUE | 18 | GSO_18
m_48280_21 | UCLV56256 | DirectTerminal | TRUE | 18 | GSO_18
m_48281_21 | UCLV56257 | DirectTerminal | TRUE | 9 | GSO_18
m_483_21 | UCLV10497 | DirectTerminal | TRUE | 20 | GSO_18
m_48353_21 | UCLV56323 | DirectTerminal | TRUE | 19 | GSO_18
m_48355_21 | UCLV56325 | DirectTerminal | TRUE | 19 | GSO_18
m_48390_21 | UCLV56357 | DirectTerminal | TRUE | 24 | GSO_18
m_484_21 | UCLV10498 | DirectTerminal | TRUE | 36 | GSO_18
m_48464_21 | UCLV56424 | DirectTerminal | TRUE | 19 | GSO_18
m_485_21 | UCLV10499 | DirectTerminal | TRUE | 37 | GSO_18
m_48525_21 | UCLV56481 | DirectTerminal | TRUE | 33 | GSO_18
m_48537_21 | UCLV56492 | DirectTerminal | TRUE | 17 | GSO_18
m_48606_21 | UCLV56555 | DirectTerminal | TRUE | 17 | GSO_18
m_48648_21 | UCLV56596 | DirectTerminal | TRUE | 23 | GSO_18
m_48719_21 | UCLV56661 | DirectTerminal | TRUE | 18 | GSO_18
m_48787_21 | UCLV56725 | DirectTerminal | TRUE | 22 | GSO_18
m_48790_21 | UCLV56728 | DirectTerminal | TRUE | 21 | GSO_18
m_488_21 | UCLV10500 | DirectTerminal | TRUE | 13 | GSO_18
m_48856_21 | UCLV56792 | DirectTerminal | TRUE | 11 | GSO_18
m_48911_21 | UCLV56841 | DirectTerminal | TRUE | 26 | GSO_18
m_48914_21 | UCLV56844 | DirectTerminal | TRUE | 17 | GSO_18
m_489_21 | UCLV10501 | DirectTerminal | TRUE | 21 | GSO_18
m_48952_21 | UCLV56879 | DirectTerminal | TRUE | 9 | GSO_18
m_48989_21 | UCLV56911 | DirectTerminal | TRUE | 19 | GSO_18
m_48994_21 | UCLV56916 | DirectTerminal | TRUE | 10 | GSO_18
m_490_21 | UCLV10502 | DirectTerminal | TRUE | 18 | GSO_18
m_49028_21 | UCLV56948 | DirectTerminal | TRUE | 8 | GSO_18
m_49065_21 | UCLV56981 | DirectTerminal | TRUE | 20 | GSO_18
m_49069_21 | UCLV56985 | DirectTerminal | TRUE | 7 | GSO_18
m_491_21 | UCLV10503 | DirectTerminal | TRUE | 22 | GSO_18
m_49136_21 | UCLV57048 | DirectTerminal | TRUE | 23 | GSO_18
m_49202_21 | UCLV57110 | DirectTerminal | TRUE | 20 | GSO_18
m_49206_21 | UCLV57114 | DirectTerminal | TRUE | 10 | GSO_18
m_492_21 | UCLV10504 | DirectTerminal | TRUE | 22 | GSO_18
m_49274_21 | UCLV57176 | DirectTerminal | TRUE | 26 | GSO_18
m_49276_21 | UCLV57178 | DirectTerminal | TRUE | 17 | GSO_18
m_493_21 | UCLV10505 | DirectTerminal | TRUE | 30 | GSO_18
m_49349_21 | UCLV57243 | DirectTerminal | TRUE | 18 | GSO_18
m_49396_21 | UCLV57286 | DirectTerminal | TRUE | 12 | GSO_18
m_49398_21 | UCLV57288 | DirectTerminal | TRUE | 16 | GSO_18
m_49399_21 | UCLV57289 | DirectTerminal | TRUE | 12 | GSO_18
m_494_21 | UCLV10506 | DirectTerminal | TRUE | 15 | GSO_18
m_49470_21 | UCLV57355 | DirectTerminal | TRUE | 19 | GSO_18
m_49537_21 | UCLV57419 | DirectTerminal | TRUE | 20 | GSO_18
m_49600_21 | UCLV57477 | DirectTerminal | TRUE | 19 | GSO_18
m_49665_21 | UCLV57539 | DirectTerminal | TRUE | 16 | GSO_18
m_49738_21 | UCLV57604 | DirectTerminal | TRUE | 20 | GSO_18
m_49740_21 | UCLV57606 | DirectTerminal | TRUE | 16 | GSO_18
m_49807_21 | UCLV57668 | DirectTerminal | TRUE | 17 | GSO_18
m_49811_21 | UCLV57671 | DirectTerminal | TRUE | 9 | GSO_18
m_49854_21 | UCLV57711 | DirectTerminal | TRUE | 19 | GSO_18
m_49925_21 | UCLV57778 | DirectTerminal | TRUE | 22 | GSO_18
m_49928_21 | UCLV57780 | DirectTerminal | TRUE | 21 | GSO_18
m_49986_21 | UCLV57835 | DirectTerminal | TRUE | 22 | GSO_18
m_49988_21 | UCLV57837 | DirectTerminal | TRUE | 15 | GSO_18
m_50087_21 | UCLV57927 | DirectTerminal | TRUE | 19 | GSO_18
m_50107_21 | UCLV57945 | DirectTerminal | TRUE | 33 | GSO_18
m_50118_21 | UCLV57955 | DirectTerminal | TRUE | 16 | GSO_18
m_50184_21 | UCLV58018 | DirectTerminal | TRUE | 22 | GSO_18
m_50252_21 | UCLV58083 | DirectTerminal | TRUE | 16 | GSO_18
m_50255_21 | UCLV58086 | DirectTerminal | TRUE | 17 | GSO_18
m_50257_21 | UCLV58088 | DirectTerminal | TRUE | 17 | GSO_18
m_50321_21 | UCLV58148 | DirectTerminal | TRUE | 42 | GSO_18
m_50333_21 | UCLV58159 | DirectTerminal | TRUE | 20 | GSO_18
m_50336_21 | UCLV58161 | DirectTerminal | TRUE | 16 | GSO_18
m_50398_21 | UCLV58219 | DirectTerminal | TRUE | 24 | GSO_18
m_50462_21 | UCLV58278 | DirectTerminal | TRUE | 21 | GSO_18
m_50466_21 | UCLV58281 | DirectTerminal | TRUE | 12 | GSO_18
m_50524_21 | UCLV58339 | DirectTerminal | TRUE | 6 | GSO_18
m_50564_21 | UCLV58376 | DirectTerminal | TRUE | 21 | GSO_18
m_50618_21 | UCLV58427 | DirectTerminal | TRUE | 44 | GSO_18
m_50629_21 | UCLV58437 | DirectTerminal | TRUE | 24 | GSO_18
m_50631_21 | UCLV58439 | DirectTerminal | TRUE | 20 | GSO_18
m_50635_21 | UCLV58442 | DirectTerminal | TRUE | 14 | GSO_18
m_50697_21 | UCLV58499 | DirectTerminal | TRUE | 22 | GSO_18
m_50702_21 | UCLV58502 | DirectTerminal | TRUE | 15 | GSO_18
m_50755_21 | UCLV58550 | DirectTerminal | TRUE | 19 | GSO_18
m_50757_21 | UCLV58552 | DirectTerminal | TRUE | 15 | GSO_18
m_50809_21 | UCLV58601 | DirectTerminal | TRUE | 31 | GSO_18
m_50821_21 | UCLV58612 | DirectTerminal | TRUE | 18 | GSO_18
m_50823_21 | UCLV58614 | DirectTerminal | TRUE | 18 | GSO_18
m_50891_21 | UCLV58679 | DirectTerminal | TRUE | 17 | GSO_18
m_50895_21 | UCLV58682 | DirectTerminal | TRUE | 6 | GSO_18
m_51002_21 | UCLV58781 | DirectTerminal | TRUE | 17 | GSO_18
m_51071_21 | UCLV58846 | DirectTerminal | TRUE | 20 | GSO_18
m_51073_21 | UCLV58848 | DirectTerminal | TRUE | 16 | GSO_18
m_51076_21 | UCLV58850 | DirectTerminal | TRUE | 12 | GSO_18
m_51148_21 | UCLV58916 | DirectTerminal | TRUE | 12 | GSO_18
m_51196_21 | UCLV58961 | DirectTerminal | TRUE | 23 | GSO_18
m_51199_21 | UCLV58964 | DirectTerminal | TRUE | 22 | GSO_18
m_51273_21 | UCLV59030 | DirectTerminal | TRUE | 14 | GSO_18
m_51403_21 | UCLV59155 | DirectTerminal | TRUE | 23 | GSO_18
m_51466_21 | UCLV59215 | DirectTerminal | TRUE | 20 | GSO_18
m_51468_21 | UCLV59217 | DirectTerminal | TRUE | 18 | GSO_18
m_51517_21 | UCLV59265 | DirectTerminal | TRUE | 39 | GSO_18
m_51529_21 | UCLV59276 | DirectTerminal | TRUE | 19 | GSO_18
m_51601_21 | UCLV59342 | DirectTerminal | TRUE | 19 | GSO_18
m_51692_21 | UCLV59430 | DirectTerminal | TRUE | 26 | GSO_18
m_51693_21 | UCLV59431 | DirectTerminal | TRUE | 24 | GSO_18
m_51763_21 | UCLV59497 | DirectTerminal | TRUE | 17 | GSO_18
m_51765_21 | UCLV59499 | DirectTerminal | TRUE | 12 | GSO_18
m_51837_21 | UCLV59566 | DirectTerminal | TRUE | 20 | GSO_18
m_51879_21 | UCLV59605 | DirectTerminal | TRUE | 17 | GSO_18
m_51948_21 | UCLV59670 | DirectTerminal | TRUE | 21 | GSO_18
m_52018_21 | UCLV59736 | DirectTerminal | TRUE | 20 | GSO_18
m_52020_21 | UCLV59738 | DirectTerminal | TRUE | 11 | GSO_18
m_52090_21 | UCLV59803 | DirectTerminal | TRUE | 18 | GSO_18
m_52113_21 | UCLV59825 | DirectTerminal | TRUE | 25 | GSO_18
m_52144_21 | UCLV59854 | DirectTerminal | TRUE | 26 | GSO_18
m_52146_21 | UCLV59856 | DirectTerminal | TRUE | 21 | GSO_18
m_52217_21 | UCLV59922 | DirectTerminal | TRUE | 20 | GSO_18
m_52219_21 | UCLV59924 | DirectTerminal | TRUE | 9 | GSO_18
m_52282_21 | UCLV59985 | DirectTerminal | TRUE | 22 | GSO_18
m_52325_21 | UCLV60024 | DirectTerminal | TRUE | 23 | GSO_18
m_52328_21 | UCLV60027 | DirectTerminal | TRUE | 8 | GSO_18
m_52390_21 | UCLV60086 | DirectTerminal | TRUE | 25 | GSO_18
m_52392_21 | UCLV60088 | DirectTerminal | TRUE | 22 | GSO_18
m_52449_21 | UCLV60142 | DirectTerminal | TRUE | 42 | GSO_18
m_52460_21 | UCLV60152 | DirectTerminal | TRUE | 20 | GSO_18
m_52533_21 | UCLV60218 | DirectTerminal | TRUE | 20 | GSO_18
m_52588_21 | UCLV60270 | DirectTerminal | TRUE | 17 | GSO_18
m_52660_21 | UCLV60337 | DirectTerminal | TRUE | 16 | GSO_18
m_52731_21 | UCLV60404 | DirectTerminal | TRUE | 21 | GSO_18
m_52733_21 | UCLV60406 | DirectTerminal | TRUE | 23 | GSO_18
m_52787_21 | UCLV60459 | DirectTerminal | TRUE | 19 | GSO_18
m_52851_21 | UCLV60520 | DirectTerminal | TRUE | 22 | GSO_18
m_52853_21 | UCLV60522 | DirectTerminal | TRUE | 20 | GSO_18
m_52926_21 | UCLV60590 | DirectTerminal | TRUE | 19 | GSO_18
m_52928_21 | UCLV60592 | DirectTerminal | TRUE | 18 | GSO_18
m_52997_21 | UCLV60658 | DirectTerminal | TRUE | 21 | GSO_18
m_53016_21 | UCLV60676 | DirectTerminal | TRUE | 44 | GSO_18
m_53029_21 | UCLV60688 | DirectTerminal | TRUE | 24 | GSO_18
m_53032_21 | UCLV60690 | DirectTerminal | TRUE | 23 | GSO_18
m_53085_21 | UCLV60740 | DirectTerminal | TRUE | 36 | GSO_18
m_53098_21 | UCLV60752 | DirectTerminal | TRUE | 22 | GSO_18
m_53166_21 | UCLV60818 | DirectTerminal | TRUE | 16 | GSO_18
m_53170_21 | UCLV60821 | DirectTerminal | TRUE | 17 | GSO_18
m_53233_21 | UCLV60884 | DirectTerminal | TRUE | 21 | GSO_18
m_53280_21 | UCLV60927 | DirectTerminal | TRUE | 22 | GSO_18
m_53334_21 | UCLV60979 | DirectTerminal | TRUE | 48 | GSO_18
m_53347_21 | UCLV60990 | DirectTerminal | TRUE | 23 | GSO_18
m_53407_21 | UCLV61045 | DirectTerminal | TRUE | 39 | GSO_18
m_53415_21 | UCLV61052 | DirectTerminal | TRUE | 22 | GSO_18
m_53476_21 | UCLV61110 | DirectTerminal | TRUE | 19 | GSO_18
m_53538_21 | UCLV61167 | DirectTerminal | TRUE | 17 | GSO_18
m_53615_21 | UCLV61238 | DirectTerminal | TRUE | 25 | GSO_18
m_53686_21 | UCLV61303 | DirectTerminal | TRUE | 23 | GSO_18
m_53688_21 | UCLV61305 | DirectTerminal | TRUE | 18 | GSO_18
m_53728_21 | UCLV61344 | DirectTerminal | TRUE | 21 | GSO_18
m_53791_21 | UCLV61403 | DirectTerminal | TRUE | 20 | GSO_18
m_53793_21 | UCLV61405 | DirectTerminal | TRUE | 17 | GSO_18
m_53860_21 | UCLV61467 | DirectTerminal | TRUE | 17 | GSO_18
m_53991_21 | UCLV61587 | DirectTerminal | TRUE | 11 | GSO_18
m_53996_21 | UCLV61592 | DirectTerminal | TRUE | 10 | GSO_18
m_54064_21 | UCLV61653 | DirectTerminal | TRUE | 17 | GSO_18
m_54069_21 | UCLV61658 | DirectTerminal | TRUE | 7 | GSO_18
m_54130_21 | UCLV61717 | DirectTerminal | TRUE | 20 | GSO_18
m_54132_21 | UCLV61719 | DirectTerminal | TRUE | 16 | GSO_18
m_54198_21 | UCLV61782 | DirectTerminal | TRUE | 20 | GSO_18
m_54201_21 | UCLV61785 | DirectTerminal | TRUE | 15 | GSO_18
m_54259_21 | UCLV61839 | DirectTerminal | TRUE | 25 | GSO_18
m_54261_21 | UCLV61840 | DirectTerminal | TRUE | 16 | GSO_18
m_54330_21 | UCLV61904 | DirectTerminal | TRUE | 19 | GSO_18
m_54334_21 | UCLV61908 | DirectTerminal | TRUE | 5 | GSO_18
m_54430_21 | UCLV61995 | DirectTerminal | TRUE | 20 | GSO_18
m_54432_21 | UCLV61997 | DirectTerminal | TRUE | 19 | GSO_18
m_54508_21 | UCLV62065 | DirectTerminal | TRUE | 13 | GSO_18
m_54577_21 | UCLV62128 | DirectTerminal | TRUE | 15 | GSO_18
m_54691_21 | UCLV62235 | DirectTerminal | TRUE | 19 | GSO_18
m_54697_21 | UCLV62240 | DirectTerminal | TRUE | 8 | GSO_18
m_54756_21 | UCLV62297 | DirectTerminal | TRUE | 22 | GSO_18
m_54758_21 | UCLV62299 | DirectTerminal | TRUE | 22 | GSO_18
m_54879_21 | UCLV62412 | DirectTerminal | TRUE | 22 | GSO_18
m_54881_21 | UCLV62414 | DirectTerminal | TRUE | 22 | GSO_18
m_54953_21 | UCLV62481 | DirectTerminal | TRUE | 13 | GSO_18
m_54955_21 | UCLV62483 | DirectTerminal | TRUE | 15 | GSO_18
m_55027_21 | UCLV62550 | DirectTerminal | TRUE | 18 | GSO_18
m_55031_21 | UCLV62554 | DirectTerminal | TRUE | 17 | GSO_18
m_55140_21 | UCLV62658 | DirectTerminal | TRUE | 22 | GSO_18
m_55144_21 | UCLV62661 | DirectTerminal | TRUE | 7 | GSO_18
m_55202_21 | UCLV62716 | DirectTerminal | TRUE | 15 | GSO_18
m_55270_21 | UCLV62779 | DirectTerminal | TRUE | 20 | GSO_18
m_55274_21 | UCLV62782 | DirectTerminal | TRUE | 4 | GSO_18
m_55310_21 | UCLV62819 | DirectTerminal | TRUE | 20 | GSO_18
m_55379_21 | UCLV62885 | DirectTerminal | TRUE | 16 | GSO_18
m_55454_21 | UCLV62955 | DirectTerminal | TRUE | 20 | GSO_18
m_55456_21 | UCLV62957 | DirectTerminal | TRUE | 19 | GSO_18
m_55507_21 | UCLV63004 | DirectTerminal | TRUE | 42 | GSO_18
m_55517_21 | UCLV63013 | DirectTerminal | TRUE | 26 | GSO_18
m_55571_21 | UCLV63067 | DirectTerminal | TRUE | 24 | GSO_18
m_55575_21 | UCLV63070 | DirectTerminal | TRUE | 28 | GSO_18
m_55644_21 | UCLV63138 | DirectTerminal | TRUE | 19 | GSO_18
m_55716_21 | UCLV63205 | DirectTerminal | TRUE | 22 | GSO_18
m_55718_21 | UCLV63207 | DirectTerminal | TRUE | 16 | GSO_18
m_55771_21 | UCLV63258 | DirectTerminal | TRUE | 19 | GSO_18
m_55827_21 | UCLV63310 | DirectTerminal | TRUE | 44 | GSO_18
m_55839_21 | UCLV63321 | DirectTerminal | TRUE | 23 | GSO_18
m_55876_21 | UCLV63355 | DirectTerminal | TRUE | 21 | GSO_18
m_55904_21 | UCLV63382 | DirectTerminal | TRUE | 21 | GSO_18
m_55907_21 | UCLV63385 | DirectTerminal | TRUE | 14 | GSO_18
m_55983_21 | UCLV63455 | DirectTerminal | TRUE | 14 | GSO_18
m_55984_21 | UCLV63456 | DirectTerminal | TRUE | 5 | GSO_18
m_56044_21 | UCLV63511 | DirectTerminal | TRUE | 22 | GSO_18
m_56114_21 | UCLV63578 | DirectTerminal | TRUE | 24 | GSO_18
m_56180_21 | UCLV63639 | DirectTerminal | TRUE | 19 | GSO_18
m_56183_21 | UCLV63641 | DirectTerminal | TRUE | 18 | GSO_18
m_56185_21 | UCLV63643 | DirectTerminal | TRUE | 13 | GSO_18
m_56220_21 | UCLV63675 | DirectTerminal | TRUE | 21 | GSO_18
m_56285_21 | UCLV63738 | DirectTerminal | TRUE | 22 | GSO_18
m_56288_21 | UCLV63740 | DirectTerminal | TRUE | 18 | GSO_18
m_56290_21 | UCLV63742 | DirectTerminal | TRUE | 13 | GSO_18
m_56358_21 | UCLV63807 | DirectTerminal | TRUE | 25 | GSO_18
m_56427_21 | UCLV63870 | DirectTerminal | TRUE | 18 | GSO_18
m_56468_21 | UCLV63908 | DirectTerminal | TRUE | 17 | GSO_18
m_56471_21 | UCLV63910 | DirectTerminal | TRUE | 17 | GSO_18
m_56473_21 | UCLV63912 | DirectTerminal | TRUE | 11 | GSO_18
m_56543_21 | UCLV63979 | DirectTerminal | TRUE | 21 | GSO_18
m_56608_21 | UCLV64039 | DirectTerminal | TRUE | 23 | GSO_18
m_56612_21 | UCLV64042 | DirectTerminal | TRUE | 15 | GSO_18
m_56730_21 | UCLV64154 | DirectTerminal | TRUE | 42 | GSO_18
m_56741_21 | UCLV64164 | DirectTerminal | TRUE | 20 | GSO_18
m_56743_21 | UCLV64166 | DirectTerminal | TRUE | 15 | GSO_18
m_56785_21 | UCLV64203 | DirectTerminal | TRUE | 9 | GSO_18
m_56818_21 | UCLV64233 | DirectTerminal | TRUE | 20 | GSO_18
m_56821_21 | UCLV64236 | DirectTerminal | TRUE | 10 | GSO_18
m_56852_21 | UCLV64267 | DirectTerminal | TRUE | 15 | GSO_18
m_56885_21 | UCLV64297 | DirectTerminal | TRUE | 21 | GSO_18
m_58172_21 | UCLV790 | DirectTerminal | TRUE | 7 | GSO_18
m_58185_21 | UCLV795 | DirectTerminal | TRUE | 6 | GSO_18
m_58252_21 | UCLV801 | DirectTerminal | TRUE | 14 | GSO_18
m_58263_21 | UCLV802 | DirectTerminal | TRUE | 8 | GSO_18
m_58274_21 | UCLV803 | DirectTerminal | TRUE | 13 | GSO_18
m_58285_21 | UCLV804 | DirectTerminal | TRUE | 14 | GSO_18
m_58295_21 | UCLV805 | DirectTerminal | TRUE | 14 | GSO_18
m_58306_21 | UCLV806 | DirectTerminal | TRUE | 13 | GSO_18
m_58316_21 | UCLV807 | DirectTerminal | TRUE | 14 | GSO_18
m_58327_21 | UCLV808 | DirectTerminal | TRUE | 12 | GSO_18
m_58338_21 | UCLV809 | DirectTerminal | TRUE | 13 | GSO_18
m_58350_21 | UCLV810 | DirectTerminal | TRUE | 16 | GSO_18
m_58361_21 | UCLV811 | DirectTerminal | TRUE | 10 | GSO_18
m_58372_21 | UCLV812 | DirectTerminal | TRUE | 11 | GSO_18
m_58382_21 | UCLV813 | DirectTerminal | TRUE | 14 | GSO_18
m_58393_21 | UCLV814 | DirectTerminal | TRUE | 13 | GSO_18
m_58624_21 | UCLV842 | DirectTerminal | TRUE | 22 | GSO_18
m_58635_21 | UCLV843 | DirectTerminal | TRUE | 26 | GSO_18
m_58646_21 | UCLV844 | DirectTerminal | TRUE | 25 | GSO_18
m_58657_21 | UCLV845 | DirectTerminal | TRUE | 19 | GSO_18
m_58690_21 | UCLV848 | DirectTerminal | TRUE | 16 | GSO_18
m_58713_21 | UCLV850 | DirectTerminal | TRUE | 18 | GSO_18
m_58724_21 | UCLV851 | DirectTerminal | TRUE | 20 | GSO_18
m_58735_21 | UCLV852 | DirectTerminal | TRUE | 18 | GSO_18
m_58768_21 | UCLV855 | DirectTerminal | TRUE | 24 | GSO_18
m_58790_21 | UCLV857 | DirectTerminal | TRUE | 20 | GSO_18
m_5880_21 | UCLV15920 | DirectTerminal | TRUE | 23 | GSO_18
m_58808_21 | UCLV8586 | DirectTerminal | TRUE | 21 | GSO_18
m_58809_21 | UCLV8587 | DirectTerminal | TRUE | 20 | GSO_18
m_58810_21 | UCLV8588 | DirectTerminal | TRUE | 18 | GSO_18
m_58811_21 | UCLV8589 | DirectTerminal | TRUE | 27 | GSO_18
m_5881_21 | UCLV15921 | DirectTerminal | TRUE | 22 | GSO_18
m_59998_21 | UCMV21 | DirectTerminal | TRUE | 19 | GSO_18
m_59999_21 | UCMV22 | DirectTerminal | TRUE | 27 | GSO_18
m_2755_22 | UCMV43 | DirectTerminal | TRUE | 2 | GSO_127

## Assumptions
Item | Assumption
Model purpose | Time-series thermal hosting capacity model used as the physical feasibility engine before optimization and Monte Carlo.
Primary measured total | Five-minute circuit-breaker SCADA is treated as feeder-level net real-power truth because it is the highest-frequency measured feeder total available.
Spatial load allocation | Hourly meter kWh determines relative spatial shares within each hour. Those shares are applied to every five-minute breaker observation in that hour.
Why hourly meter data are not interpolated to artificial five-minute behavior | The model does not invent intra-hour customer shapes. It holds each meter's observed hourly spatial share constant within the hour and lets measured five-minute breaker SCADA provide the actual intra-hour feeder magnitude.
Meter-breaker validation | Meter totals are re-audited against hourly breaker energy using correlation, normalized MAE, and annual energy ratio. This validates source consistency; it is not used as a fitted predictive relationship.
Physical constraints vs statistical weights | Line, transformer, and breaker ratings are hard engineering limits in the thermal model. They are not statistically weighted or selected based on correlation.
Topology | Open switchable elements are excluded. If the active network is radial, the breaker-to-load path is unique. If cycles remain, a shortest-path tree is used and the feeder is explicitly flagged for review.
Parallel elements | Without impedance, current sharing between truly parallel elements cannot be calculated. For a parallel node pair the lowest usable individual thermal rating is used conservatively and any candidate crossing that pair is flagged.
Meter mapping | Meters are attached to reachable topology terminals, then upstream-element connectivity. Unresolved meters are retained at the feeder root and the mapping percentage is reported; they are not silently discarded.
Power factor base case | 0.95 is the base screening power factor used to translate apparent/current equipment ratings to real-power capacity.
Power factor sensitivity | Candidate results are recalculated at PF values [0.9, 0.95, 1.0] so conclusions are not dependent on a single untested PF assumption.
Three-phase line capacity | P_limit = sqrt(3) x V_LL x I_rating x PF.
Two-phase line capacity | P_limit = V_LL x I_rating x PF.
Single-phase line capacity | V_LN is approximated as V_LL / sqrt(3), then P_limit = V_LN x I_rating x PF.
Transformer capacity | Real-power thermal limit = rating_kVA / 1000 x PF.
Breaker capacity | Real-power thermal limit = rating_kVA / 1000 x PF.
Incremental data-center load | A positive data-center load is added at the candidate point and therefore adds to every constrained element on its breaker path.
Existing reverse flow | Existing branch flows retain their modeled sign. Incremental positive-load headroom is capacity minus signed existing flow, while any pre-existing absolute rating exceedance is set to zero available hosting for that interval.
Baseline rating exceedances | Existing modeled rating exceedances are audited separately and are not automatically assumed to represent a real utility violation. Candidate-path exceedances are explicitly flagged.
Unrelated downstream exceedances | An existing exceedance on a branch that the candidate data-center load does not traverse does not directly reduce that candidate's path headroom, but remains in the audit output.
Substation capacity | Explicit substation available capacity is still unavailable, so no substation-capacity ceiling is enforced. Shared-substation constraints must be added when reliable capacity values are obtained.
Voltage and AC power flow | Line R/X and transformer impedance are unavailable. The model therefore does not claim voltage-drop, reactive-power, losses, or AC power-flow validation.
PV and EV | Existing net effects are already present in breaker SCADA. Their exact spatial electrical injections are not separately inferred unless measured element-level profiles are explicitly modeled later.
Interpretation | Outputs are modeled five-minute thermal hosting capacity under the available EDM data, not utility-approved interconnection capacity.