## MILP_Readiness
ThermalRank | CandidateKey | GridID | SubstationID | CandidateLineID | CandidateNode | OriginalScreeningHostingMW | CandidateConfidenceFromPriorScreen | ModelStatus | ReviewFlags | Modeled5MinIntervals | ModeledHoursEquivalent | FirmHostingMW | HostingAvailable99PctIntervalsMW | HostingAvailable95PctIntervalsMW | MedianHostingMW | MeanHostingMW | MaximumHostingMW | FirmToMedianGapMW | IntervalsWithNoAdditionalHosting | PctIntervalsWithNoAdditionalHosting | BaselinePathRatingExceedanceIntervals | BaselinePathRatingExceedancePct | MostFrequentLimitingElementID | MostFrequentLimitingElementPct | FirmLimitTimestampUTC | FirmLimitElementID | PathHops | PathLineCount | PathTransformerCount | ParallelAmbiguityOnPath | MeterTopologyMappingPct | MeterBreakerCorrelation | MeterBreakerNMAEPct | FeederIsRadial | CycleRank_x | SubstationCapacityConstraintApplied | VoltageConstraintApplied | BasePowerFactor | TopologyResolution | TopologyMateriality | CycleRank_y | CandidatePathEdgesInCycles | AllCandidatePathEdgesAreBridges | CandidateLineIsBridge | UnresolvedMeterCount | UnresolvedAnnualEnergySharePct | PeakEstimatedUnresolved5MinMW | MappingMaterialityStatus | MappingMaterialityExplanation | FirmHostingAtMinimumPFMW | FirmHostingAtBasePFMW | FirmHostingAtMaximumPFMW | FirmHostingRangeAcrossPFMW | MaxRankShiftAcrossPF | PFRankingStatus | TopologyClearedForBaseMILP | MappingClearedForBaseMILP | NoBaselineCandidatePathExceedance | ThermalCandidateModelCompleted | ReadyForFeederBoundMILP | ReadyForFinalSubstationConstrainedMILP | RemainingFinalMILPBlocker | MILPReadinessNote | SubstationCandidateCount | SubstationSumFirmHostingMW_UpperBoundOnly
1 | GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | S_nCCTT45 | 13.5096 | High | Ready |  | 105348 | 8779 | 13.5096 | 13.516 | 13.5183 | 13.5228 | 13.5226 | 13.5312 | 0.013224 | 0 | 0 | 0 | 0 | line_5852_22 | 100 | 2024-01-20 07:00 | line_5852_22 | 2 | 1 | 0 | FALSE | 100 | 0.99996 | 3.8462 | TRUE | 0 | FALSE | FALSE | 0.95 | CLEAR_RADIAL | No mesh ambiguity remains after open-switch removal. | 0 | 0 | TRUE | TRUE | 0 | 0 | 0 | CLEAR_NO_UNRESOLVED_METERS | Every modeled meter is topologically resolved. | 12.7969 | 13.5096 | 14.2224 | 1.4255 | 0 | RANK_STABLE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | Explicit substation capacity not yet available | Ready for feeder-bound MILP; final portfolio still needs substation capacity. | 4 | 53.2566
2 | GSO_124¦line_6716_22 | GSO_124 | hvmv_1_22 | line_6716_22 | S_nCCTT913 | 13.4085 | High | Ready |  | 105348 | 8779 | 13.4085 | 13.4374 | 13.4467 | 13.4653 | 13.4646 | 13.4947 | 0.056832 | 0 | 0 | 0 | 0 | line_6716_22 | 100 | 2024-01-22 04:00 | line_6716_22 | 2 | 1 | 0 | FALSE | 100 | 0.99997 | 3.8457 | TRUE | 0 | FALSE | FALSE | 0.95 | CLEAR_RADIAL | No mesh ambiguity remains after open-switch removal. | 0 | 0 | TRUE | TRUE | 0 | 0 | 0 | CLEAR_NO_UNRESOLVED_METERS | Every modeled meter is topologically resolved. | 12.6957 | 13.4085 | 14.1213 | 1.4255 | 0 | RANK_STABLE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | Explicit substation capacity not yet available | Ready for feeder-bound MILP; final portfolio still needs substation capacity. | 4 | 53.2566
3 | GSO_123¦line_6019_22 | GSO_123 | hvmv_1_22 | line_6019_22 | S_nCCTT521 | 13.1777 | High | Ready |  | 105348 | 8779 | 13.1777 | 13.2323 | 13.2536 | 13.2976 | 13.2942 | 13.3495 | 0.11988 | 0 | 0 | 0 | 0 | line_6019_22 | 100 | 2024-01-22 04:00 | line_6019_22 | 2 | 1 | 0 | FALSE | 100 | 0.99993 | 3.8463 | TRUE | 0 | FALSE | FALSE | 0.95 | CLEAR_RADIAL | No mesh ambiguity remains after open-switch removal. | 0 | 0 | TRUE | TRUE | 0 | 0 | 0 | CLEAR_NO_UNRESOLVED_METERS | Every modeled meter is topologically resolved. | 12.465 | 13.1777 | 13.8905 | 1.4255 | 0 | RANK_STABLE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | Explicit substation capacity not yet available | Ready for feeder-bound MILP; final portfolio still needs substation capacity. | 4 | 53.2566
4 | GSO_121¦line_3530_22 | GSO_121 | hvmv_1_22 | line_3530_22 | S_nCCTT0 | 13.1607 | High | ReadyWithReviewFlags | MeshedTopologyUsesShortestPathTree | 105348 | 8779 | 13.1607 | 13.2094 | 13.2378 | 13.3041 | 13.2977 | 13.3561 | 0.14333 | 0 | 0 | 0 | 0 | line_3530_22 | 100 | 2024-01-17 23:00 | line_3530_22 | 2 | 1 | 0 | FALSE | 100 | 0.98983 | 3.0957 | FALSE | 1 | FALSE | FALSE | 0.95 | CLEAR_CYCLES_OFF_CANDIDATE_PATH | Cycles exist elsewhere on the feeder, but every candidate-path edge is a bridge and none lies in a cycle. | 1 | 0 | TRUE | TRUE | 0 | 0 | 0 | CLEAR_NO_UNRESOLVED_METERS | Every modeled meter is topologically resolved. | 12.448 | 13.1607 | 13.8735 | 1.4255 | 0 | RANK_STABLE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | Explicit substation capacity not yet available | Ready for feeder-bound MILP; final portfolio still needs substation capacity. | 4 | 53.2566
5 | GSO_144¦line_5978_22 | GSO_144 | hvmv_5_22 | line_5978_22 | S_nCCTT504 | 11.2671 | High | Ready |  | 105348 | 8779 | 11.2671 | 11.2951 | 11.3099 | 11.3464 | 11.3426 | 11.3674 | 0.079236 | 0 | 0 | 0 | 0 | br_024_22 | 100 | 2024-01-20 21:00 | br_024_22 | 2 | 1 | 0 | FALSE | 100 | 0.99998 | 3.8453 | TRUE | 0 | FALSE | FALSE | 0.95 | CLEAR_RADIAL | No mesh ambiguity remains after open-switch removal. | 0 | 0 | TRUE | TRUE | 0 | 0 | 0 | CLEAR_NO_UNRESOLVED_METERS | Every modeled meter is topologically resolved. | 10.6671 | 11.2671 | 11.8671 | 1.2 | 0 | RANK_STABLE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | Explicit substation capacity not yet available | Ready for feeder-bound MILP; final portfolio still needs substation capacity. | 4 | 43.5602
6 | GSO_141¦line_4565_22 | GSO_141 | hvmv_5_22 | line_4565_22 | S_nCCTT1344 | 11.02 | High | Ready |  | 105348 | 8779 | 11.02 | 11.0816 | 11.1093 | 11.1705 | 11.1652 | 11.2388 | 0.15049 | 0 | 0 | 0 | 0 | br_021_22 | 100 | 2024-01-21 01:00 | br_021_22 | 2 | 1 | 0 | FALSE | 100 | 0.99996 | 3.8441 | TRUE | 0 | FALSE | FALSE | 0.95 | CLEAR_RADIAL | No mesh ambiguity remains after open-switch removal. | 0 | 0 | TRUE | TRUE | 0 | 0 | 0 | CLEAR_NO_UNRESOLVED_METERS | Every modeled meter is topologically resolved. | 10.42 | 11.02 | 11.62 | 1.2 | 0 | RANK_STABLE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | Explicit substation capacity not yet available | Ready for feeder-bound MILP; final portfolio still needs substation capacity. | 4 | 43.5602
7 | GSO_145¦line_6170_22 | GSO_145 | hvmv_5_22 | line_6170_22 | S_nCCTT59 | 10.6656 | Medium | ReadyWithReviewFlags | MeterTopologyMapping<95% ¦ MeshedTopologyUsesShortestPathTree | 105348 | 8779 | 10.6656 | 10.7801 | 10.8397 | 10.9717 | 10.9595 | 11.105 | 0.30613 | 0 | 0 | 0 | 0 | br_025_22 | 100 | 2024-01-21 04:00 | br_025_22 | 2 | 1 | 0 | FALSE | 90.9677 | 0.90219 | 4.8665 | FALSE | 1 | FALSE | FALSE | 0.95 | CLEAR_CYCLES_OFF_CANDIDATE_PATH | Cycles exist elsewhere on the feeder, but every candidate-path edge is a bridge and none lies in a cycle. | 1 | 0 | TRUE | TRUE | 14 | 4.7141 | 0.045772 | CLEAR_FOR_CURRENT_CANDIDATE_USING_MODELED_5MIN_UNRESOLVED_SHARE | Even after conservatively placing the largest modeled five-minute unresolved-meter contribution onto the non-breaker candidate path, the breaker remains the binding firm constraint. | 10.0656 | 10.6656 | 11.2656 | 1.2 | 0 | RANK_STABLE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | Explicit substation capacity not yet available | Ready for feeder-bound MILP; final portfolio still needs substation capacity. | 4 | 43.5602
8 | GSO_142¦line_5429_22 | GSO_142 | hvmv_5_22 | line_5429_22 | S_nCCTT245 | 10.6074 | High | ReadyWithReviewFlags | MeshedTopologyUsesShortestPathTree | 105348 | 8779 | 10.6074 | 10.7211 | 10.7752 | 10.8838 | 10.8749 | 11.0003 | 0.27642 | 0 | 0 | 0 | 0 | br_022_22 | 100 | 2024-07-09 | br_022_22 | 2 | 1 | 0 | FALSE | 100 | 0.9917 | 3.1071 | FALSE | 2 | FALSE | FALSE | 0.95 | CLEAR_CYCLES_OFF_CANDIDATE_PATH | Cycles exist elsewhere on the feeder, but every candidate-path edge is a bridge and none lies in a cycle. | 2 | 0 | TRUE | TRUE | 0 | 0 | 0 | CLEAR_NO_UNRESOLVED_METERS | Every modeled meter is topologically resolved. | 10.0074 | 10.6074 | 11.2074 | 1.2 | 0 | RANK_STABLE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | Explicit substation capacity not yet available | Ready for feeder-bound MILP; final portfolio still needs substation capacity. | 4 | 43.5602
9 | GSO_18¦line_108323_21 | GSO_18 | hvmv_4_21 | line_108323_21 | S_nCCTT10746 | 10.3769 | High | ReadyWithReviewFlags | MeshedTopologyUsesShortestPathTree | 105348 | 8779 | 10.3769 | 10.7346 | 10.9536 | 11.5317 | 11.4776 | 11.8543 | 1.1548 | 0 | 0 | 0 | 0 | br_025_21 | 100 | 2024-01-21 | br_025_21 | 2 | 1 | 0 | FALSE | 100 | 0.9914 | 3.2888 | FALSE | 2 | FALSE | FALSE | 0.95 | CLEAR_CYCLES_OFF_CANDIDATE_PATH | Cycles exist elsewhere on the feeder, but every candidate-path edge is a bridge and none lies in a cycle. | 2 | 0 | TRUE | TRUE | 0 | 0 | 0 | CLEAR_NO_UNRESOLVED_METERS | Every modeled meter is topologically resolved. | 9.7102 | 10.3769 | 11.0436 | 1.3333 | 0 | RANK_STABLE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | Explicit substation capacity not yet available | Ready for feeder-bound MILP; final portfolio still needs substation capacity. | 1 | 10.3769
10 | GSO_127¦line_6871_22 | GSO_127 | hvmv_2_22 | line_6871_22 | UCMV43 | 9.4748 | High | Ready |  | 105348 | 8779 | 9.4748 | 9.4814 | 9.4833 | 9.4875 | 9.4874 | 9.4959 | 0.012732 | 0 | 0 | 0 | 0 | br_07_22 | 100 | 2024-01-20 21:00 | br_07_22 | 2 | 1 | 0 | FALSE | 100 | 0.99998 | 3.8459 | TRUE | 0 | FALSE | FALSE | 0.95 | CLEAR_RADIAL | No mesh ambiguity remains after open-switch removal. | 0 | 0 | TRUE | TRUE | 0 | 0 | 0 | CLEAR_NO_UNRESOLVED_METERS | Every modeled meter is topologically resolved. | 8.9748 | 9.4748 | 9.9748 | 1 | 0 | RANK_STABLE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE | Explicit substation capacity not yet available | Ready for feeder-bound MILP; final portfolio still needs substation capacity. | 1 | 9.4748

## Topology_Summary
GridID | CandidateLineID | CandidateNode | CandidateNodeMethod | BreakerID | RootNode | ConnectedNodes | ConnectedEdges | CycleRank | CycleCount | FeederIsRadial | CandidatePathEdgeCount | CandidatePathEdgesInCycles | AllCandidatePathEdgesAreBridges | CandidateLineIsBridge | CandidateLineIsInCycle | ParallelNodePairCount | TopologyResolution | TopologyMateriality
GSO_122 | line_5852_22 | S_nCCTT45 | CandidateNodeFromThermalOutput | br_02_22 | S_nSSEE0_12.47 | 11 | 10 | 0 | 0 | TRUE | 2 | 0 | TRUE | TRUE | FALSE | 0 | CLEAR_RADIAL | No mesh ambiguity remains after open-switch removal.
GSO_124 | line_6716_22 | S_nCCTT913 | CandidateNodeFromThermalOutput | br_04_22 | S_nSSEE0_12.47 | 58 | 57 | 0 | 0 | TRUE | 2 | 0 | TRUE | TRUE | FALSE | 0 | CLEAR_RADIAL | No mesh ambiguity remains after open-switch removal.
GSO_123 | line_6019_22 | S_nCCTT521 | CandidateNodeFromThermalOutput | br_03_22 | S_nSSEE0_12.47 | 183 | 182 | 0 | 0 | TRUE | 2 | 0 | TRUE | TRUE | FALSE | 0 | CLEAR_RADIAL | No mesh ambiguity remains after open-switch removal.
GSO_121 | line_3530_22 | S_nCCTT0 | CandidateNodeFromThermalOutput | br_01_22 | S_nSSEE0_12.47 | 280 | 280 | 1 | 1 | FALSE | 2 | 0 | TRUE | TRUE | FALSE | 0 | CLEAR_CYCLES_OFF_CANDIDATE_PATH | Cycles exist elsewhere on the feeder, but every candidate-path edge is a bridge and none lies in a cycle.
GSO_144 | line_5978_22 | S_nCCTT504 | CandidateNodeFromThermalOutput | br_024_22 | S_nSSEE4_12.47 | 80 | 79 | 0 | 0 | TRUE | 2 | 0 | TRUE | TRUE | FALSE | 0 | CLEAR_RADIAL | No mesh ambiguity remains after open-switch removal.
GSO_141 | line_4565_22 | S_nCCTT1344 | CandidateNodeFromThermalOutput | br_021_22 | S_nSSEE4_12.47 | 240 | 239 | 0 | 0 | TRUE | 2 | 0 | TRUE | TRUE | FALSE | 0 | CLEAR_RADIAL | No mesh ambiguity remains after open-switch removal.
GSO_145 | line_6170_22 | S_nCCTT59 | CandidateNodeFromThermalOutput | br_025_22 | S_nSSEE4_12.47 | 455 | 455 | 1 | 1 | FALSE | 2 | 0 | TRUE | TRUE | FALSE | 0 | CLEAR_CYCLES_OFF_CANDIDATE_PATH | Cycles exist elsewhere on the feeder, but every candidate-path edge is a bridge and none lies in a cycle.
GSO_142 | line_5429_22 | S_nCCTT245 | CandidateNodeFromThermalOutput | br_022_22 | S_nSSEE4_12.47 | 563 | 564 | 2 | 2 | FALSE | 2 | 0 | TRUE | TRUE | FALSE | 0 | CLEAR_CYCLES_OFF_CANDIDATE_PATH | Cycles exist elsewhere on the feeder, but every candidate-path edge is a bridge and none lies in a cycle.
GSO_18 | line_108323_21 | S_nCCTT10746 | CandidateNodeFromThermalOutput | br_025_21 | S_nSSEE11_12.47 | 1416 | 1417 | 2 | 2 | FALSE | 2 | 0 | TRUE | TRUE | FALSE | 0 | CLEAR_CYCLES_OFF_CANDIDATE_PATH | Cycles exist elsewhere on the feeder, but every candidate-path edge is a bridge and none lies in a cycle.
GSO_127 | line_6871_22 | UCMV43 | CandidateNodeFromThermalOutput | br_07_22 | S_nSSEE1_12.47 | 3 | 2 | 0 | 0 | TRUE | 2 | 0 | TRUE | TRUE | FALSE | 0 | CLEAR_RADIAL | No mesh ambiguity remains after open-switch removal.

## Cycle_Summary
GridID | CycleNumber | CycleLengthEdges | CycleNodeCount | CycleNodes | CycleEdges
GSO_121 | 1 | 19 | 19 | S_nCCTT869 ¦ S_nCCTT43 ¦ S_nCCTT349 ¦ S_nCCTT552 ¦ S_nCCTT633 ¦ S_nCCTT46 ¦ S_nCCTT46_A_S_nCCTT728 ¦ S_nCCTT728 ¦ S_nCCTT728_B_S_nCCTT520 ¦ S_nCCTT520 ¦ S_nCCTT520_A_S_nCCTT553 ¦ S_nCCTT553 ¦ S_nCCTT785 ¦ S_nCCTT309_A_S_nCCTT785 ¦ S_nCCTT309 ¦ S_nCCTT828 ¦ S_nCCTT44 ¦ S_nCCTT580 ¦ S_nCCTT616 | S_nCCTT43<->S_nCCTT869 ¦ S_nCCTT349<->S_nCCTT43 ¦ S_nCCTT349<->S_nCCTT552 ¦ S_nCCTT552<->S_nCCTT633 ¦ S_nCCTT46<->S_nCCTT633 ¦ S_nCCTT46<->S_nCCTT46_A_S_nCCTT728 ¦ S_nCCTT46_A_S_nCCTT728<->S_nCCTT728 ¦ S_nCCTT728<->S_nCCTT728_B_S_nCCTT520 ¦ S_nCCTT520<->S_nCCTT728_B_S_nCCTT520 ¦ S_nCCTT520<->S_nCCTT520_A_S_nCCTT553 ¦ S_nCCTT520_A_S_nCCTT553<->S_nCCTT553 ¦ S_nCCTT553<->S_nCCTT785 ¦ S_nCCTT309_A_S_nCCTT785<->S_nCCTT785 ¦ S_nCCTT309<->S_nCCTT309_A_S_nCCTT785 ¦ S_nCCTT309<->S_nCCTT828 ¦ S_nCCTT44<->S_nCCTT828 ¦ S_nCCTT44<->S_nCCTT580 ¦ S_nCCTT580<->S_nCCTT616 ¦ S_nCCTT616<->S_nCCTT869
GSO_145 | 1 | 10 | 10 | S_nCCTT1288 ¦ S_nCCTT577 ¦ S_nCCTT855 ¦ S_nCCTT231 ¦ S_nCCTT1426 ¦ S_nCCTT694 ¦ S_nCCTT373 ¦ S_nCCTT453 ¦ S_nCCTT1236_A_S_nCCTT453 ¦ S_nCCTT1236 | S_nCCTT1288<->S_nCCTT577 ¦ S_nCCTT577<->S_nCCTT855 ¦ S_nCCTT231<->S_nCCTT855 ¦ S_nCCTT1426<->S_nCCTT231 ¦ S_nCCTT1426<->S_nCCTT694 ¦ S_nCCTT373<->S_nCCTT694 ¦ S_nCCTT373<->S_nCCTT453 ¦ S_nCCTT1236_A_S_nCCTT453<->S_nCCTT453 ¦ S_nCCTT1236<->S_nCCTT1236_A_S_nCCTT453 ¦ S_nCCTT1236<->S_nCCTT1288
GSO_142 | 1 | 52 | 52 | S_nCCTT158_B_S_nCCTT76 ¦ S_nCCTT158 ¦ S_nCCTT112 ¦ S_nCCTT269 ¦ S_nCCTT299 ¦ S_nCCTT256 ¦ S_nCCTT1567 ¦ S_nCCTT149 ¦ S_nCCTT77 ¦ S_nCCTT1562 ¦ S_nCCTT1462 ¦ S_nCCTT419 ¦ S_nCCTT93 ¦ S_nCCTT93_A_S_nCCTT134 ¦ S_nCCTT134 ¦ S_nCCTT134_B_S_nCCTT1338 ¦ S_nCCTT1338 ¦ S_nCCTT1338_B_S_nCCTT1350 ¦ S_nCCTT1350 ¦ S_nCCTT1350_B_S_nCCTT1554 ¦ S_nCCTT1554 ¦ S_nCCTT1554_A_S_nCCTT1474 ¦ S_nCCTT1474 ¦ S_nCCTT1474_B_S_nCCTT155 ¦ S_nCCTT155 ¦ S_nCCTT155_B_S_nCCTT1147 ¦ S_nCCTT1147 ¦ S_nCCTT1147_A_S_nCCTT143 ¦ S_nCCTT143 ¦ S_nCCTT111 ¦ S_nCCTT111_A_S_nCCTT1242 ¦ S_nCCTT1242 ¦ S_nCCTT1242_A_S_nCCTT1584 ¦ S_nCCTT1584 ¦ S_nCCTT1584_B_S_nCCTT315 ¦ S_nCCTT315 ¦ S_nCCTT315_A_S_nCCTT1443 ¦ S_nCCTT1443 ¦ S_nCCTT1443_B_S_nCCTT1286 ¦ S_nCCTT1286 ¦ S_nCCTT1286_B_S_nCCTT1377 ¦ S_nCCTT1377 ¦ S_nCCTT1457_A_S_nCCTT1377 ¦ S_nCCTT1457 ¦ S_nCCTT266_A_S_nCCTT1457 ¦ S_nCCTT266 ¦ S_nCCTT104_A_S_nCCTT266 ¦ S_nCCTT104 ¦ S_nCCTT88_B_S_nCCTT104 ¦ S_nCCTT88 ¦ S_nCCTT76_A_S_nCCTT88 ¦ S_nCCTT76 | S_nCCTT158<->S_nCCTT158_B_S_nCCTT76 ¦ S_nCCTT112<->S_nCCTT158 ¦ S_nCCTT112<->S_nCCTT269 ¦ S_nCCTT269<->S_nCCTT299 ¦ S_nCCTT256<->S_nCCTT299 ¦ S_nCCTT1567<->S_nCCTT256 ¦ S_nCCTT149<->S_nCCTT1567 ¦ S_nCCTT149<->S_nCCTT77 ¦ S_nCCTT1562<->S_nCCTT77 ¦ S_nCCTT1462<->S_nCCTT1562 ¦ S_nCCTT1462<->S_nCCTT419 ¦ S_nCCTT419<->S_nCCTT93 ¦ S_nCCTT93<->S_nCCTT93_A_S_nCCTT134 ¦ S_nCCTT134<->S_nCCTT93_A_S_nCCTT134 ¦ S_nCCTT134<->S_nCCTT134_B_S_nCCTT1338 ¦ S_nCCTT1338<->S_nCCTT134_B_S_nCCTT1338 ¦ S_nCCTT1338<->S_nCCTT1338_B_S_nCCTT1350 ¦ S_nCCTT1338_B_S_nCCTT1350<->S_nCCTT1350 ¦ S_nCCTT1350<->S_nCCTT1350_B_S_nCCTT1554 ¦ S_nCCTT1350_B_S_nCCTT1554<->S_nCCTT1554 ¦ S_nCCTT1554<->S_nCCTT1554_A_S_nCCTT1474 ¦ S_nCCTT1474<->S_nCCTT1554_A_S_nCCTT1474 ¦ S_nCCTT1474<->S_nCCTT1474_B_S_nCCTT155 ¦ S_nCCTT1474_B_S_nCCTT155<->S_nCCTT155 ¦ S_nCCTT155<->S_nCCTT155_B_S_nCCTT1147 ¦ S_nCCTT1147<->S_nCCTT155_B_S_nCCTT1147 ¦ S_nCCTT1147<->S_nCCTT1147_A_S_nCCTT143 ¦ S_nCCTT1147_A_S_nCCTT143<->S_nCCTT143 ¦ S_nCCTT111<->S_nCCTT143 ¦ S_nCCTT111<->S_nCCTT111_A_S_nCCTT1242 ¦ S_nCCTT111_A_S_nCCTT1242<->S_nCCTT1242 ¦ S_nCCTT1242<->S_nCCTT1242_A_S_nCCTT1584 ¦ S_nCCTT1242_A_S_nCCTT1584<->S_nCCTT1584 ¦ S_nCCTT1584<->S_nCCTT1584_B_S_nCCTT315 ¦ S_nCCTT1584_B_S_nCCTT315<->S_nCCTT315 ¦ S_nCCTT315<->S_nCCTT315_A_S_nCCTT1443 ¦ S_nCCTT1443<->S_nCCTT315_A_S_nCCTT1443 ¦ S_nCCTT1443<->S_nCCTT1443_B_S_nCCTT1286 ¦ S_nCCTT1286<->S_nCCTT1443_B_S_nCCTT1286 ¦ S_nCCTT1286<->S_nCCTT1286_B_S_nCCTT1377 ¦ S_nCCTT1286_B_S_nCCTT1377<->S_nCCTT1377 ¦ S_nCCTT1377<->S_nCCTT1457_A_S_nCCTT1377 ¦ S_nCCTT1457<->S_nCCTT1457_A_S_nCCTT1377 ¦ S_nCCTT1457<->S_nCCTT266_A_S_nCCTT1457 ¦ S_nCCTT266<->S_nCCTT266_A_S_nCCTT1457 ¦ S_nCCTT104_A_S_nCCTT266<->S_nCCTT266 ¦ S_nCCTT104<->S_nCCTT104_A_S_nCCTT266 ¦ S_nCCTT104<->S_nCCTT88_B_S_nCCTT104 ¦ S_nCCTT88<->S_nCCTT88_B_S_nCCTT104 ¦ S_nCCTT76_A_S_nCCTT88<->S_nCCTT88 ¦ S_nCCTT76<->S_nCCTT76_A_S_nCCTT88 ¦ S_nCCTT158_B_S_nCCTT76<->S_nCCTT76
GSO_142 | 2 | 26 | 26 | S_nCCTT136 ¦ S_nCCTT1467 ¦ S_nCCTT244 ¦ S_nCCTT82 ¦ S_nCCTT1388 ¦ S_nCCTT66 ¦ S_nCCTT328 ¦ S_nCCTT1477 ¦ S_nCCTT1473 ¦ S_nCCTT95 ¦ S_nCCTT1483 ¦ S_nCCTT1331 ¦ S_nCCTT1429 ¦ S_nCCTT1301 ¦ S_nCCTT1572 ¦ S_nCCTT115 ¦ S_nCCTT115_A_S_nCCTT250 ¦ S_nCCTT250 ¦ S_nCCTT1343 ¦ S_nCCTT305 ¦ S_nCCTT158 ¦ S_nCCTT112 ¦ S_nCCTT269 ¦ S_nCCTT299 ¦ S_nCCTT256 ¦ S_nCCTT1567 | S_nCCTT136<->S_nCCTT1467 ¦ S_nCCTT1467<->S_nCCTT244 ¦ S_nCCTT244<->S_nCCTT82 ¦ S_nCCTT1388<->S_nCCTT82 ¦ S_nCCTT1388<->S_nCCTT66 ¦ S_nCCTT328<->S_nCCTT66 ¦ S_nCCTT1477<->S_nCCTT328 ¦ S_nCCTT1473<->S_nCCTT1477 ¦ S_nCCTT1473<->S_nCCTT95 ¦ S_nCCTT1483<->S_nCCTT95 ¦ S_nCCTT1331<->S_nCCTT1483 ¦ S_nCCTT1331<->S_nCCTT1429 ¦ S_nCCTT1301<->S_nCCTT1429 ¦ S_nCCTT1301<->S_nCCTT1572 ¦ S_nCCTT115<->S_nCCTT1572 ¦ S_nCCTT115<->S_nCCTT115_A_S_nCCTT250 ¦ S_nCCTT115_A_S_nCCTT250<->S_nCCTT250 ¦ S_nCCTT1343<->S_nCCTT250 ¦ S_nCCTT1343<->S_nCCTT305 ¦ S_nCCTT158<->S_nCCTT305 ¦ S_nCCTT112<->S_nCCTT158 ¦ S_nCCTT112<->S_nCCTT269 ¦ S_nCCTT269<->S_nCCTT299 ¦ S_nCCTT256<->S_nCCTT299 ¦ S_nCCTT1567<->S_nCCTT256 ¦ S_nCCTT136<->S_nCCTT1567
GSO_18 | 1 | 25 | 25 | S_nCCTT11937_A_S_nCCTT12664 ¦ S_nCCTT12664 ¦ S_nCCTT6562 ¦ S_nCCTT10607 ¦ S_nCCTT10108 ¦ S_nCCTT12242 ¦ S_nCCTT12475 ¦ S_nCCTT6610 ¦ S_nCCTT11312 ¦ S_nCCTT11341 ¦ S_nCCTT11189 ¦ S_nCCTT6824 ¦ S_nCCTT10741 ¦ S_nCCTT6705 ¦ S_nCCTT10687 ¦ S_nCCTT2058 ¦ S_nCCTT8115 ¦ S_nCCTT7751 ¦ S_nCCTT9228 ¦ UCMV21 ¦ S_nCCTT2016 ¦ S_nCCTT2126 ¦ S_nCCTT12196 ¦ S_nCCTT6762 ¦ S_nCCTT11937 | S_nCCTT11937_A_S_nCCTT12664<->S_nCCTT12664 ¦ S_nCCTT12664<->S_nCCTT6562 ¦ S_nCCTT10607<->S_nCCTT6562 ¦ S_nCCTT10108<->S_nCCTT10607 ¦ S_nCCTT10108<->S_nCCTT12242 ¦ S_nCCTT12242<->S_nCCTT12475 ¦ S_nCCTT12475<->S_nCCTT6610 ¦ S_nCCTT11312<->S_nCCTT6610 ¦ S_nCCTT11312<->S_nCCTT11341 ¦ S_nCCTT11189<->S_nCCTT11341 ¦ S_nCCTT11189<->S_nCCTT6824 ¦ S_nCCTT10741<->S_nCCTT6824 ¦ S_nCCTT10741<->S_nCCTT6705 ¦ S_nCCTT10687<->S_nCCTT6705 ¦ S_nCCTT10687<->S_nCCTT2058 ¦ S_nCCTT2058<->S_nCCTT8115 ¦ S_nCCTT7751<->S_nCCTT8115 ¦ S_nCCTT7751<->S_nCCTT9228 ¦ S_nCCTT9228<->UCMV21 ¦ S_nCCTT2016<->UCMV21 ¦ S_nCCTT2016<->S_nCCTT2126 ¦ S_nCCTT12196<->S_nCCTT2126 ¦ S_nCCTT12196<->S_nCCTT6762 ¦ S_nCCTT11937<->S_nCCTT6762 ¦ S_nCCTT11937<->S_nCCTT11937_A_S_nCCTT12664
GSO_18 | 2 | 17 | 17 | S_nCCTT10183 ¦ S_nCCTT6871 ¦ S_nCCTT11779 ¦ S_nCCTT8119 ¦ S_nCCTT8111 ¦ S_nCCTT11726 ¦ S_nCCTT8121 ¦ S_nCCTT12034 ¦ S_nCCTT3902 ¦ S_nCCTT6740 ¦ S_nCCTT12360 ¦ S_nCCTT11528 ¦ S_nCCTT9628 ¦ S_nCCTT9622 ¦ S_nCCTT7601 ¦ S_nCCTT7601_A_S_nCCTT6861 ¦ S_nCCTT6861 | S_nCCTT10183<->S_nCCTT6871 ¦ S_nCCTT11779<->S_nCCTT6871 ¦ S_nCCTT11779<->S_nCCTT8119 ¦ S_nCCTT8111<->S_nCCTT8119 ¦ S_nCCTT11726<->S_nCCTT8111 ¦ S_nCCTT11726<->S_nCCTT8121 ¦ S_nCCTT12034<->S_nCCTT8121 ¦ S_nCCTT12034<->S_nCCTT3902 ¦ S_nCCTT3902<->S_nCCTT6740 ¦ S_nCCTT12360<->S_nCCTT6740 ¦ S_nCCTT11528<->S_nCCTT12360 ¦ S_nCCTT11528<->S_nCCTT9628 ¦ S_nCCTT9622<->S_nCCTT9628 ¦ S_nCCTT7601<->S_nCCTT9622 ¦ S_nCCTT7601<->S_nCCTT7601_A_S_nCCTT6861 ¦ S_nCCTT6861<->S_nCCTT7601_A_S_nCCTT6861 ¦ S_nCCTT10183<->S_nCCTT6861

## Cycle_Edges
GridID | CycleNumber | CycleLengthEdges | NodeA | NodeB | ElementID | ElementType | ElementClass | IsSwitchable | SwitchIsOpen | UpstreamGridElementID
GSO_121 | 1 | 19 | S_nCCTT43 | S_nCCTT869 | line_5800_22 | ACLineSegment | Line | FALSE | FALSE
GSO_121 | 1 | 19 | S_nCCTT349 | S_nCCTT43 | line_5618_22 | ACLineSegment | Line | FALSE | FALSE
GSO_121 | 1 | 19 | S_nCCTT349 | S_nCCTT552 | line_5619_22 | ACLineSegment | Line | FALSE | FALSE
GSO_121 | 1 | 19 | S_nCCTT552 | S_nCCTT633 | line_6085_22 | ACLineSegment | Line | FALSE | FALSE
GSO_121 | 1 | 19 | S_nCCTT46 | S_nCCTT633 | line_5872_22 | ACLineSegment | Line | FALSE | FALSE
GSO_121 | 1 | 19 | S_nCCTT46 | S_nCCTT46_A_S_nCCTT728 | switch_683_22 | Switch | Switch | TRUE | FALSE
GSO_121 | 1 | 19 | S_nCCTT46_A_S_nCCTT728 | S_nCCTT728 | line_5873_22 | ACLineSegment | Line | FALSE | FALSE
GSO_121 | 1 | 19 | S_nCCTT728 | S_nCCTT728_B_S_nCCTT520 | line_6017_22 | ACLineSegment | Line | FALSE | FALSE
GSO_121 | 1 | 19 | S_nCCTT520 | S_nCCTT728_B_S_nCCTT520 | switch_717_22 | Switch | Switch | TRUE | FALSE
GSO_121 | 1 | 19 | S_nCCTT520 | S_nCCTT520_A_S_nCCTT553 | switch_714_22 | Switch | Switch | TRUE | FALSE
GSO_121 | 1 | 19 | S_nCCTT520_A_S_nCCTT553 | S_nCCTT553 | line_6016_22 | ACLineSegment | Line | FALSE | FALSE
GSO_121 | 1 | 19 | S_nCCTT553 | S_nCCTT785 | line_6088_22 | ACLineSegment | Line | FALSE | FALSE
GSO_121 | 1 | 19 | S_nCCTT309_A_S_nCCTT785 | S_nCCTT785 | line_5524_22 | ACLineSegment | Line | FALSE | FALSE
GSO_121 | 1 | 19 | S_nCCTT309 | S_nCCTT309_A_S_nCCTT785 | switch_648_22 | Switch | Switch | TRUE | FALSE
GSO_121 | 1 | 19 | S_nCCTT309 | S_nCCTT828 | line_5525_22 | ACLineSegment | Line | FALSE | FALSE
GSO_121 | 1 | 19 | S_nCCTT44 | S_nCCTT828 | line_5826_22 | ACLineSegment | Line | FALSE | FALSE
GSO_121 | 1 | 19 | S_nCCTT44 | S_nCCTT580 | line_5825_22 | ACLineSegment | Line | FALSE | FALSE
GSO_121 | 1 | 19 | S_nCCTT580 | S_nCCTT616 | line_6144_22 | ACLineSegment | Line | FALSE | FALSE
GSO_121 | 1 | 19 | S_nCCTT616 | S_nCCTT869 | line_6235_22 | ACLineSegment | Line | FALSE | FALSE
GSO_145 | 1 | 10 | S_nCCTT1288 | S_nCCTT577 | line_4397_22 | ACLineSegment | Line | FALSE | FALSE
GSO_145 | 1 | 10 | S_nCCTT577 | S_nCCTT855 | line_6138_22 | ACLineSegment | Line | FALSE | FALSE
GSO_145 | 1 | 10 | S_nCCTT231 | S_nCCTT855 | line_5401_22 | ACLineSegment | Line | FALSE | FALSE
GSO_145 | 1 | 10 | S_nCCTT1426 | S_nCCTT231 | line_4785_22 | ACLineSegment | Line | FALSE | FALSE
GSO_145 | 1 | 10 | S_nCCTT1426 | S_nCCTT694 | line_4788_22 | ACLineSegment | Line | FALSE | FALSE
GSO_145 | 1 | 10 | S_nCCTT373 | S_nCCTT694 | line_5672_22 | ACLineSegment | Line | FALSE | FALSE
GSO_145 | 1 | 10 | S_nCCTT373 | S_nCCTT453 | line_5671_22 | ACLineSegment | Line | FALSE | FALSE
GSO_145 | 1 | 10 | S_nCCTT1236_A_S_nCCTT453 | S_nCCTT453 | line_4244_22 | ACLineSegment | Line | FALSE | FALSE
GSO_145 | 1 | 10 | S_nCCTT1236 | S_nCCTT1236_A_S_nCCTT453 | switch_379_22 | Switch | Switch | TRUE | FALSE
GSO_145 | 1 | 10 | S_nCCTT1236 | S_nCCTT1288 | line_4242_22 | ACLineSegment | Line | FALSE | FALSE
GSO_142 | 1 | 52 | S_nCCTT158 | S_nCCTT158_B_S_nCCTT76 | line_5157_22 | ACLineSegment | Line | FALSE | FALSE
GSO_142 | 1 | 52 | S_nCCTT112 | S_nCCTT158 | line_3912_22 | ACLineSegment | Line | FALSE | FALSE
GSO_142 | 1 | 52 | S_nCCTT112 | S_nCCTT269 | line_3913_22 | ACLineSegment | Line | FALSE | FALSE
GSO_142 | 1 | 52 | S_nCCTT269 | S_nCCTT299 | line_5463_22 | ACLineSegment | Line | FALSE | FALSE
GSO_142 | 1 | 52 | S_nCCTT256 | S_nCCTT299 | line_5442_22 | ACLineSegment | Line | FALSE | FALSE
GSO_142 | 1 | 52 | S_nCCTT1567 | S_nCCTT256 | line_5129_22 | ACLineSegment | Line | FALSE | FALSE
GSO_142 | 1 | 52 | S_nCCTT149 | S_nCCTT1567 | line_4938_22 | ACLineSegment | Line | FALSE | FALSE
GSO_142 | 1 | 52 | S_nCCTT149 | S_nCCTT77 | line_4939_22 | ACLineSegment | Line | FALSE | FALSE
GSO_142 | 1 | 52 | S_nCCTT1562 | S_nCCTT77 | line_5117_22 | ACLineSegment | Line | FALSE | FALSE
GSO_142 | 1 | 52 | S_nCCTT1462 | S_nCCTT1562 | line_4875_22 | ACLineSegment | Line | FALSE | FALSE
GSO_142 | 1 | 52 | S_nCCTT1462 | S_nCCTT419 | line_4876_22 | ACLineSegment | Line | FALSE | FALSE
GSO_142 | 1 | 52 | S_nCCTT419 | S_nCCTT93 | line_5777_22 | ACLineSegment | Line | FALSE | FALSE
GSO_142 | 1 | 52 | S_nCCTT93 | S_nCCTT93_A_S_nCCTT134 | switch_450_22 | Switch | Switch | TRUE | FALSE
GSO_142 | 1 | 52 | S_nCCTT134 | S_nCCTT93_A_S_nCCTT134 | line_4554_22 | ACLineSegment | Line | FALSE | FALSE
GSO_142 | 1 | 52 | S_nCCTT134 | S_nCCTT134_B_S_nCCTT1338 | line_4545_22 | ACLineSegment | Line | FALSE | FALSE
GSO_142 | 1 | 52 | S_nCCTT1338 | S_nCCTT134_B_S_nCCTT1338 | switch_445_22 | Switch | Switch | TRUE | FALSE
GSO_142 | 1 | 52 | S_nCCTT1338 | S_nCCTT1338_B_S_nCCTT1350 | line_4546_22 | ACLineSegment | Line | FALSE | FALSE
GSO_142 | 1 | 52 | S_nCCTT1338_B_S_nCCTT1350 | S_nCCTT1350 | switch_447_22 | Switch | Switch | TRUE | FALSE
GSO_142 | 1 | 52 | S_nCCTT1350 | S_nCCTT1350_B_S_nCCTT1554 | line_4584_22 | ACLineSegment | Line | FALSE | FALSE
GSO_142 | 1 | 52 | S_nCCTT1350_B_S_nCCTT1554 | S_nCCTT1554 | switch_462_22 | Switch | Switch | TRUE | FALSE
GSO_142 | 1 | 52 | S_nCCTT1554 | S_nCCTT1554_A_S_nCCTT1474 | switch_532_22 | Switch | Switch | TRUE | FALSE
GSO_142 | 1 | 52 | S_nCCTT1474 | S_nCCTT1554_A_S_nCCTT1474 | line_4908_22 | ACLineSegment | Line | FALSE | FALSE
GSO_142 | 1 | 52 | S_nCCTT1474 | S_nCCTT1474_B_S_nCCTT155 | line_4907_22 | ACLineSegment | Line | FALSE | FALSE
GSO_142 | 1 | 52 | S_nCCTT1474_B_S_nCCTT155 | S_nCCTT155 | switch_531_22 | Switch | Switch | TRUE | FALSE
GSO_142 | 1 | 52 | S_nCCTT155 | S_nCCTT155_B_S_nCCTT1147 | line_3984_22 | ACLineSegment | Line | FALSE | FALSE
GSO_142 | 1 | 52 | S_nCCTT1147 | S_nCCTT155_B_S_nCCTT1147 | switch_290_22 | Switch | Switch | TRUE | FALSE
GSO_142 | 1 | 52 | S_nCCTT1147 | S_nCCTT1147_A_S_nCCTT143 | recloser_157_22 | Switch | Switch | TRUE | FALSE
GSO_142 | 1 | 52 | S_nCCTT1147_A_S_nCCTT143 | S_nCCTT143 | line_3983_22 | ACLineSegment | Line | FALSE | FALSE
GSO_142 | 1 | 52 | S_nCCTT111 | S_nCCTT143 | line_3886_22 | ACLineSegment | Line | FALSE | FALSE
GSO_142 | 1 | 52 | S_nCCTT111 | S_nCCTT111_A_S_nCCTT1242 | switch_263_22 | Switch | Switch | TRUE | FALSE
GSO_142 | 1 | 52 | S_nCCTT111_A_S_nCCTT1242 | S_nCCTT1242 | line_3885_22 | ACLineSegment | Line | FALSE | FALSE
GSO_142 | 1 | 52 | S_nCCTT1242 | S_nCCTT1242_A_S_nCCTT1584 | switch_380_22 | Switch | Switch | TRUE | FALSE
GSO_142 | 1 | 52 | S_nCCTT1242_A_S_nCCTT1584 | S_nCCTT1584 | line_4262_22 | ACLineSegment | Line | FALSE | FALSE
GSO_142 | 1 | 52 | S_nCCTT1584 | S_nCCTT1584_B_S_nCCTT315 | line_5168_22 | ACLineSegment | Line | FALSE | FALSE
GSO_142 | 1 | 52 | S_nCCTT1584_B_S_nCCTT315 | S_nCCTT315 | switch_586_22 | Switch | Switch | TRUE | FALSE
GSO_142 | 1 | 52 | S_nCCTT315 | S_nCCTT315_A_S_nCCTT1443 | switch_504_22 | Switch | Switch | TRUE | FALSE
GSO_142 | 1 | 52 | S_nCCTT1443 | S_nCCTT315_A_S_nCCTT1443 | line_4830_22 | ACLineSegment | Line | FALSE | FALSE
GSO_142 | 1 | 52 | S_nCCTT1443 | S_nCCTT1443_B_S_nCCTT1286 | line_4392_22 | ACLineSegment | Line | FALSE | FALSE
GSO_142 | 1 | 52 | S_nCCTT1286 | S_nCCTT1443_B_S_nCCTT1286 | switch_413_22 | Switch | Switch | TRUE | FALSE
GSO_142 | 1 | 52 | S_nCCTT1286 | S_nCCTT1286_B_S_nCCTT1377 | line_4391_22 | ACLineSegment | Line | FALSE | FALSE
GSO_142 | 1 | 52 | S_nCCTT1286_B_S_nCCTT1377 | S_nCCTT1377 | switch_411_22 | Switch | Switch | TRUE | FALSE
GSO_142 | 1 | 52 | S_nCCTT1377 | S_nCCTT1457_A_S_nCCTT1377 | line_4658_22 | ACLineSegment | Line | FALSE | FALSE
GSO_142 | 1 | 52 | S_nCCTT1457 | S_nCCTT1457_A_S_nCCTT1377 | switch_475_22 | Switch | Switch | TRUE | FALSE
GSO_142 | 1 | 52 | S_nCCTT1457 | S_nCCTT266_A_S_nCCTT1457 | line_4864_22 | ACLineSegment | Line | FALSE | FALSE
GSO_142 | 1 | 52 | S_nCCTT266 | S_nCCTT266_A_S_nCCTT1457 | switch_516_22 | Switch | Switch | TRUE | FALSE
GSO_142 | 1 | 52 | S_nCCTT104_A_S_nCCTT266 | S_nCCTT266 | line_3662_22 | ACLineSegment | Line | FALSE | FALSE
GSO_142 | 1 | 52 | S_nCCTT104 | S_nCCTT104_A_S_nCCTT266 | switch_226_22 | Switch | Switch | TRUE | FALSE
GSO_142 | 1 | 52 | S_nCCTT104 | S_nCCTT88_B_S_nCCTT104 | switch_229_22 | Switch | Switch | TRUE | FALSE
GSO_142 | 1 | 52 | S_nCCTT88 | S_nCCTT88_B_S_nCCTT104 | line_3663_22 | ACLineSegment | Line | FALSE | FALSE
GSO_142 | 1 | 52 | S_nCCTT76_A_S_nCCTT88 | S_nCCTT88 | line_6503_22 | ACLineSegment | Line | FALSE | FALSE
GSO_142 | 1 | 52 | S_nCCTT76 | S_nCCTT76_A_S_nCCTT88 | switch_769_22 | Switch | Switch | TRUE | FALSE
GSO_142 | 1 | 52 | S_nCCTT158_B_S_nCCTT76 | S_nCCTT76 | switch_582_22 | Switch | Switch | TRUE | FALSE
GSO_142 | 2 | 26 | S_nCCTT136 | S_nCCTT1467 | line_4608_22 | ACLineSegment | Line | FALSE | FALSE
GSO_142 | 2 | 26 | S_nCCTT1467 | S_nCCTT244 | line_4889_22 | ACLineSegment | Line | FALSE | FALSE
GSO_142 | 2 | 26 | S_nCCTT244 | S_nCCTT82 | line_5427_22 | ACLineSegment | Line | FALSE | FALSE
GSO_142 | 2 | 26 | S_nCCTT1388 | S_nCCTT82 | line_4685_22 | ACLineSegment | Line | FALSE | FALSE
GSO_142 | 2 | 26 | S_nCCTT1388 | S_nCCTT66 | line_4684_22 | ACLineSegment | Line | FALSE | FALSE
GSO_142 | 2 | 26 | S_nCCTT328 | S_nCCTT66 | line_5565_22 | ACLineSegment | Line | FALSE | FALSE
GSO_142 | 2 | 26 | S_nCCTT1477 | S_nCCTT328 | line_4913_22 | ACLineSegment | Line | FALSE | FALSE
GSO_142 | 2 | 26 | S_nCCTT1473 | S_nCCTT1477 | line_4904_22 | ACLineSegment | Line | FALSE | FALSE
GSO_142 | 2 | 26 | S_nCCTT1473 | S_nCCTT95 | line_4905_22 | ACLineSegment | Line | FALSE | FALSE
GSO_142 | 2 | 26 | S_nCCTT1483 | S_nCCTT95 | line_4924_22 | ACLineSegment | Line | FALSE | FALSE
GSO_142 | 2 | 26 | S_nCCTT1331 | S_nCCTT1483 | line_4528_22 | ACLineSegment | Line | FALSE | FALSE
GSO_142 | 2 | 26 | S_nCCTT1331 | S_nCCTT1429 | line_4527_22 | ACLineSegment | Line | FALSE | FALSE
GSO_142 | 2 | 26 | S_nCCTT1301 | S_nCCTT1429 | line_4439_22 | ACLineSegment | Line | FALSE | FALSE
GSO_142 | 2 | 26 | S_nCCTT1301 | S_nCCTT1572 | line_4440_22 | ACLineSegment | Line | FALSE | FALSE
GSO_142 | 2 | 26 | S_nCCTT115 | S_nCCTT1572 | line_3988_22 | ACLineSegment | Line | FALSE | FALSE
GSO_142 | 2 | 26 | S_nCCTT115 | S_nCCTT115_A_S_nCCTT250 | switch_291_22 | Switch | Switch | TRUE | FALSE
GSO_142 | 2 | 26 | S_nCCTT115_A_S_nCCTT250 | S_nCCTT250 | line_3989_22 | ACLineSegment | Line | FALSE | FALSE
GSO_142 | 2 | 26 | S_nCCTT1343 | S_nCCTT250 | line_4560_22 | ACLineSegment | Line | FALSE | FALSE
GSO_142 | 2 | 26 | S_nCCTT1343 | S_nCCTT305 | line_4561_22 | ACLineSegment | Line | FALSE | FALSE
GSO_142 | 2 | 26 | S_nCCTT158 | S_nCCTT305 | line_5156_22 | ACLineSegment | Line | FALSE | FALSE
GSO_142 | 2 | 26 | S_nCCTT112 | S_nCCTT158 | line_3912_22 | ACLineSegment | Line | FALSE | FALSE
GSO_142 | 2 | 26 | S_nCCTT112 | S_nCCTT269 | line_3913_22 | ACLineSegment | Line | FALSE | FALSE
GSO_142 | 2 | 26 | S_nCCTT269 | S_nCCTT299 | line_5463_22 | ACLineSegment | Line | FALSE | FALSE
GSO_142 | 2 | 26 | S_nCCTT256 | S_nCCTT299 | line_5442_22 | ACLineSegment | Line | FALSE | FALSE
GSO_142 | 2 | 26 | S_nCCTT1567 | S_nCCTT256 | line_5129_22 | ACLineSegment | Line | FALSE | FALSE
GSO_142 | 2 | 26 | S_nCCTT136 | S_nCCTT1567 | line_4609_22 | ACLineSegment | Line | FALSE | FALSE
GSO_18 | 1 | 25 | S_nCCTT11937_A_S_nCCTT12664 | S_nCCTT12664 | line_111905_21 | ACLineSegment | Line | FALSE | FALSE
GSO_18 | 1 | 25 | S_nCCTT12664 | S_nCCTT6562 | line_113658_21 | ACLineSegment | Line | FALSE | FALSE
GSO_18 | 1 | 25 | S_nCCTT10607 | S_nCCTT6562 | line_107863_21 | ACLineSegment | Line | FALSE | FALSE
GSO_18 | 1 | 25 | S_nCCTT10108 | S_nCCTT10607 | line_106218_21 | ACLineSegment | Line | FALSE | FALSE
GSO_18 | 1 | 25 | S_nCCTT10108 | S_nCCTT12242 | line_106219_21 | ACLineSegment | Line | FALSE | FALSE
GSO_18 | 1 | 25 | S_nCCTT12242 | S_nCCTT12475 | line_112666_21 | ACLineSegment | Line | FALSE | FALSE
GSO_18 | 1 | 25 | S_nCCTT12475 | S_nCCTT6610 | line_113231_21 | ACLineSegment | Line | FALSE | FALSE
GSO_18 | 1 | 25 | S_nCCTT11312 | S_nCCTT6610 | line_110126_21 | ACLineSegment | Line | FALSE | FALSE
GSO_18 | 1 | 25 | S_nCCTT11312 | S_nCCTT11341 | line_110125_21 | ACLineSegment | Line | FALSE | FALSE
GSO_18 | 1 | 25 | S_nCCTT11189 | S_nCCTT11341 | line_109743_21 | ACLineSegment | Line | FALSE | FALSE
GSO_18 | 1 | 25 | S_nCCTT11189 | S_nCCTT6824 | line_109744_21 | ACLineSegment | Line | FALSE | FALSE
GSO_18 | 1 | 25 | S_nCCTT10741 | S_nCCTT6824 | line_108305_21 | ACLineSegment | Line | FALSE | FALSE
GSO_18 | 1 | 25 | S_nCCTT10741 | S_nCCTT6705 | line_108304_21 | ACLineSegment | Line | FALSE | FALSE
GSO_18 | 1 | 25 | S_nCCTT10687 | S_nCCTT6705 | line_108117_21 | ACLineSegment | Line | FALSE | FALSE
GSO_18 | 1 | 25 | S_nCCTT10687 | S_nCCTT2058 | line_108116_21 | ACLineSegment | Line | FALSE | FALSE
GSO_18 | 1 | 25 | S_nCCTT2058 | S_nCCTT8115 | line_116127_21 | ACLineSegment | Line | FALSE | FALSE
GSO_18 | 1 | 25 | S_nCCTT7751 | S_nCCTT8115 | line_128625_21 | ACLineSegment | Line | FALSE | FALSE
GSO_18 | 1 | 25 | S_nCCTT7751 | S_nCCTT9228 | line_128626_21 | ACLineSegment | Line | FALSE | FALSE
GSO_18 | 1 | 25 | S_nCCTT9228 | UCMV21 | line_131276_21 | ACLineSegment | Line | FALSE | FALSE
GSO_18 | 1 | 25 | S_nCCTT2016 | UCMV21 | line_116038_21 | ACLineSegment | Line | FALSE | FALSE
GSO_18 | 1 | 25 | S_nCCTT2016 | S_nCCTT2126 | line_116037_21 | ACLineSegment | Line | FALSE | FALSE
GSO_18 | 1 | 25 | S_nCCTT12196 | S_nCCTT2126 | line_112560_21 | ACLineSegment | Line | FALSE | FALSE
GSO_18 | 1 | 25 | S_nCCTT12196 | S_nCCTT6762 | line_112561_21 | ACLineSegment | Line | FALSE | FALSE
GSO_18 | 1 | 25 | S_nCCTT11937 | S_nCCTT6762 | line_111906_21 | ACLineSegment | Line | FALSE | FALSE
GSO_18 | 1 | 25 | S_nCCTT11937 | S_nCCTT11937_A_S_nCCTT12664 | switch_3888_21 | Switch | Switch | TRUE | FALSE
GSO_18 | 2 | 17 | S_nCCTT10183 | S_nCCTT6871 | line_106466_21 | ACLineSegment | Line | FALSE | FALSE
GSO_18 | 2 | 17 | S_nCCTT11779 | S_nCCTT6871 | line_111484_21 | ACLineSegment | Line | FALSE | FALSE
GSO_18 | 2 | 17 | S_nCCTT11779 | S_nCCTT8119 | line_111485_21 | ACLineSegment | Line | FALSE | FALSE
GSO_18 | 2 | 17 | S_nCCTT8111 | S_nCCTT8119 | line_129249_21 | ACLineSegment | Line | FALSE | FALSE
GSO_18 | 2 | 17 | S_nCCTT11726 | S_nCCTT8111 | line_111342_21 | ACLineSegment | Line | FALSE | FALSE
GSO_18 | 2 | 17 | S_nCCTT11726 | S_nCCTT8121 | line_111343_21 | ACLineSegment | Line | FALSE | FALSE
GSO_18 | 2 | 17 | S_nCCTT12034 | S_nCCTT8121 | line_112168_21 | ACLineSegment | Line | FALSE | FALSE
GSO_18 | 2 | 17 | S_nCCTT12034 | S_nCCTT3902 | line_112167_21 | ACLineSegment | Line | FALSE | FALSE
GSO_18 | 2 | 17 | S_nCCTT3902 | S_nCCTT6740 | line_120823_21 | ACLineSegment | Line | FALSE | FALSE
GSO_18 | 2 | 17 | S_nCCTT12360 | S_nCCTT6740 | line_112965_21 | ACLineSegment | Line | FALSE | FALSE
GSO_18 | 2 | 17 | S_nCCTT11528 | S_nCCTT12360 | line_110779_21 | ACLineSegment | Line | FALSE | FALSE
GSO_18 | 2 | 17 | S_nCCTT11528 | S_nCCTT9628 | line_110780_21 | ACLineSegment | Line | FALSE | FALSE
GSO_18 | 2 | 17 | S_nCCTT9622 | S_nCCTT9628 | line_131950_21 | ACLineSegment | Line | FALSE | FALSE
GSO_18 | 2 | 17 | S_nCCTT7601 | S_nCCTT9622 | line_128347_21 | ACLineSegment | Line | FALSE | FALSE
GSO_18 | 2 | 17 | S_nCCTT7601 | S_nCCTT7601_A_S_nCCTT6861 | switch_7276_21 | Switch | Switch | TRUE | FALSE
GSO_18 | 2 | 17 | S_nCCTT6861 | S_nCCTT7601_A_S_nCCTT6861 | line_127115_21 | ACLineSegment | Line | FALSE | FALSE
GSO_18 | 2 | 17 | S_nCCTT10183 | S_nCCTT6861 | line_106465_21 | ACLineSegment | Line | FALSE | FALSE

## Candidate_Path_Bridges
GridID | CandidateLineID | PathSequence | NodeA | NodeB | ElementID | ElementType | ElementClass | IsBridge | IsInAnyCycle | ParallelElementCount
GSO_122 | line_5852_22 | 1 | S_nSSEE0_12.47 | S_nSSEE0_12.47_A_S_nCCTT45 | recloser_186_22 | Switch | Switch | TRUE | FALSE | 1
GSO_122 | line_5852_22 | 2 | S_nCCTT45 | S_nSSEE0_12.47_A_S_nCCTT45 | line_5852_22 | ACLineSegment | Line | TRUE | FALSE | 1
GSO_124 | line_6716_22 | 1 | S_nSSEE0_12.47 | S_nSSEE0_12.47_A_S_nCCTT913 | recloser_198_22 | Switch | Switch | TRUE | FALSE | 1
GSO_124 | line_6716_22 | 2 | S_nCCTT913 | S_nSSEE0_12.47_A_S_nCCTT913 | line_6716_22 | ACLineSegment | Line | TRUE | FALSE | 1
GSO_123 | line_6019_22 | 1 | S_nSSEE0_12.47 | S_nSSEE0_12.47_A_S_nCCTT521 | recloser_189_22 | Switch | Switch | TRUE | FALSE | 1
GSO_123 | line_6019_22 | 2 | S_nCCTT521 | S_nSSEE0_12.47_A_S_nCCTT521 | line_6019_22 | ACLineSegment | Line | TRUE | FALSE | 1
GSO_121 | line_3530_22 | 1 | S_nSSEE0_12.47 | S_nSSEE0_12.47_A_S_nCCTT0 | recloser_151_22 | Switch | Switch | TRUE | FALSE | 1
GSO_121 | line_3530_22 | 2 | S_nCCTT0 | S_nSSEE0_12.47_A_S_nCCTT0 | line_3530_22 | ACLineSegment | Line | TRUE | FALSE | 1
GSO_144 | line_5978_22 | 1 | S_nSSEE4_12.47 | S_nSSEE4_12.47_A_S_nCCTT504 | recloser_188_22 | Switch | Switch | TRUE | FALSE | 1
GSO_144 | line_5978_22 | 2 | S_nCCTT504 | S_nSSEE4_12.47_A_S_nCCTT504 | line_5978_22 | ACLineSegment | Line | TRUE | FALSE | 1
GSO_141 | line_4565_22 | 1 | S_nSSEE4_12.47 | S_nSSEE4_12.47_A_S_nCCTT1344 | recloser_168_22 | Switch | Switch | TRUE | FALSE | 1
GSO_141 | line_4565_22 | 2 | S_nCCTT1344 | S_nSSEE4_12.47_A_S_nCCTT1344 | line_4565_22 | ACLineSegment | Line | TRUE | FALSE | 1
GSO_145 | line_6170_22 | 1 | S_nSSEE4_12.47 | S_nSSEE4_12.47_A_S_nCCTT59 | recloser_192_22 | Switch | Switch | TRUE | FALSE | 1
GSO_145 | line_6170_22 | 2 | S_nCCTT59 | S_nSSEE4_12.47_A_S_nCCTT59 | line_6170_22 | ACLineSegment | Line | TRUE | FALSE | 1
GSO_142 | line_5429_22 | 1 | S_nSSEE4_12.47 | S_nSSEE4_12.47_A_S_nCCTT245 | recloser_177_22 | Switch | Switch | TRUE | FALSE | 1
GSO_142 | line_5429_22 | 2 | S_nCCTT245 | S_nSSEE4_12.47_A_S_nCCTT245 | line_5429_22 | ACLineSegment | Line | TRUE | FALSE | 1
GSO_18 | line_108323_21 | 1 | S_nSSEE11_12.47 | S_nSSEE11_12.47_A_S_nCCTT10746 | recloser_1790_21 | Switch | Switch | TRUE | FALSE | 1
GSO_18 | line_108323_21 | 2 | S_nCCTT10746 | S_nSSEE11_12.47_A_S_nCCTT10746 | line_108323_21 | ACLineSegment | Line | TRUE | FALSE | 1
GSO_127 | line_6871_22 | 1 | S_nSSEE1_12.47 | S_nSSEE1_12.47_A_UCMV43 | recloser_204_22 | Switch | Switch | TRUE | FALSE | 1
GSO_127 | line_6871_22 | 2 | S_nSSEE1_12.47_A_UCMV43 | UCMV43 | line_6871_22 | ACLineSegment | Line | TRUE | FALSE | 1

## Mapping_Summary
GridID | CandidateLineID | MeterTopologyMappingPct | MeterCountInMappingSheet | UnresolvedMeterCount | UnresolvedAnnualEnergyMWh | TotalMeterAnnualEnergyMWh | UnresolvedAnnualEnergySharePct | PeakEstimatedUnresolved5MinMW | NonBreakerMinPathHeadroomMW | FirmHostingMW | ConservativeNonBreakerHeadroomAfterUnresolvedPeakMW | BreakEvenUnresolvedMultiplier | MappingMaterialityStatus | MappingMaterialityExplanation | BreakerLimited
GSO_122 | line_5852_22 | 100 | 3 | 0 | 0 |  | 0 | 0 |  | 13.5096 |  | inf | CLEAR_NO_UNRESOLVED_METERS | Every modeled meter is topologically resolved.
GSO_124 | line_6716_22 | 100 | 16 | 0 | 0 |  | 0 | 0 |  | 13.4085 |  | inf | CLEAR_NO_UNRESOLVED_METERS | Every modeled meter is topologically resolved.
GSO_123 | line_6019_22 | 100 | 47 | 0 | 0 |  | 0 | 0 |  | 13.1777 |  | inf | CLEAR_NO_UNRESOLVED_METERS | Every modeled meter is topologically resolved.
GSO_121 | line_3530_22 | 100 | 72 | 0 | 0 |  | 0 | 0 |  | 13.1607 |  | inf | CLEAR_NO_UNRESOLVED_METERS | Every modeled meter is topologically resolved.
GSO_144 | line_5978_22 | 100 | 32 | 0 | 0 |  | 0 | 0 |  | 11.2671 |  | inf | CLEAR_NO_UNRESOLVED_METERS | Every modeled meter is topologically resolved.
GSO_141 | line_4565_22 | 100 | 68 | 0 | 0 |  | 0 | 0 |  | 11.02 |  | inf | CLEAR_NO_UNRESOLVED_METERS | Every modeled meter is topologically resolved.
GSO_145 | line_6170_22 | 90.9677 | 155 | 14 | 191.158 | 4055.0377 | 4.7141 | 0.045772 | 12.8507 | 10.6656 | 12.8049 | 47.7395 | CLEAR_FOR_CURRENT_CANDIDATE_USING_MODELED_5MIN_UNRESOLVED_SHARE | Even after conservatively placing the largest modeled five-minute unresolved-meter contribution onto the non-breaker candidate path, the breaker remains the binding firm constraint. | TRUE
GSO_142 | line_5429_22 | 100 | 140 | 0 | 0 |  | 0 | 0 |  | 10.6074 |  | inf | CLEAR_NO_UNRESOLVED_METERS | Every modeled meter is topologically resolved.
GSO_18 | line_108323_21 | 100 | 584 | 0 | 0 |  | 0 | 0 |  | 10.3769 |  | inf | CLEAR_NO_UNRESOLVED_METERS | Every modeled meter is topologically resolved.
GSO_127 | line_6871_22 | 100 | 1 | 0 | 0 |  | 0 | 0 |  | 9.4748 |  | inf | CLEAR_NO_UNRESOLVED_METERS | Every modeled meter is topologically resolved.

## Unresolved_Mapping
MeterID | LoadNode | MappingMethod | Resolved | Depth | GridID | ResolvedBool | CandidateLineID
m_1102_22 | S_nSSEE4_12.47 | RootFallback | FALSE | 0 | GSO_145 | FALSE | line_6170_22
m_1633_22 | S_nSSEE4_12.47 | RootFallback | FALSE | 0 | GSO_145 | FALSE | line_6170_22
m_1755_22 | S_nSSEE4_12.47 | RootFallback | FALSE | 0 | GSO_145 | FALSE | line_6170_22
m_1765_22 | S_nSSEE4_12.47 | RootFallback | FALSE | 0 | GSO_145 | FALSE | line_6170_22
m_1888_22 | S_nSSEE4_12.47 | RootFallback | FALSE | 0 | GSO_145 | FALSE | line_6170_22
m_1975_22 | S_nSSEE4_12.47 | RootFallback | FALSE | 0 | GSO_145 | FALSE | line_6170_22
m_1991_22 | S_nSSEE4_12.47 | RootFallback | FALSE | 0 | GSO_145 | FALSE | line_6170_22
m_2089_22 | S_nSSEE4_12.47 | RootFallback | FALSE | 0 | GSO_145 | FALSE | line_6170_22
m_2123_22 | S_nSSEE4_12.47 | RootFallback | FALSE | 0 | GSO_145 | FALSE | line_6170_22
m_2392_22 | S_nSSEE4_12.47 | RootFallback | FALSE | 0 | GSO_145 | FALSE | line_6170_22
m_2423_22 | S_nSSEE4_12.47 | RootFallback | FALSE | 0 | GSO_145 | FALSE | line_6170_22
m_2424_22 | S_nSSEE4_12.47 | RootFallback | FALSE | 0 | GSO_145 | FALSE | line_6170_22
m_53_22 | S_nSSEE4_12.47 | RootFallback | FALSE | 0 | GSO_145 | FALSE | line_6170_22
m_835_22 | S_nSSEE4_12.47 | RootFallback | FALSE | 0 | GSO_145 | FALSE | line_6170_22

## Unresolved_Meter_Energy
GridID | MeterID | AnnualEnergyMWh | RawObservationCount | CandidateLineID
GSO_145 | m_1765_22 | 19.6701 | 8779 | line_6170_22
GSO_145 | m_1102_22 | 19.4603 | 8779 | line_6170_22
GSO_145 | m_1633_22 | 18.4349 | 8779 | line_6170_22
GSO_145 | m_2424_22 | 15.1491 | 8779 | line_6170_22
GSO_145 | m_1888_22 | 14.4253 | 8779 | line_6170_22
GSO_145 | m_1991_22 | 13.7852 | 8779 | line_6170_22
GSO_145 | m_835_22 | 13.6885 | 8779 | line_6170_22
GSO_145 | m_2089_22 | 13.6429 | 8779 | line_6170_22
GSO_145 | m_1975_22 | 13.5627 | 8779 | line_6170_22
GSO_145 | m_2123_22 | 13.2801 | 8779 | line_6170_22
GSO_145 | m_1755_22 | 10.2509 | 8779 | line_6170_22
GSO_145 | m_53_22 | 9.3748 | 8779 | line_6170_22
GSO_145 | m_2392_22 | 8.5073 | 8779 | line_6170_22
GSO_145 | m_2423_22 | 7.926 | 8779 | line_6170_22

## PF_Sensitivity_Review
CandidateKey | GridID | SubstationID | CandidateLineID | MinimumTestedPF | MaximumTestedPF | FirmHostingAtMinimumPFMW | FirmHostingAtBasePFMW | FirmHostingAtMaximumPFMW | FirmHostingRangeAcrossPFMW | Rank_PF_0.90 | Rank_PF_0.95 | Rank_PF_1.00 | MaxRankShiftAcrossPF | PFRankingStatus | FirmHostingPctRangeVsBase
GSO_121¦line_3530_22 | GSO_121 | hvmv_1_22 | line_3530_22 | 0.9 | 1 | 12.448 | 13.1607 | 13.8735 | 1.4255 | 4 | 4 | 4 | 0 | RANK_STABLE | 10.8315
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 0.9 | 1 | 12.7969 | 13.5096 | 14.2224 | 1.4255 | 1 | 1 | 1 | 0 | RANK_STABLE | 10.5518
GSO_123¦line_6019_22 | GSO_123 | hvmv_1_22 | line_6019_22 | 0.9 | 1 | 12.465 | 13.1777 | 13.8905 | 1.4255 | 3 | 3 | 3 | 0 | RANK_STABLE | 10.8176
GSO_124¦line_6716_22 | GSO_124 | hvmv_1_22 | line_6716_22 | 0.9 | 1 | 12.6957 | 13.4085 | 14.1213 | 1.4255 | 2 | 2 | 2 | 0 | RANK_STABLE | 10.6314
GSO_127¦line_6871_22 | GSO_127 | hvmv_2_22 | line_6871_22 | 0.9 | 1 | 8.9748 | 9.4748 | 9.9748 | 1 | 10 | 10 | 10 | 0 | RANK_STABLE | 10.5543
GSO_141¦line_4565_22 | GSO_141 | hvmv_5_22 | line_4565_22 | 0.9 | 1 | 10.42 | 11.02 | 11.62 | 1.2 | 6 | 6 | 6 | 0 | RANK_STABLE | 10.8892
GSO_142¦line_5429_22 | GSO_142 | hvmv_5_22 | line_5429_22 | 0.9 | 1 | 10.0074 | 10.6074 | 11.2074 | 1.2 | 8 | 8 | 8 | 0 | RANK_STABLE | 11.3128
GSO_144¦line_5978_22 | GSO_144 | hvmv_5_22 | line_5978_22 | 0.9 | 1 | 10.6671 | 11.2671 | 11.8671 | 1.2 | 5 | 5 | 5 | 0 | RANK_STABLE | 10.6504
GSO_145¦line_6170_22 | GSO_145 | hvmv_5_22 | line_6170_22 | 0.9 | 1 | 10.0656 | 10.6656 | 11.2656 | 1.2 | 7 | 7 | 7 | 0 | RANK_STABLE | 11.2512
GSO_18¦line_108323_21 | GSO_18 | hvmv_4_21 | line_108323_21 | 0.9 | 1 | 9.7102 | 10.3769 | 11.0436 | 1.3333 | 9 | 9 | 9 | 0 | RANK_STABLE | 12.849

## Substation_Upper_Bounds
SubstationID | CandidateCount | SumIndividualFirmHostingMW_UpperBoundOnly | AllCandidatesReadyForFeederBoundMILP
hvmv_1_22 | 4 | 53.2566 | TRUE
hvmv_5_22 | 4 | 43.5602 | TRUE
hvmv_4_21 | 1 | 10.3769 | TRUE
hvmv_2_22 | 1 | 9.4748 | TRUE

## Audit_Assumptions
AuditArea | Rule
Topology cycles | A feeder-level cycle is not automatically material. It is cleared for central siting when the candidate path does not intersect any cycle and all candidate-path edges are graph bridges.
Topology cycles | If a candidate-path edge participates in a cycle, exact flow sharing is not inferred without impedance or a known operational switching state.
Unmapped meters | Unresolved meters are quantified by energy and by their estimated five-minute feeder contribution using the same hourly spatial-share assumption as the thermal model.
Unmapped meters | For a breaker-limited candidate, the mapping flag can be cleared for the current central-site analysis if placing the largest estimated unresolved five-minute contribution onto the non-breaker path still leaves the breaker as the firm constraint.
Power factor | The audit reviews the already-computed PF 0.90/0.95/1.00 results for MW sensitivity and rank stability rather than inventing another PF assumption.
MILP readiness | A candidate is ready for the first feeder-bound MILP when topology and mapping flags are materially cleared, the thermal model completed, and no baseline rating exceedance exists on the candidate path.
Final MILP readiness | No candidate is marked ready for the final shared-substation portfolio MILP until explicit substation capacity is available. Feeder-level sums by substation are upper bounds only.