## Final_Location_Ranking
GlobalRank | RankWithinFeeder | GridID | CandidateLineID | CandidateNode | EstimatedBaseHostingMW | CandidateConfidence | NominalVoltageKV | CandidateLineCapacityMW | CandidateLineExistingLoadMW | CandidateLineResidualMW | FeederPeakMW | BreakerCapacityMW | BreakerResidualMW | LimitingElementID | LimitingElementType | LimitingElementClass | LimitingElementCapacityMW | LimitingElementExistingLoadMW | LimitingElementResidualMW | ElectricalDistanceHops | PathLineCount | PathTransformerCount | LoadPointReachabilityPct | HoursWithin10PctOfPeak | PctTimeWithin10PctOfPeak | CentroidX | CentroidY | PathElementIDs | CandidateKey | CandidateLineType | CandidateLineRatingA | BreakerRatingKVA_x | LoadAllocationMethod | BreakerID | SubstationID | BreakerRatingKVA_y | Substation_ExpectedFeederCount | Substation_LoadedFeederCount | Substation_AllMappedFeedersLoaded | Substation_AverageLoadMW | Substation_P95LoadMW | Substation_PeakLoadMW | Substation_PeakTimestampUTC | Substation_SumIndividualFeederPeaksMW | Substation_CoincidenceFactor | Substation_DiversityFactor | Substation_DataCoveragePct | Substation_LoadProfileConfidence | Substation_AvailableCapacityMW | Substation_CapacityResolutionStatus | Substation_CapacitySource | Substation_CapacitySourceKey | Substation_CapacitySourceUnit | Substation_Preferred80PctLimitMW | Substation_Preferred90PctLimitMW | Substation_Hard100PctLimitMW | Substation_Preferred80PctHeadroomMW | Substation_Preferred90PctHeadroomMW | Substation_Hard100PctHeadroomMW | Substation_PeakSubstationUtilizationPct | Substation_OverloadLimitPct | Substation_OverloadDurationHours | Substation_OverloadLimitMW | Substation_OverloadHeadroomMW | FeederPathHostingMW | SubstationHardHeadroomMW | SubstationPreferred90HeadroomMW | SubstationPreferred80HeadroomMW | FinalBaseHostingMW | Preferred90HostingMW | Preferred80HostingMW | FinalConstraintClass | FinalConstraintID | FinalRankingStatus | FinalRank | CandidateCountOnSharedSubstation
60 | 1 | GSO_121 | line_3530_22 | S_nCCTT0 | 13.1607 | High | 12.47 | 13.5424 | 0.38162 | 13.1607 | 0.38162 | 14.25 | 13.8684 | line_3530_22 | ACLineSegment | Line | 13.5424 | 0.38162 | 13.1607 | 2 | 1 | 0 | 100 | 40.6667 | 0.46323 | -79.9724 | 36.0836 | recloser_151_22 -> line_3530_22 | GSO_121¦line_3530_22 | ACLineSegment | 660 | 15000 | Meter | br_01_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.1607 | [6 empty] | SubstationCapacityUnresolved | line_3530_22 | Substation capacity unresolved |  | 116
61 | 2 | GSO_121 | line_3529_22 | S_nCCTT370 | 13.1607 | High | 12.47 | 13.5424 | 0.37632 | 13.166 | 0.38162 | 14.25 | 13.8684 | line_3530_22 | ACLineSegment | Line | 13.5424 | 0.38162 | 13.1607 | 3 | 2 | 0 | 100 | 40.6667 | 0.46323 | -79.9721 | 36.0845 | recloser_151_22 -> line_3530_22 -> line_3529_22 | GSO_121¦line_3529_22 | ACLineSegment | 660 | 15000 | Meter | br_01_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.1607 | [6 empty] | SubstationCapacityUnresolved | line_3530_22 | Substation capacity unresolved |  | 116
62 | 3 | GSO_121 | line_5665_22 | S_nCCTT713 | 13.1607 | High | 12.47 | 13.5424 | 0.37102 | 13.1713 | 0.38162 | 14.25 | 13.8684 | line_3530_22 | ACLineSegment | Line | 13.5424 | 0.38162 | 13.1607 | 4 | 3 | 0 | 100 | 40.6667 | 0.46323 | -79.9737 | 36.0846 | recloser_151_22 -> line_3530_22 -> line_3529_22 -> line_5665_22 | GSO_121¦line_5665_22 | ACLineSegment | 660 | 15000 | Meter | br_01_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.1607 | [6 empty] | SubstationCapacityUnresolved | line_3530_22 | Substation capacity unresolved |  | 116
63 | 4 | GSO_121 | line_6422_22 | UCMV95 | 13.1607 | High | 12.47 | 13.5424 | 0.13251 | 13.4099 | 0.38162 | 14.25 | 13.8684 | line_3530_22 | ACLineSegment | Line | 13.5424 | 0.38162 | 13.1607 | 5 | 4 | 0 | 100 | 40.6667 | 0.46323 | -79.9747 | 36.0855 | recloser_151_22 -> line_3530_22 -> line_3529_22 -> line_5665_22 -> line_6422_22 | GSO_121¦line_6422_22 | ACLineSegment | 660 | 15000 | Meter | br_01_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.1607 | [6 empty] | SubstationCapacityUnresolved | line_3530_22 | Substation capacity unresolved |  | 116
64 | 5 | GSO_121 | line_6234_22 | S_nCCTT616 | 13.1607 | High | 12.47 | 13.5424 | 0.23321 | 13.3092 | 0.38162 | 14.25 | 13.8684 | line_3530_22 | ACLineSegment | Line | 13.5424 | 0.38162 | 13.1607 | 6 | 4 | 0 | 100 | 40.6667 | 0.46323 | -79.9761 | 36.0854 | recloser_151_22 -> line_3530_22 -> line_3529_22 -> line_5665_22 -> recloser_193_22 -> line_6234_22 | GSO_121¦line_6234_22 | ACLineSegment | 660 | 15000 | Meter | br_01_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.1607 | [6 empty] | SubstationCapacityUnresolved | line_3530_22 | Substation capacity unresolved |  | 116
65 | 6 | GSO_121 | line_6474_22 | S_nCCTT741 | 13.1607 | High | 12.47 | 13.5424 | 0.12721 | 13.4152 | 0.38162 | 14.25 | 13.8684 | line_3530_22 | ACLineSegment | Line | 13.5424 | 0.38162 | 13.1607 | 6 | 5 | 0 | 100 | 40.6667 | 0.46323 | -79.9743 | 36.0867 | recloser_151_22 -> line_3530_22 -> line_3529_22 -> line_5665_22 -> line_6422_22 -> line_6474_22 | GSO_121¦line_6474_22 | ACLineSegment | 660 | 15000 | Meter | br_01_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.1607 | [6 empty] | SubstationCapacityUnresolved | line_3530_22 | Substation capacity unresolved |  | 116
66 | 7 | GSO_121 | line_6235_22 | S_nCCTT869 | 13.1607 | High | 12.47 | 13.5424 | 0.19081 | 13.3516 | 0.38162 | 14.25 | 13.8684 | line_3530_22 | ACLineSegment | Line | 13.5424 | 0.38162 | 13.1607 | 7 | 5 | 0 | 100 | 40.6667 | 0.46323 | -79.9778 | 36.0855 | recloser_151_22 -> line_3530_22 -> line_3529_22 -> line_5665_22 -> recloser_193_22 -> line_6234_22 -> line_6235_22 | GSO_121¦line_6235_22 | ACLineSegment | 660 | 15000 | Meter | br_01_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.1607 | [6 empty] | SubstationCapacityUnresolved | line_3530_22 | Substation capacity unresolved |  | 116
67 | 8 | GSO_121 | line_6144_22 | S_nCCTT580 | 13.1607 | High | 12.47 | 13.5424 | 0.037102 | 13.5053 | 0.38162 | 14.25 | 13.8684 | line_3530_22 | ACLineSegment | Line | 13.5424 | 0.38162 | 13.1607 | 7 | 5 | 0 | 100 | 40.6667 | 0.46323 | -79.9781 | 36.0867 | recloser_151_22 -> line_3530_22 -> line_3529_22 -> line_5665_22 -> recloser_193_22 -> line_6234_22 -> line_6144_22 | GSO_121¦line_6144_22 | ACLineSegment | 660 | 15000 | Meter | br_01_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.1607 | [6 empty] | SubstationCapacityUnresolved | line_3530_22 | Substation capacity unresolved |  | 116
68 | 9 | GSO_121 | line_6249_22 | S_nCCTT622 | 13.1607 | High | 12.47 | 13.5424 | 0.12191 | 13.4205 | 0.38162 | 14.25 | 13.8684 | line_3530_22 | ACLineSegment | Line | 13.5424 | 0.38162 | 13.1607 | 7 | 6 | 0 | 100 | 40.6667 | 0.46323 | -79.9743 | 36.0873 | recloser_151_22 -> line_3530_22 -> line_3529_22 -> line_5665_22 -> line_6422_22 -> line_6474_22 -> line_6249_22 | GSO_121¦line_6249_22 | ACLineSegment | 660 | 15000 | Meter | br_01_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.1607 | [6 empty] | SubstationCapacityUnresolved | line_3530_22 | Substation capacity unresolved |  | 116
69 | 10 | GSO_121 | line_5800_22 | S_nCCTT43 | 13.1607 | High | 12.47 | 13.5424 | 0.18021 | 13.3622 | 0.38162 | 14.25 | 13.8684 | line_3530_22 | ACLineSegment | Line | 13.5424 | 0.38162 | 13.1607 | 8 | 6 | 0 | 100 | 40.6667 | 0.46323 | -79.9802 | 36.0848 | recloser_151_22 -> line_3530_22 -> line_3529_22 -> line_5665_22 -> recloser_193_22 -> line_6234_22 -> line_6235_22 -> line_5800_22 | GSO_121¦line_5800_22 | ACLineSegment | 660 | 15000 | Meter | br_01_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.1607 | [6 empty] | SubstationCapacityUnresolved | line_3530_22 | Substation capacity unresolved |  | 116
70 | 11 | GSO_121 | line_5825_22 | S_nCCTT44 | 13.1607 | High | 12.47 | 13.5424 | 0.031802 | 13.5106 | 0.38162 | 14.25 | 13.8684 | line_3530_22 | ACLineSegment | Line | 13.5424 | 0.38162 | 13.1607 | 8 | 6 | 0 | 100 | 40.6667 | 0.46323 | -79.9805 | 36.0874 | recloser_151_22 -> line_3530_22 -> line_3529_22 -> line_5665_22 -> recloser_193_22 -> line_6234_22 -> line_6144_22 -> line_5825_22 | GSO_121¦line_5825_22 | ACLineSegment | 660 | 15000 | Meter | br_01_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.1607 | [6 empty] | SubstationCapacityUnresolved | line_3530_22 | Substation capacity unresolved |  | 116
71 | 12 | GSO_121 | line_5826_22 | S_nCCTT828 | 13.1607 | High | 12.47 | 13.5424 | 0.026502 | 13.5159 | 0.38162 | 14.25 | 13.8684 | line_3530_22 | ACLineSegment | Line | 13.5424 | 0.38162 | 13.1607 | 9 | 7 | 0 | 100 | 40.6667 | 0.46323 | -79.9827 | 36.0878 | recloser_151_22 -> line_3530_22 -> line_3529_22 -> line_5665_22 -> recloser_193_22 -> line_6234_22 -> line_6144_22 -> line_5825_22 -> line_5826_22 | GSO_121¦line_5826_22 | ACLineSegment | 660 | 15000 | Meter | br_01_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.1607 | [6 empty] | SubstationCapacityUnresolved | line_3530_22 | Substation capacity unresolved |  | 116
72 | 13 | GSO_121 | line_5618_22 | S_nCCTT349 | 13.1607 | High | 12.47 | 13.5424 | 0.16961 | 13.3728 | 0.38162 | 14.25 | 13.8684 | line_3530_22 | ACLineSegment | Line | 13.5424 | 0.38162 | 13.1607 | 9 | 7 | 0 | 100 | 40.6667 | 0.46323 | -79.9829 | 36.0851 | recloser_151_22 -> line_3530_22 -> line_3529_22 -> line_5665_22 -> recloser_193_22 -> line_6234_22 -> line_6235_22 -> line_5800_22 -> line_5618_22 | GSO_121¦line_5618_22 | ACLineSegment | 660 | 15000 | Meter | br_01_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.1607 | [6 empty] | SubstationCapacityUnresolved | line_3530_22 | Substation capacity unresolved |  | 116
73 | 14 | GSO_121 | line_5801_22 | UCMV81 | 13.1607 | High | 12.47 | 13.5424 | 0.0053003 | 13.5371 | 0.38162 | 14.25 | 13.8684 | line_3530_22 | ACLineSegment | Line | 13.5424 | 0.38162 | 13.1607 | 9 | 7 | 0 | 100 | 40.6667 | 0.46323 | -79.9818 | 36.0832 | recloser_151_22 -> line_3530_22 -> line_3529_22 -> line_5665_22 -> recloser_193_22 -> line_6234_22 -> line_6235_22 -> line_5800_22 -> line_5801_22 | GSO_121¦line_5801_22 | ACLineSegment | 660 | 15000 | Meter | br_01_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.1607 | [6 empty] | SubstationCapacityUnresolved | line_3530_22 | Substation capacity unresolved |  | 116
74 | 15 | GSO_121 | line_5619_22 | S_nCCTT552 | 13.1607 | High | 12.47 | 13.5424 | 0.15901 | 13.3834 | 0.38162 | 14.25 | 13.8684 | line_3530_22 | ACLineSegment | Line | 13.5424 | 0.38162 | 13.1607 | 10 | 8 | 0 | 100 | 40.6667 | 0.46323 | -79.9847 | 36.0858 | recloser_151_22 -> line_3530_22 -> line_3529_22 -> line_5665_22 -> recloser_193_22 -> line_6234_22 -> line_6235_22 -> line_5800_22 -> line_5618_22 -> line_5619_22 | GSO_121¦line_5619_22 | ACLineSegment | 660 | 15000 | Meter | br_01_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.1607 | [6 empty] | SubstationCapacityUnresolved | line_3530_22 | Substation capacity unresolved |  | 116
75 | 16 | GSO_121 | line_5525_22 | S_nCCTT309 | 13.1607 | High | 12.47 | 13.5424 | 0.021201 | 13.5212 | 0.38162 | 14.25 | 13.8684 | line_3530_22 | ACLineSegment | Line | 13.5424 | 0.38162 | 13.1607 | 10 | 8 | 0 | 100 | 40.6667 | 0.46323 | -79.984 | 36.0885 | recloser_151_22 -> line_3530_22 -> line_3529_22 -> line_5665_22 -> recloser_193_22 -> line_6234_22 -> line_6144_22 -> line_5825_22 -> line_5826_22 -> line_5525_22 | GSO_121¦line_5525_22 | ACLineSegment | 660 | 15000 | Meter | br_01_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.1607 | [6 empty] | SubstationCapacityUnresolved | line_3530_22 | Substation capacity unresolved |  | 116
76 | 17 | GSO_121 | line_6085_22 | S_nCCTT633 | 13.1607 | High | 12.47 | 13.5424 | 0.13251 | 13.4099 | 0.38162 | 14.25 | 13.8684 | line_3530_22 | ACLineSegment | Line | 13.5424 | 0.38162 | 13.1607 | 11 | 9 | 0 | 100 | 40.6667 | 0.46323 | -79.9862 | 36.0859 | recloser_151_22 -> line_3530_22 -> line_3529_22 -> line_5665_22 -> recloser_193_22 -> line_6234_22 -> line_6235_22 -> line_5800_22 -> line_5618_22 -> line_5619_22 -> line_6085_22 | GSO_121¦line_6085_22 | ACLineSegment | 660 | 15000 | Meter | br_01_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.1607 | [6 empty] | SubstationCapacityUnresolved | line_3530_22 | Substation capacity unresolved |  | 116
77 | 18 | GSO_121 | line_5524_22 | S_nCCTT785 | 13.1607 | High | 12.47 | 13.5424 | 0.015901 | 13.5265 | 0.38162 | 14.25 | 13.8684 | line_3530_22 | ACLineSegment | Line | 13.5424 | 0.38162 | 13.1607 | 12 | 9 | 0 | 100 | 40.6667 | 0.46323 | -79.9859 | 36.0885 | recloser_151_22 -> line_3530_22 -> line_3529_22 -> line_5665_22 -> recloser_193_22 -> line_6234_22 -> line_6144_22 -> line_5825_22 -> line_5826_22 -> line_5525_22 -> switch_648_22 -> line_5524_22 | GSO_121¦line_5524_22 | ACLineSegment | 660 | 15000 | Meter | br_01_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.1607 | [6 empty] | SubstationCapacityUnresolved | line_3530_22 | Substation capacity unresolved |  | 116
78 | 19 | GSO_121 | line_5872_22 | S_nCCTT46 | 13.1607 | High | 12.47 | 13.5424 | 0.12721 | 13.4152 | 0.38162 | 14.25 | 13.8684 | line_3530_22 | ACLineSegment | Line | 13.5424 | 0.38162 | 13.1607 | 12 | 10 | 0 | 100 | 40.6667 | 0.46323 | -79.9882 | 36.0864 | recloser_151_22 -> line_3530_22 -> line_3529_22 -> line_5665_22 -> recloser_193_22 -> line_6234_22 -> line_6235_22 -> line_5800_22 -> line_5618_22 -> line_5619_22 -> line_6085_22 -> line_5872_22 | GSO_121¦line_5872_22 | ACLineSegment | 660 | 15000 | Meter | br_01_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.1607 | [6 empty] | SubstationCapacityUnresolved | line_3530_22 | Substation capacity unresolved |  | 116
79 | 20 | GSO_121 | line_6088_22 | S_nCCTT553 | 13.1607 | High | 12.47 | 13.5424 | 0.010601 | 13.5318 | 0.38162 | 14.25 | 13.8684 | line_3530_22 | ACLineSegment | Line | 13.5424 | 0.38162 | 13.1607 | 13 | 10 | 0 | 100 | 40.6667 | 0.46323 | -79.988 | 36.0885 | recloser_151_22 -> line_3530_22 -> line_3529_22 -> line_5665_22 -> recloser_193_22 -> line_6234_22 -> line_6144_22 -> line_5825_22 -> line_5826_22 -> line_5525_22 -> switch_648_22 -> line_5524_22 -> line_6088_22 | GSO_121¦line_6088_22 | ACLineSegment | 660 | 15000 | Meter | br_01_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.1607 | [6 empty] | SubstationCapacityUnresolved | line_3530_22 | Substation capacity unresolved |  | 116
80 | 21 | GSO_121 | line_6016_22 | S_nCCTT520_A_S_nCCTT553 | 12.3059 | High | 12.47 | 12.3112 | 0.0053003 | 12.3059 | 0.38162 | 14.25 | 13.8684 | line_6016_22 | ACLineSegment | Line | 12.3112 | 0.0053003 | 12.3059 | 14 | 11 | 0 | 100 | 40.6667 | 0.46323 | -79.9887 | 36.0887 | recloser_151_22 -> line_3530_22 -> line_3529_22 -> line_5665_22 -> recloser_193_22 -> line_6234_22 -> line_6144_22 -> line_5825_22 -> line_5826_22 -> line_5525_22 -> switch_648_22 -> line_5524_22 -> line_6088_22 -> line_6016_22 | GSO_121¦line_6016_22 | ACLineSegment | 600 | 15000 | Meter | br_01_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 12.3059 | [6 empty] | SubstationCapacityUnresolved | line_6016_22 | Substation capacity unresolved |  | 116
82 | 22 | GSO_121 | line_5873_22 | S_nCCTT728 | 12.3006 | High | 12.47 | 12.3112 | 0.010601 | 12.3006 | 0.38162 | 14.25 | 13.8684 | line_5873_22 | ACLineSegment | Line | 12.3112 | 0.010601 | 12.3006 | 14 | 11 | 0 | 100 | 40.6667 | 0.46323 | -79.9896 | 36.0872 | recloser_151_22 -> line_3530_22 -> line_3529_22 -> line_5665_22 -> recloser_193_22 -> line_6234_22 -> line_6235_22 -> line_5800_22 -> line_5618_22 -> line_5619_22 -> line_6085_22 -> line_5872_22 -> switch_683_22 -> line_5873_22 | GSO_121¦line_5873_22 | ACLineSegment | 600 | 15000 | Meter | br_01_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 12.3006 | [6 empty] | SubstationCapacityUnresolved | line_5873_22 | Substation capacity unresolved |  | 116
83 | 23 | GSO_121 | line_6017_22 | S_nCCTT728_B_S_nCCTT520 | 12.3006 | High | 12.47 | 12.3112 | 0 | 12.3112 | 0.38162 | 14.25 | 13.8684 | line_5873_22 | ACLineSegment | Line | 12.3112 | 0.010601 | 12.3006 | 15 | 12 | 0 | 100 | 40.6667 | 0.46323 | -79.9893 | 36.0881 | recloser_151_22 -> line_3530_22 -> line_3529_22 -> line_5665_22 -> recloser_193_22 -> line_6234_22 -> line_6235_22 -> line_5800_22 -> line_5618_22 -> line_5619_22 -> line_6085_22 -> line_5872_22 -> switch_683_22 -> line_5873_22 -> line_6017_22 | GSO_121¦line_6017_22 | ACLineSegment | 600 | 15000 | Meter | br_01_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 12.3006 | [6 empty] | SubstationCapacityUnresolved | line_5873_22 | Substation capacity unresolved |  | 116
86 | 24 | GSO_121 | line_6250_22 | S_nCCTT801 | 12.1999 | High | 12.47 | 12.3112 | 0.11131 | 12.1999 | 0.38162 | 14.25 | 13.8684 | line_6250_22 | ACLineSegment | Line | 12.3112 | 0.11131 | 12.1999 | 9 | 7 | 0 | 100 | 40.6667 | 0.46323 | -79.9742 | 36.0877 | recloser_151_22 -> line_3530_22 -> line_3529_22 -> line_5665_22 -> line_6422_22 -> line_6474_22 -> line_6249_22 -> switch_752_22 -> line_6250_22 | GSO_121¦line_6250_22 | ACLineSegment | 600 | 15000 | Meter | br_01_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 12.1999 | [6 empty] | SubstationCapacityUnresolved | line_6250_22 | Substation capacity unresolved |  | 116
87 | 25 | GSO_121 | line_5901_22 | S_nCCTT470 | 12.1999 | High | 12.47 | 12.3112 | 0.10601 | 12.2052 | 0.38162 | 14.25 | 13.8684 | line_6250_22 | ACLineSegment | Line | 12.3112 | 0.11131 | 12.1999 | 11 | 8 | 0 | 100 | 40.6667 | 0.46323 | -79.9742 | 36.0881 | recloser_151_22 -> line_3530_22 -> line_3529_22 -> line_5665_22 -> line_6422_22 -> line_6474_22 -> line_6249_22 -> switch_752_22 -> line_6250_22 -> switch_695_22 -> line_5901_22 | GSO_121¦line_5901_22 | ACLineSegment | 600 | 15000 | Meter | br_01_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 12.1999 | [6 empty] | SubstationCapacityUnresolved | line_6250_22 | Substation capacity unresolved |  | 116
88 | 26 | GSO_121 | line_4707_22 | S_nCCTT1397 | 12.1999 | High | 12.47 | 12.3112 | 0.10071 | 12.2105 | 0.38162 | 14.25 | 13.8684 | line_6250_22 | ACLineSegment | Line | 12.3112 | 0.11131 | 12.1999 | 13 | 9 | 0 | 100 | 40.6667 | 0.46323 | -79.9742 | 36.0885 | recloser_151_22 -> line_3530_22 -> line_3529_22 -> line_5665_22 -> line_6422_22 -> line_6474_22 -> line_6249_22 -> switch_752_22 -> line_6250_22 -> switch_695_22 -> line_5901_22 -> switch_489_22 -> line_4707_22 | GSO_121¦line_4707_22 | ACLineSegment | 600 | 15000 | Meter | br_01_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 12.1999 | [6 empty] | SubstationCapacityUnresolved | line_6250_22 | Substation capacity unresolved |  | 116
89 | 27 | GSO_121 | line_4513_22 | S_nCCTT1327 | 12.1999 | High | 12.47 | 13.5424 | 0.095406 | 13.447 | 0.38162 | 14.25 | 13.8684 | line_6250_22 | ACLineSegment | Line | 12.3112 | 0.11131 | 12.1999 | 14 | 10 | 0 | 100 | 40.6667 | 0.46323 | -79.9744 | 36.0892 | recloser_151_22 -> line_3530_22 -> line_3529_22 -> line_5665_22 -> line_6422_22 -> line_6474_22 -> line_6249_22 -> switch_752_22 -> line_6250_22 -> switch_695_22 -> line_5901_22 -> switch_489_22 -> line_4707_22 -> line_4513_22 | GSO_121¦line_4513_22 | ACLineSegment | 660 | 15000 | Meter | br_01_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 12.1999 | [6 empty] | SubstationCapacityUnresolved | line_6250_22 | Substation capacity unresolved |  | 116
90 | 28 | GSO_121 | line_4512_22 | S_nCCTT1370 | 12.1999 | High | 12.47 | 13.5424 | 0.090106 | 13.4523 | 0.38162 | 14.25 | 13.8684 | line_6250_22 | ACLineSegment | Line | 12.3112 | 0.11131 | 12.1999 | 15 | 11 | 0 | 100 | 40.6667 | 0.46323 | -79.9741 | 36.0894 | recloser_151_22 -> line_3530_22 -> line_3529_22 -> line_5665_22 -> line_6422_22 -> line_6474_22 -> line_6249_22 -> switch_752_22 -> line_6250_22 -> switch_695_22 -> line_5901_22 -> switch_489_22 -> line_4707_22 -> line_4513_22 -> line_4512_22 | GSO_121¦line_4512_22 | ACLineSegment | 660 | 15000 | Meter | br_01_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 12.1999 | [6 empty] | SubstationCapacityUnresolved | line_6250_22 | Substation capacity unresolved |  | 116
91 | 29 | GSO_121 | line_4639_22 | S_nCCTT281 | 12.1999 | High | 12.47 | 12.3112 | 0.084805 | 12.2264 | 0.38162 | 14.25 | 13.8684 | line_6250_22 | ACLineSegment | Line | 12.3112 | 0.11131 | 12.1999 | 17 | 12 | 0 | 100 | 40.6667 | 0.46323 | -79.9729 | 36.0896 | recloser_151_22 -> line_3530_22 -> line_3529_22 -> line_5665_22 -> line_6422_22 -> line_6474_22 -> line_6249_22 -> switch_752_22 -> line_6250_22 -> switch_695_22 -> line_5901_22 -> switch_489_22 -> line_4707_22 -> line_4513_22 -> line_4512_22 -> switch_471_22 -> line_4639_22 | GSO_121¦line_4639_22 | ACLineSegment | 600 | 15000 | Meter | br_01_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 12.1999 | [6 empty] | SubstationCapacityUnresolved | line_6250_22 | Substation capacity unresolved |  | 116
92 | 30 | GSO_121 | line_5483_22 | S_nCCTT737 | 12.1999 | High | 12.47 | 12.3112 | 0.079505 | 12.2317 | 0.38162 | 14.25 | 13.8684 | line_6250_22 | ACLineSegment | Line | 12.3112 | 0.11131 | 12.1999 | 19 | 13 | 0 | 100 | 40.6667 | 0.46323 | -79.9723 | 36.0896 | recloser_151_22 -> line_3530_22 -> line_3529_22 -> line_5665_22 -> line_6422_22 -> line_6474_22 -> line_6249_22 -> switch_752_22 -> line_6250_22 -> switch_695_22 -> line_5901_22 -> switch_489_22 -> line_4707_22 -> line_4513_22 -> line_4512_22 -> switch_471_22 -> line_4639_22 -> switch_643_22 -> line_5483_22 | GSO_121¦line_5483_22 | ACLineSegment | 600 | 15000 | Meter | br_01_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 12.1999 | [6 empty] | SubstationCapacityUnresolved | line_6250_22 | Substation capacity unresolved |  | 116
93 | 31 | GSO_121 | line_6051_22 | S_nCCTT737_B_S_nCCTT540 | 12.1999 | High | 12.47 | 12.3112 | 0.010601 | 12.3006 | 0.38162 | 14.25 | 13.8684 | line_6250_22 | ACLineSegment | Line | 12.3112 | 0.11131 | 12.1999 | 20 | 14 | 0 | 100 | 40.6667 | 0.46323 | -79.972 | 36.0908 | recloser_151_22 -> line_3530_22 -> line_3529_22 -> line_5665_22 -> line_6422_22 -> line_6474_22 -> line_6249_22 -> switch_752_22 -> line_6250_22 -> switch_695_22 -> line_5901_22 -> switch_489_22 -> line_4707_22 -> line_4513_22 -> line_4512_22 -> switch_471_22 -> line_4639_22 -> switch_643_22 -> line_5483_22 -> line_6051_22 | GSO_121¦line_6051_22 | ACLineSegment | 600 | 15000 | Meter | br_01_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 12.1999 | [6 empty] | SubstationCapacityUnresolved | line_6250_22 | Substation capacity unresolved |  | 116
94 | 32 | GSO_121 | line_5372_22 | S_nCCTT220 | 12.1999 | High | 12.47 | 12.3112 | 0.063604 | 12.2476 | 0.38162 | 14.25 | 13.8684 | line_6250_22 | ACLineSegment | Line | 12.3112 | 0.11131 | 12.1999 | 21 | 14 | 0 | 100 | 40.6667 | 0.46323 | -79.9718 | 36.0896 | recloser_151_22 -> line_3530_22 -> line_3529_22 -> line_5665_22 -> line_6422_22 -> line_6474_22 -> line_6249_22 -> switch_752_22 -> line_6250_22 -> switch_695_22 -> line_5901_22 -> switch_489_22 -> line_4707_22 -> line_4513_22 -> line_4512_22 -> switch_471_22 -> line_4639_22 -> switch_643_22 -> line_5483_22 -> switch_622_22 -> line_5372_22 | GSO_121¦line_5372_22 | ACLineSegment | 600 | 15000 | Meter | br_01_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 12.1999 | [6 empty] | SubstationCapacityUnresolved | line_6250_22 | Substation capacity unresolved |  | 116
95 | 33 | GSO_121 | line_4865_22 | S_nCCTT1458 | 12.1999 | High | 12.47 | 12.3112 | 0.058304 | 12.2529 | 0.38162 | 14.25 | 13.8684 | line_6250_22 | ACLineSegment | Line | 12.3112 | 0.11131 | 12.1999 | 23 | 15 | 0 | 100 | 40.6667 | 0.46323 | -79.9709 | 36.0893 | recloser_151_22 -> line_3530_22 -> line_3529_22 -> line_5665_22 -> line_6422_22 -> line_6474_22 -> line_6249_22 -> switch_752_22 -> line_6250_22 -> switch_695_22 -> line_5901_22 -> switch_489_22 -> line_4707_22 -> line_4513_22 -> line_4512_22 -> switch_471_22 -> line_4639_22 -> switch_643_22 -> line_5483_22 -> switch_622_22 -> line_5372_22 -> switch_518_22 -> line_4865_22 | GSO_121¦line_4865_22 | ACLineSegment | 600 | 15000 | Meter | br_01_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 12.1999 | [6 empty] | SubstationCapacityUnresolved | line_6250_22 | Substation capacity unresolved |  | 116
96 | 34 | GSO_121 | line_4866_22 | S_nCCTT402 | 12.1999 | High | 12.47 | 12.3112 | 0.042403 | 12.2688 | 0.38162 | 14.25 | 13.8684 | line_6250_22 | ACLineSegment | Line | 12.3112 | 0.11131 | 12.1999 | 25 | 16 | 0 | 100 | 40.6667 | 0.46323 | -79.9701 | 36.089 | recloser_151_22 -> line_3530_22 -> line_3529_22 -> line_5665_22 -> line_6422_22 -> line_6474_22 -> line_6249_22 -> switch_752_22 -> line_6250_22 -> switch_695_22 -> line_5901_22 -> switch_489_22 -> line_4707_22 -> line_4513_22 -> line_4512_22 -> switch_471_22 -> line_4639_22 -> switch_643_22 -> line_5483_22 -> switch_622_22 -> line_5372_22 -> switch_518_22 -> line_4865_22 -> switch_520_22 -> line_4866_22 | GSO_121¦line_4866_22 | ACLineSegment | 600 | 15000 | Meter | br_01_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 12.1999 | [6 empty] | SubstationCapacityUnresolved | line_6250_22 | Substation capacity unresolved |  | 116
97 | 35 | GSO_121 | line_4473_22 | S_nCCTT1314 | 12.1999 | High | 12.47 | 12.3112 | 0.037102 | 12.2741 | 0.38162 | 14.25 | 13.8684 | line_6250_22 | ACLineSegment | Line | 12.3112 | 0.11131 | 12.1999 | 27 | 17 | 0 | 100 | 40.6667 | 0.46323 | -79.9697 | 36.0889 | recloser_151_22 -> line_3530_22 -> line_3529_22 -> line_5665_22 -> line_6422_22 -> line_6474_22 -> line_6249_22 -> switch_752_22 -> line_6250_22 -> switch_695_22 -> line_5901_22 -> switch_489_22 -> line_4707_22 -> line_4513_22 -> line_4512_22 -> switch_471_22 -> line_4639_22 -> switch_643_22 -> line_5483_22 -> switch_622_22 -> line_5372_22 -> switch_518_22 -> line_4865_22 -> switch_520_22 -> line_4866_22 -> switch_430_22 -> line_4473_22 | GSO_121¦line_4473_22 | ACLineSegment | 600 | 15000 | Meter | br_01_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 12.1999 | [6 empty] | SubstationCapacityUnresolved | line_6250_22 | Substation capacity unresolved |  | 116
98 | 36 | GSO_121 | line_4474_22 | S_nCCTT872 | 12.1999 | High | 12.47 | 12.3112 | 0.031802 | 12.2794 | 0.38162 | 14.25 | 13.8684 | line_6250_22 | ACLineSegment | Line | 12.3112 | 0.11131 | 12.1999 | 29 | 18 | 0 | 100 | 40.6667 | 0.46323 | -79.9693 | 36.0887 | recloser_151_22 -> line_3530_22 -> line_3529_22 -> line_5665_22 -> line_6422_22 -> line_6474_22 -> line_6249_22 -> switch_752_22 -> line_6250_22 -> switch_695_22 -> line_5901_22 -> switch_489_22 -> line_4707_22 -> line_4513_22 -> line_4512_22 -> switch_471_22 -> line_4639_22 -> switch_643_22 -> line_5483_22 -> switch_622_22 -> line_5372_22 -> switch_518_22 -> line_4865_22 -> switch_520_22 -> line_4866_22 -> switch_430_22 -> line_4473_22 -> switch_432_22 -> line_4474_22 | GSO_121¦line_4474_22 | ACLineSegment | 600 | 15000 | Meter | br_01_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 12.1999 | [6 empty] | SubstationCapacityUnresolved | line_6250_22 | Substation capacity unresolved |  | 116
99 | 37 | GSO_121 | line_4573_22 | S_nCCTT1347 | 12.1999 | High | 12.47 | 12.3112 | 0.026502 | 12.2847 | 0.38162 | 14.25 | 13.8684 | line_6250_22 | ACLineSegment | Line | 12.3112 | 0.11131 | 12.1999 | 31 | 19 | 0 | 100 | 40.6667 | 0.46323 | -79.9686 | 36.0886 | recloser_151_22 -> line_3530_22 -> line_3529_22 -> line_5665_22 -> line_6422_22 -> line_6474_22 -> line_6249_22 -> switch_752_22 -> line_6250_22 -> switch_695_22 -> line_5901_22 -> switch_489_22 -> line_4707_22 -> line_4513_22 -> line_4512_22 -> switch_471_22 -> line_4639_22 -> switch_643_22 -> line_5483_22 -> switch_622_22 -> line_5372_22 -> switch_518_22 -> line_4865_22 -> switch_520_22 -> line_4866_22 -> switch_430_22 -> line_4473_22 -> switch_432_22 -> line_4474_22 -> switch_455_22 -> line_4573_22 | GSO_121¦line_4573_22 | ACLineSegment | 600 | 15000 | Meter | br_01_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 12.1999 | [6 empty] | SubstationCapacityUnresolved | line_6250_22 | Substation capacity unresolved |  | 116
100 | 38 | GSO_121 | line_4572_22 | S_nCCTT1347_B_S_nCCTT425 | 12.1999 | High | 12.47 | 12.3112 | 0.021201 | 12.29 | 0.38162 | 14.25 | 13.8684 | line_6250_22 | ACLineSegment | Line | 12.3112 | 0.11131 | 12.1999 | 32 | 20 | 0 | 100 | 40.6667 | 0.46323 | -79.9684 | 36.0884 | recloser_151_22 -> line_3530_22 -> line_3529_22 -> line_5665_22 -> line_6422_22 -> line_6474_22 -> line_6249_22 -> switch_752_22 -> line_6250_22 -> switch_695_22 -> line_5901_22 -> switch_489_22 -> line_4707_22 -> line_4513_22 -> line_4512_22 -> switch_471_22 -> line_4639_22 -> switch_643_22 -> line_5483_22 -> switch_622_22 -> line_5372_22 -> switch_518_22 -> line_4865_22 -> switch_520_22 -> line_4866_22 -> switch_430_22 -> line_4473_22 -> switch_432_22 -> line_4474_22 -> switch_455_22 -> line_4573_22 -> line_4572_22 | GSO_121¦line_4572_22 | ACLineSegment | 600 | 15000 | Meter | br_01_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 12.1999 | [6 empty] | SubstationCapacityUnresolved | line_6250_22 | Substation capacity unresolved |  | 116
101 | 39 | GSO_121 | line_5479_22 | S_nCCTT425_B_S_nCCTT279 | 12.1999 | High | 12.47 | 12.3112 | 0.015901 | 12.2953 | 0.38162 | 14.25 | 13.8684 | line_6250_22 | ACLineSegment | Line | 12.3112 | 0.11131 | 12.1999 | 34 | 21 | 0 | 100 | 40.6667 | 0.46323 | -79.9687 | 36.0879 | recloser_151_22 -> line_3530_22 -> line_3529_22 -> line_5665_22 -> line_6422_22 -> line_6474_22 -> line_6249_22 -> switch_752_22 -> line_6250_22 -> switch_695_22 -> line_5901_22 -> switch_489_22 -> line_4707_22 -> line_4513_22 -> line_4512_22 -> switch_471_22 -> line_4639_22 -> switch_643_22 -> line_5483_22 -> switch_622_22 -> line_5372_22 -> switch_518_22 -> line_4865_22 -> switch_520_22 -> line_4866_22 -> switch_430_22 -> line_4473_22 -> switch_432_22 -> line_4474_22 -> switch_455_22 -> line_4573_22 -> line_4572_22 -> switch_454_22 -> line_5479_22 | GSO_121¦line_5479_22 | ACLineSegment | 600 | 15000 | Meter | br_01_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 12.1999 | [6 empty] | SubstationCapacityUnresolved | line_6250_22 | Substation capacity unresolved |  | 116
500 | 40 | GSO_121 | line_5900_22 | S_nCCTT47 | 7.103 | High | 7.2 | 7.1083 | 0.0053003 | 7.103 | 0.38162 | 14.25 | 13.8684 | line_5900_22 | ACLineSegment | Line | 7.1083 | 0.0053003 | 7.103 | 16 | 12 | 0 | 100 | 40.6667 | 0.46323 | -79.9901 | 36.088 | recloser_151_22 -> line_3530_22 -> line_3529_22 -> line_5665_22 -> recloser_193_22 -> line_6234_22 -> line_6235_22 -> line_5800_22 -> line_5618_22 -> line_5619_22 -> line_6085_22 -> line_5872_22 -> switch_683_22 -> line_5873_22 -> switch_693_22 -> line_5900_22 | GSO_121¦line_5900_22 | ACLineSegment | 600 | 15000 | Meter | br_01_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 7.103 | [6 empty] | SubstationCapacityUnresolved | line_5900_22 | Substation capacity unresolved |  | 116
503 | 41 | GSO_121 | line_4867_22 | S_nCCTT476 | 7.0977 | High | 7.2 | 7.1083 | 0.010601 | 7.0977 | 0.38162 | 14.25 | 13.8684 | line_4867_22 | ACLineSegment | Line | 7.1083 | 0.010601 | 7.0977 | 25 | 16 | 0 | 100 | 40.6667 | 0.46323 | -79.9705 | 36.0884 | recloser_151_22 -> line_3530_22 -> line_3529_22 -> line_5665_22 -> line_6422_22 -> line_6474_22 -> line_6249_22 -> switch_752_22 -> line_6250_22 -> switch_695_22 -> line_5901_22 -> switch_489_22 -> line_4707_22 -> line_4513_22 -> line_4512_22 -> switch_471_22 -> line_4639_22 -> switch_643_22 -> line_5483_22 -> switch_622_22 -> line_5372_22 -> switch_518_22 -> line_4865_22 -> fuse_80_22 -> line_4867_22 | GSO_121¦line_4867_22 | ACLineSegment | 600 | 15000 | Meter | br_01_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 7.0977 | [6 empty] | SubstationCapacityUnresolved | line_4867_22 | Substation capacity unresolved |  | 116
504 | 42 | GSO_121 | line_5478_22 | S_nCCTT358 | 7.0977 | High | 7.2 | 7.1083 | 0.010601 | 7.0977 | 0.38162 | 14.25 | 13.8684 | line_5478_22 | ACLineSegment | Line | 7.1083 | 0.010601 | 7.0977 | 37 | 22 | 0 | 100 | 40.6667 | 0.46323 | -79.9689 | 36.0874 | recloser_151_22 -> line_3530_22 -> line_3529_22 -> line_5665_22 -> line_6422_22 -> line_6474_22 -> line_6249_22 -> switch_752_22 -> line_6250_22 -> switch_695_22 -> line_5901_22 -> switch_489_22 -> line_4707_22 -> line_4513_22 -> line_4512_22 -> switch_471_22 -> line_4639_22 -> switch_643_22 -> line_5483_22 -> switch_622_22 -> line_5372_22 -> switch_518_22 -> line_4865_22 -> switch_520_22 -> line_4866_22 -> switch_430_22 -> line_4473_22 -> switch_432_22 -> line_4474_22 -> switch_455_22 -> line_4573_22 -> line_4572_22 -> switch_454_22 -> line_5479_22 -> switch_642_22 -> switch_639_22 -> line_5478_22 | GSO_121¦line_5478_22 | ACLineSegment | 600 | 15000 | Meter | br_01_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 7.0977 | [6 empty] | SubstationCapacityUnresolved | line_5478_22 | Substation capacity unresolved |  | 116
507 | 43 | GSO_121 | line_5634_22 | S_nCCTT46_B_S_nCCTT356 | 6.997 | High | 7.2 | 7.1083 | 0.11131 | 6.997 | 0.38162 | 14.25 | 13.8684 | line_5634_22 | ACLineSegment | Line | 7.1083 | 0.11131 | 6.997 | 13 | 11 | 0 | 100 | 40.6667 | 0.46323 | -79.9898 | 36.0865 | recloser_151_22 -> line_3530_22 -> line_3529_22 -> line_5665_22 -> recloser_193_22 -> line_6234_22 -> line_6235_22 -> line_5800_22 -> line_5618_22 -> line_5619_22 -> line_6085_22 -> line_5872_22 -> line_5634_22 | GSO_121¦line_5634_22 | ACLineSegment | 600 | 15000 | Meter | br_01_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 6.997 | [6 empty] | SubstationCapacityUnresolved | line_5634_22 | Substation capacity unresolved |  | 116
508 | 44 | GSO_121 | line_5635_22 | S_nCCTT817 | 6.997 | High | 7.2 | 7.1083 | 0.10071 | 7.0076 | 0.38162 | 14.25 | 13.8684 | line_5634_22 | ACLineSegment | Line | 7.1083 | 0.11131 | 6.997 | 16 | 12 | 0 | 100 | 40.6667 | 0.46323 | -79.9908 | 36.0862 | recloser_151_22 -> line_3530_22 -> line_3529_22 -> line_5665_22 -> recloser_193_22 -> line_6234_22 -> line_6235_22 -> line_5800_22 -> line_5618_22 -> line_5619_22 -> line_6085_22 -> line_5872_22 -> line_5634_22 -> switch_656_22 -> switch_657_22 -> line_5635_22 | GSO_121¦line_5635_22 | ACLineSegment | 600 | 15000 | Meter | br_01_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 6.997 | [6 empty] | SubstationCapacityUnresolved | line_5634_22 | Substation capacity unresolved |  | 116
509 | 45 | GSO_121 | line_4701_22 | S_nCCTT1394 | 6.997 | High | 7.2 | 7.1083 | 0.015901 | 7.0924 | 0.38162 | 14.25 | 13.8684 | line_5634_22 | ACLineSegment | Line | 7.1083 | 0.11131 | 6.997 | 18 | 13 | 0 | 100 | 40.6667 | 0.46323 | -79.9922 | 36.0868 | recloser_151_22 -> line_3530_22 -> line_3529_22 -> line_5665_22 -> recloser_193_22 -> line_6234_22 -> line_6235_22 -> line_5800_22 -> line_5618_22 -> line_5619_22 -> line_6085_22 -> line_5872_22 -> line_5634_22 -> switch_656_22 -> switch_657_22 -> line_5635_22 -> switch_487_22 -> line_4701_22 | GSO_121¦line_4701_22 | ACLineSegment | 600 | 15000 | Meter | br_01_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 6.997 | [6 empty] | SubstationCapacityUnresolved | line_5634_22 | Substation capacity unresolved |  | 116
510 | 46 | GSO_121 | line_4838_22 | S_nCCTT1446 | 6.997 | High | 7.2 | 7.1083 | 0.079505 | 7.0288 | 0.38162 | 14.25 | 13.8684 | line_5634_22 | ACLineSegment | Line | 7.1083 | 0.11131 | 6.997 | 18 | 13 | 0 | 100 | 40.6667 | 0.46323 | -79.9924 | 36.0862 | recloser_151_22 -> line_3530_22 -> line_3529_22 -> line_5665_22 -> recloser_193_22 -> line_6234_22 -> line_6235_22 -> line_5800_22 -> line_5618_22 -> line_5619_22 -> line_6085_22 -> line_5872_22 -> line_5634_22 -> switch_656_22 -> switch_657_22 -> line_5635_22 -> switch_510_22 -> line_4838_22 | GSO_121¦line_4838_22 | ACLineSegment | 600 | 15000 | Meter | br_01_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 6.997 | [6 empty] | SubstationCapacityUnresolved | line_5634_22 | Substation capacity unresolved |  | 116
511 | 47 | GSO_121 | line_4700_22 | S_nCCTT36 | 6.997 | High | 7.2 | 7.1083 | 0.010601 | 7.0977 | 0.38162 | 14.25 | 13.8684 | line_5634_22 | ACLineSegment | Line | 7.1083 | 0.11131 | 6.997 | 20 | 14 | 0 | 100 | 40.6667 | 0.46323 | -79.9928 | 36.0878 | recloser_151_22 -> line_3530_22 -> line_3529_22 -> line_5665_22 -> recloser_193_22 -> line_6234_22 -> line_6235_22 -> line_5800_22 -> line_5618_22 -> line_5619_22 -> line_6085_22 -> line_5872_22 -> line_5634_22 -> switch_656_22 -> switch_657_22 -> line_5635_22 -> switch_487_22 -> line_4701_22 -> switch_485_22 -> line_4700_22 | GSO_121¦line_4700_22 | ACLineSegment | 600 | 15000 | Meter | br_01_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 6.997 | [6 empty] | SubstationCapacityUnresolved | line_5634_22 | Substation capacity unresolved |  | 116
512 | 48 | GSO_121 | line_4836_22 | S_nCCTT32 | 6.997 | High | 7.2 | 7.1083 | 0.058304 | 7.05 | 0.38162 | 14.25 | 13.8684 | line_5634_22 | ACLineSegment | Line | 7.1083 | 0.11131 | 6.997 | 20 | 14 | 0 | 100 | 40.6667 | 0.46323 | -79.9932 | 36.0855 | recloser_151_22 -> line_3530_22 -> line_3529_22 -> line_5665_22 -> recloser_193_22 -> line_6234_22 -> line_6235_22 -> line_5800_22 -> line_5618_22 -> line_5619_22 -> line_6085_22 -> line_5872_22 -> line_5634_22 -> switch_656_22 -> switch_657_22 -> line_5635_22 -> switch_510_22 -> line_4838_22 -> switch_506_22 -> line_4836_22 | GSO_121¦line_4836_22 | ACLineSegment | 600 | 15000 | Meter | br_01_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 6.997 | [6 empty] | SubstationCapacityUnresolved | line_5634_22 | Substation capacity unresolved |  | 116
513 | 49 | GSO_121 | line_4837_22 | S_nCCTT38 | 6.997 | High | 7.2 | 7.1083 | 0.015901 | 7.0924 | 0.38162 | 14.25 | 13.8684 | line_5634_22 | ACLineSegment | Line | 7.1083 | 0.11131 | 6.997 | 20 | 14 | 0 | 100 | 40.6667 | 0.46323 | -79.9939 | 36.0863 | recloser_151_22 -> line_3530_22 -> line_3529_22 -> line_5665_22 -> recloser_193_22 -> line_6234_22 -> line_6235_22 -> line_5800_22 -> line_5618_22 -> line_5619_22 -> line_6085_22 -> line_5872_22 -> line_5634_22 -> switch_656_22 -> switch_657_22 -> line_5635_22 -> switch_510_22 -> line_4838_22 -> switch_508_22 -> line_4837_22 | GSO_121¦line_4837_22 | ACLineSegment | 600 | 15000 | Meter | br_01_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 6.997 | [6 empty] | SubstationCapacityUnresolved | line_5634_22 | Substation capacity unresolved |  | 116
514 | 50 | GSO_121 | line_5553_22 | S_nCCTT32_B_S_nCCTT51 | 6.997 | High | 7.2 | 7.1083 | 0.053003 | 7.0553 | 0.38162 | 14.25 | 13.8684 | line_5634_22 | ACLineSegment | Line | 7.1083 | 0.11131 | 6.997 | 21 | 15 | 0 | 100 | 40.6667 | 0.46323 | -79.992 | 36.0842 | recloser_151_22 -> line_3530_22 -> line_3529_22 -> line_5665_22 -> recloser_193_22 -> line_6234_22 -> line_6235_22 -> line_5800_22 -> line_5618_22 -> line_5619_22 -> line_6085_22 -> line_5872_22 -> line_5634_22 -> switch_656_22 -> switch_657_22 -> line_5635_22 -> switch_510_22 -> line_4838_22 -> switch_506_22 -> line_4836_22 -> line_5553_22 | GSO_121¦line_5553_22 | ACLineSegment | 600 | 15000 | Meter | br_01_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 6.997 | [6 empty] | SubstationCapacityUnresolved | line_5634_22 | Substation capacity unresolved |  | 116
515 | 51 | GSO_121 | line_5690_22 | S_nCCTT39 | 6.997 | High | 7.2 | 7.1083 | 0.010601 | 7.0977 | 0.38162 | 14.25 | 13.8684 | line_5634_22 | ACLineSegment | Line | 7.1083 | 0.11131 | 6.997 | 22 | 15 | 0 | 100 | 40.6667 | 0.46323 | -79.9948 | 36.0874 | recloser_151_22 -> line_3530_22 -> line_3529_22 -> line_5665_22 -> recloser_193_22 -> line_6234_22 -> line_6235_22 -> line_5800_22 -> line_5618_22 -> line_5619_22 -> line_6085_22 -> line_5872_22 -> line_5634_22 -> switch_656_22 -> switch_657_22 -> line_5635_22 -> switch_510_22 -> line_4838_22 -> switch_508_22 -> line_4837_22 -> switch_672_22 -> line_5690_22 | GSO_121¦line_5690_22 | ACLineSegment | 600 | 15000 | Meter | br_01_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 6.997 | [6 empty] | SubstationCapacityUnresolved | line_5634_22 | Substation capacity unresolved |  | 116
516 | 52 | GSO_121 | line_4618_22 | S_nCCTT1363 | 6.997 | High | 7.2 | 7.1083 | 0.031802 | 7.0765 | 0.38162 | 14.25 | 13.8684 | line_5634_22 | ACLineSegment | Line | 7.1083 | 0.11131 | 6.997 | 24 | 16 | 0 | 100 | 40.6667 | 0.46323 | -79.991 | 36.084 | recloser_151_22 -> line_3530_22 -> line_3529_22 -> line_5665_22 -> recloser_193_22 -> line_6234_22 -> line_6235_22 -> line_5800_22 -> line_5618_22 -> line_5619_22 -> line_6085_22 -> line_5872_22 -> line_5634_22 -> switch_656_22 -> switch_657_22 -> line_5635_22 -> switch_510_22 -> line_4838_22 -> switch_506_22 -> line_4836_22 -> line_5553_22 -> switch_650_22 -> switch_465_22 -> line_4618_22 | GSO_121¦line_4618_22 | ACLineSegment | 600 | 15000 | Meter | br_01_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 6.997 | [6 empty] | SubstationCapacityUnresolved | line_5634_22 | Substation capacity unresolved |  | 116
517 | 53 | GSO_121 | line_4619_22 | S_nCCTT528 | 6.997 | High | 7.2 | 7.1083 | 0.021201 | 7.0871 | 0.38162 | 14.25 | 13.8684 | line_5634_22 | ACLineSegment | Line | 7.1083 | 0.11131 | 6.997 | 26 | 17 | 0 | 100 | 40.6667 | 0.46323 | -79.9901 | 36.0834 | recloser_151_22 -> line_3530_22 -> line_3529_22 -> line_5665_22 -> recloser_193_22 -> line_6234_22 -> line_6235_22 -> line_5800_22 -> line_5618_22 -> line_5619_22 -> line_6085_22 -> line_5872_22 -> line_5634_22 -> switch_656_22 -> switch_657_22 -> line_5635_22 -> switch_510_22 -> line_4838_22 -> switch_506_22 -> line_4836_22 -> line_5553_22 -> switch_650_22 -> switch_465_22 -> line_4618_22 -> switch_467_22 -> line_4619_22 | GSO_121¦line_4619_22 | ACLineSegment | 600 | 15000 | Meter | br_01_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 6.997 | [6 empty] | SubstationCapacityUnresolved | line_5634_22 | Substation capacity unresolved |  | 116
549 | 54 | GSO_121 | line_6086_22 | S_nCCTT859 | 2.8327 | High | 7.2 | 2.8433 | 0.010601 | 2.8327 | 0.38162 | 14.25 | 13.8684 | line_6086_22 | ACLineSegment | Line | 2.8433 | 0.010601 | 2.8327 | 12 | 9 | 0 | 100 | 40.6667 | 0.46323 | -79.9853 | 36.0851 | recloser_151_22 -> line_3530_22 -> line_3529_22 -> line_5665_22 -> recloser_193_22 -> line_6234_22 -> line_6235_22 -> line_5800_22 -> line_5618_22 -> line_5619_22 -> fuse_143_22 -> line_6086_22 | GSO_121¦line_6086_22 | ACLineSegment | 240 | 15000 | Meter | br_01_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.8327 | [6 empty] | SubstationCapacityUnresolved | line_6086_22 | Substation capacity unresolved |  | 116
1 | 1 | GSO_122 | line_5852_22 | S_nCCTT45 | 13.5096 | High | 12.47 | 13.5424 | 0.03276 | 13.5096 | 0.03276 | 14.25 | 14.2172 | line_5852_22 | ACLineSegment | Line | 13.5424 | 0.03276 | 13.5096 | 2 | 1 | 0 | 100 | 5.1667 | 0.058853 | -79.9736 | 36.0826 | recloser_186_22 -> line_5852_22 | GSO_122¦line_5852_22 | ACLineSegment | 660 | 15000 | Meter | br_02_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.5096 | [6 empty] | SubstationCapacityUnresolved | line_5852_22 | Substation capacity unresolved |  | 116
2 | 2 | GSO_122 | line_5376_22 | S_nCCTT222 | 13.5096 | High | 12.47 | 13.5424 | 0.02184 | 13.5205 | 0.03276 | 14.25 | 14.2172 | line_5852_22 | ACLineSegment | Line | 13.5424 | 0.03276 | 13.5096 | 3 | 2 | 0 | 100 | 5.1667 | 0.058853 | -79.9739 | 36.0812 | recloser_186_22 -> line_5852_22 -> line_5376_22 | GSO_122¦line_5376_22 | ACLineSegment | 660 | 15000 | Meter | br_02_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.5096 | [6 empty] | SubstationCapacityUnresolved | line_5852_22 | Substation capacity unresolved |  | 116
3 | 3 | GSO_122 | line_5377_22 | UCMV107 | 13.5096 | High | 12.47 | 13.5424 | 0.01092 | 13.5314 | 0.03276 | 14.25 | 14.2172 | line_5852_22 | ACLineSegment | Line | 13.5424 | 0.03276 | 13.5096 | 4 | 3 | 0 | 100 | 5.1667 | 0.058853 | -79.9742 | 36.0806 | recloser_186_22 -> line_5852_22 -> line_5376_22 -> line_5377_22 | GSO_122¦line_5377_22 | ACLineSegment | 660 | 15000 | Meter | br_02_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.5096 | [6 empty] | SubstationCapacityUnresolved | line_5852_22 | Substation capacity unresolved |  | 116
16 | 1 | GSO_123 | line_6019_22 | S_nCCTT521 | 13.1777 | High | 12.47 | 13.5424 | 0.36464 | 13.1777 | 0.36464 | 14.25 | 13.8854 | line_6019_22 | ACLineSegment | Line | 13.5424 | 0.36464 | 13.1777 | 2 | 1 | 0 | 100 | 10.25 | 0.11676 | -79.9741 | 36.0862 | recloser_189_22 -> line_6019_22 | GSO_123¦line_6019_22 | ACLineSegment | 660 | 15000 | Meter | br_03_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved |  | 116
17 | 2 | GSO_123 | line_3606_22 | S_nCCTT1023 | 13.1777 | High | 12.47 | 13.5424 | 0.34913 | 13.1932 | 0.36464 | 14.25 | 13.8854 | line_6019_22 | ACLineSegment | Line | 13.5424 | 0.36464 | 13.1777 | 3 | 2 | 0 | 100 | 10.25 | 0.11676 | -79.9759 | 36.0894 | recloser_189_22 -> line_6019_22 -> line_3606_22 | GSO_123¦line_3606_22 | ACLineSegment | 660 | 15000 | Meter | br_03_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved |  | 116
18 | 3 | GSO_123 | line_4780_22 | S_nCCTT1424 | 13.1777 | High | 12.47 | 13.5424 | 0.0077584 | 13.5346 | 0.36464 | 14.25 | 13.8854 | line_6019_22 | ACLineSegment | Line | 13.5424 | 0.36464 | 13.1777 | 3 | 2 | 0 | 100 | 10.25 | 0.11676 | -79.9755 | 36.0893 | recloser_189_22 -> line_6019_22 -> line_4780_22 | GSO_123¦line_4780_22 | ACLineSegment | 660 | 15000 | Meter | br_03_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved |  | 116
19 | 4 | GSO_123 | line_3605_22 | S_nCCTT450 | 13.1777 | High | 12.47 | 13.5424 | 0.34137 | 13.201 | 0.36464 | 14.25 | 13.8854 | line_6019_22 | ACLineSegment | Line | 13.5424 | 0.36464 | 13.1777 | 4 | 3 | 0 | 100 | 10.25 | 0.11676 | -79.9767 | 36.0895 | recloser_189_22 -> line_6019_22 -> line_3606_22 -> line_3605_22 | GSO_123¦line_3605_22 | ACLineSegment | 660 | 15000 | Meter | br_03_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved |  | 116
20 | 5 | GSO_123 | line_5721_22 | S_nCCTT393 | 13.1777 | High | 12.47 | 13.5424 | 0.33361 | 13.2088 | 0.36464 | 14.25 | 13.8854 | line_6019_22 | ACLineSegment | Line | 13.5424 | 0.36464 | 13.1777 | 5 | 4 | 0 | 100 | 10.25 | 0.11676 | -79.9774 | 36.0896 | recloser_189_22 -> line_6019_22 -> line_3606_22 -> line_3605_22 -> line_5721_22 | GSO_123¦line_5721_22 | ACLineSegment | 660 | 15000 | Meter | br_03_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved |  | 116
21 | 6 | GSO_123 | line_4425_22 | S_nCCTT1298 | 13.1777 | High | 12.47 | 13.5424 | 0.0077584 | 13.5346 | 0.36464 | 14.25 | 13.8854 | line_6019_22 | ACLineSegment | Line | 13.5424 | 0.36464 | 13.1777 | 6 | 5 | 0 | 100 | 10.25 | 0.11676 | -79.9776 | 36.0897 | recloser_189_22 -> line_6019_22 -> line_3606_22 -> line_3605_22 -> line_5721_22 -> line_4425_22 | GSO_123¦line_4425_22 | ACLineSegment | 660 | 15000 | Meter | br_03_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved |  | 116
22 | 7 | GSO_123 | line_4627_22 | S_nCCTT1367 | 13.1777 | High | 12.47 | 13.5424 | 0.31809 | 13.2243 | 0.36464 | 14.25 | 13.8854 | line_6019_22 | ACLineSegment | Line | 13.5424 | 0.36464 | 13.1777 | 6 | 5 | 0 | 100 | 10.25 | 0.11676 | -79.9782 | 36.0898 | recloser_189_22 -> line_6019_22 -> line_3606_22 -> line_3605_22 -> line_5721_22 -> line_4627_22 | GSO_123¦line_4627_22 | ACLineSegment | 660 | 15000 | Meter | br_03_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved |  | 116
23 | 8 | GSO_123 | line_4628_22 | S_nCCTT516 | 13.1777 | High | 12.47 | 13.5424 | 0.31034 | 13.232 | 0.36464 | 14.25 | 13.8854 | line_6019_22 | ACLineSegment | Line | 13.5424 | 0.36464 | 13.1777 | 7 | 6 | 0 | 100 | 10.25 | 0.11676 | -79.9788 | 36.0899 | recloser_189_22 -> line_6019_22 -> line_3606_22 -> line_3605_22 -> line_5721_22 -> line_4627_22 -> line_4628_22 | GSO_123¦line_4628_22 | ACLineSegment | 660 | 15000 | Meter | br_03_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved |  | 116
24 | 9 | GSO_123 | line_5588_22 | S_nCCTT338 | 13.1777 | High | 12.47 | 13.5424 | 0.30258 | 13.2398 | 0.36464 | 14.25 | 13.8854 | line_6019_22 | ACLineSegment | Line | 13.5424 | 0.36464 | 13.1777 | 8 | 7 | 0 | 100 | 10.25 | 0.11676 | -79.9797 | 36.09 | recloser_189_22 -> line_6019_22 -> line_3606_22 -> line_3605_22 -> line_5721_22 -> line_4627_22 -> line_4628_22 -> line_5588_22 | GSO_123¦line_5588_22 | ACLineSegment | 660 | 15000 | Meter | br_03_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved |  | 116
25 | 10 | GSO_123 | line_5587_22 | S_nCCTT477 | 13.1777 | High | 12.47 | 13.5424 | 0.29482 | 13.2475 | 0.36464 | 14.25 | 13.8854 | line_6019_22 | ACLineSegment | Line | 13.5424 | 0.36464 | 13.1777 | 9 | 8 | 0 | 100 | 10.25 | 0.11676 | -79.9802 | 36.0902 | recloser_189_22 -> line_6019_22 -> line_3606_22 -> line_3605_22 -> line_5721_22 -> line_4627_22 -> line_4628_22 -> line_5588_22 -> line_5587_22 | GSO_123¦line_5587_22 | ACLineSegment | 660 | 15000 | Meter | br_03_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved |  | 116
26 | 11 | GSO_123 | line_5430_22 | S_nCCTT247 | 13.1777 | High | 12.47 | 13.5424 | 0.28706 | 13.2553 | 0.36464 | 14.25 | 13.8854 | line_6019_22 | ACLineSegment | Line | 13.5424 | 0.36464 | 13.1777 | 10 | 9 | 0 | 100 | 10.25 | 0.11676 | -79.9802 | 36.0919 | recloser_189_22 -> line_6019_22 -> line_3606_22 -> line_3605_22 -> line_5721_22 -> line_4627_22 -> line_4628_22 -> line_5588_22 -> line_5587_22 -> line_5430_22 | GSO_123¦line_5430_22 | ACLineSegment | 660 | 15000 | Meter | br_03_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved |  | 116
27 | 12 | GSO_123 | line_3954_22 | S_nCCTT1135 | 13.1777 | High | 12.47 | 13.5424 | 0.2793 | 13.2631 | 0.36464 | 14.25 | 13.8854 | line_6019_22 | ACLineSegment | Line | 13.5424 | 0.36464 | 13.1777 | 11 | 10 | 0 | 100 | 10.25 | 0.11676 | -79.9798 | 36.0933 | recloser_189_22 -> line_6019_22 -> line_3606_22 -> line_3605_22 -> line_5721_22 -> line_4627_22 -> line_4628_22 -> line_5588_22 -> line_5587_22 -> line_5430_22 -> line_3954_22 | GSO_123¦line_3954_22 | ACLineSegment | 660 | 15000 | Meter | br_03_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved |  | 116
28 | 13 | GSO_123 | line_3953_22 | S_nCCTT1162 | 13.1777 | High | 12.47 | 13.5424 | 0.27154 | 13.2708 | 0.36464 | 14.25 | 13.8854 | line_6019_22 | ACLineSegment | Line | 13.5424 | 0.36464 | 13.1777 | 12 | 11 | 0 | 100 | 10.25 | 0.11676 | -79.9794 | 36.0938 | recloser_189_22 -> line_6019_22 -> line_3606_22 -> line_3605_22 -> line_5721_22 -> line_4627_22 -> line_4628_22 -> line_5588_22 -> line_5587_22 -> line_5430_22 -> line_3954_22 -> line_3953_22 | GSO_123¦line_3953_22 | ACLineSegment | 660 | 15000 | Meter | br_03_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved |  | 116
29 | 14 | GSO_123 | line_4022_22 | S_nCCTT1285 | 13.1777 | High | 12.47 | 13.5424 | 0.26379 | 13.2786 | 0.36464 | 14.25 | 13.8854 | line_6019_22 | ACLineSegment | Line | 13.5424 | 0.36464 | 13.1777 | 13 | 12 | 0 | 100 | 10.25 | 0.11676 | -79.9786 | 36.0934 | recloser_189_22 -> line_6019_22 -> line_3606_22 -> line_3605_22 -> line_5721_22 -> line_4627_22 -> line_4628_22 -> line_5588_22 -> line_5587_22 -> line_5430_22 -> line_3954_22 -> line_3953_22 -> line_4022_22 | GSO_123¦line_4022_22 | ACLineSegment | 660 | 15000 | Meter | br_03_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved |  | 116
30 | 15 | GSO_123 | line_4389_22 | S_nCCTT759 | 13.1777 | High | 12.47 | 13.5424 | 0.25603 | 13.2863 | 0.36464 | 14.25 | 13.8854 | line_6019_22 | ACLineSegment | Line | 13.5424 | 0.36464 | 13.1777 | 14 | 13 | 0 | 100 | 10.25 | 0.11676 | -79.9777 | 36.0929 | recloser_189_22 -> line_6019_22 -> line_3606_22 -> line_3605_22 -> line_5721_22 -> line_4627_22 -> line_4628_22 -> line_5588_22 -> line_5587_22 -> line_5430_22 -> line_3954_22 -> line_3953_22 -> line_4022_22 -> line_4389_22 | GSO_123¦line_4389_22 | ACLineSegment | 660 | 15000 | Meter | br_03_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved |  | 116
31 | 16 | GSO_123 | line_4507_22 | S_nCCTT1325 | 13.1777 | High | 12.47 | 13.5424 | 0.21723 | 13.3251 | 0.36464 | 14.25 | 13.8854 | line_6019_22 | ACLineSegment | Line | 13.5424 | 0.36464 | 13.1777 | 15 | 14 | 0 | 100 | 10.25 | 0.11676 | -79.9775 | 36.093 | recloser_189_22 -> line_6019_22 -> line_3606_22 -> line_3605_22 -> line_5721_22 -> line_4627_22 -> line_4628_22 -> line_5588_22 -> line_5587_22 -> line_5430_22 -> line_3954_22 -> line_3953_22 -> line_4022_22 -> line_4389_22 -> line_4507_22 | GSO_123¦line_4507_22 | ACLineSegment | 660 | 15000 | Meter | br_03_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved |  | 116
32 | 17 | GSO_123 | line_5492_22 | S_nCCTT287 | 13.1777 | High | 12.47 | 13.5424 | 0.031034 | 13.5113 | 0.36464 | 14.25 | 13.8854 | line_6019_22 | ACLineSegment | Line | 13.5424 | 0.36464 | 13.1777 | 15 | 14 | 0 | 100 | 10.25 | 0.11676 | -79.9773 | 36.0927 | recloser_189_22 -> line_6019_22 -> line_3606_22 -> line_3605_22 -> line_5721_22 -> line_4627_22 -> line_4628_22 -> line_5588_22 -> line_5587_22 -> line_5430_22 -> line_3954_22 -> line_3953_22 -> line_4022_22 -> line_4389_22 -> line_5492_22 | GSO_123¦line_5492_22 | ACLineSegment | 660 | 15000 | Meter | br_03_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved |  | 116
33 | 18 | GSO_123 | line_4185_22 | S_nCCTT1223 | 13.1777 | High | 12.47 | 13.5424 | 0.20948 | 13.3329 | 0.36464 | 14.25 | 13.8854 | line_6019_22 | ACLineSegment | Line | 13.5424 | 0.36464 | 13.1777 | 16 | 15 | 0 | 100 | 10.25 | 0.11676 | -79.9773 | 36.0935 | recloser_189_22 -> line_6019_22 -> line_3606_22 -> line_3605_22 -> line_5721_22 -> line_4627_22 -> line_4628_22 -> line_5588_22 -> line_5587_22 -> line_5430_22 -> line_3954_22 -> line_3953_22 -> line_4022_22 -> line_4389_22 -> line_4507_22 -> line_4185_22 | GSO_123¦line_4185_22 | ACLineSegment | 660 | 15000 | Meter | br_03_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved |  | 116
34 | 19 | GSO_123 | line_5491_22 | S_nCCTT663 | 13.1777 | High | 12.47 | 13.5424 | 0.023275 | 13.5191 | 0.36464 | 14.25 | 13.8854 | line_6019_22 | ACLineSegment | Line | 13.5424 | 0.36464 | 13.1777 | 16 | 15 | 0 | 100 | 10.25 | 0.11676 | -79.9772 | 36.0926 | recloser_189_22 -> line_6019_22 -> line_3606_22 -> line_3605_22 -> line_5721_22 -> line_4627_22 -> line_4628_22 -> line_5588_22 -> line_5587_22 -> line_5430_22 -> line_3954_22 -> line_3953_22 -> line_4022_22 -> line_4389_22 -> line_5492_22 -> line_5491_22 | GSO_123¦line_5491_22 | ACLineSegment | 660 | 15000 | Meter | br_03_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved |  | 116
35 | 20 | GSO_123 | line_3591_22 | S_nCCTT1019 | 13.1777 | High | 12.47 | 13.5424 | 0.20172 | 13.3407 | 0.36464 | 14.25 | 13.8854 | line_6019_22 | ACLineSegment | Line | 13.5424 | 0.36464 | 13.1777 | 17 | 16 | 0 | 100 | 10.25 | 0.11676 | -79.9771 | 36.0943 | recloser_189_22 -> line_6019_22 -> line_3606_22 -> line_3605_22 -> line_5721_22 -> line_4627_22 -> line_4628_22 -> line_5588_22 -> line_5587_22 -> line_5430_22 -> line_3954_22 -> line_3953_22 -> line_4022_22 -> line_4389_22 -> line_4507_22 -> line_4185_22 -> line_3591_22 | GSO_123¦line_3591_22 | ACLineSegment | 660 | 15000 | Meter | br_03_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved |  | 116
36 | 21 | GSO_123 | line_6329_22 | S_nCCTT862 | 13.1777 | High | 12.47 | 13.5424 | 0.015517 | 13.5269 | 0.36464 | 14.25 | 13.8854 | line_6019_22 | ACLineSegment | Line | 13.5424 | 0.36464 | 13.1777 | 17 | 16 | 0 | 100 | 10.25 | 0.11676 | -79.9761 | 36.0923 | recloser_189_22 -> line_6019_22 -> line_3606_22 -> line_3605_22 -> line_5721_22 -> line_4627_22 -> line_4628_22 -> line_5588_22 -> line_5587_22 -> line_5430_22 -> line_3954_22 -> line_3953_22 -> line_4022_22 -> line_4389_22 -> line_5492_22 -> line_5491_22 -> line_6329_22 | GSO_123¦line_6329_22 | ACLineSegment | 660 | 15000 | Meter | br_03_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved |  | 116
37 | 22 | GSO_123 | line_3592_22 | UCMV44 | 13.1777 | High | 12.47 | 13.5424 | 0.19396 | 13.3484 | 0.36464 | 14.25 | 13.8854 | line_6019_22 | ACLineSegment | Line | 13.5424 | 0.36464 | 13.1777 | 18 | 17 | 0 | 100 | 10.25 | 0.11676 | -79.9769 | 36.095 | recloser_189_22 -> line_6019_22 -> line_3606_22 -> line_3605_22 -> line_5721_22 -> line_4627_22 -> line_4628_22 -> line_5588_22 -> line_5587_22 -> line_5430_22 -> line_3954_22 -> line_3953_22 -> line_4022_22 -> line_4389_22 -> line_4507_22 -> line_4185_22 -> line_3591_22 -> line_3592_22 | GSO_123¦line_3592_22 | ACLineSegment | 660 | 15000 | Meter | br_03_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved |  | 116
38 | 23 | GSO_123 | line_6642_22 | S_nCCTT990 | 13.1777 | High | 12.47 | 13.5424 | 0.0077584 | 13.5346 | 0.36464 | 14.25 | 13.8854 | line_6019_22 | ACLineSegment | Line | 13.5424 | 0.36464 | 13.1777 | 18 | 17 | 0 | 100 | 10.25 | 0.11676 | -79.9749 | 36.093 | recloser_189_22 -> line_6019_22 -> line_3606_22 -> line_3605_22 -> line_5721_22 -> line_4627_22 -> line_4628_22 -> line_5588_22 -> line_5587_22 -> line_5430_22 -> line_3954_22 -> line_3953_22 -> line_4022_22 -> line_4389_22 -> line_5492_22 -> line_5491_22 -> line_6329_22 -> line_6642_22 | GSO_123¦line_6642_22 | ACLineSegment | 660 | 15000 | Meter | br_03_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved |  | 116
39 | 24 | GSO_123 | line_6181_22 | S_nCCTT594 | 13.1777 | High | 12.47 | 13.5424 | 0.031034 | 13.5113 | 0.36464 | 14.25 | 13.8854 | line_6019_22 | ACLineSegment | Line | 13.5424 | 0.36464 | 13.1777 | 19 | 18 | 0 | 100 | 10.25 | 0.11676 | -79.9756 | 36.0954 | recloser_189_22 -> line_6019_22 -> line_3606_22 -> line_3605_22 -> line_5721_22 -> line_4627_22 -> line_4628_22 -> line_5588_22 -> line_5587_22 -> line_5430_22 -> line_3954_22 -> line_3953_22 -> line_4022_22 -> line_4389_22 -> line_4507_22 -> line_4185_22 -> line_3591_22 -> line_3592_22 -> line_6181_22 | GSO_123¦line_6181_22 | ACLineSegment | 660 | 15000 | Meter | br_03_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved |  | 116
40 | 25 | GSO_123 | line_4033_22 | S_nCCTT1166 | 13.1777 | High | 12.47 | 13.5424 | 0.15517 | 13.3872 | 0.36464 | 14.25 | 13.8854 | line_6019_22 | ACLineSegment | Line | 13.5424 | 0.36464 | 13.1777 | 20 | 18 | 0 | 100 | 10.25 | 0.11676 | -79.9769 | 36.0952 | recloser_189_22 -> line_6019_22 -> line_3606_22 -> line_3605_22 -> line_5721_22 -> line_4627_22 -> line_4628_22 -> line_5588_22 -> line_5587_22 -> line_5430_22 -> line_3954_22 -> line_3953_22 -> line_4022_22 -> line_4389_22 -> line_4507_22 -> line_4185_22 -> line_3591_22 -> line_3592_22 -> recloser_160_22 -> line_4033_22 | GSO_123¦line_4033_22 | ACLineSegment | 660 | 15000 | Meter | br_03_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved |  | 116
41 | 26 | GSO_123 | line_4142_22 | S_nCCTT1209 | 13.1777 | High | 12.47 | 13.5424 | 0.023275 | 13.5191 | 0.36464 | 14.25 | 13.8854 | line_6019_22 | ACLineSegment | Line | 13.5424 | 0.36464 | 13.1777 | 20 | 19 | 0 | 100 | 10.25 | 0.11676 | -79.9733 | 36.0956 | recloser_189_22 -> line_6019_22 -> line_3606_22 -> line_3605_22 -> line_5721_22 -> line_4627_22 -> line_4628_22 -> line_5588_22 -> line_5587_22 -> line_5430_22 -> line_3954_22 -> line_3953_22 -> line_4022_22 -> line_4389_22 -> line_4507_22 -> line_4185_22 -> line_3591_22 -> line_3592_22 -> line_6181_22 -> line_4142_22 | GSO_123¦line_4142_22 | ACLineSegment | 660 | 15000 | Meter | br_03_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved |  | 116
42 | 27 | GSO_123 | line_4032_22 | S_nCCTT908 | 13.1777 | High | 12.47 | 13.5424 | 0.14741 | 13.395 | 0.36464 | 14.25 | 13.8854 | line_6019_22 | ACLineSegment | Line | 13.5424 | 0.36464 | 13.1777 | 21 | 19 | 0 | 100 | 10.25 | 0.11676 | -79.9769 | 36.0955 | recloser_189_22 -> line_6019_22 -> line_3606_22 -> line_3605_22 -> line_5721_22 -> line_4627_22 -> line_4628_22 -> line_5588_22 -> line_5587_22 -> line_5430_22 -> line_3954_22 -> line_3953_22 -> line_4022_22 -> line_4389_22 -> line_4507_22 -> line_4185_22 -> line_3591_22 -> line_3592_22 -> recloser_160_22 -> line_4033_22 -> line_4032_22 | GSO_123¦line_4032_22 | ACLineSegment | 660 | 15000 | Meter | br_03_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved |  | 116
43 | 28 | GSO_123 | line_6691_22 | S_nCCTT894 | 13.1777 | High | 12.47 | 13.5424 | 0.13965 | 13.4027 | 0.36464 | 14.25 | 13.8854 | line_6019_22 | ACLineSegment | Line | 13.5424 | 0.36464 | 13.1777 | 22 | 20 | 0 | 100 | 10.25 | 0.11676 | -79.9769 | 36.0958 | recloser_189_22 -> line_6019_22 -> line_3606_22 -> line_3605_22 -> line_5721_22 -> line_4627_22 -> line_4628_22 -> line_5588_22 -> line_5587_22 -> line_5430_22 -> line_3954_22 -> line_3953_22 -> line_4022_22 -> line_4389_22 -> line_4507_22 -> line_4185_22 -> line_3591_22 -> line_3592_22 -> recloser_160_22 -> line_4033_22 -> line_4032_22 -> line_6691_22 | GSO_123¦line_6691_22 | ACLineSegment | 660 | 15000 | Meter | br_03_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved |  | 116
44 | 29 | GSO_123 | line_3742_22 | S_nCCTT1067 | 13.1777 | High | 12.47 | 13.5424 | 0.13189 | 13.4105 | 0.36464 | 14.25 | 13.8854 | line_6019_22 | ACLineSegment | Line | 13.5424 | 0.36464 | 13.1777 | 23 | 21 | 0 | 100 | 10.25 | 0.11676 | -79.9769 | 36.0962 | recloser_189_22 -> line_6019_22 -> line_3606_22 -> line_3605_22 -> line_5721_22 -> line_4627_22 -> line_4628_22 -> line_5588_22 -> line_5587_22 -> line_5430_22 -> line_3954_22 -> line_3953_22 -> line_4022_22 -> line_4389_22 -> line_4507_22 -> line_4185_22 -> line_3591_22 -> line_3592_22 -> recloser_160_22 -> line_4033_22 -> line_4032_22 -> line_6691_22 -> line_3742_22 | GSO_123¦line_3742_22 | ACLineSegment | 660 | 15000 | Meter | br_03_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved |  | 116
45 | 30 | GSO_123 | line_3743_22 | S_nCCTT905 | 13.1777 | High | 12.47 | 13.5424 | 0.12413 | 13.4182 | 0.36464 | 14.25 | 13.8854 | line_6019_22 | ACLineSegment | Line | 13.5424 | 0.36464 | 13.1777 | 24 | 22 | 0 | 100 | 10.25 | 0.11676 | -79.9769 | 36.0966 | recloser_189_22 -> line_6019_22 -> line_3606_22 -> line_3605_22 -> line_5721_22 -> line_4627_22 -> line_4628_22 -> line_5588_22 -> line_5587_22 -> line_5430_22 -> line_3954_22 -> line_3953_22 -> line_4022_22 -> line_4389_22 -> line_4507_22 -> line_4185_22 -> line_3591_22 -> line_3592_22 -> recloser_160_22 -> line_4033_22 -> line_4032_22 -> line_6691_22 -> line_3742_22 -> line_3743_22 | GSO_123¦line_3743_22 | ACLineSegment | 660 | 15000 | Meter | br_03_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved |  | 116
46 | 31 | GSO_123 | line_6670_22 | S_nCCTT883 | 13.1777 | High | 12.47 | 13.5424 | 0.11638 | 13.426 | 0.36464 | 14.25 | 13.8854 | line_6019_22 | ACLineSegment | Line | 13.5424 | 0.36464 | 13.1777 | 25 | 23 | 0 | 100 | 10.25 | 0.11676 | -79.9769 | 36.0971 | recloser_189_22 -> line_6019_22 -> line_3606_22 -> line_3605_22 -> line_5721_22 -> line_4627_22 -> line_4628_22 -> line_5588_22 -> line_5587_22 -> line_5430_22 -> line_3954_22 -> line_3953_22 -> line_4022_22 -> line_4389_22 -> line_4507_22 -> line_4185_22 -> line_3591_22 -> line_3592_22 -> recloser_160_22 -> line_4033_22 -> line_4032_22 -> line_6691_22 -> line_3742_22 -> line_3743_22 -> line_6670_22 | GSO_123¦line_6670_22 | ACLineSegment | 660 | 15000 | Meter | br_03_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved |  | 116
47 | 32 | GSO_123 | line_3745_22 | S_nCCTT1068 | 13.1777 | High | 12.47 | 13.5424 | 0.0077584 | 13.5346 | 0.36464 | 14.25 | 13.8854 | line_6019_22 | ACLineSegment | Line | 13.5424 | 0.36464 | 13.1777 | 26 | 24 | 0 | 100 | 10.25 | 0.11676 | -79.9769 | 36.0975 | recloser_189_22 -> line_6019_22 -> line_3606_22 -> line_3605_22 -> line_5721_22 -> line_4627_22 -> line_4628_22 -> line_5588_22 -> line_5587_22 -> line_5430_22 -> line_3954_22 -> line_3953_22 -> line_4022_22 -> line_4389_22 -> line_4507_22 -> line_4185_22 -> line_3591_22 -> line_3592_22 -> recloser_160_22 -> line_4033_22 -> line_4032_22 -> line_6691_22 -> line_3742_22 -> line_3743_22 -> line_6670_22 -> line_3745_22 | GSO_123¦line_3745_22 | ACLineSegment | 660 | 15000 | Meter | br_03_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved |  | 116
48 | 33 | GSO_123 | line_6357_22 | S_nCCTT679 | 13.1777 | High | 12.47 | 13.5424 | 0.10086 | 13.4415 | 0.36464 | 14.25 | 13.8854 | line_6019_22 | ACLineSegment | Line | 13.5424 | 0.36464 | 13.1777 | 26 | 24 | 0 | 100 | 10.25 | 0.11676 | -79.9769 | 36.0979 | recloser_189_22 -> line_6019_22 -> line_3606_22 -> line_3605_22 -> line_5721_22 -> line_4627_22 -> line_4628_22 -> line_5588_22 -> line_5587_22 -> line_5430_22 -> line_3954_22 -> line_3953_22 -> line_4022_22 -> line_4389_22 -> line_4507_22 -> line_4185_22 -> line_3591_22 -> line_3592_22 -> recloser_160_22 -> line_4033_22 -> line_4032_22 -> line_6691_22 -> line_3742_22 -> line_3743_22 -> line_6670_22 -> line_6357_22 | GSO_123¦line_6357_22 | ACLineSegment | 660 | 15000 | Meter | br_03_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved |  | 116
49 | 34 | GSO_123 | line_5692_22 | S_nCCTT381 | 13.1777 | High | 12.47 | 13.5424 | 0.015517 | 13.5269 | 0.36464 | 14.25 | 13.8854 | line_6019_22 | ACLineSegment | Line | 13.5424 | 0.36464 | 13.1777 | 27 | 25 | 0 | 100 | 10.25 | 0.11676 | -79.9763 | 36.0992 | recloser_189_22 -> line_6019_22 -> line_3606_22 -> line_3605_22 -> line_5721_22 -> line_4627_22 -> line_4628_22 -> line_5588_22 -> line_5587_22 -> line_5430_22 -> line_3954_22 -> line_3953_22 -> line_4022_22 -> line_4389_22 -> line_4507_22 -> line_4185_22 -> line_3591_22 -> line_3592_22 -> recloser_160_22 -> line_4033_22 -> line_4032_22 -> line_6691_22 -> line_3742_22 -> line_3743_22 -> line_6670_22 -> line_6357_22 -> line_5692_22 | GSO_123¦line_5692_22 | ACLineSegment | 660 | 15000 | Meter | br_03_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved |  | 116
50 | 35 | GSO_123 | line_5844_22 | S_nCCTT447 | 13.1777 | High | 12.47 | 13.5424 | 0.077584 | 13.4648 | 0.36464 | 14.25 | 13.8854 | line_6019_22 | ACLineSegment | Line | 13.5424 | 0.36464 | 13.1777 | 27 | 25 | 0 | 100 | 10.25 | 0.11676 | -79.9769 | 36.0993 | recloser_189_22 -> line_6019_22 -> line_3606_22 -> line_3605_22 -> line_5721_22 -> line_4627_22 -> line_4628_22 -> line_5588_22 -> line_5587_22 -> line_5430_22 -> line_3954_22 -> line_3953_22 -> line_4022_22 -> line_4389_22 -> line_4507_22 -> line_4185_22 -> line_3591_22 -> line_3592_22 -> recloser_160_22 -> line_4033_22 -> line_4032_22 -> line_6691_22 -> line_3742_22 -> line_3743_22 -> line_6670_22 -> line_6357_22 -> line_5844_22 | GSO_123¦line_5844_22 | ACLineSegment | 660 | 15000 | Meter | br_03_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved |  | 116
51 | 36 | GSO_123 | line_3731_22 | S_nCCTT1063 | 13.1777 | High | 12.47 | 13.5424 | 0.0077584 | 13.5346 | 0.36464 | 14.25 | 13.8854 | line_6019_22 | ACLineSegment | Line | 13.5424 | 0.36464 | 13.1777 | 28 | 26 | 0 | 100 | 10.25 | 0.11676 | -79.976 | 36.1001 | recloser_189_22 -> line_6019_22 -> line_3606_22 -> line_3605_22 -> line_5721_22 -> line_4627_22 -> line_4628_22 -> line_5588_22 -> line_5587_22 -> line_5430_22 -> line_3954_22 -> line_3953_22 -> line_4022_22 -> line_4389_22 -> line_4507_22 -> line_4185_22 -> line_3591_22 -> line_3592_22 -> recloser_160_22 -> line_4033_22 -> line_4032_22 -> line_6691_22 -> line_3742_22 -> line_3743_22 -> line_6670_22 -> line_6357_22 -> line_5692_22 -> line_3731_22 | GSO_123¦line_3731_22 | ACLineSegment | 660 | 15000 | Meter | br_03_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved |  | 116
52 | 37 | GSO_123 | line_5843_22 | S_nCCTT549 | 13.1777 | High | 12.47 | 13.5424 | 0.062067 | 13.4803 | 0.36464 | 14.25 | 13.8854 | line_6019_22 | ACLineSegment | Line | 13.5424 | 0.36464 | 13.1777 | 28 | 26 | 0 | 100 | 10.25 | 0.11676 | -79.9781 | 36.1002 | recloser_189_22 -> line_6019_22 -> line_3606_22 -> line_3605_22 -> line_5721_22 -> line_4627_22 -> line_4628_22 -> line_5588_22 -> line_5587_22 -> line_5430_22 -> line_3954_22 -> line_3953_22 -> line_4022_22 -> line_4389_22 -> line_4507_22 -> line_4185_22 -> line_3591_22 -> line_3592_22 -> recloser_160_22 -> line_4033_22 -> line_4032_22 -> line_6691_22 -> line_3742_22 -> line_3743_22 -> line_6670_22 -> line_6357_22 -> line_5844_22 -> line_5843_22 | GSO_123¦line_5843_22 | ACLineSegment | 660 | 15000 | Meter | br_03_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved |  | 116
53 | 38 | GSO_123 | line_6075_22 | S_nCCTT924 | 13.1777 | High | 12.47 | 13.5424 | 0.054309 | 13.4881 | 0.36464 | 14.25 | 13.8854 | line_6019_22 | ACLineSegment | Line | 13.5424 | 0.36464 | 13.1777 | 29 | 27 | 0 | 100 | 10.25 | 0.11676 | -79.9787 | 36.1009 | recloser_189_22 -> line_6019_22 -> line_3606_22 -> line_3605_22 -> line_5721_22 -> line_4627_22 -> line_4628_22 -> line_5588_22 -> line_5587_22 -> line_5430_22 -> line_3954_22 -> line_3953_22 -> line_4022_22 -> line_4389_22 -> line_4507_22 -> line_4185_22 -> line_3591_22 -> line_3592_22 -> recloser_160_22 -> line_4033_22 -> line_4032_22 -> line_6691_22 -> line_3742_22 -> line_3743_22 -> line_6670_22 -> line_6357_22 -> line_5844_22 -> line_5843_22 -> line_6075_22 | GSO_123¦line_6075_22 | ACLineSegment | 660 | 15000 | Meter | br_03_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved |  | 116
54 | 39 | GSO_123 | line_5158_22 | S_nCCTT1580 | 13.1777 | High | 12.47 | 13.5424 | 0.0077584 | 13.5346 | 0.36464 | 14.25 | 13.8854 | line_6019_22 | ACLineSegment | Line | 13.5424 | 0.36464 | 13.1777 | 30 | 28 | 0 | 100 | 10.25 | 0.11676 | -79.9786 | 36.1015 | recloser_189_22 -> line_6019_22 -> line_3606_22 -> line_3605_22 -> line_5721_22 -> line_4627_22 -> line_4628_22 -> line_5588_22 -> line_5587_22 -> line_5430_22 -> line_3954_22 -> line_3953_22 -> line_4022_22 -> line_4389_22 -> line_4507_22 -> line_4185_22 -> line_3591_22 -> line_3592_22 -> recloser_160_22 -> line_4033_22 -> line_4032_22 -> line_6691_22 -> line_3742_22 -> line_3743_22 -> line_6670_22 -> line_6357_22 -> line_5844_22 -> line_5843_22 -> line_6075_22 -> line_5158_22 | GSO_123¦line_5158_22 | ACLineSegment | 660 | 15000 | Meter | br_03_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved |  | 116
55 | 40 | GSO_123 | line_6628_22 | S_nCCTT851 | 13.1777 | High | 12.47 | 13.5424 | 0.038792 | 13.5036 | 0.36464 | 14.25 | 13.8854 | line_6019_22 | ACLineSegment | Line | 13.5424 | 0.36464 | 13.1777 | 30 | 28 | 0 | 100 | 10.25 | 0.11676 | -79.9795 | 36.1007 | recloser_189_22 -> line_6019_22 -> line_3606_22 -> line_3605_22 -> line_5721_22 -> line_4627_22 -> line_4628_22 -> line_5588_22 -> line_5587_22 -> line_5430_22 -> line_3954_22 -> line_3953_22 -> line_4022_22 -> line_4389_22 -> line_4507_22 -> line_4185_22 -> line_3591_22 -> line_3592_22 -> recloser_160_22 -> line_4033_22 -> line_4032_22 -> line_6691_22 -> line_3742_22 -> line_3743_22 -> line_6670_22 -> line_6357_22 -> line_5844_22 -> line_5843_22 -> line_6075_22 -> line_6628_22 | GSO_123¦line_6628_22 | ACLineSegment | 660 | 15000 | Meter | br_03_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved |  | 116
56 | 41 | GSO_123 | line_6584_22 | S_nCCTT818 | 13.1777 | High | 12.47 | 13.5424 | 0.023275 | 13.5191 | 0.36464 | 14.25 | 13.8854 | line_6019_22 | ACLineSegment | Line | 13.5424 | 0.36464 | 13.1777 | 31 | 29 | 0 | 100 | 10.25 | 0.11676 | -79.9807 | 36.0999 | recloser_189_22 -> line_6019_22 -> line_3606_22 -> line_3605_22 -> line_5721_22 -> line_4627_22 -> line_4628_22 -> line_5588_22 -> line_5587_22 -> line_5430_22 -> line_3954_22 -> line_3953_22 -> line_4022_22 -> line_4389_22 -> line_4507_22 -> line_4185_22 -> line_3591_22 -> line_3592_22 -> recloser_160_22 -> line_4033_22 -> line_4032_22 -> line_6691_22 -> line_3742_22 -> line_3743_22 -> line_6670_22 -> line_6357_22 -> line_5844_22 -> line_5843_22 -> line_6075_22 -> line_6628_22 -> line_6584_22 | GSO_123¦line_6584_22 | ACLineSegment | 660 | 15000 | Meter | br_03_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved |  | 116
57 | 42 | GSO_123 | line_6463_22 | S_nCCTT739 | 13.1777 | High | 12.47 | 13.5424 | 0.0077584 | 13.5346 | 0.36464 | 14.25 | 13.8854 | line_6019_22 | ACLineSegment | Line | 13.5424 | 0.36464 | 13.1777 | 31 | 29 | 0 | 100 | 10.25 | 0.11676 | -79.9802 | 36.0993 | recloser_189_22 -> line_6019_22 -> line_3606_22 -> line_3605_22 -> line_5721_22 -> line_4627_22 -> line_4628_22 -> line_5588_22 -> line_5587_22 -> line_5430_22 -> line_3954_22 -> line_3953_22 -> line_4022_22 -> line_4389_22 -> line_4507_22 -> line_4185_22 -> line_3591_22 -> line_3592_22 -> recloser_160_22 -> line_4033_22 -> line_4032_22 -> line_6691_22 -> line_3742_22 -> line_3743_22 -> line_6670_22 -> line_6357_22 -> line_5844_22 -> line_5843_22 -> line_6075_22 -> line_6628_22 -> line_6463_22 | GSO_123¦line_6463_22 | ACLineSegment | 660 | 15000 | Meter | br_03_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved |  | 116
58 | 43 | GSO_123 | line_4047_22 | S_nCCTT1172 | 13.1777 | High | 12.47 | 13.5424 | 0.0077584 | 13.5346 | 0.36464 | 14.25 | 13.8854 | line_6019_22 | ACLineSegment | Line | 13.5424 | 0.36464 | 13.1777 | 32 | 30 | 0 | 100 | 10.25 | 0.11676 | -79.9813 | 36.1004 | recloser_189_22 -> line_6019_22 -> line_3606_22 -> line_3605_22 -> line_5721_22 -> line_4627_22 -> line_4628_22 -> line_5588_22 -> line_5587_22 -> line_5430_22 -> line_3954_22 -> line_3953_22 -> line_4022_22 -> line_4389_22 -> line_4507_22 -> line_4185_22 -> line_3591_22 -> line_3592_22 -> recloser_160_22 -> line_4033_22 -> line_4032_22 -> line_6691_22 -> line_3742_22 -> line_3743_22 -> line_6670_22 -> line_6357_22 -> line_5844_22 -> line_5843_22 -> line_6075_22 -> line_6628_22 -> line_6584_22 -> line_4047_22 | GSO_123¦line_4047_22 | ACLineSegment | 660 | 15000 | Meter | br_03_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved |  | 116
59 | 44 | GSO_123 | line_6585_22 | UCMV29 | 13.1777 | High | 12.47 | 13.5424 | 0.0077584 | 13.5346 | 0.36464 | 14.25 | 13.8854 | line_6019_22 | ACLineSegment | Line | 13.5424 | 0.36464 | 13.1777 | 32 | 30 | 0 | 100 | 10.25 | 0.11676 | -79.9812 | 36.101 | recloser_189_22 -> line_6019_22 -> line_3606_22 -> line_3605_22 -> line_5721_22 -> line_4627_22 -> line_4628_22 -> line_5588_22 -> line_5587_22 -> line_5430_22 -> line_3954_22 -> line_3953_22 -> line_4022_22 -> line_4389_22 -> line_4507_22 -> line_4185_22 -> line_3591_22 -> line_3592_22 -> recloser_160_22 -> line_4033_22 -> line_4032_22 -> line_6691_22 -> line_3742_22 -> line_3743_22 -> line_6670_22 -> line_6357_22 -> line_5844_22 -> line_5843_22 -> line_6075_22 -> line_6628_22 -> line_6584_22 -> line_6585_22 | GSO_123¦line_6585_22 | ACLineSegment | 660 | 15000 | Meter | br_03_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved |  | 116
84 | 45 | GSO_123 | line_4141_22 | S_nCCTT1209_B_S_nCCTT1221 | 12.2957 | High | 12.47 | 12.3112 | 0.015517 | 12.2957 | 0.36464 | 14.25 | 13.8854 | line_4141_22 | ACLineSegment | Line | 12.3112 | 0.015517 | 12.2957 | 21 | 20 | 0 | 100 | 10.25 | 0.11676 | -79.9718 | 36.0958 | recloser_189_22 -> line_6019_22 -> line_3606_22 -> line_3605_22 -> line_5721_22 -> line_4627_22 -> line_4628_22 -> line_5588_22 -> line_5587_22 -> line_5430_22 -> line_3954_22 -> line_3953_22 -> line_4022_22 -> line_4389_22 -> line_4507_22 -> line_4185_22 -> line_3591_22 -> line_3592_22 -> line_6181_22 -> line_4142_22 -> line_4141_22 | GSO_123¦line_4141_22 | ACLineSegment | 600 | 15000 | Meter | br_03_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 12.2957 | [6 empty] | SubstationCapacityUnresolved | line_4141_22 | Substation capacity unresolved |  | 116
85 | 46 | GSO_123 | line_3878_22 | S_nCCTT1107 | 12.2957 | High | 12.47 | 13.5424 | 0.0077584 | 13.5346 | 0.36464 | 14.25 | 13.8854 | line_4141_22 | ACLineSegment | Line | 12.3112 | 0.015517 | 12.2957 | 23 | 21 | 0 | 100 | 10.25 | 0.11676 | -79.973 | 36.0974 | recloser_189_22 -> line_6019_22 -> line_3606_22 -> line_3605_22 -> line_5721_22 -> line_4627_22 -> line_4628_22 -> line_5588_22 -> line_5587_22 -> line_5430_22 -> line_3954_22 -> line_3953_22 -> line_4022_22 -> line_4389_22 -> line_4507_22 -> line_4185_22 -> line_3591_22 -> line_3592_22 -> line_6181_22 -> line_4142_22 -> line_4141_22 -> switch_343_22 -> line_3878_22 | GSO_123¦line_3878_22 | ACLineSegment | 660 | 15000 | Meter | br_03_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 12.2957 | [6 empty] | SubstationCapacityUnresolved | line_4141_22 | Substation capacity unresolved |  | 116
4 | 1 | GSO_124 | line_6716_22 | S_nCCTT913 | 13.4085 | High | 12.47 | 13.5424 | 0.13387 | 13.4085 | 0.13387 | 14.25 | 14.1161 | line_6716_22 | ACLineSegment | Line | 13.5424 | 0.13387 | 13.4085 | 2 | 1 | 0 | 100 | 2.75 | 0.031325 | -79.9769 | 36.0885 | recloser_198_22 -> line_6716_22 | GSO_124¦line_6716_22 | ACLineSegment | 660 | 15000 | Meter | br_04_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.4085 | [6 empty] | SubstationCapacityUnresolved | line_6716_22 | Substation capacity unresolved |  | 116
5 | 2 | GSO_124 | line_3831_22 | S_nCCTT1093 | 13.4085 | High | 12.47 | 13.5424 | 0.12551 | 13.4169 | 0.13387 | 14.25 | 14.1161 | line_6716_22 | ACLineSegment | Line | 13.5424 | 0.13387 | 13.4085 | 3 | 2 | 0 | 100 | 2.75 | 0.031325 | -79.9857 | 36.0945 | recloser_198_22 -> line_6716_22 -> line_3831_22 | GSO_124¦line_3831_22 | ACLineSegment | 660 | 15000 | Meter | br_04_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.4085 | [6 empty] | SubstationCapacityUnresolved | line_6716_22 | Substation capacity unresolved |  | 116
6 | 3 | GSO_124 | line_3830_22 | S_nCCTT804 | 13.4085 | High | 12.47 | 13.5424 | 0.066936 | 13.4754 | 0.13387 | 14.25 | 14.1161 | line_6716_22 | ACLineSegment | Line | 13.5424 | 0.13387 | 13.4085 | 4 | 3 | 0 | 100 | 2.75 | 0.031325 | -79.9866 | 36.0942 | recloser_198_22 -> line_6716_22 -> line_3831_22 -> line_3830_22 | GSO_124¦line_3830_22 | ACLineSegment | 660 | 15000 | Meter | br_04_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.4085 | [6 empty] | SubstationCapacityUnresolved | line_6716_22 | Substation capacity unresolved |  | 116
7 | 4 | GSO_124 | line_3829_22 | S_nCCTT1204 | 13.4085 | High | 12.47 | 13.5424 | 0.050202 | 13.4922 | 0.13387 | 14.25 | 14.1161 | line_6716_22 | ACLineSegment | Line | 13.5424 | 0.13387 | 13.4085 | 4 | 3 | 0 | 100 | 2.75 | 0.031325 | -79.9855 | 36.0942 | recloser_198_22 -> line_6716_22 -> line_3831_22 -> line_3829_22 | GSO_124¦line_3829_22 | ACLineSegment | 660 | 15000 | Meter | br_04_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.4085 | [6 empty] | SubstationCapacityUnresolved | line_6716_22 | Substation capacity unresolved |  | 116
8 | 5 | GSO_124 | line_3767_22 | S_nCCTT1075 | 13.4085 | High | 12.47 | 13.5424 | 0.050202 | 13.4922 | 0.13387 | 14.25 | 14.1161 | line_6716_22 | ACLineSegment | Line | 13.5424 | 0.13387 | 13.4085 | 5 | 4 | 0 | 100 | 2.75 | 0.031325 | -79.9875 | 36.0942 | recloser_198_22 -> line_6716_22 -> line_3831_22 -> line_3830_22 -> line_3767_22 | GSO_124¦line_3767_22 | ACLineSegment | 660 | 15000 | Meter | br_04_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.4085 | [6 empty] | SubstationCapacityUnresolved | line_6716_22 | Substation capacity unresolved |  | 116
9 | 6 | GSO_124 | line_4130_22 | UCMV3 | 13.4085 | High | 12.47 | 13.5424 | 0.041835 | 13.5005 | 0.13387 | 14.25 | 14.1161 | line_6716_22 | ACLineSegment | Line | 13.5424 | 0.13387 | 13.4085 | 5 | 4 | 0 | 100 | 2.75 | 0.031325 | -79.9842 | 36.094 | recloser_198_22 -> line_6716_22 -> line_3831_22 -> line_3829_22 -> line_4130_22 | GSO_124¦line_4130_22 | ACLineSegment | 660 | 15000 | Meter | br_04_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.4085 | [6 empty] | SubstationCapacityUnresolved | line_6716_22 | Substation capacity unresolved |  | 116
10 | 7 | GSO_124 | line_3766_22 | S_nCCTT597 | 13.4085 | High | 12.47 | 13.5424 | 0.041835 | 13.5005 | 0.13387 | 14.25 | 14.1161 | line_6716_22 | ACLineSegment | Line | 13.5424 | 0.13387 | 13.4085 | 6 | 5 | 0 | 100 | 2.75 | 0.031325 | -79.9879 | 36.0937 | recloser_198_22 -> line_6716_22 -> line_3831_22 -> line_3830_22 -> line_3767_22 -> line_3766_22 | GSO_124¦line_3766_22 | ACLineSegment | 660 | 15000 | Meter | br_04_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.4085 | [6 empty] | SubstationCapacityUnresolved | line_6716_22 | Substation capacity unresolved |  | 116
11 | 8 | GSO_124 | line_3773_22 | S_nCCTT1077 | 13.4085 | High | 12.47 | 13.5424 | 0.016734 | 13.5256 | 0.13387 | 14.25 | 14.1161 | line_6716_22 | ACLineSegment | Line | 13.5424 | 0.13387 | 13.4085 | 6 | 5 | 0 | 100 | 2.75 | 0.031325 | -79.9832 | 36.094 | recloser_198_22 -> line_6716_22 -> line_3831_22 -> line_3829_22 -> line_4130_22 -> line_3773_22 | GSO_124¦line_3773_22 | ACLineSegment | 660 | 15000 | Meter | br_04_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.4085 | [6 empty] | SubstationCapacityUnresolved | line_6716_22 | Substation capacity unresolved |  | 116
12 | 9 | GSO_124 | line_5663_22 | S_nCCTT37 | 13.4085 | High | 12.47 | 13.5424 | 0.016734 | 13.5256 | 0.13387 | 14.25 | 14.1161 | line_6716_22 | ACLineSegment | Line | 13.5424 | 0.13387 | 13.4085 | 6 | 5 | 0 | 100 | 2.75 | 0.031325 | -79.9834 | 36.0931 | recloser_198_22 -> line_6716_22 -> line_3831_22 -> line_3829_22 -> line_4130_22 -> line_5663_22 | GSO_124¦line_5663_22 | ACLineSegment | 660 | 15000 | Meter | br_04_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.4085 | [6 empty] | SubstationCapacityUnresolved | line_6716_22 | Substation capacity unresolved |  | 116
13 | 10 | GSO_124 | line_5515_22 | S_nCCTT303 | 13.4085 | High | 12.47 | 13.5424 | 0.033468 | 13.5089 | 0.13387 | 14.25 | 14.1161 | line_6716_22 | ACLineSegment | Line | 13.5424 | 0.13387 | 13.4085 | 7 | 6 | 0 | 100 | 2.75 | 0.031325 | -79.9876 | 36.0927 | recloser_198_22 -> line_6716_22 -> line_3831_22 -> line_3830_22 -> line_3767_22 -> line_3766_22 -> line_5515_22 | GSO_124¦line_5515_22 | ACLineSegment | 660 | 15000 | Meter | br_04_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.4085 | [6 empty] | SubstationCapacityUnresolved | line_6716_22 | Substation capacity unresolved |  | 116
14 | 11 | GSO_124 | line_3772_22 | S_nCCTT904 | 13.4085 | High | 12.47 | 13.5424 | 0.008367 | 13.534 | 0.13387 | 14.25 | 14.1161 | line_6716_22 | ACLineSegment | Line | 13.5424 | 0.13387 | 13.4085 | 7 | 6 | 0 | 100 | 2.75 | 0.031325 | -79.9824 | 36.0945 | recloser_198_22 -> line_6716_22 -> line_3831_22 -> line_3829_22 -> line_4130_22 -> line_3773_22 -> line_3772_22 | GSO_124¦line_3772_22 | ACLineSegment | 660 | 15000 | Meter | br_04_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.4085 | [6 empty] | SubstationCapacityUnresolved | line_6716_22 | Substation capacity unresolved |  | 116
15 | 12 | GSO_124 | line_5664_22 | UCMV4 | 13.4085 | High | 12.47 | 13.5424 | 0.008367 | 13.534 | 0.13387 | 14.25 | 14.1161 | line_6716_22 | ACLineSegment | Line | 13.5424 | 0.13387 | 13.4085 | 7 | 6 | 0 | 100 | 2.75 | 0.031325 | -79.9843 | 36.0926 | recloser_198_22 -> line_6716_22 -> line_3831_22 -> line_3829_22 -> line_4130_22 -> line_5663_22 -> line_5664_22 | GSO_124¦line_5664_22 | ACLineSegment | 660 | 15000 | Meter | br_04_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 13.4085 | [6 empty] | SubstationCapacityUnresolved | line_6716_22 | Substation capacity unresolved |  | 116
81 | 13 | GSO_124 | line_5514_22 | S_nCCTT303_B_S_nCCTT572 | 12.3029 | High | 12.47 | 12.3112 | 0.008367 | 12.3029 | 0.13387 | 14.25 | 14.1161 | line_5514_22 | ACLineSegment | Line | 12.3112 | 0.008367 | 12.3029 | 8 | 7 | 0 | 100 | 2.75 | 0.031325 | -79.9884 | 36.0922 | recloser_198_22 -> line_6716_22 -> line_3831_22 -> line_3830_22 -> line_3767_22 -> line_3766_22 -> line_5515_22 -> line_5514_22 | GSO_124¦line_5514_22 | ACLineSegment | 600 | 15000 | Meter | br_04_22 | hvmv_1_22 | 15000.0 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 12.3029 | [6 empty] | SubstationCapacityUnresolved | line_5514_22 | Substation capacity unresolved |  | 116
452 | 1 | GSO_125 | line_3656_22 | S_nCCTT1038 | 9.1759 | High | 12.47 | 13.5424 | 0.3241 | 13.2183 | 0.3241 | 9.5 | 9.1759 | br_05_22 | CircuitBreaker | Breaker | 9.5 | 0.3241 | 9.1759 | 2 | 1 | 0 | 100 | 13.25 | 0.15093 | -79.9236 | 36.0975 | recloser_153_22 -> line_3656_22 | GSO_125¦line_3656_22 | ACLineSegment | 660 | 10000 | Meter | br_05_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved |  | 101
453 | 2 | GSO_125 | line_3654_22 | S_nCCTT1208 | 9.1759 | High | 12.47 | 13.5424 | 0.30319 | 13.2392 | 0.3241 | 9.5 | 9.1759 | br_05_22 | CircuitBreaker | Breaker | 9.5 | 0.3241 | 9.1759 | 3 | 2 | 0 | 100 | 13.25 | 0.15093 | -79.9224 | 36.0985 | recloser_153_22 -> line_3656_22 -> line_3654_22 | GSO_125¦line_3654_22 | ACLineSegment | 660 | 10000 | Meter | br_05_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved |  | 101
454 | 3 | GSO_125 | line_3655_22 | S_nCCTT810 | 9.1759 | High | 12.47 | 13.5424 | 0.015682 | 13.5267 | 0.3241 | 9.5 | 9.1759 | br_05_22 | CircuitBreaker | Breaker | 9.5 | 0.3241 | 9.1759 | 3 | 2 | 0 | 100 | 13.25 | 0.15093 | -79.9248 | 36.0986 | recloser_153_22 -> line_3656_22 -> line_3655_22 | GSO_125¦line_3655_22 | ACLineSegment | 660 | 10000 | Meter | br_05_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved |  | 101
455 | 4 | GSO_125 | line_6571_22 | S_nCCTT810_B_UCMV48 | 9.1759 | High | 12.47 | 12.3112 | 0.0052274 | 12.306 | 0.3241 | 9.5 | 9.1759 | br_05_22 | CircuitBreaker | Breaker | 9.5 | 0.3241 | 9.1759 | 4 | 3 | 0 | 100 | 13.25 | 0.15093 | -79.9251 | 36.1002 | recloser_153_22 -> line_3656_22 -> line_3655_22 -> line_6571_22 | GSO_125¦line_6571_22 | ACLineSegment | 600 | 10000 | Meter | br_05_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved |  | 101
456 | 5 | GSO_125 | line_4139_22 | S_nCCTT9 | 9.1759 | High | 12.47 | 12.3112 | 0.29796 | 12.0133 | 0.3241 | 9.5 | 9.1759 | br_05_22 | CircuitBreaker | Breaker | 9.5 | 0.3241 | 9.1759 | 5 | 3 | 0 | 100 | 13.25 | 0.15093 | -79.9222 | 36.1004 | recloser_153_22 -> line_3656_22 -> line_3654_22 -> switch_340_22 -> line_4139_22 | GSO_125¦line_4139_22 | ACLineSegment | 600 | 10000 | Meter | br_05_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved |  | 101
457 | 6 | GSO_125 | line_6701_22 | S_nCCTT9_B_UCMV66 | 9.1759 | High | 12.47 | 12.3112 | 0.29273 | 12.0185 | 0.3241 | 9.5 | 9.1759 | br_05_22 | CircuitBreaker | Breaker | 9.5 | 0.3241 | 9.1759 | 6 | 4 | 0 | 100 | 13.25 | 0.15093 | -79.9227 | 36.1018 | recloser_153_22 -> line_3656_22 -> line_3654_22 -> switch_340_22 -> line_4139_22 -> line_6701_22 | GSO_125¦line_6701_22 | ACLineSegment | 600 | 10000 | Meter | br_05_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved |  | 101
458 | 7 | GSO_125 | line_5656_22 | S_nCCTT365 | 9.1759 | High | 12.47 | 12.3112 | 0.2875 | 12.0237 | 0.3241 | 9.5 | 9.1759 | br_05_22 | CircuitBreaker | Breaker | 9.5 | 0.3241 | 9.1759 | 9 | 5 | 0 | 100 | 13.25 | 0.15093 | -79.9207 | 36.104 | recloser_153_22 -> line_3656_22 -> line_3654_22 -> switch_340_22 -> line_4139_22 -> line_6701_22 -> switch_784_22 -> switch_661_22 -> line_5656_22 | GSO_125¦line_5656_22 | ACLineSegment | 600 | 10000 | Meter | br_05_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved |  | 101
459 | 8 | GSO_125 | line_5655_22 | S_nCCTT365_B_S_nCCTT800 | 9.1759 | High | 12.47 | 12.3112 | 0.27182 | 12.0394 | 0.3241 | 9.5 | 9.1759 | br_05_22 | CircuitBreaker | Breaker | 9.5 | 0.3241 | 9.1759 | 10 | 6 | 0 | 100 | 13.25 | 0.15093 | -79.9181 | 36.1082 | recloser_153_22 -> line_3656_22 -> line_3654_22 -> switch_340_22 -> line_4139_22 -> line_6701_22 -> switch_784_22 -> switch_661_22 -> line_5656_22 -> line_5655_22 | GSO_125¦line_5655_22 | ACLineSegment | 600 | 10000 | Meter | br_05_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved |  | 101
460 | 9 | GSO_125 | line_4056_22 | S_nCCTT1176 | 9.1759 | High | 12.47 | 12.3112 | 0.010455 | 12.3008 | 0.3241 | 9.5 | 9.1759 | br_05_22 | CircuitBreaker | Breaker | 9.5 | 0.3241 | 9.1759 | 11 | 6 | 0 | 100 | 13.25 | 0.15093 | -79.9184 | 36.104 | recloser_153_22 -> line_3656_22 -> line_3654_22 -> switch_340_22 -> line_4139_22 -> line_6701_22 -> switch_784_22 -> switch_661_22 -> line_5656_22 -> switch_315_22 -> line_4056_22 | GSO_125¦line_4056_22 | ACLineSegment | 600 | 10000 | Meter | br_05_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved |  | 101
461 | 10 | GSO_125 | line_3995_22 | S_nCCTT1152 | 9.1759 | High | 12.47 | 13.5424 | 0.26137 | 13.281 | 0.3241 | 9.5 | 9.1759 | br_05_22 | CircuitBreaker | Breaker | 9.5 | 0.3241 | 9.1759 | 13 | 7 | 0 | 100 | 13.25 | 0.15093 | -79.9186 | 36.1122 | recloser_153_22 -> line_3656_22 -> line_3654_22 -> switch_340_22 -> line_4139_22 -> line_6701_22 -> switch_784_22 -> switch_661_22 -> line_5656_22 -> line_5655_22 -> switch_660_22 -> recloser_158_22 -> line_3995_22 | GSO_125¦line_3995_22 | ACLineSegment | 660 | 10000 | Meter | br_05_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved |  | 101
462 | 11 | GSO_125 | line_4027_22 | S_nCCTT1164 | 9.1759 | High | 12.47 | 12.3112 | 0.0052274 | 12.306 | 0.3241 | 9.5 | 9.1759 | br_05_22 | CircuitBreaker | Breaker | 9.5 | 0.3241 | 9.1759 | 13 | 7 | 0 | 100 | 13.25 | 0.15093 | -79.9165 | 36.102 | recloser_153_22 -> line_3656_22 -> line_3654_22 -> switch_340_22 -> line_4139_22 -> line_6701_22 -> switch_784_22 -> switch_661_22 -> line_5656_22 -> switch_315_22 -> line_4056_22 -> switch_302_22 -> line_4027_22 | GSO_125¦line_4027_22 | ACLineSegment | 600 | 10000 | Meter | br_05_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved |  | 101
463 | 12 | GSO_125 | line_3996_22 | UCMV23 | 9.1759 | High | 12.47 | 13.5424 | 0.25614 | 13.2862 | 0.3241 | 9.5 | 9.1759 | br_05_22 | CircuitBreaker | Breaker | 9.5 | 0.3241 | 9.1759 | 14 | 8 | 0 | 100 | 13.25 | 0.15093 | -79.9198 | 36.116 | recloser_153_22 -> line_3656_22 -> line_3654_22 -> switch_340_22 -> line_4139_22 -> line_6701_22 -> switch_784_22 -> switch_661_22 -> line_5656_22 -> line_5655_22 -> switch_660_22 -> recloser_158_22 -> line_3995_22 -> line_3996_22 | GSO_125¦line_3996_22 | ACLineSegment | 660 | 10000 | Meter | br_05_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved |  | 101
464 | 13 | GSO_125 | line_3787_22 | S_nCCTT1081 | 9.1759 | High | 12.47 | 13.5424 | 0.07841 | 13.464 | 0.3241 | 9.5 | 9.1759 | br_05_22 | CircuitBreaker | Breaker | 9.5 | 0.3241 | 9.1759 | 15 | 9 | 0 | 100 | 13.25 | 0.15093 | -79.9228 | 36.1174 | recloser_153_22 -> line_3656_22 -> line_3654_22 -> switch_340_22 -> line_4139_22 -> line_6701_22 -> switch_784_22 -> switch_661_22 -> line_5656_22 -> line_5655_22 -> switch_660_22 -> recloser_158_22 -> line_3995_22 -> line_3996_22 -> line_3787_22 | GSO_125¦line_3787_22 | ACLineSegment | 660 | 10000 | Meter | br_05_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved |  | 101
465 | 14 | GSO_125 | line_3786_22 | S_nCCTT1187 | 9.1759 | High | 12.47 | 13.5424 | 0.073183 | 13.4692 | 0.3241 | 9.5 | 9.1759 | br_05_22 | CircuitBreaker | Breaker | 9.5 | 0.3241 | 9.1759 | 16 | 10 | 0 | 100 | 13.25 | 0.15093 | -79.9259 | 36.1169 | recloser_153_22 -> line_3656_22 -> line_3654_22 -> switch_340_22 -> line_4139_22 -> line_6701_22 -> switch_784_22 -> switch_661_22 -> line_5656_22 -> line_5655_22 -> switch_660_22 -> recloser_158_22 -> line_3995_22 -> line_3996_22 -> line_3787_22 -> line_3786_22 | GSO_125¦line_3786_22 | ACLineSegment | 660 | 10000 | Meter | br_05_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved |  | 101
466 | 15 | GSO_125 | line_6150_22 | S_nCCTT583 | 9.1759 | High | 12.47 | 13.5424 | 0.1725 | 13.3699 | 0.3241 | 9.5 | 9.1759 | br_05_22 | CircuitBreaker | Breaker | 9.5 | 0.3241 | 9.1759 | 16 | 9 | 0 | 100 | 13.25 | 0.15093 | -79.9192 | 36.1187 | recloser_153_22 -> line_3656_22 -> line_3654_22 -> switch_340_22 -> line_4139_22 -> line_6701_22 -> switch_784_22 -> switch_661_22 -> line_5656_22 -> line_5655_22 -> switch_660_22 -> recloser_158_22 -> line_3995_22 -> line_3996_22 -> recloser_191_22 -> line_6150_22 | GSO_125¦line_6150_22 | ACLineSegment | 660 | 10000 | Meter | br_05_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved |  | 101
467 | 16 | GSO_125 | line_4087_22 | S_nCCTT895 | 9.1759 | High | 12.47 | 13.5424 | 0.010455 | 13.5319 | 0.3241 | 9.5 | 9.1759 | br_05_22 | CircuitBreaker | Breaker | 9.5 | 0.3241 | 9.1759 | 17 | 11 | 0 | 100 | 13.25 | 0.15093 | -79.9259 | 36.1184 | recloser_153_22 -> line_3656_22 -> line_3654_22 -> switch_340_22 -> line_4139_22 -> line_6701_22 -> switch_784_22 -> switch_661_22 -> line_5656_22 -> line_5655_22 -> switch_660_22 -> recloser_158_22 -> line_3995_22 -> line_3996_22 -> line_3787_22 -> line_3786_22 -> line_4087_22 | GSO_125¦line_4087_22 | ACLineSegment | 660 | 10000 | Meter | br_05_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved |  | 101
468 | 17 | GSO_125 | line_6149_22 | S_nCCTT907 | 9.1759 | High | 12.47 | 13.5424 | 0.16728 | 13.3751 | 0.3241 | 9.5 | 9.1759 | br_05_22 | CircuitBreaker | Breaker | 9.5 | 0.3241 | 9.1759 | 17 | 10 | 0 | 100 | 13.25 | 0.15093 | -79.9149 | 36.1207 | recloser_153_22 -> line_3656_22 -> line_3654_22 -> switch_340_22 -> line_4139_22 -> line_6701_22 -> switch_784_22 -> switch_661_22 -> line_5656_22 -> line_5655_22 -> switch_660_22 -> recloser_158_22 -> line_3995_22 -> line_3996_22 -> recloser_191_22 -> line_6150_22 -> line_6149_22 | GSO_125¦line_6149_22 | ACLineSegment | 660 | 10000 | Meter | br_05_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved |  | 101
469 | 18 | GSO_125 | line_4086_22 | S_nCCTT1207 | 9.1759 | High | 12.47 | 13.5424 | 0.057501 | 13.4849 | 0.3241 | 9.5 | 9.1759 | br_05_22 | CircuitBreaker | Breaker | 9.5 | 0.3241 | 9.1759 | 17 | 11 | 0 | 100 | 13.25 | 0.15093 | -79.9269 | 36.1171 | recloser_153_22 -> line_3656_22 -> line_3654_22 -> switch_340_22 -> line_4139_22 -> line_6701_22 -> switch_784_22 -> switch_661_22 -> line_5656_22 -> line_5655_22 -> switch_660_22 -> recloser_158_22 -> line_3995_22 -> line_3996_22 -> line_3787_22 -> line_3786_22 -> line_4086_22 | GSO_125¦line_4086_22 | ACLineSegment | 660 | 10000 | Meter | br_05_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved |  | 101
470 | 19 | GSO_125 | line_3770_22 | S_nCCTT1076 | 9.1759 | High | 12.47 | 13.5424 | 0.16205 | 13.3803 | 0.3241 | 9.5 | 9.1759 | br_05_22 | CircuitBreaker | Breaker | 9.5 | 0.3241 | 9.1759 | 18 | 11 | 0 | 100 | 13.25 | 0.15093 | -79.9108 | 36.1242 | recloser_153_22 -> line_3656_22 -> line_3654_22 -> switch_340_22 -> line_4139_22 -> line_6701_22 -> switch_784_22 -> switch_661_22 -> line_5656_22 -> line_5655_22 -> switch_660_22 -> recloser_158_22 -> line_3995_22 -> line_3996_22 -> recloser_191_22 -> line_6150_22 -> line_6149_22 -> line_3770_22 | GSO_125¦line_3770_22 | ACLineSegment | 660 | 10000 | Meter | br_05_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved |  | 101
471 | 20 | GSO_125 | line_4137_22 | S_nCCTT1564 | 9.1759 | High | 12.47 | 13.5424 | 0.052274 | 13.4901 | 0.3241 | 9.5 | 9.1759 | br_05_22 | CircuitBreaker | Breaker | 9.5 | 0.3241 | 9.1759 | 18 | 12 | 0 | 100 | 13.25 | 0.15093 | -79.9275 | 36.1169 | recloser_153_22 -> line_3656_22 -> line_3654_22 -> switch_340_22 -> line_4139_22 -> line_6701_22 -> switch_784_22 -> switch_661_22 -> line_5656_22 -> line_5655_22 -> switch_660_22 -> recloser_158_22 -> line_3995_22 -> line_3996_22 -> line_3787_22 -> line_3786_22 -> line_4086_22 -> line_4137_22 | GSO_125¦line_4137_22 | ACLineSegment | 660 | 10000 | Meter | br_05_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved |  | 101
472 | 21 | GSO_125 | line_3769_22 | S_nCCTT1195 | 9.1759 | High | 12.47 | 13.5424 | 0.15682 | 13.3855 | 0.3241 | 9.5 | 9.1759 | br_05_22 | CircuitBreaker | Breaker | 9.5 | 0.3241 | 9.1759 | 19 | 12 | 0 | 100 | 13.25 | 0.15093 | -79.9098 | 36.1251 | recloser_153_22 -> line_3656_22 -> line_3654_22 -> switch_340_22 -> line_4139_22 -> line_6701_22 -> switch_784_22 -> switch_661_22 -> line_5656_22 -> line_5655_22 -> switch_660_22 -> recloser_158_22 -> line_3995_22 -> line_3996_22 -> recloser_191_22 -> line_6150_22 -> line_6149_22 -> line_3770_22 -> line_3769_22 | GSO_125¦line_3769_22 | ACLineSegment | 660 | 10000 | Meter | br_05_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved |  | 101
473 | 22 | GSO_125 | line_5122_22 | S_nCCTT814 | 9.1759 | High | 12.47 | 13.5424 | 0.041819 | 13.5005 | 0.3241 | 9.5 | 9.1759 | br_05_22 | CircuitBreaker | Breaker | 9.5 | 0.3241 | 9.1759 | 19 | 13 | 0 | 100 | 13.25 | 0.15093 | -79.9277 | 36.1159 | recloser_153_22 -> line_3656_22 -> line_3654_22 -> switch_340_22 -> line_4139_22 -> line_6701_22 -> switch_784_22 -> switch_661_22 -> line_5656_22 -> line_5655_22 -> switch_660_22 -> recloser_158_22 -> line_3995_22 -> line_3996_22 -> line_3787_22 -> line_3786_22 -> line_4086_22 -> line_4137_22 -> line_5122_22 | GSO_125¦line_5122_22 | ACLineSegment | 660 | 10000 | Meter | br_05_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved |  | 101
474 | 23 | GSO_125 | line_6578_22 | S_nCCTT861 | 9.1759 | High | 12.47 | 13.5424 | 0.036591 | 13.5058 | 0.3241 | 9.5 | 9.1759 | br_05_22 | CircuitBreaker | Breaker | 9.5 | 0.3241 | 9.1759 | 20 | 14 | 0 | 100 | 13.25 | 0.15093 | -79.9275 | 36.1134 | recloser_153_22 -> line_3656_22 -> line_3654_22 -> switch_340_22 -> line_4139_22 -> line_6701_22 -> switch_784_22 -> switch_661_22 -> line_5656_22 -> line_5655_22 -> switch_660_22 -> recloser_158_22 -> line_3995_22 -> line_3996_22 -> line_3787_22 -> line_3786_22 -> line_4086_22 -> line_4137_22 -> line_5122_22 -> line_6578_22 | GSO_125¦line_6578_22 | ACLineSegment | 660 | 10000 | Meter | br_05_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved |  | 101
475 | 24 | GSO_125 | line_4108_22 | S_nCCTT902 | 9.1759 | High | 12.47 | 13.5424 | 0.13068 | 13.4117 | 0.3241 | 9.5 | 9.1759 | br_05_22 | CircuitBreaker | Breaker | 9.5 | 0.3241 | 9.1759 | 20 | 13 | 0 | 100 | 13.25 | 0.15093 | -79.9085 | 36.1251 | recloser_153_22 -> line_3656_22 -> line_3654_22 -> switch_340_22 -> line_4139_22 -> line_6701_22 -> switch_784_22 -> switch_661_22 -> line_5656_22 -> line_5655_22 -> switch_660_22 -> recloser_158_22 -> line_3995_22 -> line_3996_22 -> recloser_191_22 -> line_6150_22 -> line_6149_22 -> line_3770_22 -> line_3769_22 -> line_4108_22 | GSO_125¦line_4108_22 | ACLineSegment | 660 | 10000 | Meter | br_05_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved |  | 101
476 | 25 | GSO_125 | line_3842_22 | S_nCCTT1097 | 9.1759 | High | 12.47 | 13.5424 | 0.020909 | 13.5215 | 0.3241 | 9.5 | 9.1759 | br_05_22 | CircuitBreaker | Breaker | 9.5 | 0.3241 | 9.1759 | 21 | 15 | 0 | 100 | 13.25 | 0.15093 | -79.9272 | 36.1115 | recloser_153_22 -> line_3656_22 -> line_3654_22 -> switch_340_22 -> line_4139_22 -> line_6701_22 -> switch_784_22 -> switch_661_22 -> line_5656_22 -> line_5655_22 -> switch_660_22 -> recloser_158_22 -> line_3995_22 -> line_3996_22 -> line_3787_22 -> line_3786_22 -> line_4086_22 -> line_4137_22 -> line_5122_22 -> line_6578_22 -> line_3842_22 | GSO_125¦line_3842_22 | ACLineSegment | 660 | 10000 | Meter | br_05_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved |  | 101
477 | 26 | GSO_125 | line_3698_22 | S_nCCTT1052 | 9.1759 | High | 12.47 | 13.5424 | 0.12546 | 13.4169 | 0.3241 | 9.5 | 9.1759 | br_05_22 | CircuitBreaker | Breaker | 9.5 | 0.3241 | 9.1759 | 21 | 14 | 0 | 100 | 13.25 | 0.15093 | -79.9079 | 36.1254 | recloser_153_22 -> line_3656_22 -> line_3654_22 -> switch_340_22 -> line_4139_22 -> line_6701_22 -> switch_784_22 -> switch_661_22 -> line_5656_22 -> line_5655_22 -> switch_660_22 -> recloser_158_22 -> line_3995_22 -> line_3996_22 -> recloser_191_22 -> line_6150_22 -> line_6149_22 -> line_3770_22 -> line_3769_22 -> line_4108_22 -> line_3698_22 | GSO_125¦line_3698_22 | ACLineSegment | 660 | 10000 | Meter | br_05_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved |  | 101
478 | 27 | GSO_125 | line_3696_22 | S_nCCTT1150 | 9.1759 | High | 12.47 | 13.5424 | 0.10455 | 13.4378 | 0.3241 | 9.5 | 9.1759 | br_05_22 | CircuitBreaker | Breaker | 9.5 | 0.3241 | 9.1759 | 22 | 15 | 0 | 100 | 13.25 | 0.15093 | -79.9075 | 36.1255 | recloser_153_22 -> line_3656_22 -> line_3654_22 -> switch_340_22 -> line_4139_22 -> line_6701_22 -> switch_784_22 -> switch_661_22 -> line_5656_22 -> line_5655_22 -> switch_660_22 -> recloser_158_22 -> line_3995_22 -> line_3996_22 -> recloser_191_22 -> line_6150_22 -> line_6149_22 -> line_3770_22 -> line_3769_22 -> line_4108_22 -> line_3698_22 -> line_3696_22 | GSO_125¦line_3696_22 | ACLineSegment | 660 | 10000 | Meter | br_05_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved |  | 101
479 | 28 | GSO_125 | line_3697_22 | S_nCCTT886 | 9.1759 | High | 12.47 | 13.5424 | 0.010455 | 13.5319 | 0.3241 | 9.5 | 9.1759 | br_05_22 | CircuitBreaker | Breaker | 9.5 | 0.3241 | 9.1759 | 22 | 15 | 0 | 100 | 13.25 | 0.15093 | -79.9081 | 36.1258 | recloser_153_22 -> line_3656_22 -> line_3654_22 -> switch_340_22 -> line_4139_22 -> line_6701_22 -> switch_784_22 -> switch_661_22 -> line_5656_22 -> line_5655_22 -> switch_660_22 -> recloser_158_22 -> line_3995_22 -> line_3996_22 -> recloser_191_22 -> line_6150_22 -> line_6149_22 -> line_3770_22 -> line_3769_22 -> line_4108_22 -> line_3698_22 -> line_3697_22 | GSO_125¦line_3697_22 | ACLineSegment | 660 | 10000 | Meter | br_05_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved |  | 101
480 | 29 | GSO_125 | line_3843_22 | UCMV58 | 9.1759 | High | 12.47 | 13.5424 | 0.015682 | 13.5267 | 0.3241 | 9.5 | 9.1759 | br_05_22 | CircuitBreaker | Breaker | 9.5 | 0.3241 | 9.1759 | 22 | 16 | 0 | 100 | 13.25 | 0.15093 | -79.9272 | 36.1101 | recloser_153_22 -> line_3656_22 -> line_3654_22 -> switch_340_22 -> line_4139_22 -> line_6701_22 -> switch_784_22 -> switch_661_22 -> line_5656_22 -> line_5655_22 -> switch_660_22 -> recloser_158_22 -> line_3995_22 -> line_3996_22 -> line_3787_22 -> line_3786_22 -> line_4086_22 -> line_4137_22 -> line_5122_22 -> line_6578_22 -> line_3842_22 -> line_3843_22 | GSO_125¦line_3843_22 | ACLineSegment | 660 | 10000 | Meter | br_05_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved |  | 101
481 | 30 | GSO_125 | line_3681_22 | S_nCCTT1047 | 9.1759 | High | 12.47 | 13.5424 | 0.09932 | 13.443 | 0.3241 | 9.5 | 9.1759 | br_05_22 | CircuitBreaker | Breaker | 9.5 | 0.3241 | 9.1759 | 23 | 16 | 0 | 100 | 13.25 | 0.15093 | -79.9072 | 36.1252 | recloser_153_22 -> line_3656_22 -> line_3654_22 -> switch_340_22 -> line_4139_22 -> line_6701_22 -> switch_784_22 -> switch_661_22 -> line_5656_22 -> line_5655_22 -> switch_660_22 -> recloser_158_22 -> line_3995_22 -> line_3996_22 -> recloser_191_22 -> line_6150_22 -> line_6149_22 -> line_3770_22 -> line_3769_22 -> line_4108_22 -> line_3698_22 -> line_3696_22 -> line_3681_22 | GSO_125¦line_3681_22 | ACLineSegment | 660 | 10000 | Meter | br_05_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved |  | 101
482 | 31 | GSO_125 | line_3963_22 | S_nCCTT886_B_S_nCCTT1139 | 9.1759 | High | 12.47 | 12.3112 | 0.0052274 | 12.306 | 0.3241 | 9.5 | 9.1759 | br_05_22 | CircuitBreaker | Breaker | 9.5 | 0.3241 | 9.1759 | 23 | 16 | 0 | 100 | 13.25 | 0.15093 | -79.9087 | 36.1264 | recloser_153_22 -> line_3656_22 -> line_3654_22 -> switch_340_22 -> line_4139_22 -> line_6701_22 -> switch_784_22 -> switch_661_22 -> line_5656_22 -> line_5655_22 -> switch_660_22 -> recloser_158_22 -> line_3995_22 -> line_3996_22 -> recloser_191_22 -> line_6150_22 -> line_6149_22 -> line_3770_22 -> line_3769_22 -> line_4108_22 -> line_3698_22 -> line_3697_22 -> line_3963_22 | GSO_125¦line_3963_22 | ACLineSegment | 600 | 10000 | Meter | br_05_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved |  | 101
483 | 32 | GSO_125 | line_6288_22 | S_nCCTT644 | 9.1759 | High | 12.47 | 13.5424 | 0.010455 | 13.5319 | 0.3241 | 9.5 | 9.1759 | br_05_22 | CircuitBreaker | Breaker | 9.5 | 0.3241 | 9.1759 | 23 | 17 | 0 | 100 | 13.25 | 0.15093 | -79.9284 | 36.1098 | recloser_153_22 -> line_3656_22 -> line_3654_22 -> switch_340_22 -> line_4139_22 -> line_6701_22 -> switch_784_22 -> switch_661_22 -> line_5656_22 -> line_5655_22 -> switch_660_22 -> recloser_158_22 -> line_3995_22 -> line_3996_22 -> line_3787_22 -> line_3786_22 -> line_4086_22 -> line_4137_22 -> line_5122_22 -> line_6578_22 -> line_3842_22 -> line_3843_22 -> line_6288_22 | GSO_125¦line_6288_22 | ACLineSegment | 660 | 10000 | Meter | br_05_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved |  | 101
484 | 33 | GSO_125 | line_3682_22 | S_nCCTT909 | 9.1759 | High | 12.47 | 13.5424 | 0.083638 | 13.4587 | 0.3241 | 9.5 | 9.1759 | br_05_22 | CircuitBreaker | Breaker | 9.5 | 0.3241 | 9.1759 | 24 | 17 | 0 | 100 | 13.25 | 0.15093 | -79.9068 | 36.1247 | recloser_153_22 -> line_3656_22 -> line_3654_22 -> switch_340_22 -> line_4139_22 -> line_6701_22 -> switch_784_22 -> switch_661_22 -> line_5656_22 -> line_5655_22 -> switch_660_22 -> recloser_158_22 -> line_3995_22 -> line_3996_22 -> recloser_191_22 -> line_6150_22 -> line_6149_22 -> line_3770_22 -> line_3769_22 -> line_4108_22 -> line_3698_22 -> line_3696_22 -> line_3681_22 -> line_3682_22 | GSO_125¦line_3682_22 | ACLineSegment | 660 | 10000 | Meter | br_05_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved |  | 101
485 | 34 | GSO_125 | line_3967_22 | S_nCCTT1140 | 9.1759 | High | 12.47 | 13.5424 | 0.0052274 | 13.5371 | 0.3241 | 9.5 | 9.1759 | br_05_22 | CircuitBreaker | Breaker | 9.5 | 0.3241 | 9.1759 | 24 | 18 | 0 | 100 | 13.25 | 0.15093 | -79.9297 | 36.1107 | recloser_153_22 -> line_3656_22 -> line_3654_22 -> switch_340_22 -> line_4139_22 -> line_6701_22 -> switch_784_22 -> switch_661_22 -> line_5656_22 -> line_5655_22 -> switch_660_22 -> recloser_158_22 -> line_3995_22 -> line_3996_22 -> line_3787_22 -> line_3786_22 -> line_4086_22 -> line_4137_22 -> line_5122_22 -> line_6578_22 -> line_3842_22 -> line_3843_22 -> line_6288_22 -> line_3967_22 | GSO_125¦line_3967_22 | ACLineSegment | 660 | 10000 | Meter | br_05_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved |  | 101
486 | 35 | GSO_125 | line_4025_22 | S_nCCTT1163 | 9.1759 | High | 12.47 | 13.5424 | 0.010455 | 13.5319 | 0.3241 | 9.5 | 9.1759 | br_05_22 | CircuitBreaker | Breaker | 9.5 | 0.3241 | 9.1759 | 25 | 18 | 0 | 100 | 13.25 | 0.15093 | -79.9067 | 36.1245 | recloser_153_22 -> line_3656_22 -> line_3654_22 -> switch_340_22 -> line_4139_22 -> line_6701_22 -> switch_784_22 -> switch_661_22 -> line_5656_22 -> line_5655_22 -> switch_660_22 -> recloser_158_22 -> line_3995_22 -> line_3996_22 -> recloser_191_22 -> line_6150_22 -> line_6149_22 -> line_3770_22 -> line_3769_22 -> line_4108_22 -> line_3698_22 -> line_3696_22 -> line_3681_22 -> line_3682_22 -> line_4025_22 | GSO_125¦line_4025_22 | ACLineSegment | 660 | 10000 | Meter | br_05_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved |  | 101
487 | 36 | GSO_125 | line_4187_22 | S_nCCTT1224 | 9.1759 | High | 12.47 | 13.5424 | 0.067956 | 13.4744 | 0.3241 | 9.5 | 9.1759 | br_05_22 | CircuitBreaker | Breaker | 9.5 | 0.3241 | 9.1759 | 25 | 18 | 0 | 100 | 13.25 | 0.15093 | -79.9064 | 36.1243 | recloser_153_22 -> line_3656_22 -> line_3654_22 -> switch_340_22 -> line_4139_22 -> line_6701_22 -> switch_784_22 -> switch_661_22 -> line_5656_22 -> line_5655_22 -> switch_660_22 -> recloser_158_22 -> line_3995_22 -> line_3996_22 -> recloser_191_22 -> line_6150_22 -> line_6149_22 -> line_3770_22 -> line_3769_22 -> line_4108_22 -> line_3698_22 -> line_3696_22 -> line_3681_22 -> line_3682_22 -> line_4187_22 | GSO_125¦line_4187_22 | ACLineSegment | 660 | 10000 | Meter | br_05_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved |  | 101
488 | 37 | GSO_125 | line_3737_22 | S_nCCTT1065 | 9.1759 | High | 12.47 | 13.5424 | 0.015682 | 13.5267 | 0.3241 | 9.5 | 9.1759 | br_05_22 | CircuitBreaker | Breaker | 9.5 | 0.3241 | 9.1759 | 26 | 19 | 0 | 100 | 13.25 | 0.15093 | -79.9063 | 36.1238 | recloser_153_22 -> line_3656_22 -> line_3654_22 -> switch_340_22 -> line_4139_22 -> line_6701_22 -> switch_784_22 -> switch_661_22 -> line_5656_22 -> line_5655_22 -> switch_660_22 -> recloser_158_22 -> line_3995_22 -> line_3996_22 -> recloser_191_22 -> line_6150_22 -> line_6149_22 -> line_3770_22 -> line_3769_22 -> line_4108_22 -> line_3698_22 -> line_3696_22 -> line_3681_22 -> line_3682_22 -> line_4187_22 -> line_3737_22 | GSO_125¦line_3737_22 | ACLineSegment | 660 | 10000 | Meter | br_05_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved |  | 101
489 | 38 | GSO_125 | line_4188_22 | S_nCCTT926 | 9.1759 | High | 12.47 | 13.5424 | 0.047046 | 13.4953 | 0.3241 | 9.5 | 9.1759 | br_05_22 | CircuitBreaker | Breaker | 9.5 | 0.3241 | 9.1759 | 26 | 19 | 0 | 100 | 13.25 | 0.15093 | -79.9061 | 36.124 | recloser_153_22 -> line_3656_22 -> line_3654_22 -> switch_340_22 -> line_4139_22 -> line_6701_22 -> switch_784_22 -> switch_661_22 -> line_5656_22 -> line_5655_22 -> switch_660_22 -> recloser_158_22 -> line_3995_22 -> line_3996_22 -> recloser_191_22 -> line_6150_22 -> line_6149_22 -> line_3770_22 -> line_3769_22 -> line_4108_22 -> line_3698_22 -> line_3696_22 -> line_3681_22 -> line_3682_22 -> line_4187_22 -> line_4188_22 | GSO_125¦line_4188_22 | ACLineSegment | 660 | 10000 | Meter | br_05_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved |  | 101
490 | 39 | GSO_125 | line_4024_22 | S_nCCTT1199 | 9.1759 | High | 12.47 | 13.5424 | 0.0052274 | 13.5371 | 0.3241 | 9.5 | 9.1759 | br_05_22 | CircuitBreaker | Breaker | 9.5 | 0.3241 | 9.1759 | 26 | 19 | 0 | 100 | 13.25 | 0.15093 | -79.9069 | 36.1243 | recloser_153_22 -> line_3656_22 -> line_3654_22 -> switch_340_22 -> line_4139_22 -> line_6701_22 -> switch_784_22 -> switch_661_22 -> line_5656_22 -> line_5655_22 -> switch_660_22 -> recloser_158_22 -> line_3995_22 -> line_3996_22 -> recloser_191_22 -> line_6150_22 -> line_6149_22 -> line_3770_22 -> line_3769_22 -> line_4108_22 -> line_3698_22 -> line_3696_22 -> line_3681_22 -> line_3682_22 -> line_4025_22 -> line_4024_22 | GSO_125¦line_4024_22 | ACLineSegment | 660 | 10000 | Meter | br_05_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved |  | 101
491 | 40 | GSO_125 | line_3736_22 | S_nCCTT1184 | 9.1759 | High | 12.47 | 13.5424 | 0.010455 | 13.5319 | 0.3241 | 9.5 | 9.1759 | br_05_22 | CircuitBreaker | Breaker | 9.5 | 0.3241 | 9.1759 | 27 | 20 | 0 | 100 | 13.25 | 0.15093 | -79.9062 | 36.1235 | recloser_153_22 -> line_3656_22 -> line_3654_22 -> switch_340_22 -> line_4139_22 -> line_6701_22 -> switch_784_22 -> switch_661_22 -> line_5656_22 -> line_5655_22 -> switch_660_22 -> recloser_158_22 -> line_3995_22 -> line_3996_22 -> recloser_191_22 -> line_6150_22 -> line_6149_22 -> line_3770_22 -> line_3769_22 -> line_4108_22 -> line_3698_22 -> line_3696_22 -> line_3681_22 -> line_3682_22 -> line_4187_22 -> line_3737_22 -> line_3736_22 | GSO_125¦line_3736_22 | ACLineSegment | 660 | 10000 | Meter | br_05_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved |  | 101
492 | 41 | GSO_125 | line_4147_22 | S_nCCTT1210 | 9.1759 | High | 12.47 | 13.5424 | 0.036591 | 13.5058 | 0.3241 | 9.5 | 9.1759 | br_05_22 | CircuitBreaker | Breaker | 9.5 | 0.3241 | 9.1759 | 27 | 20 | 0 | 100 | 13.25 | 0.15093 | -79.9059 | 36.1244 | recloser_153_22 -> line_3656_22 -> line_3654_22 -> switch_340_22 -> line_4139_22 -> line_6701_22 -> switch_784_22 -> switch_661_22 -> line_5656_22 -> line_5655_22 -> switch_660_22 -> recloser_158_22 -> line_3995_22 -> line_3996_22 -> recloser_191_22 -> line_6150_22 -> line_6149_22 -> line_3770_22 -> line_3769_22 -> line_4108_22 -> line_3698_22 -> line_3696_22 -> line_3681_22 -> line_3682_22 -> line_4187_22 -> line_4188_22 -> line_4147_22 | GSO_125¦line_4147_22 | ACLineSegment | 660 | 10000 | Meter | br_05_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved |  | 101
493 | 42 | GSO_125 | line_3978_22 | S_nCCTT1145 | 9.1759 | High | 12.47 | 13.5424 | 0.0052274 | 13.5371 | 0.3241 | 9.5 | 9.1759 | br_05_22 | CircuitBreaker | Breaker | 9.5 | 0.3241 | 9.1759 | 28 | 21 | 0 | 100 | 13.25 | 0.15093 | -79.9063 | 36.1234 | recloser_153_22 -> line_3656_22 -> line_3654_22 -> switch_340_22 -> line_4139_22 -> line_6701_22 -> switch_784_22 -> switch_661_22 -> line_5656_22 -> line_5655_22 -> switch_660_22 -> recloser_158_22 -> line_3995_22 -> line_3996_22 -> recloser_191_22 -> line_6150_22 -> line_6149_22 -> line_3770_22 -> line_3769_22 -> line_4108_22 -> line_3698_22 -> line_3696_22 -> line_3681_22 -> line_3682_22 -> line_4187_22 -> line_3737_22 -> line_3736_22 -> line_3978_22 | GSO_125¦line_3978_22 | ACLineSegment | 660 | 10000 | Meter | br_05_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved |  | 101
494 | 43 | GSO_125 | line_4097_22 | S_nCCTT1190 | 9.1759 | High | 12.47 | 13.5424 | 0.031364 | 13.511 | 0.3241 | 9.5 | 9.1759 | br_05_22 | CircuitBreaker | Breaker | 9.5 | 0.3241 | 9.1759 | 28 | 21 | 0 | 100 | 13.25 | 0.15093 | -79.9062 | 36.1249 | recloser_153_22 -> line_3656_22 -> line_3654_22 -> switch_340_22 -> line_4139_22 -> line_6701_22 -> switch_784_22 -> switch_661_22 -> line_5656_22 -> line_5655_22 -> switch_660_22 -> recloser_158_22 -> line_3995_22 -> line_3996_22 -> recloser_191_22 -> line_6150_22 -> line_6149_22 -> line_3770_22 -> line_3769_22 -> line_4108_22 -> line_3698_22 -> line_3696_22 -> line_3681_22 -> line_3682_22 -> line_4187_22 -> line_4188_22 -> line_4147_22 -> line_4097_22 | GSO_125¦line_4097_22 | ACLineSegment | 660 | 10000 | Meter | br_05_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved |  | 101
495 | 44 | GSO_125 | line_4098_22 | S_nCCTT1555 | 9.1759 | High | 12.47 | 13.5424 | 0.026137 | 13.5162 | 0.3241 | 9.5 | 9.1759 | br_05_22 | CircuitBreaker | Breaker | 9.5 | 0.3241 | 9.1759 | 29 | 22 | 0 | 100 | 13.25 | 0.15093 | -79.9062 | 36.1256 | recloser_153_22 -> line_3656_22 -> line_3654_22 -> switch_340_22 -> line_4139_22 -> line_6701_22 -> switch_784_22 -> switch_661_22 -> line_5656_22 -> line_5655_22 -> switch_660_22 -> recloser_158_22 -> line_3995_22 -> line_3996_22 -> recloser_191_22 -> line_6150_22 -> line_6149_22 -> line_3770_22 -> line_3769_22 -> line_4108_22 -> line_3698_22 -> line_3696_22 -> line_3681_22 -> line_3682_22 -> line_4187_22 -> line_4188_22 -> line_4147_22 -> line_4097_22 -> line_4098_22 | GSO_125¦line_4098_22 | ACLineSegment | 660 | 10000 | Meter | br_05_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved |  | 101
496 | 45 | GSO_125 | line_5101_22 | S_nCCTT922 | 9.1759 | High | 12.47 | 13.5424 | 0.020909 | 13.5215 | 0.3241 | 9.5 | 9.1759 | br_05_22 | CircuitBreaker | Breaker | 9.5 | 0.3241 | 9.1759 | 30 | 23 | 0 | 100 | 13.25 | 0.15093 | -79.9054 | 36.1261 | recloser_153_22 -> line_3656_22 -> line_3654_22 -> switch_340_22 -> line_4139_22 -> line_6701_22 -> switch_784_22 -> switch_661_22 -> line_5656_22 -> line_5655_22 -> switch_660_22 -> recloser_158_22 -> line_3995_22 -> line_3996_22 -> recloser_191_22 -> line_6150_22 -> line_6149_22 -> line_3770_22 -> line_3769_22 -> line_4108_22 -> line_3698_22 -> line_3696_22 -> line_3681_22 -> line_3682_22 -> line_4187_22 -> line_4188_22 -> line_4147_22 -> line_4097_22 -> line_4098_22 -> line_5101_22 | GSO_125¦line_5101_22 | ACLineSegment | 660 | 10000 | Meter | br_05_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved |  | 101
497 | 46 | GSO_125 | line_6324_22 | S_nCCTT660 | 9.1759 | High | 12.47 | 13.5424 | 0.015682 | 13.5267 | 0.3241 | 9.5 | 9.1759 | br_05_22 | CircuitBreaker | Breaker | 9.5 | 0.3241 | 9.1759 | 31 | 24 | 0 | 100 | 13.25 | 0.15093 | -79.9047 | 36.1265 | recloser_153_22 -> line_3656_22 -> line_3654_22 -> switch_340_22 -> line_4139_22 -> line_6701_22 -> switch_784_22 -> switch_661_22 -> line_5656_22 -> line_5655_22 -> switch_660_22 -> recloser_158_22 -> line_3995_22 -> line_3996_22 -> recloser_191_22 -> line_6150_22 -> line_6149_22 -> line_3770_22 -> line_3769_22 -> line_4108_22 -> line_3698_22 -> line_3696_22 -> line_3681_22 -> line_3682_22 -> line_4187_22 -> line_4188_22 -> line_4147_22 -> line_4097_22 -> line_4098_22 -> line_5101_22 -> line_6324_22 | GSO_125¦line_6324_22 | ACLineSegment | 660 | 10000 | Meter | br_05_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved |  | 101
535 | 47 | GSO_125 | line_5647_22 | S_nCCTT361 | 2.8381 | High | 7.2 | 2.8433 | 0.0052274 | 2.8381 | 0.3241 | 9.5 | 9.1759 | line_5647_22 | ACLineSegment | Line | 2.8433 | 0.0052274 | 2.8381 | 19 | 12 | 0 | 100 | 13.25 | 0.15093 | -79.9245 | 36.1206 | recloser_153_22 -> line_3656_22 -> line_3654_22 -> switch_340_22 -> line_4139_22 -> line_6701_22 -> switch_784_22 -> switch_661_22 -> line_5656_22 -> line_5655_22 -> switch_660_22 -> recloser_158_22 -> line_3995_22 -> line_3996_22 -> line_3787_22 -> line_3786_22 -> line_4087_22 -> fuse_125_22 -> line_5647_22 | GSO_125¦line_5647_22 | ACLineSegment | 240 | 10000 | Meter | br_05_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.8381 | [6 empty] | SubstationCapacityUnresolved | line_5647_22 | Substation capacity unresolved |  | 101
547 | 48 | GSO_125 | line_5915_22 | S_nCCTT478 | 2.8329 | High | 7.2 | 2.8433 | 0.010455 | 2.8329 | 0.3241 | 9.5 | 9.1759 | line_5915_22 | ACLineSegment | Line | 2.8433 | 0.010455 | 2.8329 | 22 | 15 | 0 | 100 | 13.25 | 0.15093 | -79.9278 | 36.1119 | recloser_153_22 -> line_3656_22 -> line_3654_22 -> switch_340_22 -> line_4139_22 -> line_6701_22 -> switch_784_22 -> switch_661_22 -> line_5656_22 -> line_5655_22 -> switch_660_22 -> recloser_158_22 -> line_3995_22 -> line_3996_22 -> line_3787_22 -> line_3786_22 -> line_4086_22 -> line_4137_22 -> line_5122_22 -> line_6578_22 -> fuse_137_22 -> line_5915_22 | GSO_125¦line_5915_22 | ACLineSegment | 240 | 10000 | Meter | br_05_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.8329 | [6 empty] | SubstationCapacityUnresolved | line_5915_22 | Substation capacity unresolved |  | 101
548 | 49 | GSO_125 | line_6131_22 | S_nCCTT573 | 2.8329 | High | 7.2 | 2.8433 | 0.010455 | 2.8329 | 0.3241 | 9.5 | 9.1759 | line_6131_22 | ACLineSegment | Line | 2.8433 | 0.010455 | 2.8329 | 33 | 25 | 0 | 100 | 13.25 | 0.15093 | -79.9045 | 36.1264 | recloser_153_22 -> line_3656_22 -> line_3654_22 -> switch_340_22 -> line_4139_22 -> line_6701_22 -> switch_784_22 -> switch_661_22 -> line_5656_22 -> line_5655_22 -> switch_660_22 -> recloser_158_22 -> line_3995_22 -> line_3996_22 -> recloser_191_22 -> line_6150_22 -> line_6149_22 -> line_3770_22 -> line_3769_22 -> line_4108_22 -> line_3698_22 -> line_3696_22 -> line_3681_22 -> line_3682_22 -> line_4187_22 -> line_4188_22 -> line_4147_22 -> line_4097_22 -> line_4098_22 -> line_5101_22 -> line_6324_22 -> fuse_144_22 -> line_6131_22 | GSO_125¦line_6131_22 | ACLineSegment | 240 | 10000 | Meter | br_05_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.8329 | [6 empty] | SubstationCapacityUnresolved | line_6131_22 | Substation capacity unresolved |  | 101
566 | 50 | GSO_125 | line_3761_22 | S_nCCTT1073 | 2.8224 | High | 7.2 | 2.8433 | 0.020909 | 2.8224 | 0.3241 | 9.5 | 9.1759 | line_3761_22 | ACLineSegment | Line | 2.8433 | 0.020909 | 2.8224 | 21 | 13 | 0 | 100 | 13.25 | 0.15093 | -79.9089 | 36.1249 | recloser_153_22 -> line_3656_22 -> line_3654_22 -> switch_340_22 -> line_4139_22 -> line_6701_22 -> switch_784_22 -> switch_661_22 -> line_5656_22 -> line_5655_22 -> switch_660_22 -> recloser_158_22 -> line_3995_22 -> line_3996_22 -> recloser_191_22 -> line_6150_22 -> line_6149_22 -> line_3770_22 -> line_3769_22 -> fuse_16_22 -> line_3761_22 | GSO_125¦line_3761_22 | ACLineSegment | 240 | 10000 | Meter | br_05_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.8224 | [6 empty] | SubstationCapacityUnresolved | line_3761_22 | Substation capacity unresolved |  | 101
567 | 51 | GSO_125 | line_3762_22 | S_nCCTT816 | 2.8224 | High | 7.2 | 2.8433 | 0.015682 | 2.8277 | 0.3241 | 9.5 | 9.1759 | line_3761_22 | ACLineSegment | Line | 2.8433 | 0.020909 | 2.8224 | 22 | 14 | 0 | 100 | 13.25 | 0.15093 | -79.909 | 36.1243 | recloser_153_22 -> line_3656_22 -> line_3654_22 -> switch_340_22 -> line_4139_22 -> line_6701_22 -> switch_784_22 -> switch_661_22 -> line_5656_22 -> line_5655_22 -> switch_660_22 -> recloser_158_22 -> line_3995_22 -> line_3996_22 -> recloser_191_22 -> line_6150_22 -> line_6149_22 -> line_3770_22 -> line_3769_22 -> fuse_16_22 -> line_3761_22 -> line_3762_22 | GSO_125¦line_3762_22 | ACLineSegment | 240 | 10000 | Meter | br_05_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.8224 | [6 empty] | SubstationCapacityUnresolved | line_3761_22 | Substation capacity unresolved |  | 101
568 | 52 | GSO_125 | line_6490_22 | S_nCCTT751 | 2.8224 | High | 7.2 | 2.8433 | 0.010455 | 2.8329 | 0.3241 | 9.5 | 9.1759 | line_3761_22 | ACLineSegment | Line | 2.8433 | 0.020909 | 2.8224 | 23 | 15 | 0 | 100 | 13.25 | 0.15093 | -79.9087 | 36.1235 | recloser_153_22 -> line_3656_22 -> line_3654_22 -> switch_340_22 -> line_4139_22 -> line_6701_22 -> switch_784_22 -> switch_661_22 -> line_5656_22 -> line_5655_22 -> switch_660_22 -> recloser_158_22 -> line_3995_22 -> line_3996_22 -> recloser_191_22 -> line_6150_22 -> line_6149_22 -> line_3770_22 -> line_3769_22 -> fuse_16_22 -> line_3761_22 -> line_3762_22 -> line_6490_22 | GSO_125¦line_6490_22 | ACLineSegment | 240 | 10000 | Meter | br_05_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.8224 | [6 empty] | SubstationCapacityUnresolved | line_3761_22 | Substation capacity unresolved |  | 101
569 | 53 | GSO_125 | line_6438_22 | S_nCCTT721 | 2.8224 | High | 7.2 | 2.8433 | 0.0052274 | 2.8381 | 0.3241 | 9.5 | 9.1759 | line_3761_22 | ACLineSegment | Line | 2.8433 | 0.020909 | 2.8224 | 24 | 16 | 0 | 100 | 13.25 | 0.15093 | -79.9084 | 36.1227 | recloser_153_22 -> line_3656_22 -> line_3654_22 -> switch_340_22 -> line_4139_22 -> line_6701_22 -> switch_784_22 -> switch_661_22 -> line_5656_22 -> line_5655_22 -> switch_660_22 -> recloser_158_22 -> line_3995_22 -> line_3996_22 -> recloser_191_22 -> line_6150_22 -> line_6149_22 -> line_3770_22 -> line_3769_22 -> fuse_16_22 -> line_3761_22 -> line_3762_22 -> line_6490_22 -> line_6438_22 | GSO_125¦line_6438_22 | ACLineSegment | 240 | 10000 | Meter | br_05_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.8224 | [6 empty] | SubstationCapacityUnresolved | line_3761_22 | Substation capacity unresolved |  | 101
420 | 1 | GSO_126 | line_6387_22 | S_nCCTT691 | 9.2578 | High | 12.47 | 13.5424 | 0.24218 | 13.3002 | 0.24218 | 9.5 | 9.2578 | br_06_22 | CircuitBreaker | Breaker | 9.5 | 0.24218 | 9.2578 | 2 | 1 | 0 | 100 | 17.25 | 0.19649 | -79.9277 | 36.1035 | recloser_194_22 -> line_6387_22 | GSO_126¦line_6387_22 | ACLineSegment | 660 | 10000 | Meter | br_06_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.2578 | [6 empty] | SubstationCapacityUnresolved | br_06_22 | Substation capacity unresolved |  | 101
421 | 2 | GSO_126 | line_6386_22 | S_nCCTT840 | 9.2578 | High | 12.47 | 13.5424 | 0.23564 | 13.3067 | 0.24218 | 9.5 | 9.2578 | br_06_22 | CircuitBreaker | Breaker | 9.5 | 0.24218 | 9.2578 | 3 | 2 | 0 | 100 | 17.25 | 0.19649 | -79.9319 | 36.1096 | recloser_194_22 -> line_6387_22 -> line_6386_22 | GSO_126¦line_6386_22 | ACLineSegment | 660 | 10000 | Meter | br_06_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.2578 | [6 empty] | SubstationCapacityUnresolved | br_06_22 | Substation capacity unresolved |  | 101
422 | 3 | GSO_126 | line_6613_22 | UCMV7 | 9.2578 | High | 12.47 | 13.5424 | 0.216 | 13.3264 | 0.24218 | 9.5 | 9.2578 | br_06_22 | CircuitBreaker | Breaker | 9.5 | 0.24218 | 9.2578 | 4 | 3 | 0 | 100 | 17.25 | 0.19649 | -79.9331 | 36.1078 | recloser_194_22 -> line_6387_22 -> line_6386_22 -> line_6613_22 | GSO_126¦line_6613_22 | ACLineSegment | 660 | 10000 | Meter | br_06_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.2578 | [6 empty] | SubstationCapacityUnresolved | br_06_22 | Substation capacity unresolved |  | 101
423 | 4 | GSO_126 | line_6580_22 | S_nCCTT815 | 9.2578 | High | 12.47 | 13.5424 | 0.013091 | 13.5293 | 0.24218 | 9.5 | 9.2578 | br_06_22 | CircuitBreaker | Breaker | 9.5 | 0.24218 | 9.2578 | 4 | 3 | 0 | 100 | 17.25 | 0.19649 | -79.9311 | 36.1088 | recloser_194_22 -> line_6387_22 -> line_6386_22 -> line_6580_22 | GSO_126¦line_6580_22 | ACLineSegment | 660 | 10000 | Meter | br_06_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.2578 | [6 empty] | SubstationCapacityUnresolved | br_06_22 | Substation capacity unresolved |  | 101
424 | 5 | GSO_126 | line_3859_22 | UCMV7_B_S_nCCTT1100 | 9.2578 | High | 12.47 | 12.3112 | 0.20946 | 12.1018 | 0.24218 | 9.5 | 9.2578 | br_06_22 | CircuitBreaker | Breaker | 9.5 | 0.24218 | 9.2578 | 5 | 4 | 0 | 100 | 17.25 | 0.19649 | -79.9361 | 36.1067 | recloser_194_22 -> line_6387_22 -> line_6386_22 -> line_6613_22 -> line_3859_22 | GSO_126¦line_3859_22 | ACLineSegment | 600 | 10000 | Meter | br_06_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.2578 | [6 empty] | SubstationCapacityUnresolved | br_06_22 | Substation capacity unresolved |  | 101
425 | 6 | GSO_126 | line_6337_22 | S_nCCTT668 | 9.2578 | High | 12.47 | 13.5424 | 0.0065455 | 13.5358 | 0.24218 | 9.5 | 9.2578 | br_06_22 | CircuitBreaker | Breaker | 9.5 | 0.24218 | 9.2578 | 5 | 4 | 0 | 100 | 17.25 | 0.19649 | -79.9307 | 36.1079 | recloser_194_22 -> line_6387_22 -> line_6386_22 -> line_6580_22 -> line_6337_22 | GSO_126¦line_6337_22 | ACLineSegment | 660 | 10000 | Meter | br_06_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.2578 | [6 empty] | SubstationCapacityUnresolved | br_06_22 | Substation capacity unresolved |  | 101
426 | 7 | GSO_126 | line_3858_22 | UCMV6 | 9.2578 | High | 12.47 | 13.5424 | 0.20291 | 13.3395 | 0.24218 | 9.5 | 9.2578 | br_06_22 | CircuitBreaker | Breaker | 9.5 | 0.24218 | 9.2578 | 7 | 5 | 0 | 100 | 17.25 | 0.19649 | -79.9381 | 36.1055 | recloser_194_22 -> line_6387_22 -> line_6386_22 -> line_6613_22 -> line_3859_22 -> switch_262_22 -> line_3858_22 | GSO_126¦line_3858_22 | ACLineSegment | 660 | 10000 | Meter | br_06_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.2578 | [6 empty] | SubstationCapacityUnresolved | br_06_22 | Substation capacity unresolved |  | 101
427 | 8 | GSO_126 | line_3784_22 | S_nCCTT1080 | 9.2578 | High | 12.47 | 13.5424 | 0.19637 | 13.346 | 0.24218 | 9.5 | 9.2578 | br_06_22 | CircuitBreaker | Breaker | 9.5 | 0.24218 | 9.2578 | 9 | 6 | 0 | 100 | 17.25 | 0.19649 | -79.9395 | 36.1053 | recloser_194_22 -> line_6387_22 -> line_6386_22 -> line_6613_22 -> line_3859_22 -> switch_262_22 -> line_3858_22 -> recloser_154_22 -> line_3784_22 | GSO_126¦line_3784_22 | ACLineSegment | 660 | 10000 | Meter | br_06_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.2578 | [6 empty] | SubstationCapacityUnresolved | br_06_22 | Substation capacity unresolved |  | 101
428 | 9 | GSO_126 | line_3783_22 | S_nCCTT914 | 9.2578 | High | 12.47 | 13.5424 | 0.18982 | 13.3525 | 0.24218 | 9.5 | 9.2578 | br_06_22 | CircuitBreaker | Breaker | 9.5 | 0.24218 | 9.2578 | 10 | 7 | 0 | 100 | 17.25 | 0.19649 | -79.941 | 36.106 | recloser_194_22 -> line_6387_22 -> line_6386_22 -> line_6613_22 -> line_3859_22 -> switch_262_22 -> line_3858_22 -> recloser_154_22 -> line_3784_22 -> line_3783_22 | GSO_126¦line_3783_22 | ACLineSegment | 660 | 10000 | Meter | br_06_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.2578 | [6 empty] | SubstationCapacityUnresolved | br_06_22 | Substation capacity unresolved |  | 101
429 | 10 | GSO_126 | line_5621_22 | S_nCCTT35 | 9.2578 | High | 12.47 | 13.5424 | 0.18327 | 13.3591 | 0.24218 | 9.5 | 9.2578 | br_06_22 | CircuitBreaker | Breaker | 9.5 | 0.24218 | 9.2578 | 11 | 8 | 0 | 100 | 17.25 | 0.19649 | -79.9428 | 36.1065 | recloser_194_22 -> line_6387_22 -> line_6386_22 -> line_6613_22 -> line_3859_22 -> switch_262_22 -> line_3858_22 -> recloser_154_22 -> line_3784_22 -> line_3783_22 -> line_5621_22 | GSO_126¦line_5621_22 | ACLineSegment | 660 | 10000 | Meter | br_06_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.2578 | [6 empty] | SubstationCapacityUnresolved | br_06_22 | Substation capacity unresolved |  | 101
430 | 11 | GSO_126 | line_4081_22 | S_nCCTT1185 | 9.2578 | High | 12.47 | 13.5424 | 0.17673 | 13.3656 | 0.24218 | 9.5 | 9.2578 | br_06_22 | CircuitBreaker | Breaker | 9.5 | 0.24218 | 9.2578 | 12 | 9 | 0 | 100 | 17.25 | 0.19649 | -79.9449 | 36.1055 | recloser_194_22 -> line_6387_22 -> line_6386_22 -> line_6613_22 -> line_3859_22 -> switch_262_22 -> line_3858_22 -> recloser_154_22 -> line_3784_22 -> line_3783_22 -> line_5621_22 -> line_4081_22 | GSO_126¦line_4081_22 | ACLineSegment | 660 | 10000 | Meter | br_06_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.2578 | [6 empty] | SubstationCapacityUnresolved | br_06_22 | Substation capacity unresolved |  | 101
431 | 12 | GSO_126 | line_4082_22 | S_nCCTT795 | 9.2578 | High | 12.47 | 13.5424 | 0.17018 | 13.3722 | 0.24218 | 9.5 | 9.2578 | br_06_22 | CircuitBreaker | Breaker | 9.5 | 0.24218 | 9.2578 | 13 | 10 | 0 | 100 | 17.25 | 0.19649 | -79.9464 | 36.1034 | recloser_194_22 -> line_6387_22 -> line_6386_22 -> line_6613_22 -> line_3859_22 -> switch_262_22 -> line_3858_22 -> recloser_154_22 -> line_3784_22 -> line_3783_22 -> line_5621_22 -> line_4081_22 -> line_4082_22 | GSO_126¦line_4082_22 | ACLineSegment | 660 | 10000 | Meter | br_06_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.2578 | [6 empty] | SubstationCapacityUnresolved | br_06_22 | Substation capacity unresolved |  | 101
432 | 13 | GSO_126 | line_6424_22 | S_nCCTT714 | 9.2578 | High | 12.47 | 13.5424 | 0.13746 | 13.4049 | 0.24218 | 9.5 | 9.2578 | br_06_22 | CircuitBreaker | Breaker | 9.5 | 0.24218 | 9.2578 | 14 | 11 | 0 | 100 | 17.25 | 0.19649 | -79.9453 | 36.1013 | recloser_194_22 -> line_6387_22 -> line_6386_22 -> line_6613_22 -> line_3859_22 -> switch_262_22 -> line_3858_22 -> recloser_154_22 -> line_3784_22 -> line_3783_22 -> line_5621_22 -> line_4081_22 -> line_4082_22 -> line_6424_22 | GSO_126¦line_6424_22 | ACLineSegment | 660 | 10000 | Meter | br_06_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.2578 | [6 empty] | SubstationCapacityUnresolved | br_06_22 | Substation capacity unresolved |  | 101
433 | 14 | GSO_126 | line_5819_22 | S_nCCTT438 | 9.2578 | High | 12.47 | 13.5424 | 0.026182 | 13.5162 | 0.24218 | 9.5 | 9.2578 | br_06_22 | CircuitBreaker | Breaker | 9.5 | 0.24218 | 9.2578 | 14 | 11 | 0 | 100 | 17.25 | 0.19649 | -79.9463 | 36.1012 | recloser_194_22 -> line_6387_22 -> line_6386_22 -> line_6613_22 -> line_3859_22 -> switch_262_22 -> line_3858_22 -> recloser_154_22 -> line_3784_22 -> line_3783_22 -> line_5621_22 -> line_4081_22 -> line_4082_22 -> line_5819_22 | GSO_126¦line_5819_22 | ACLineSegment | 660 | 10000 | Meter | br_06_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.2578 | [6 empty] | SubstationCapacityUnresolved | br_06_22 | Substation capacity unresolved |  | 101
434 | 15 | GSO_126 | line_5818_22 | S_nCCTT738 | 9.2578 | High | 12.47 | 13.5424 | 0.019637 | 13.5227 | 0.24218 | 9.5 | 9.2578 | br_06_22 | CircuitBreaker | Breaker | 9.5 | 0.24218 | 9.2578 | 15 | 12 | 0 | 100 | 17.25 | 0.19649 | -79.9468 | 36.1011 | recloser_194_22 -> line_6387_22 -> line_6386_22 -> line_6613_22 -> line_3859_22 -> switch_262_22 -> line_3858_22 -> recloser_154_22 -> line_3784_22 -> line_3783_22 -> line_5621_22 -> line_4081_22 -> line_4082_22 -> line_5819_22 -> line_5818_22 | GSO_126¦line_5818_22 | ACLineSegment | 660 | 10000 | Meter | br_06_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.2578 | [6 empty] | SubstationCapacityUnresolved | br_06_22 | Substation capacity unresolved |  | 101
435 | 16 | GSO_126 | line_6196_22 | S_nCCTT603 | 9.2578 | High | 12.47 | 13.5424 | 0.12436 | 13.418 | 0.24218 | 9.5 | 9.2578 | br_06_22 | CircuitBreaker | Breaker | 9.5 | 0.24218 | 9.2578 | 15 | 12 | 0 | 100 | 17.25 | 0.19649 | -79.9442 | 36.1006 | recloser_194_22 -> line_6387_22 -> line_6386_22 -> line_6613_22 -> line_3859_22 -> switch_262_22 -> line_3858_22 -> recloser_154_22 -> line_3784_22 -> line_3783_22 -> line_5621_22 -> line_4081_22 -> line_4082_22 -> line_6424_22 -> line_6196_22 | GSO_126¦line_6196_22 | ACLineSegment | 660 | 10000 | Meter | br_06_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.2578 | [6 empty] | SubstationCapacityUnresolved | br_06_22 | Substation capacity unresolved |  | 101
436 | 17 | GSO_126 | line_6013_22 | S_nCCTT519 | 9.2578 | High | 12.47 | 13.5424 | 0.11782 | 13.4245 | 0.24218 | 9.5 | 9.2578 | br_06_22 | CircuitBreaker | Breaker | 9.5 | 0.24218 | 9.2578 | 16 | 13 | 0 | 100 | 17.25 | 0.19649 | -79.9436 | 36.1 | recloser_194_22 -> line_6387_22 -> line_6386_22 -> line_6613_22 -> line_3859_22 -> switch_262_22 -> line_3858_22 -> recloser_154_22 -> line_3784_22 -> line_3783_22 -> line_5621_22 -> line_4081_22 -> line_4082_22 -> line_6424_22 -> line_6196_22 -> line_6013_22 | GSO_126¦line_6013_22 | ACLineSegment | 660 | 10000 | Meter | br_06_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.2578 | [6 empty] | SubstationCapacityUnresolved | br_06_22 | Substation capacity unresolved |  | 101
437 | 18 | GSO_126 | line_6012_22 | S_nCCTT590 | 9.2578 | High | 12.47 | 13.5424 | 0.091637 | 13.4507 | 0.24218 | 9.5 | 9.2578 | br_06_22 | CircuitBreaker | Breaker | 9.5 | 0.24218 | 9.2578 | 17 | 14 | 0 | 100 | 17.25 | 0.19649 | -79.9433 | 36.0995 | recloser_194_22 -> line_6387_22 -> line_6386_22 -> line_6613_22 -> line_3859_22 -> switch_262_22 -> line_3858_22 -> recloser_154_22 -> line_3784_22 -> line_3783_22 -> line_5621_22 -> line_4081_22 -> line_4082_22 -> line_6424_22 -> line_6196_22 -> line_6013_22 -> line_6012_22 | GSO_126¦line_6012_22 | ACLineSegment | 660 | 10000 | Meter | br_06_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.2578 | [6 empty] | SubstationCapacityUnresolved | br_06_22 | Substation capacity unresolved |  | 101
438 | 19 | GSO_126 | line_6014_22 | S_nCCTT841 | 9.2578 | High | 12.47 | 13.5424 | 0.019637 | 13.5227 | 0.24218 | 9.5 | 9.2578 | br_06_22 | CircuitBreaker | Breaker | 9.5 | 0.24218 | 9.2578 | 17 | 14 | 0 | 100 | 17.25 | 0.19649 | -79.9441 | 36.0997 | recloser_194_22 -> line_6387_22 -> line_6386_22 -> line_6613_22 -> line_3859_22 -> switch_262_22 -> line_3858_22 -> recloser_154_22 -> line_3784_22 -> line_3783_22 -> line_5621_22 -> line_4081_22 -> line_4082_22 -> line_6424_22 -> line_6196_22 -> line_6013_22 -> line_6014_22 | GSO_126¦line_6014_22 | ACLineSegment | 660 | 10000 | Meter | br_06_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.2578 | [6 empty] | SubstationCapacityUnresolved | br_06_22 | Substation capacity unresolved |  | 101
439 | 20 | GSO_126 | line_3794_22 | S_nCCTT1083 | 9.2578 | High | 12.47 | 13.5424 | 0.039273 | 13.5031 | 0.24218 | 9.5 | 9.2578 | br_06_22 | CircuitBreaker | Breaker | 9.5 | 0.24218 | 9.2578 | 18 | 15 | 0 | 100 | 17.25 | 0.19649 | -79.943 | 36.0995 | recloser_194_22 -> line_6387_22 -> line_6386_22 -> line_6613_22 -> line_3859_22 -> switch_262_22 -> line_3858_22 -> recloser_154_22 -> line_3784_22 -> line_3783_22 -> line_5621_22 -> line_4081_22 -> line_4082_22 -> line_6424_22 -> line_6196_22 -> line_6013_22 -> line_6012_22 -> line_3794_22 | GSO_126¦line_3794_22 | ACLineSegment | 660 | 10000 | Meter | br_06_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.2578 | [6 empty] | SubstationCapacityUnresolved | br_06_22 | Substation capacity unresolved |  | 101
440 | 21 | GSO_126 | line_3998_22 | S_nCCTT1153 | 9.2578 | High | 12.47 | 13.5424 | 0.0065455 | 13.5358 | 0.24218 | 9.5 | 9.2578 | br_06_22 | CircuitBreaker | Breaker | 9.5 | 0.24218 | 9.2578 | 18 | 15 | 0 | 100 | 17.25 | 0.19649 | -79.9433 | 36.099 | recloser_194_22 -> line_6387_22 -> line_6386_22 -> line_6613_22 -> line_3859_22 -> switch_262_22 -> line_3858_22 -> recloser_154_22 -> line_3784_22 -> line_3783_22 -> line_5621_22 -> line_4081_22 -> line_4082_22 -> line_6424_22 -> line_6196_22 -> line_6013_22 -> line_6012_22 -> line_3998_22 | GSO_126¦line_3998_22 | ACLineSegment | 660 | 10000 | Meter | br_06_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.2578 | [6 empty] | SubstationCapacityUnresolved | br_06_22 | Substation capacity unresolved |  | 101
441 | 22 | GSO_126 | line_6171_22 | S_nCCTT921 | 9.2578 | High | 12.47 | 13.5424 | 0.0065455 | 13.5358 | 0.24218 | 9.5 | 9.2578 | br_06_22 | CircuitBreaker | Breaker | 9.5 | 0.24218 | 9.2578 | 18 | 15 | 0 | 100 | 17.25 | 0.19649 | -79.9433 | 36.099 | recloser_194_22 -> line_6387_22 -> line_6386_22 -> line_6613_22 -> line_3859_22 -> switch_262_22 -> line_3858_22 -> recloser_154_22 -> line_3784_22 -> line_3783_22 -> line_5621_22 -> line_4081_22 -> line_4082_22 -> line_6424_22 -> line_6196_22 -> line_6013_22 -> line_6012_22 -> line_6171_22 | GSO_126¦line_6171_22 | ACLineSegment | 660 | 10000 | Meter | br_06_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.2578 | [6 empty] | SubstationCapacityUnresolved | br_06_22 | Substation capacity unresolved |  | 101
442 | 23 | GSO_126 | line_6172_22 | S_nCCTT925 | 9.2578 | High | 12.47 | 13.5424 | 0.032728 | 13.5096 | 0.24218 | 9.5 | 9.2578 | br_06_22 | CircuitBreaker | Breaker | 9.5 | 0.24218 | 9.2578 | 18 | 15 | 0 | 100 | 17.25 | 0.19649 | -79.9433 | 36.0988 | recloser_194_22 -> line_6387_22 -> line_6386_22 -> line_6613_22 -> line_3859_22 -> switch_262_22 -> line_3858_22 -> recloser_154_22 -> line_3784_22 -> line_3783_22 -> line_5621_22 -> line_4081_22 -> line_4082_22 -> line_6424_22 -> line_6196_22 -> line_6013_22 -> line_6012_22 -> line_6172_22 | GSO_126¦line_6172_22 | ACLineSegment | 660 | 10000 | Meter | br_06_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.2578 | [6 empty] | SubstationCapacityUnresolved | br_06_22 | Substation capacity unresolved |  | 101
443 | 24 | GSO_126 | line_3930_22 | S_nCCTT1127 | 9.2578 | High | 12.47 | 13.5424 | 0.0065455 | 13.5358 | 0.24218 | 9.5 | 9.2578 | br_06_22 | CircuitBreaker | Breaker | 9.5 | 0.24218 | 9.2578 | 18 | 15 | 0 | 100 | 17.25 | 0.19649 | -79.9453 | 36.099 | recloser_194_22 -> line_6387_22 -> line_6386_22 -> line_6613_22 -> line_3859_22 -> switch_262_22 -> line_3858_22 -> recloser_154_22 -> line_3784_22 -> line_3783_22 -> line_5621_22 -> line_4081_22 -> line_4082_22 -> line_6424_22 -> line_6196_22 -> line_6013_22 -> line_6014_22 -> line_3930_22 | GSO_126¦line_3930_22 | ACLineSegment | 660 | 10000 | Meter | br_06_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.2578 | [6 empty] | SubstationCapacityUnresolved | br_06_22 | Substation capacity unresolved |  | 101
444 | 25 | GSO_126 | line_6399_22 | S_nCCTT698 | 9.2578 | High | 12.47 | 13.5424 | 0.0065455 | 13.5358 | 0.24218 | 9.5 | 9.2578 | br_06_22 | CircuitBreaker | Breaker | 9.5 | 0.24218 | 9.2578 | 18 | 15 | 0 | 100 | 17.25 | 0.19649 | -79.9453 | 36.0999 | recloser_194_22 -> line_6387_22 -> line_6386_22 -> line_6613_22 -> line_3859_22 -> switch_262_22 -> line_3858_22 -> recloser_154_22 -> line_3784_22 -> line_3783_22 -> line_5621_22 -> line_4081_22 -> line_4082_22 -> line_6424_22 -> line_6196_22 -> line_6013_22 -> line_6014_22 -> line_6399_22 | GSO_126¦line_6399_22 | ACLineSegment | 660 | 10000 | Meter | br_06_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.2578 | [6 empty] | SubstationCapacityUnresolved | br_06_22 | Substation capacity unresolved |  | 101
445 | 26 | GSO_126 | line_6154_22 | S_nCCTT585 | 9.2578 | High | 12.47 | 13.5424 | 0.026182 | 13.5162 | 0.24218 | 9.5 | 9.2578 | br_06_22 | CircuitBreaker | Breaker | 9.5 | 0.24218 | 9.2578 | 19 | 16 | 0 | 100 | 17.25 | 0.19649 | -79.9433 | 36.0984 | recloser_194_22 -> line_6387_22 -> line_6386_22 -> line_6613_22 -> line_3859_22 -> switch_262_22 -> line_3858_22 -> recloser_154_22 -> line_3784_22 -> line_3783_22 -> line_5621_22 -> line_4081_22 -> line_4082_22 -> line_6424_22 -> line_6196_22 -> line_6013_22 -> line_6012_22 -> line_6172_22 -> line_6154_22 | GSO_126¦line_6154_22 | ACLineSegment | 660 | 10000 | Meter | br_06_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.2578 | [6 empty] | SubstationCapacityUnresolved | br_06_22 | Substation capacity unresolved |  | 101
446 | 27 | GSO_126 | line_3793_22 | S_nCCTT1175 | 9.2578 | High | 12.47 | 13.5424 | 0.0065455 | 13.5358 | 0.24218 | 9.5 | 9.2578 | br_06_22 | CircuitBreaker | Breaker | 9.5 | 0.24218 | 9.2578 | 19 | 16 | 0 | 100 | 17.25 | 0.19649 | -79.9425 | 36.0997 | recloser_194_22 -> line_6387_22 -> line_6386_22 -> line_6613_22 -> line_3859_22 -> switch_262_22 -> line_3858_22 -> recloser_154_22 -> line_3784_22 -> line_3783_22 -> line_5621_22 -> line_4081_22 -> line_4082_22 -> line_6424_22 -> line_6196_22 -> line_6013_22 -> line_6012_22 -> line_3794_22 -> line_3793_22 | GSO_126¦line_3793_22 | ACLineSegment | 660 | 10000 | Meter | br_06_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.2578 | [6 empty] | SubstationCapacityUnresolved | br_06_22 | Substation capacity unresolved |  | 101
447 | 28 | GSO_126 | line_3795_22 | S_nCCTT661 | 9.2578 | High | 12.47 | 13.5424 | 0.026182 | 13.5162 | 0.24218 | 9.5 | 9.2578 | br_06_22 | CircuitBreaker | Breaker | 9.5 | 0.24218 | 9.2578 | 19 | 16 | 0 | 100 | 17.25 | 0.19649 | -79.942 | 36.1002 | recloser_194_22 -> line_6387_22 -> line_6386_22 -> line_6613_22 -> line_3859_22 -> switch_262_22 -> line_3858_22 -> recloser_154_22 -> line_3784_22 -> line_3783_22 -> line_5621_22 -> line_4081_22 -> line_4082_22 -> line_6424_22 -> line_6196_22 -> line_6013_22 -> line_6012_22 -> line_3794_22 -> line_3795_22 | GSO_126¦line_3795_22 | ACLineSegment | 660 | 10000 | Meter | br_06_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.2578 | [6 empty] | SubstationCapacityUnresolved | br_06_22 | Substation capacity unresolved |  | 101
448 | 29 | GSO_126 | line_4199_22 | S_nCCTT1228 | 9.2578 | High | 12.47 | 13.5424 | 0.019637 | 13.5227 | 0.24218 | 9.5 | 9.2578 | br_06_22 | CircuitBreaker | Breaker | 9.5 | 0.24218 | 9.2578 | 20 | 17 | 0 | 100 | 17.25 | 0.19649 | -79.9411 | 36.1007 | recloser_194_22 -> line_6387_22 -> line_6386_22 -> line_6613_22 -> line_3859_22 -> switch_262_22 -> line_3858_22 -> recloser_154_22 -> line_3784_22 -> line_3783_22 -> line_5621_22 -> line_4081_22 -> line_4082_22 -> line_6424_22 -> line_6196_22 -> line_6013_22 -> line_6012_22 -> line_3794_22 -> line_3795_22 -> line_4199_22 | GSO_126¦line_4199_22 | ACLineSegment | 660 | 10000 | Meter | br_06_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.2578 | [6 empty] | SubstationCapacityUnresolved | br_06_22 | Substation capacity unresolved |  | 101
449 | 30 | GSO_126 | line_4078_22 | S_nCCTT1183 | 9.2578 | High | 12.47 | 13.5424 | 0.013091 | 13.5293 | 0.24218 | 9.5 | 9.2578 | br_06_22 | CircuitBreaker | Breaker | 9.5 | 0.24218 | 9.2578 | 21 | 18 | 0 | 100 | 17.25 | 0.19649 | -79.9408 | 36.1013 | recloser_194_22 -> line_6387_22 -> line_6386_22 -> line_6613_22 -> line_3859_22 -> switch_262_22 -> line_3858_22 -> recloser_154_22 -> line_3784_22 -> line_3783_22 -> line_5621_22 -> line_4081_22 -> line_4082_22 -> line_6424_22 -> line_6196_22 -> line_6013_22 -> line_6012_22 -> line_3794_22 -> line_3795_22 -> line_4199_22 -> line_4078_22 | GSO_126¦line_4078_22 | ACLineSegment | 660 | 10000 | Meter | br_06_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.2578 | [6 empty] | SubstationCapacityUnresolved | br_06_22 | Substation capacity unresolved |  | 101
450 | 31 | GSO_126 | line_3802_22 | S_nCCTT1085 | 9.2578 | High | 12.47 | 13.5424 | 0.0065455 | 13.5358 | 0.24218 | 9.5 | 9.2578 | br_06_22 | CircuitBreaker | Breaker | 9.5 | 0.24218 | 9.2578 | 22 | 19 | 0 | 100 | 17.25 | 0.19649 | -79.94 | 36.1015 | recloser_194_22 -> line_6387_22 -> line_6386_22 -> line_6613_22 -> line_3859_22 -> switch_262_22 -> line_3858_22 -> recloser_154_22 -> line_3784_22 -> line_3783_22 -> line_5621_22 -> line_4081_22 -> line_4082_22 -> line_6424_22 -> line_6196_22 -> line_6013_22 -> line_6012_22 -> line_3794_22 -> line_3795_22 -> line_4199_22 -> line_4078_22 -> line_3802_22 | GSO_126¦line_3802_22 | ACLineSegment | 660 | 10000 | Meter | br_06_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.2578 | [6 empty] | SubstationCapacityUnresolved | br_06_22 | Substation capacity unresolved |  | 101
552 | 32 | GSO_126 | line_6461_22 | S_nCCTT916 | 2.8302 | High | 7.2 | 2.8433 | 0.013091 | 2.8302 | 0.24218 | 9.5 | 9.2578 | line_6461_22 | ACLineSegment | Line | 2.8433 | 0.013091 | 2.8302 | 17 | 13 | 0 | 100 | 17.25 | 0.19649 | -79.9473 | 36.101 | recloser_194_22 -> line_6387_22 -> line_6386_22 -> line_6613_22 -> line_3859_22 -> switch_262_22 -> line_3858_22 -> recloser_154_22 -> line_3784_22 -> line_3783_22 -> line_5621_22 -> line_4081_22 -> line_4082_22 -> line_5819_22 -> line_5818_22 -> fuse_149_22 -> line_6461_22 | GSO_126¦line_6461_22 | ACLineSegment | 240 | 10000 | Meter | br_06_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.8302 | [6 empty] | SubstationCapacityUnresolved | line_6461_22 | Substation capacity unresolved |  | 101
395 | 1 | GSO_127 | line_6871_22 | UCMV43 | 9.4748 | High | 12.47 | 13.5424 | 0.025212 | 13.5172 | 0.025212 | 9.5 | 9.4748 | br_07_22 | CircuitBreaker | Breaker | 9.5 | 0.025212 | 9.4748 | 2 | 1 | 0 | 100 | 1.5833 | 0.018035 | -79.9234 | 36.0973 | recloser_204_22 -> line_6871_22 | GSO_127¦line_6871_22 | ACLineSegment | 660 | 10000 | Meter | br_07_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.4748 | [6 empty] | SubstationCapacityUnresolved | br_07_22 | Substation capacity unresolved |  | 101
406 | 1 | GSO_128 | line_6872_22 | UCMV51 | 9.3499 | High | 12.47 | 13.5424 | 0.15013 | 13.3922 | 0.15013 | 9.5 | 9.3499 | br_08_22 | CircuitBreaker | Breaker | 9.5 | 0.15013 | 9.3499 | 2 | 1 | 0 | 100 | 11.6667 | 0.13289 | -79.9277 | 36.0971 | recloser_205_22 -> line_6872_22 | GSO_128¦line_6872_22 | ACLineSegment | 660 | 10000 | Meter | br_08_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.3499 | [6 empty] | SubstationCapacityUnresolved | br_08_22 | Substation capacity unresolved |  | 101
407 | 2 | GSO_128 | line_6395_22 | S_nCCTT696 | 9.3499 | High | 12.47 | 13.5424 | 0.14075 | 13.4016 | 0.15013 | 9.5 | 9.3499 | br_08_22 | CircuitBreaker | Breaker | 9.5 | 0.15013 | 9.3499 | 3 | 2 | 0 | 100 | 11.6667 | 0.13289 | -79.9316 | 36.0946 | recloser_205_22 -> line_6872_22 -> line_6395_22 | GSO_128¦line_6395_22 | ACLineSegment | 660 | 10000 | Meter | br_08_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.3499 | [6 empty] | SubstationCapacityUnresolved | br_08_22 | Substation capacity unresolved |  | 101
408 | 3 | GSO_128 | line_6394_22 | S_nCCTT786 | 9.3499 | High | 12.47 | 13.5424 | 0.13137 | 13.411 | 0.15013 | 9.5 | 9.3499 | br_08_22 | CircuitBreaker | Breaker | 9.5 | 0.15013 | 9.3499 | 4 | 3 | 0 | 100 | 11.6667 | 0.13289 | -79.9309 | 36.0951 | recloser_205_22 -> line_6872_22 -> line_6395_22 -> line_6394_22 | GSO_128¦line_6394_22 | ACLineSegment | 660 | 10000 | Meter | br_08_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.3499 | [6 empty] | SubstationCapacityUnresolved | br_08_22 | Substation capacity unresolved |  | 101
409 | 4 | GSO_128 | line_3675_22 | S_nCCTT1044 | 9.3499 | High | 12.47 | 13.5424 | 0.12198 | 13.4204 | 0.15013 | 9.5 | 9.3499 | br_08_22 | CircuitBreaker | Breaker | 9.5 | 0.15013 | 9.3499 | 5 | 4 | 0 | 100 | 11.6667 | 0.13289 | -79.9302 | 36.0956 | recloser_205_22 -> line_6872_22 -> line_6395_22 -> line_6394_22 -> line_3675_22 | GSO_128¦line_3675_22 | ACLineSegment | 660 | 10000 | Meter | br_08_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.3499 | [6 empty] | SubstationCapacityUnresolved | br_08_22 | Substation capacity unresolved |  | 101
410 | 5 | GSO_128 | line_3674_22 | S_nCCTT1079 | 9.3499 | High | 12.47 | 13.5424 | 0.1126 | 13.4298 | 0.15013 | 9.5 | 9.3499 | br_08_22 | CircuitBreaker | Breaker | 9.5 | 0.15013 | 9.3499 | 6 | 5 | 0 | 100 | 11.6667 | 0.13289 | -79.9293 | 36.0967 | recloser_205_22 -> line_6872_22 -> line_6395_22 -> line_6394_22 -> line_3675_22 -> line_3674_22 | GSO_128¦line_3674_22 | ACLineSegment | 660 | 10000 | Meter | br_08_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.3499 | [6 empty] | SubstationCapacityUnresolved | br_08_22 | Substation capacity unresolved |  | 101
411 | 6 | GSO_128 | line_3778_22 | S_nCCTT1201 | 9.3499 | High | 12.47 | 13.5424 | 0.10322 | 13.4392 | 0.15013 | 9.5 | 9.3499 | br_08_22 | CircuitBreaker | Breaker | 9.5 | 0.15013 | 9.3499 | 7 | 6 | 0 | 100 | 11.6667 | 0.13289 | -79.9299 | 36.0978 | recloser_205_22 -> line_6872_22 -> line_6395_22 -> line_6394_22 -> line_3675_22 -> line_3674_22 -> line_3778_22 | GSO_128¦line_3778_22 | ACLineSegment | 660 | 10000 | Meter | br_08_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.3499 | [6 empty] | SubstationCapacityUnresolved | br_08_22 | Substation capacity unresolved |  | 101
412 | 7 | GSO_128 | line_3861_22 | S_nCCTT1101 | 9.3499 | High | 12.47 | 13.5424 | 0.084449 | 13.4579 | 0.15013 | 9.5 | 9.3499 | br_08_22 | CircuitBreaker | Breaker | 9.5 | 0.15013 | 9.3499 | 8 | 7 | 0 | 100 | 11.6667 | 0.13289 | -79.9301 | 36.098 | recloser_205_22 -> line_6872_22 -> line_6395_22 -> line_6394_22 -> line_3675_22 -> line_3674_22 -> line_3778_22 -> line_3861_22 | GSO_128¦line_3861_22 | ACLineSegment | 660 | 10000 | Meter | br_08_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.3499 | [6 empty] | SubstationCapacityUnresolved | br_08_22 | Substation capacity unresolved |  | 101
413 | 8 | GSO_128 | line_3862_22 | S_nCCTT977 | 9.3499 | High | 12.47 | 13.5424 | 0.065683 | 13.4767 | 0.15013 | 9.5 | 9.3499 | br_08_22 | CircuitBreaker | Breaker | 9.5 | 0.15013 | 9.3499 | 9 | 8 | 0 | 100 | 11.6667 | 0.13289 | -79.9297 | 36.0982 | recloser_205_22 -> line_6872_22 -> line_6395_22 -> line_6394_22 -> line_3675_22 -> line_3674_22 -> line_3778_22 -> line_3861_22 -> line_3862_22 | GSO_128¦line_3862_22 | ACLineSegment | 660 | 10000 | Meter | br_08_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.3499 | [6 empty] | SubstationCapacityUnresolved | br_08_22 | Substation capacity unresolved |  | 101
414 | 9 | GSO_128 | line_6830_22 | UCMV34 | 9.3499 | High | 12.47 | 13.5424 | 0.056299 | 13.4861 | 0.15013 | 9.5 | 9.3499 | br_08_22 | CircuitBreaker | Breaker | 9.5 | 0.15013 | 9.3499 | 10 | 9 | 0 | 100 | 11.6667 | 0.13289 | -79.9285 | 36.0983 | recloser_205_22 -> line_6872_22 -> line_6395_22 -> line_6394_22 -> line_3675_22 -> line_3674_22 -> line_3778_22 -> line_3861_22 -> line_3862_22 -> line_6830_22 | GSO_128¦line_6830_22 | ACLineSegment | 660 | 10000 | Meter | br_08_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.3499 | [6 empty] | SubstationCapacityUnresolved | br_08_22 | Substation capacity unresolved |  | 101
415 | 10 | GSO_128 | line_6881_22 | UCMV56 | 9.3499 | High | 12.47 | 13.5424 | 0.046916 | 13.4955 | 0.15013 | 9.5 | 9.3499 | br_08_22 | CircuitBreaker | Breaker | 9.5 | 0.15013 | 9.3499 | 11 | 10 | 0 | 100 | 11.6667 | 0.13289 | -79.9274 | 36.0974 | recloser_205_22 -> line_6872_22 -> line_6395_22 -> line_6394_22 -> line_3675_22 -> line_3674_22 -> line_3778_22 -> line_3861_22 -> line_3862_22 -> line_6830_22 -> line_6881_22 | GSO_128¦line_6881_22 | ACLineSegment | 660 | 10000 | Meter | br_08_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.3499 | [6 empty] | SubstationCapacityUnresolved | br_08_22 | Substation capacity unresolved |  | 101
416 | 11 | GSO_128 | line_6884_22 | UCMV50 | 9.3499 | High | 12.47 | 13.5424 | 0.037533 | 13.5048 | 0.15013 | 9.5 | 9.3499 | br_08_22 | CircuitBreaker | Breaker | 9.5 | 0.15013 | 9.3499 | 12 | 11 | 0 | 100 | 11.6667 | 0.13289 | -79.927 | 36.0959 | recloser_205_22 -> line_6872_22 -> line_6395_22 -> line_6394_22 -> line_3675_22 -> line_3674_22 -> line_3778_22 -> line_3861_22 -> line_3862_22 -> line_6830_22 -> line_6881_22 -> line_6884_22 | GSO_128¦line_6884_22 | ACLineSegment | 660 | 10000 | Meter | br_08_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.3499 | [6 empty] | SubstationCapacityUnresolved | br_08_22 | Substation capacity unresolved |  | 101
417 | 12 | GSO_128 | line_6882_22 | UCMV36 | 9.3499 | High | 12.47 | 13.5424 | 0.02815 | 13.5142 | 0.15013 | 9.5 | 9.3499 | br_08_22 | CircuitBreaker | Breaker | 9.5 | 0.15013 | 9.3499 | 13 | 12 | 0 | 100 | 11.6667 | 0.13289 | -79.9275 | 36.0953 | recloser_205_22 -> line_6872_22 -> line_6395_22 -> line_6394_22 -> line_3675_22 -> line_3674_22 -> line_3778_22 -> line_3861_22 -> line_3862_22 -> line_6830_22 -> line_6881_22 -> line_6884_22 -> line_6882_22 | GSO_128¦line_6882_22 | ACLineSegment | 660 | 10000 | Meter | br_08_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.3499 | [6 empty] | SubstationCapacityUnresolved | br_08_22 | Substation capacity unresolved |  | 101
418 | 13 | GSO_128 | line_3810_22 | S_nCCTT1087 | 9.3499 | High | 12.47 | 13.5424 | 0.018766 | 13.5236 | 0.15013 | 9.5 | 9.3499 | br_08_22 | CircuitBreaker | Breaker | 9.5 | 0.15013 | 9.3499 | 14 | 13 | 0 | 100 | 11.6667 | 0.13289 | -79.9279 | 36.0944 | recloser_205_22 -> line_6872_22 -> line_6395_22 -> line_6394_22 -> line_3675_22 -> line_3674_22 -> line_3778_22 -> line_3861_22 -> line_3862_22 -> line_6830_22 -> line_6881_22 -> line_6884_22 -> line_6882_22 -> line_3810_22 | GSO_128¦line_3810_22 | ACLineSegment | 660 | 10000 | Meter | br_08_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.3499 | [6 empty] | SubstationCapacityUnresolved | br_08_22 | Substation capacity unresolved |  | 101
419 | 14 | GSO_128 | line_3809_22 | S_nCCTT928 | 9.3499 | High | 12.47 | 13.5424 | 0.0093832 | 13.533 | 0.15013 | 9.5 | 9.3499 | br_08_22 | CircuitBreaker | Breaker | 9.5 | 0.15013 | 9.3499 | 15 | 14 | 0 | 100 | 11.6667 | 0.13289 | -79.9281 | 36.0935 | recloser_205_22 -> line_6872_22 -> line_6395_22 -> line_6394_22 -> line_3675_22 -> line_3674_22 -> line_3778_22 -> line_3861_22 -> line_3862_22 -> line_6830_22 -> line_6881_22 -> line_6884_22 -> line_6882_22 -> line_3810_22 -> line_3809_22 | GSO_128¦line_3809_22 | ACLineSegment | 660 | 10000 | Meter | br_08_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.3499 | [6 empty] | SubstationCapacityUnresolved | br_08_22 | Substation capacity unresolved |  | 101
546 | 15 | GSO_128 | line_4124_22 | S_nCCTT802 | 2.834 | High | 7.2 | 2.8433 | 0.0093832 | 2.834 | 0.15013 | 9.5 | 9.3499 | line_4124_22 | ACLineSegment | Line | 2.8433 | 0.0093832 | 2.834 | 9 | 7 | 0 | 100 | 11.6667 | 0.13289 | -79.9303 | 36.0978 | recloser_205_22 -> line_6872_22 -> line_6395_22 -> line_6394_22 -> line_3675_22 -> line_3674_22 -> line_3778_22 -> fuse_39_22 -> line_4124_22 | GSO_128¦line_4124_22 | ACLineSegment | 240 | 10000 | Meter | br_08_22 | hvmv_2_22 | 10000.0 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.834 | [6 empty] | SubstationCapacityUnresolved | line_4124_22 | Substation capacity unresolved |  | 101
103 | 1 | GSO_141 | line_4565_22 | S_nCCTT1344 | 11.02 | High | 12.47 | 13.5424 | 0.37996 | 13.1624 | 0.37996 | 11.4 | 11.02 | br_021_22 | CircuitBreaker | Breaker | 11.4 | 0.37996 | 11.02 | 2 | 1 | 0 | 100 | 12.9167 | 0.14713 | -79.9486 | 36.0429 | recloser_168_22 -> line_4565_22 | GSO_141¦line_4565_22 | ACLineSegment | 660 | 12000 | Meter | br_021_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved |  | 250
104 | 2 | GSO_141 | line_4566_22 | UCMV96 | 11.02 | High | 12.47 | 13.5424 | 0.37437 | 13.168 | 0.37996 | 11.4 | 11.02 | br_021_22 | CircuitBreaker | Breaker | 11.4 | 0.37996 | 11.02 | 3 | 2 | 0 | 100 | 12.9167 | 0.14713 | -79.9513 | 36.0397 | recloser_168_22 -> line_4565_22 -> line_4566_22 | GSO_141¦line_4566_22 | ACLineSegment | 660 | 12000 | Meter | br_021_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved |  | 250
105 | 3 | GSO_141 | line_5449_22 | S_nCCTT259 | 11.02 | High | 12.47 | 13.5424 | 0.011175 | 13.5312 | 0.37996 | 11.4 | 11.02 | br_021_22 | CircuitBreaker | Breaker | 11.4 | 0.37996 | 11.02 | 4 | 3 | 0 | 100 | 12.9167 | 0.14713 | -79.9537 | 36.0393 | recloser_168_22 -> line_4565_22 -> line_4566_22 -> line_5449_22 | GSO_141¦line_5449_22 | ACLineSegment | 660 | 12000 | Meter | br_021_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved |  | 250
106 | 4 | GSO_141 | line_6472_22 | S_nCCTT740 | 11.02 | High | 12.47 | 13.5424 | 0.35761 | 13.1848 | 0.37996 | 11.4 | 11.02 | br_021_22 | CircuitBreaker | Breaker | 11.4 | 0.37996 | 11.02 | 4 | 3 | 0 | 100 | 12.9167 | 0.14713 | -79.9528 | 36.0404 | recloser_168_22 -> line_4565_22 -> line_4566_22 -> line_6472_22 | GSO_141¦line_6472_22 | ACLineSegment | 660 | 12000 | Meter | br_021_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved |  | 250
107 | 5 | GSO_141 | line_5448_22 | UCMV128 | 11.02 | High | 12.47 | 13.5424 | 0.0055876 | 13.5368 | 0.37996 | 11.4 | 11.02 | br_021_22 | CircuitBreaker | Breaker | 11.4 | 0.37996 | 11.02 | 5 | 4 | 0 | 100 | 12.9167 | 0.14713 | -79.9549 | 36.0392 | recloser_168_22 -> line_4565_22 -> line_4566_22 -> line_5449_22 -> line_5448_22 | GSO_141¦line_5448_22 | ACLineSegment | 660 | 12000 | Meter | br_021_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved |  | 250
108 | 6 | GSO_141 | line_6471_22 | UCMV84 | 11.02 | High | 12.47 | 12.3112 | 0.35202 | 11.9592 | 0.37996 | 11.4 | 11.02 | br_021_22 | CircuitBreaker | Breaker | 11.4 | 0.37996 | 11.02 | 6 | 4 | 0 | 100 | 12.9167 | 0.14713 | -79.9529 | 36.0417 | recloser_168_22 -> line_4565_22 -> line_4566_22 -> line_6472_22 -> switch_765_22 -> line_6471_22 | GSO_141¦line_6471_22 | ACLineSegment | 600 | 12000 | Meter | br_021_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved |  | 250
109 | 7 | GSO_141 | line_5658_22 | UCMV84_B_S_nCCTT366 | 11.02 | High | 12.47 | 12.3112 | 0.34084 | 11.9704 | 0.37996 | 11.4 | 11.02 | br_021_22 | CircuitBreaker | Breaker | 11.4 | 0.37996 | 11.02 | 7 | 5 | 0 | 100 | 12.9167 | 0.14713 | -79.9546 | 36.0425 | recloser_168_22 -> line_4565_22 -> line_4566_22 -> line_6472_22 -> switch_765_22 -> line_6471_22 -> line_5658_22 | GSO_141¦line_5658_22 | ACLineSegment | 600 | 12000 | Meter | br_021_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved |  | 250
110 | 8 | GSO_141 | line_6887_22 | UCMV84_B_UCMV93 | 11.02 | High | 12.47 | 12.3112 | 0.0055876 | 12.3057 | 0.37996 | 11.4 | 11.02 | br_021_22 | CircuitBreaker | Breaker | 11.4 | 0.37996 | 11.02 | 7 | 5 | 0 | 100 | 12.9167 | 0.14713 | -79.9528 | 36.0428 | recloser_168_22 -> line_4565_22 -> line_4566_22 -> line_6472_22 -> switch_765_22 -> line_6471_22 -> line_6887_22 | GSO_141¦line_6887_22 | ACLineSegment | 600 | 12000 | Meter | br_021_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved |  | 250
111 | 9 | GSO_141 | line_4878_22 | S_nCCTT1463 | 11.02 | High | 12.47 | 12.3112 | 0.33526 | 11.976 | 0.37996 | 11.4 | 11.02 | br_021_22 | CircuitBreaker | Breaker | 11.4 | 0.37996 | 11.02 | 10 | 6 | 0 | 100 | 12.9167 | 0.14713 | -79.9574 | 36.0427 | recloser_168_22 -> line_4565_22 -> line_4566_22 -> line_6472_22 -> switch_765_22 -> line_6471_22 -> line_5658_22 -> switch_664_22 -> switch_524_22 -> line_4878_22 | GSO_141¦line_4878_22 | ACLineSegment | 600 | 12000 | Meter | br_021_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved |  | 250
112 | 10 | GSO_141 | line_4879_22 | UCMV77 | 11.02 | High | 12.47 | 13.5424 | 0.32967 | 13.2127 | 0.37996 | 11.4 | 11.02 | br_021_22 | CircuitBreaker | Breaker | 11.4 | 0.37996 | 11.02 | 11 | 7 | 0 | 100 | 12.9167 | 0.14713 | -79.9585 | 36.0415 | recloser_168_22 -> line_4565_22 -> line_4566_22 -> line_6472_22 -> switch_765_22 -> line_6471_22 -> line_5658_22 -> switch_664_22 -> switch_524_22 -> line_4878_22 -> line_4879_22 | GSO_141¦line_4879_22 | ACLineSegment | 660 | 12000 | Meter | br_021_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved |  | 250
113 | 11 | GSO_141 | line_5743_22 | S_nCCTT403 | 11.02 | High | 12.47 | 13.5424 | 0.32408 | 13.2183 | 0.37996 | 11.4 | 11.02 | br_021_22 | CircuitBreaker | Breaker | 11.4 | 0.37996 | 11.02 | 13 | 8 | 0 | 100 | 12.9167 | 0.14713 | -79.9584 | 36.0398 | recloser_168_22 -> line_4565_22 -> line_4566_22 -> line_6472_22 -> switch_765_22 -> line_6471_22 -> line_5658_22 -> switch_664_22 -> switch_524_22 -> line_4878_22 -> line_4879_22 -> recloser_183_22 -> line_5743_22 | GSO_141¦line_5743_22 | ACLineSegment | 660 | 12000 | Meter | br_021_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved |  | 250
114 | 12 | GSO_141 | line_4709_22 | S_nCCTT1398 | 11.02 | High | 12.47 | 13.5424 | 0.31849 | 13.2239 | 0.37996 | 11.4 | 11.02 | br_021_22 | CircuitBreaker | Breaker | 11.4 | 0.37996 | 11.02 | 14 | 9 | 0 | 100 | 12.9167 | 0.14713 | -79.9594 | 36.0392 | recloser_168_22 -> line_4565_22 -> line_4566_22 -> line_6472_22 -> switch_765_22 -> line_6471_22 -> line_5658_22 -> switch_664_22 -> switch_524_22 -> line_4878_22 -> line_4879_22 -> recloser_183_22 -> line_5743_22 -> line_4709_22 | GSO_141¦line_4709_22 | ACLineSegment | 660 | 12000 | Meter | br_021_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved |  | 250
115 | 13 | GSO_141 | line_4710_22 | S_nCCTT86 | 11.02 | High | 12.47 | 13.5424 | 0.3129 | 13.2295 | 0.37996 | 11.4 | 11.02 | br_021_22 | CircuitBreaker | Breaker | 11.4 | 0.37996 | 11.02 | 15 | 10 | 0 | 100 | 12.9167 | 0.14713 | -79.9601 | 36.0392 | recloser_168_22 -> line_4565_22 -> line_4566_22 -> line_6472_22 -> switch_765_22 -> line_6471_22 -> line_5658_22 -> switch_664_22 -> switch_524_22 -> line_4878_22 -> line_4879_22 -> recloser_183_22 -> line_5743_22 -> line_4709_22 -> line_4710_22 | GSO_141¦line_4710_22 | ACLineSegment | 660 | 12000 | Meter | br_021_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved |  | 250
116 | 14 | GSO_141 | line_4403_22 | S_nCCTT129 | 11.02 | High | 12.47 | 13.5424 | 0.30732 | 13.2351 | 0.37996 | 11.4 | 11.02 | br_021_22 | CircuitBreaker | Breaker | 11.4 | 0.37996 | 11.02 | 16 | 11 | 0 | 100 | 12.9167 | 0.14713 | -79.9614 | 36.0393 | recloser_168_22 -> line_4565_22 -> line_4566_22 -> line_6472_22 -> switch_765_22 -> line_6471_22 -> line_5658_22 -> switch_664_22 -> switch_524_22 -> line_4878_22 -> line_4879_22 -> recloser_183_22 -> line_5743_22 -> line_4709_22 -> line_4710_22 -> line_4403_22 | GSO_141¦line_4403_22 | ACLineSegment | 660 | 12000 | Meter | br_021_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved |  | 250
117 | 15 | GSO_141 | line_4401_22 | S_nCCTT1432 | 11.02 | High | 12.47 | 13.5424 | 0.30173 | 13.2406 | 0.37996 | 11.4 | 11.02 | br_021_22 | CircuitBreaker | Breaker | 11.4 | 0.37996 | 11.02 | 17 | 12 | 0 | 100 | 12.9167 | 0.14713 | -79.9621 | 36.0402 | recloser_168_22 -> line_4565_22 -> line_4566_22 -> line_6472_22 -> switch_765_22 -> line_6471_22 -> line_5658_22 -> switch_664_22 -> switch_524_22 -> line_4878_22 -> line_4879_22 -> recloser_183_22 -> line_5743_22 -> line_4709_22 -> line_4710_22 -> line_4403_22 -> line_4401_22 | GSO_141¦line_4401_22 | ACLineSegment | 660 | 12000 | Meter | br_021_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved |  | 250
118 | 16 | GSO_141 | line_4250_22 | S_nCCTT1239 | 11.02 | High | 12.47 | 13.5424 | 0.29055 | 13.2518 | 0.37996 | 11.4 | 11.02 | br_021_22 | CircuitBreaker | Breaker | 11.4 | 0.37996 | 11.02 | 18 | 13 | 0 | 100 | 12.9167 | 0.14713 | -79.9621 | 36.0411 | recloser_168_22 -> line_4565_22 -> line_4566_22 -> line_6472_22 -> switch_765_22 -> line_6471_22 -> line_5658_22 -> switch_664_22 -> switch_524_22 -> line_4878_22 -> line_4879_22 -> recloser_183_22 -> line_5743_22 -> line_4709_22 -> line_4710_22 -> line_4403_22 -> line_4401_22 -> line_4250_22 | GSO_141¦line_4250_22 | ACLineSegment | 660 | 12000 | Meter | br_021_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved |  | 250
119 | 17 | GSO_141 | line_4803_22 | S_nCCTT242 | 11.02 | High | 12.47 | 13.5424 | 0.0055876 | 13.5368 | 0.37996 | 11.4 | 11.02 | br_021_22 | CircuitBreaker | Breaker | 11.4 | 0.37996 | 11.02 | 18 | 13 | 0 | 100 | 12.9167 | 0.14713 | -79.963 | 36.0404 | recloser_168_22 -> line_4565_22 -> line_4566_22 -> line_6472_22 -> switch_765_22 -> line_6471_22 -> line_5658_22 -> switch_664_22 -> switch_524_22 -> line_4878_22 -> line_4879_22 -> recloser_183_22 -> line_5743_22 -> line_4709_22 -> line_4710_22 -> line_4403_22 -> line_4401_22 -> line_4803_22 | GSO_141¦line_4803_22 | ACLineSegment | 660 | 12000 | Meter | br_021_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved |  | 250
120 | 18 | GSO_141 | line_4251_22 | S_nCCTT29 | 11.02 | High | 12.47 | 13.5424 | 0.27938 | 13.263 | 0.37996 | 11.4 | 11.02 | br_021_22 | CircuitBreaker | Breaker | 11.4 | 0.37996 | 11.02 | 19 | 14 | 0 | 100 | 12.9167 | 0.14713 | -79.9622 | 36.0419 | recloser_168_22 -> line_4565_22 -> line_4566_22 -> line_6472_22 -> switch_765_22 -> line_6471_22 -> line_5658_22 -> switch_664_22 -> switch_524_22 -> line_4878_22 -> line_4879_22 -> recloser_183_22 -> line_5743_22 -> line_4709_22 -> line_4710_22 -> line_4403_22 -> line_4401_22 -> line_4250_22 -> line_4251_22 | GSO_141¦line_4251_22 | ACLineSegment | 660 | 12000 | Meter | br_021_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved |  | 250
121 | 19 | GSO_141 | line_4361_22 | S_nCCTT1275 | 11.02 | High | 12.47 | 13.5424 | 0.17322 | 13.3692 | 0.37996 | 11.4 | 11.02 | br_021_22 | CircuitBreaker | Breaker | 11.4 | 0.37996 | 11.02 | 20 | 15 | 0 | 100 | 12.9167 | 0.14713 | -79.9623 | 36.0427 | recloser_168_22 -> line_4565_22 -> line_4566_22 -> line_6472_22 -> switch_765_22 -> line_6471_22 -> line_5658_22 -> switch_664_22 -> switch_524_22 -> line_4878_22 -> line_4879_22 -> recloser_183_22 -> line_5743_22 -> line_4709_22 -> line_4710_22 -> line_4403_22 -> line_4401_22 -> line_4250_22 -> line_4251_22 -> line_4361_22 | GSO_141¦line_4361_22 | ACLineSegment | 660 | 12000 | Meter | br_021_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved |  | 250
122 | 20 | GSO_141 | line_4360_22 | S_nCCTT1437 | 11.02 | High | 12.47 | 13.5424 | 0.16763 | 13.3747 | 0.37996 | 11.4 | 11.02 | br_021_22 | CircuitBreaker | Breaker | 11.4 | 0.37996 | 11.02 | 22 | 16 | 0 | 100 | 12.9167 | 0.14713 | -79.9618 | 36.0438 | recloser_168_22 -> line_4565_22 -> line_4566_22 -> line_6472_22 -> switch_765_22 -> line_6471_22 -> line_5658_22 -> switch_664_22 -> switch_524_22 -> line_4878_22 -> line_4879_22 -> recloser_183_22 -> line_5743_22 -> line_4709_22 -> line_4710_22 -> line_4403_22 -> line_4401_22 -> line_4250_22 -> line_4251_22 -> line_4361_22 -> recloser_165_22 -> line_4360_22 | GSO_141¦line_4360_22 | ACLineSegment | 660 | 12000 | Meter | br_021_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved |  | 250
123 | 21 | GSO_141 | line_4095_22 | S_nCCTT119 | 11.02 | High | 12.47 | 12.3112 | 0.1341 | 12.1771 | 0.37996 | 11.4 | 11.02 | br_021_22 | CircuitBreaker | Breaker | 11.4 | 0.37996 | 11.02 | 24 | 17 | 0 | 100 | 12.9167 | 0.14713 | -79.9603 | 36.0446 | recloser_168_22 -> line_4565_22 -> line_4566_22 -> line_6472_22 -> switch_765_22 -> line_6471_22 -> line_5658_22 -> switch_664_22 -> switch_524_22 -> line_4878_22 -> line_4879_22 -> recloser_183_22 -> line_5743_22 -> line_4709_22 -> line_4710_22 -> line_4403_22 -> line_4401_22 -> line_4250_22 -> line_4251_22 -> line_4361_22 -> recloser_165_22 -> line_4360_22 -> switch_326_22 -> line_4095_22 | GSO_141¦line_4095_22 | ACLineSegment | 600 | 12000 | Meter | br_021_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved |  | 250
124 | 22 | GSO_141 | line_4815_22 | S_nCCTT1466 | 11.02 | High | 12.47 | 12.3112 | 0.027938 | 12.2833 | 0.37996 | 11.4 | 11.02 | br_021_22 | CircuitBreaker | Breaker | 11.4 | 0.37996 | 11.02 | 24 | 17 | 0 | 100 | 12.9167 | 0.14713 | -79.9618 | 36.0443 | recloser_168_22 -> line_4565_22 -> line_4566_22 -> line_6472_22 -> switch_765_22 -> line_6471_22 -> line_5658_22 -> switch_664_22 -> switch_524_22 -> line_4878_22 -> line_4879_22 -> recloser_183_22 -> line_5743_22 -> line_4709_22 -> line_4710_22 -> line_4403_22 -> line_4401_22 -> line_4250_22 -> line_4251_22 -> line_4361_22 -> recloser_165_22 -> line_4360_22 -> switch_502_22 -> line_4815_22 | GSO_141¦line_4815_22 | ACLineSegment | 600 | 12000 | Meter | br_021_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved |  | 250
125 | 23 | GSO_141 | line_4094_22 | S_nCCTT119_B_S_nCCTT1255 | 11.02 | High | 12.47 | 12.3112 | 0.11175 | 12.1995 | 0.37996 | 11.4 | 11.02 | br_021_22 | CircuitBreaker | Breaker | 11.4 | 0.37996 | 11.02 | 25 | 18 | 0 | 100 | 12.9167 | 0.14713 | -79.9597 | 36.0459 | recloser_168_22 -> line_4565_22 -> line_4566_22 -> line_6472_22 -> switch_765_22 -> line_6471_22 -> line_5658_22 -> switch_664_22 -> switch_524_22 -> line_4878_22 -> line_4879_22 -> recloser_183_22 -> line_5743_22 -> line_4709_22 -> line_4710_22 -> line_4403_22 -> line_4401_22 -> line_4250_22 -> line_4251_22 -> line_4361_22 -> recloser_165_22 -> line_4360_22 -> switch_326_22 -> line_4095_22 -> line_4094_22 | GSO_141¦line_4094_22 | ACLineSegment | 600 | 12000 | Meter | br_021_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved |  | 250
126 | 24 | GSO_141 | line_4096_22 | S_nCCTT119_B_S_nCCTT681 | 11.02 | High | 12.47 | 12.3112 | 0.016763 | 12.2945 | 0.37996 | 11.4 | 11.02 | br_021_22 | CircuitBreaker | Breaker | 11.4 | 0.37996 | 11.02 | 25 | 18 | 0 | 100 | 12.9167 | 0.14713 | -79.9589 | 36.0458 | recloser_168_22 -> line_4565_22 -> line_4566_22 -> line_6472_22 -> switch_765_22 -> line_6471_22 -> line_5658_22 -> switch_664_22 -> switch_524_22 -> line_4878_22 -> line_4879_22 -> recloser_183_22 -> line_5743_22 -> line_4709_22 -> line_4710_22 -> line_4403_22 -> line_4401_22 -> line_4250_22 -> line_4251_22 -> line_4361_22 -> recloser_165_22 -> line_4360_22 -> switch_326_22 -> line_4095_22 -> line_4096_22 | GSO_141¦line_4096_22 | ACLineSegment | 600 | 12000 | Meter | br_021_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved |  | 250
127 | 25 | GSO_141 | line_4523_22 | S_nCCTT133 | 11.02 | High | 12.47 | 13.5424 | 0.016763 | 13.5256 | 0.37996 | 11.4 | 11.02 | br_021_22 | CircuitBreaker | Breaker | 11.4 | 0.37996 | 11.02 | 25 | 18 | 0 | 100 | 12.9167 | 0.14713 | -79.9624 | 36.0444 | recloser_168_22 -> line_4565_22 -> line_4566_22 -> line_6472_22 -> switch_765_22 -> line_6471_22 -> line_5658_22 -> switch_664_22 -> switch_524_22 -> line_4878_22 -> line_4879_22 -> recloser_183_22 -> line_5743_22 -> line_4709_22 -> line_4710_22 -> line_4403_22 -> line_4401_22 -> line_4250_22 -> line_4251_22 -> line_4361_22 -> recloser_165_22 -> line_4360_22 -> switch_502_22 -> line_4815_22 -> line_4523_22 | GSO_141¦line_4523_22 | ACLineSegment | 660 | 12000 | Meter | br_021_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved |  | 250
128 | 26 | GSO_141 | line_4887_22 | S_nCCTT1466_B_S_nCCTT1478 | 11.02 | High | 12.47 | 12.3112 | 0.0055876 | 12.3057 | 0.37996 | 11.4 | 11.02 | br_021_22 | CircuitBreaker | Breaker | 11.4 | 0.37996 | 11.02 | 25 | 18 | 0 | 100 | 12.9167 | 0.14713 | -79.962 | 36.0464 | recloser_168_22 -> line_4565_22 -> line_4566_22 -> line_6472_22 -> switch_765_22 -> line_6471_22 -> line_5658_22 -> switch_664_22 -> switch_524_22 -> line_4878_22 -> line_4879_22 -> recloser_183_22 -> line_5743_22 -> line_4709_22 -> line_4710_22 -> line_4403_22 -> line_4401_22 -> line_4250_22 -> line_4251_22 -> line_4361_22 -> recloser_165_22 -> line_4360_22 -> switch_502_22 -> line_4815_22 -> line_4887_22 | GSO_141¦line_4887_22 | ACLineSegment | 600 | 12000 | Meter | br_021_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved |  | 250
129 | 27 | GSO_141 | line_4522_22 | S_nCCTT1358 | 11.02 | High | 12.47 | 13.5424 | 0.011175 | 13.5312 | 0.37996 | 11.4 | 11.02 | br_021_22 | CircuitBreaker | Breaker | 11.4 | 0.37996 | 11.02 | 26 | 19 | 0 | 100 | 12.9167 | 0.14713 | -79.9636 | 36.044 | recloser_168_22 -> line_4565_22 -> line_4566_22 -> line_6472_22 -> switch_765_22 -> line_6471_22 -> line_5658_22 -> switch_664_22 -> switch_524_22 -> line_4878_22 -> line_4879_22 -> recloser_183_22 -> line_5743_22 -> line_4709_22 -> line_4710_22 -> line_4403_22 -> line_4401_22 -> line_4250_22 -> line_4251_22 -> line_4361_22 -> recloser_165_22 -> line_4360_22 -> switch_502_22 -> line_4815_22 -> line_4523_22 -> line_4522_22 | GSO_141¦line_4522_22 | ACLineSegment | 660 | 12000 | Meter | br_021_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved |  | 250
130 | 28 | GSO_141 | line_4602_22 | S_nCCTT146 | 11.02 | High | 12.47 | 13.5424 | 0.0055876 | 13.5368 | 0.37996 | 11.4 | 11.02 | br_021_22 | CircuitBreaker | Breaker | 11.4 | 0.37996 | 11.02 | 27 | 20 | 0 | 100 | 12.9167 | 0.14713 | -79.9644 | 36.0441 | recloser_168_22 -> line_4565_22 -> line_4566_22 -> line_6472_22 -> switch_765_22 -> line_6471_22 -> line_5658_22 -> switch_664_22 -> switch_524_22 -> line_4878_22 -> line_4879_22 -> recloser_183_22 -> line_5743_22 -> line_4709_22 -> line_4710_22 -> line_4403_22 -> line_4401_22 -> line_4250_22 -> line_4251_22 -> line_4361_22 -> recloser_165_22 -> line_4360_22 -> switch_502_22 -> line_4815_22 -> line_4523_22 -> line_4522_22 -> line_4602_22 | GSO_141¦line_4602_22 | ACLineSegment | 660 | 12000 | Meter | br_021_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved |  | 250
131 | 29 | GSO_141 | line_4300_22 | S_nCCTT94 | 11.02 | High | 12.47 | 12.3112 | 0.10616 | 12.2051 | 0.37996 | 11.4 | 11.02 | br_021_22 | CircuitBreaker | Breaker | 11.4 | 0.37996 | 11.02 | 28 | 19 | 0 | 100 | 12.9167 | 0.14713 | -79.959 | 36.0468 | recloser_168_22 -> line_4565_22 -> line_4566_22 -> line_6472_22 -> switch_765_22 -> line_6471_22 -> line_5658_22 -> switch_664_22 -> switch_524_22 -> line_4878_22 -> line_4879_22 -> recloser_183_22 -> line_5743_22 -> line_4709_22 -> line_4710_22 -> line_4403_22 -> line_4401_22 -> line_4250_22 -> line_4251_22 -> line_4361_22 -> recloser_165_22 -> line_4360_22 -> switch_326_22 -> line_4095_22 -> line_4094_22 -> switch_325_22 -> switch_388_22 -> line_4300_22 | GSO_141¦line_4300_22 | ACLineSegment | 600 | 12000 | Meter | br_021_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved |  | 250
132 | 30 | GSO_141 | line_6118_22 | S_nCCTT568 | 11.02 | High | 12.47 | 12.3112 | 0.011175 | 12.3001 | 0.37996 | 11.4 | 11.02 | br_021_22 | CircuitBreaker | Breaker | 11.4 | 0.37996 | 11.02 | 28 | 19 | 0 | 100 | 12.9167 | 0.14713 | -79.9573 | 36.0461 | recloser_168_22 -> line_4565_22 -> line_4566_22 -> line_6472_22 -> switch_765_22 -> line_6471_22 -> line_5658_22 -> switch_664_22 -> switch_524_22 -> line_4878_22 -> line_4879_22 -> recloser_183_22 -> line_5743_22 -> line_4709_22 -> line_4710_22 -> line_4403_22 -> line_4401_22 -> line_4250_22 -> line_4251_22 -> line_4361_22 -> recloser_165_22 -> line_4360_22 -> switch_326_22 -> line_4095_22 -> line_4096_22 -> switch_329_22 -> switch_735_22 -> line_6118_22 | GSO_141¦line_6118_22 | ACLineSegment | 600 | 12000 | Meter | br_021_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved |  | 250
133 | 31 | GSO_141 | line_4370_22 | S_nCCTT1278 | 11.02 | High | 12.47 | 12.3112 | 0.0055876 | 12.3057 | 0.37996 | 11.4 | 11.02 | br_021_22 | CircuitBreaker | Breaker | 11.4 | 0.37996 | 11.02 | 30 | 20 | 0 | 100 | 12.9167 | 0.14713 | -79.9565 | 36.0459 | recloser_168_22 -> line_4565_22 -> line_4566_22 -> line_6472_22 -> switch_765_22 -> line_6471_22 -> line_5658_22 -> switch_664_22 -> switch_524_22 -> line_4878_22 -> line_4879_22 -> recloser_183_22 -> line_5743_22 -> line_4709_22 -> line_4710_22 -> line_4403_22 -> line_4401_22 -> line_4250_22 -> line_4251_22 -> line_4361_22 -> recloser_165_22 -> line_4360_22 -> switch_326_22 -> line_4095_22 -> line_4096_22 -> switch_329_22 -> switch_735_22 -> line_6118_22 -> switch_404_22 -> line_4370_22 | GSO_141¦line_4370_22 | ACLineSegment | 600 | 12000 | Meter | br_021_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved |  | 250
134 | 32 | GSO_141 | line_5677_22 | S_nCCTT375 | 11.02 | High | 12.47 | 12.3112 | 0.10058 | 12.2107 | 0.37996 | 11.4 | 11.02 | br_021_22 | CircuitBreaker | Breaker | 11.4 | 0.37996 | 11.02 | 30 | 20 | 0 | 100 | 12.9167 | 0.14713 | -79.9589 | 36.0479 | recloser_168_22 -> line_4565_22 -> line_4566_22 -> line_6472_22 -> switch_765_22 -> line_6471_22 -> line_5658_22 -> switch_664_22 -> switch_524_22 -> line_4878_22 -> line_4879_22 -> recloser_183_22 -> line_5743_22 -> line_4709_22 -> line_4710_22 -> line_4403_22 -> line_4401_22 -> line_4250_22 -> line_4251_22 -> line_4361_22 -> recloser_165_22 -> line_4360_22 -> switch_326_22 -> line_4095_22 -> line_4094_22 -> switch_325_22 -> switch_388_22 -> line_4300_22 -> switch_669_22 -> line_5677_22 | GSO_141¦line_5677_22 | ACLineSegment | 600 | 12000 | Meter | br_021_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved |  | 250
135 | 33 | GSO_141 | line_5676_22 | S_nCCTT515 | 11.02 | High | 12.47 | 12.3112 | 0.094989 | 12.2163 | 0.37996 | 11.4 | 11.02 | br_021_22 | CircuitBreaker | Breaker | 11.4 | 0.37996 | 11.02 | 32 | 21 | 0 | 100 | 12.9167 | 0.14713 | -79.9575 | 36.0485 | recloser_168_22 -> line_4565_22 -> line_4566_22 -> line_6472_22 -> switch_765_22 -> line_6471_22 -> line_5658_22 -> switch_664_22 -> switch_524_22 -> line_4878_22 -> line_4879_22 -> recloser_183_22 -> line_5743_22 -> line_4709_22 -> line_4710_22 -> line_4403_22 -> line_4401_22 -> line_4250_22 -> line_4251_22 -> line_4361_22 -> recloser_165_22 -> line_4360_22 -> switch_326_22 -> line_4095_22 -> line_4094_22 -> switch_325_22 -> switch_388_22 -> line_4300_22 -> switch_669_22 -> line_5677_22 -> switch_667_22 -> line_5676_22 | GSO_141¦line_5676_22 | ACLineSegment | 600 | 12000 | Meter | br_021_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved |  | 250
136 | 34 | GSO_141 | line_6007_22 | S_nCCTT797 | 11.02 | High | 12.47 | 12.3112 | 0.089401 | 12.2218 | 0.37996 | 11.4 | 11.02 | br_021_22 | CircuitBreaker | Breaker | 11.4 | 0.37996 | 11.02 | 34 | 22 | 0 | 100 | 12.9167 | 0.14713 | -79.9556 | 36.049 | recloser_168_22 -> line_4565_22 -> line_4566_22 -> line_6472_22 -> switch_765_22 -> line_6471_22 -> line_5658_22 -> switch_664_22 -> switch_524_22 -> line_4878_22 -> line_4879_22 -> recloser_183_22 -> line_5743_22 -> line_4709_22 -> line_4710_22 -> line_4403_22 -> line_4401_22 -> line_4250_22 -> line_4251_22 -> line_4361_22 -> recloser_165_22 -> line_4360_22 -> switch_326_22 -> line_4095_22 -> line_4094_22 -> switch_325_22 -> switch_388_22 -> line_4300_22 -> switch_669_22 -> line_5677_22 -> switch_667_22 -> line_5676_22 -> switch_712_22 -> line_6007_22 | GSO_141¦line_6007_22 | ACLineSegment | 600 | 12000 | Meter | br_021_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved |  | 250
137 | 35 | GSO_141 | line_6175_22 | S_nCCTT797_B_S_nCCTT591 | 11.02 | High | 12.47 | 12.3112 | 0.072639 | 12.2386 | 0.37996 | 11.4 | 11.02 | br_021_22 | CircuitBreaker | Breaker | 11.4 | 0.37996 | 11.02 | 35 | 23 | 0 | 100 | 12.9167 | 0.14713 | -79.9551 | 36.0503 | recloser_168_22 -> line_4565_22 -> line_4566_22 -> line_6472_22 -> switch_765_22 -> line_6471_22 -> line_5658_22 -> switch_664_22 -> switch_524_22 -> line_4878_22 -> line_4879_22 -> recloser_183_22 -> line_5743_22 -> line_4709_22 -> line_4710_22 -> line_4403_22 -> line_4401_22 -> line_4250_22 -> line_4251_22 -> line_4361_22 -> recloser_165_22 -> line_4360_22 -> switch_326_22 -> line_4095_22 -> line_4094_22 -> switch_325_22 -> switch_388_22 -> line_4300_22 -> switch_669_22 -> line_5677_22 -> switch_667_22 -> line_5676_22 -> switch_712_22 -> line_6007_22 -> line_6175_22 | GSO_141¦line_6175_22 | ACLineSegment | 600 | 12000 | Meter | br_021_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved |  | 250
138 | 36 | GSO_141 | line_6241_22 | S_nCCTT619 | 11.02 | High | 12.47 | 12.3112 | 0.011175 | 12.3001 | 0.37996 | 11.4 | 11.02 | br_021_22 | CircuitBreaker | Breaker | 11.4 | 0.37996 | 11.02 | 36 | 23 | 0 | 100 | 12.9167 | 0.14713 | -79.9549 | 36.0491 | recloser_168_22 -> line_4565_22 -> line_4566_22 -> line_6472_22 -> switch_765_22 -> line_6471_22 -> line_5658_22 -> switch_664_22 -> switch_524_22 -> line_4878_22 -> line_4879_22 -> recloser_183_22 -> line_5743_22 -> line_4709_22 -> line_4710_22 -> line_4403_22 -> line_4401_22 -> line_4250_22 -> line_4251_22 -> line_4361_22 -> recloser_165_22 -> line_4360_22 -> switch_326_22 -> line_4095_22 -> line_4094_22 -> switch_325_22 -> switch_388_22 -> line_4300_22 -> switch_669_22 -> line_5677_22 -> switch_667_22 -> line_5676_22 -> switch_712_22 -> line_6007_22 -> switch_748_22 -> line_6241_22 | GSO_141¦line_6241_22 | ACLineSegment | 600 | 12000 | Meter | br_021_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved |  | 250
139 | 37 | GSO_141 | line_5932_22 | S_nCCTT619_B_S_nCCTT486 | 11.02 | High | 12.47 | 12.3112 | 0.0055876 | 12.3057 | 0.37996 | 11.4 | 11.02 | br_021_22 | CircuitBreaker | Breaker | 11.4 | 0.37996 | 11.02 | 37 | 24 | 0 | 100 | 12.9167 | 0.14713 | -79.9544 | 36.0487 | recloser_168_22 -> line_4565_22 -> line_4566_22 -> line_6472_22 -> switch_765_22 -> line_6471_22 -> line_5658_22 -> switch_664_22 -> switch_524_22 -> line_4878_22 -> line_4879_22 -> recloser_183_22 -> line_5743_22 -> line_4709_22 -> line_4710_22 -> line_4403_22 -> line_4401_22 -> line_4250_22 -> line_4251_22 -> line_4361_22 -> recloser_165_22 -> line_4360_22 -> switch_326_22 -> line_4095_22 -> line_4094_22 -> switch_325_22 -> switch_388_22 -> line_4300_22 -> switch_669_22 -> line_5677_22 -> switch_667_22 -> line_5676_22 -> switch_712_22 -> line_6007_22 -> switch_748_22 -> line_6241_22 -> line_5932_22 | GSO_141¦line_5932_22 | ACLineSegment | 600 | 12000 | Meter | br_021_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved |  | 250
140 | 38 | GSO_141 | line_6174_22 | S_nCCTT731 | 11.02 | High | 12.47 | 12.3112 | 0.067051 | 12.2442 | 0.37996 | 11.4 | 11.02 | br_021_22 | CircuitBreaker | Breaker | 11.4 | 0.37996 | 11.02 | 38 | 24 | 0 | 100 | 12.9167 | 0.14713 | -79.955 | 36.0515 | recloser_168_22 -> line_4565_22 -> line_4566_22 -> line_6472_22 -> switch_765_22 -> line_6471_22 -> line_5658_22 -> switch_664_22 -> switch_524_22 -> line_4878_22 -> line_4879_22 -> recloser_183_22 -> line_5743_22 -> line_4709_22 -> line_4710_22 -> line_4403_22 -> line_4401_22 -> line_4250_22 -> line_4251_22 -> line_4361_22 -> recloser_165_22 -> line_4360_22 -> switch_326_22 -> line_4095_22 -> line_4094_22 -> switch_325_22 -> switch_388_22 -> line_4300_22 -> switch_669_22 -> line_5677_22 -> switch_667_22 -> line_5676_22 -> switch_712_22 -> line_6007_22 -> line_6175_22 -> switch_743_22 -> switch_740_22 -> line_6174_22 | GSO_141¦line_6174_22 | ACLineSegment | 600 | 12000 | Meter | br_021_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved |  | 250
141 | 39 | GSO_141 | line_6294_22 | S_nCCTT646 | 11.02 | High | 12.47 | 12.3112 | 0.061463 | 12.2498 | 0.37996 | 11.4 | 11.02 | br_021_22 | CircuitBreaker | Breaker | 11.4 | 0.37996 | 11.02 | 40 | 25 | 0 | 100 | 12.9167 | 0.14713 | -79.9555 | 36.0522 | recloser_168_22 -> line_4565_22 -> line_4566_22 -> line_6472_22 -> switch_765_22 -> line_6471_22 -> line_5658_22 -> switch_664_22 -> switch_524_22 -> line_4878_22 -> line_4879_22 -> recloser_183_22 -> line_5743_22 -> line_4709_22 -> line_4710_22 -> line_4403_22 -> line_4401_22 -> line_4250_22 -> line_4251_22 -> line_4361_22 -> recloser_165_22 -> line_4360_22 -> switch_326_22 -> line_4095_22 -> line_4094_22 -> switch_325_22 -> switch_388_22 -> line_4300_22 -> switch_669_22 -> line_5677_22 -> switch_667_22 -> line_5676_22 -> switch_712_22 -> line_6007_22 -> line_6175_22 -> switch_743_22 -> switch_740_22 -> line_6174_22 -> switch_760_22 -> line_6294_22 | GSO_141¦line_6294_22 | ACLineSegment | 600 | 12000 | Meter | br_021_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved |  | 250
142 | 40 | GSO_141 | line_6060_22 | S_nCCTT543 | 11.02 | High | 12.47 | 12.3112 | 0.055876 | 12.2554 | 0.37996 | 11.4 | 11.02 | br_021_22 | CircuitBreaker | Breaker | 11.4 | 0.37996 | 11.02 | 42 | 26 | 0 | 100 | 12.9167 | 0.14713 | -79.9563 | 36.053 | recloser_168_22 -> line_4565_22 -> line_4566_22 -> line_6472_22 -> switch_765_22 -> line_6471_22 -> line_5658_22 -> switch_664_22 -> switch_524_22 -> line_4878_22 -> line_4879_22 -> recloser_183_22 -> line_5743_22 -> line_4709_22 -> line_4710_22 -> line_4403_22 -> line_4401_22 -> line_4250_22 -> line_4251_22 -> line_4361_22 -> recloser_165_22 -> line_4360_22 -> switch_326_22 -> line_4095_22 -> line_4094_22 -> switch_325_22 -> switch_388_22 -> line_4300_22 -> switch_669_22 -> line_5677_22 -> switch_667_22 -> line_5676_22 -> switch_712_22 -> line_6007_22 -> line_6175_22 -> switch_743_22 -> switch_740_22 -> line_6174_22 -> switch_760_22 -> line_6294_22 -> switch_728_22 -> line_6060_22 | GSO_141¦line_6060_22 | ACLineSegment | 600 | 12000 | Meter | br_021_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved |  | 250
143 | 41 | GSO_141 | line_4849_22 | S_nCCTT543_B_S_nCCTT1450 | 11.02 | High | 12.47 | 12.3112 | 0.0055876 | 12.3057 | 0.37996 | 11.4 | 11.02 | br_021_22 | CircuitBreaker | Breaker | 11.4 | 0.37996 | 11.02 | 43 | 27 | 0 | 100 | 12.9167 | 0.14713 | -79.9571 | 36.0523 | recloser_168_22 -> line_4565_22 -> line_4566_22 -> line_6472_22 -> switch_765_22 -> line_6471_22 -> line_5658_22 -> switch_664_22 -> switch_524_22 -> line_4878_22 -> line_4879_22 -> recloser_183_22 -> line_5743_22 -> line_4709_22 -> line_4710_22 -> line_4403_22 -> line_4401_22 -> line_4250_22 -> line_4251_22 -> line_4361_22 -> recloser_165_22 -> line_4360_22 -> switch_326_22 -> line_4095_22 -> line_4094_22 -> switch_325_22 -> switch_388_22 -> line_4300_22 -> switch_669_22 -> line_5677_22 -> switch_667_22 -> line_5676_22 -> switch_712_22 -> line_6007_22 -> line_6175_22 -> switch_743_22 -> switch_740_22 -> line_6174_22 -> switch_760_22 -> line_6294_22 -> switch_728_22 -> line_6060_22 -> line_4849_22 | GSO_141¦line_4849_22 | ACLineSegment | 600 | 12000 | Meter | br_021_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved |  | 250
144 | 42 | GSO_141 | line_6059_22 | S_nCCTT543_B_S_nCCTT598 | 11.02 | High | 12.47 | 12.3112 | 0.044701 | 12.2665 | 0.37996 | 11.4 | 11.02 | br_021_22 | CircuitBreaker | Breaker | 11.4 | 0.37996 | 11.02 | 43 | 27 | 0 | 100 | 12.9167 | 0.14713 | -79.9578 | 36.0529 | recloser_168_22 -> line_4565_22 -> line_4566_22 -> line_6472_22 -> switch_765_22 -> line_6471_22 -> line_5658_22 -> switch_664_22 -> switch_524_22 -> line_4878_22 -> line_4879_22 -> recloser_183_22 -> line_5743_22 -> line_4709_22 -> line_4710_22 -> line_4403_22 -> line_4401_22 -> line_4250_22 -> line_4251_22 -> line_4361_22 -> recloser_165_22 -> line_4360_22 -> switch_326_22 -> line_4095_22 -> line_4094_22 -> switch_325_22 -> switch_388_22 -> line_4300_22 -> switch_669_22 -> line_5677_22 -> switch_667_22 -> line_5676_22 -> switch_712_22 -> line_6007_22 -> line_6175_22 -> switch_743_22 -> switch_740_22 -> line_6174_22 -> switch_760_22 -> line_6294_22 -> switch_728_22 -> line_6060_22 -> line_6059_22 | GSO_141¦line_6059_22 | ACLineSegment | 600 | 12000 | Meter | br_021_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved |  | 250
145 | 43 | GSO_141 | line_4502_22 | S_nCCTT598_B_S_nCCTT1323 | 11.02 | High | 12.47 | 12.3112 | 0.0055876 | 12.3057 | 0.37996 | 11.4 | 11.02 | br_021_22 | CircuitBreaker | Breaker | 11.4 | 0.37996 | 11.02 | 45 | 28 | 0 | 100 | 12.9167 | 0.14713 | -79.9594 | 36.0522 | recloser_168_22 -> line_4565_22 -> line_4566_22 -> line_6472_22 -> switch_765_22 -> line_6471_22 -> line_5658_22 -> switch_664_22 -> switch_524_22 -> line_4878_22 -> line_4879_22 -> recloser_183_22 -> line_5743_22 -> line_4709_22 -> line_4710_22 -> line_4403_22 -> line_4401_22 -> line_4250_22 -> line_4251_22 -> line_4361_22 -> recloser_165_22 -> line_4360_22 -> switch_326_22 -> line_4095_22 -> line_4094_22 -> switch_325_22 -> switch_388_22 -> line_4300_22 -> switch_669_22 -> line_5677_22 -> switch_667_22 -> line_5676_22 -> switch_712_22 -> line_6007_22 -> line_6175_22 -> switch_743_22 -> switch_740_22 -> line_6174_22 -> switch_760_22 -> line_6294_22 -> switch_728_22 -> line_6060_22 -> line_6059_22 -> switch_727_22 -> line_4502_22 | GSO_141¦line_4502_22 | ACLineSegment | 600 | 12000 | Meter | br_021_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved |  | 250
146 | 44 | GSO_141 | line_4758_22 | S_nCCTT1414 | 11.02 | High | 12.47 | 12.3112 | 0.033526 | 12.2777 | 0.37996 | 11.4 | 11.02 | br_021_22 | CircuitBreaker | Breaker | 11.4 | 0.37996 | 11.02 | 46 | 28 | 0 | 100 | 12.9167 | 0.14713 | -79.9587 | 36.0531 | recloser_168_22 -> line_4565_22 -> line_4566_22 -> line_6472_22 -> switch_765_22 -> line_6471_22 -> line_5658_22 -> switch_664_22 -> switch_524_22 -> line_4878_22 -> line_4879_22 -> recloser_183_22 -> line_5743_22 -> line_4709_22 -> line_4710_22 -> line_4403_22 -> line_4401_22 -> line_4250_22 -> line_4251_22 -> line_4361_22 -> recloser_165_22 -> line_4360_22 -> switch_326_22 -> line_4095_22 -> line_4094_22 -> switch_325_22 -> switch_388_22 -> line_4300_22 -> switch_669_22 -> line_5677_22 -> switch_667_22 -> line_5676_22 -> switch_712_22 -> line_6007_22 -> line_6175_22 -> switch_743_22 -> switch_740_22 -> line_6174_22 -> switch_760_22 -> line_6294_22 -> switch_728_22 -> line_6060_22 -> line_6059_22 -> switch_727_22 -> switch_498_22 -> line_4758_22 | GSO_141¦line_4758_22 | ACLineSegment | 600 | 12000 | Meter | br_021_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved |  | 250
573 | 45 | GSO_141 | line_4258_22 | S_nCCTT1240 | 2.8154 | High | 7.2 | 2.8433 | 0.027938 | 2.8154 | 0.37996 | 11.4 | 11.02 | line_4258_22 | ACLineSegment | Line | 2.8433 | 0.027938 | 2.8154 | 48 | 29 | 0 | 100 | 12.9167 | 0.14713 | -79.9596 | 36.054 | recloser_168_22 -> line_4565_22 -> line_4566_22 -> line_6472_22 -> switch_765_22 -> line_6471_22 -> line_5658_22 -> switch_664_22 -> switch_524_22 -> line_4878_22 -> line_4879_22 -> recloser_183_22 -> line_5743_22 -> line_4709_22 -> line_4710_22 -> line_4403_22 -> line_4401_22 -> line_4250_22 -> line_4251_22 -> line_4361_22 -> recloser_165_22 -> line_4360_22 -> switch_326_22 -> line_4095_22 -> line_4094_22 -> switch_325_22 -> switch_388_22 -> line_4300_22 -> switch_669_22 -> line_5677_22 -> switch_667_22 -> line_5676_22 -> switch_712_22 -> line_6007_22 -> line_6175_22 -> switch_743_22 -> switch_740_22 -> line_6174_22 -> switch_760_22 -> line_6294_22 -> switch_728_22 -> line_6060_22 -> line_6059_22 -> switch_727_22 -> switch_498_22 -> line_4758_22 -> fuse_45_22 -> line_4258_22 | GSO_141¦line_4258_22 | ACLineSegment | 240 | 12000 | Meter | br_021_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.8154 | [6 empty] | SubstationCapacityUnresolved | line_4258_22 | Substation capacity unresolved |  | 250
574 | 46 | GSO_141 | line_4257_22 | S_nCCTT1300 | 2.8154 | High | 7.2 | 2.8433 | 0.02235 | 2.821 | 0.37996 | 11.4 | 11.02 | line_4258_22 | ACLineSegment | Line | 2.8433 | 0.027938 | 2.8154 | 49 | 30 | 0 | 100 | 12.9167 | 0.14713 | -79.9604 | 36.0551 | recloser_168_22 -> line_4565_22 -> line_4566_22 -> line_6472_22 -> switch_765_22 -> line_6471_22 -> line_5658_22 -> switch_664_22 -> switch_524_22 -> line_4878_22 -> line_4879_22 -> recloser_183_22 -> line_5743_22 -> line_4709_22 -> line_4710_22 -> line_4403_22 -> line_4401_22 -> line_4250_22 -> line_4251_22 -> line_4361_22 -> recloser_165_22 -> line_4360_22 -> switch_326_22 -> line_4095_22 -> line_4094_22 -> switch_325_22 -> switch_388_22 -> line_4300_22 -> switch_669_22 -> line_5677_22 -> switch_667_22 -> line_5676_22 -> switch_712_22 -> line_6007_22 -> line_6175_22 -> switch_743_22 -> switch_740_22 -> line_6174_22 -> switch_760_22 -> line_6294_22 -> switch_728_22 -> line_6060_22 -> line_6059_22 -> switch_727_22 -> switch_498_22 -> line_4758_22 -> fuse_45_22 -> line_4258_22 -> line_4257_22 | GSO_141¦line_4257_22 | ACLineSegment | 240 | 12000 | Meter | br_021_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.8154 | [6 empty] | SubstationCapacityUnresolved | line_4258_22 | Substation capacity unresolved |  | 250
575 | 47 | GSO_141 | line_4268_22 | S_nCCTT1244 | 2.8154 | High | 7.2 | 2.8433 | 0.0055876 | 2.8377 | 0.37996 | 11.4 | 11.02 | line_4258_22 | ACLineSegment | Line | 2.8433 | 0.027938 | 2.8154 | 50 | 31 | 0 | 100 | 12.9167 | 0.14713 | -79.9611 | 36.0556 | recloser_168_22 -> line_4565_22 -> line_4566_22 -> line_6472_22 -> switch_765_22 -> line_6471_22 -> line_5658_22 -> switch_664_22 -> switch_524_22 -> line_4878_22 -> line_4879_22 -> recloser_183_22 -> line_5743_22 -> line_4709_22 -> line_4710_22 -> line_4403_22 -> line_4401_22 -> line_4250_22 -> line_4251_22 -> line_4361_22 -> recloser_165_22 -> line_4360_22 -> switch_326_22 -> line_4095_22 -> line_4094_22 -> switch_325_22 -> switch_388_22 -> line_4300_22 -> switch_669_22 -> line_5677_22 -> switch_667_22 -> line_5676_22 -> switch_712_22 -> line_6007_22 -> line_6175_22 -> switch_743_22 -> switch_740_22 -> line_6174_22 -> switch_760_22 -> line_6294_22 -> switch_728_22 -> line_6060_22 -> line_6059_22 -> switch_727_22 -> switch_498_22 -> line_4758_22 -> fuse_45_22 -> line_4258_22 -> line_4257_22 -> line_4268_22 | GSO_141¦line_4268_22 | ACLineSegment | 240 | 12000 | Meter | br_021_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.8154 | [6 empty] | SubstationCapacityUnresolved | line_4258_22 | Substation capacity unresolved |  | 250
576 | 48 | GSO_141 | line_4437_22 | S_nCCTT235 | 2.8154 | High | 7.2 | 2.8433 | 0.011175 | 2.8322 | 0.37996 | 11.4 | 11.02 | line_4258_22 | ACLineSegment | Line | 2.8433 | 0.027938 | 2.8154 | 50 | 31 | 0 | 100 | 12.9167 | 0.14713 | -79.9595 | 36.0564 | recloser_168_22 -> line_4565_22 -> line_4566_22 -> line_6472_22 -> switch_765_22 -> line_6471_22 -> line_5658_22 -> switch_664_22 -> switch_524_22 -> line_4878_22 -> line_4879_22 -> recloser_183_22 -> line_5743_22 -> line_4709_22 -> line_4710_22 -> line_4403_22 -> line_4401_22 -> line_4250_22 -> line_4251_22 -> line_4361_22 -> recloser_165_22 -> line_4360_22 -> switch_326_22 -> line_4095_22 -> line_4094_22 -> switch_325_22 -> switch_388_22 -> line_4300_22 -> switch_669_22 -> line_5677_22 -> switch_667_22 -> line_5676_22 -> switch_712_22 -> line_6007_22 -> line_6175_22 -> switch_743_22 -> switch_740_22 -> line_6174_22 -> switch_760_22 -> line_6294_22 -> switch_728_22 -> line_6060_22 -> line_6059_22 -> switch_727_22 -> switch_498_22 -> line_4758_22 -> fuse_45_22 -> line_4258_22 -> line_4257_22 -> line_4437_22 | GSO_141¦line_4437_22 | ACLineSegment | 240 | 12000 | Meter | br_021_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.8154 | [6 empty] | SubstationCapacityUnresolved | line_4258_22 | Substation capacity unresolved |  | 250
216 | 1 | GSO_142 | line_5429_22 | S_nCCTT245 | 10.6074 | High | 12.47 | 13.5424 | 0.79259 | 12.7498 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 2 | 1 | 0 | 100 | 23.0833 | 0.26294 | -79.9532 | 36.0417 | recloser_177_22 -> line_5429_22 | GSO_142¦line_5429_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
217 | 2 | GSO_142 | line_5428_22 | S_nCCTT328 | 10.6074 | High | 12.47 | 13.5424 | 0.78693 | 12.7554 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 3 | 2 | 0 | 100 | 23.0833 | 0.26294 | -79.9596 | 36.037 | recloser_177_22 -> line_5429_22 -> line_5428_22 | GSO_142¦line_5428_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
218 | 3 | GSO_142 | line_5565_22 | S_nCCTT66 | 10.6074 | High | 12.47 | 13.5424 | 0.66238 | 12.88 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 4 | 3 | 0 | 100 | 23.0833 | 0.26294 | -79.96 | 36.0365 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 | GSO_142¦line_5565_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
219 | 4 | GSO_142 | line_4913_22 | S_nCCTT1477 | 10.6074 | High | 12.47 | 13.5424 | 0.11323 | 13.4291 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 4 | 3 | 0 | 100 | 23.0833 | 0.26294 | -79.9594 | 36.0363 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_4913_22 | GSO_142¦line_4913_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
220 | 5 | GSO_142 | line_5566_22 | S_nCCTT69 | 10.6074 | High | 12.47 | 13.5424 | 0.0056613 | 13.5367 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 4 | 3 | 0 | 100 | 23.0833 | 0.26294 | -79.9598 | 36.0364 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5566_22 | GSO_142¦line_5566_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
221 | 6 | GSO_142 | line_4904_22 | S_nCCTT1473 | 10.6074 | High | 12.47 | 13.5424 | 0.10757 | 13.4348 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 5 | 4 | 0 | 100 | 23.0833 | 0.26294 | -79.959 | 36.0362 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_4913_22 -> line_4904_22 | GSO_142¦line_4904_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
222 | 7 | GSO_142 | line_4684_22 | S_nCCTT1388 | 10.6074 | High | 12.47 | 13.5424 | 0.65672 | 12.8857 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 5 | 4 | 0 | 100 | 23.0833 | 0.26294 | -79.9605 | 36.0364 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 | GSO_142¦line_4684_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
223 | 8 | GSO_142 | line_4350_22 | S_nCCTT1272 | 10.6074 | High | 12.47 | 13.5424 | 0.011323 | 13.531 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 6 | 5 | 0 | 100 | 23.0833 | 0.26294 | -79.9606 | 36.0366 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4350_22 | GSO_142¦line_4350_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
224 | 9 | GSO_142 | line_3966_22 | S_nCCTT114 | 10.6074 | High | 12.47 | 13.5424 | 0.011323 | 13.531 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 6 | 5 | 0 | 100 | 23.0833 | 0.26294 | -79.9591 | 36.0359 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_4913_22 -> line_4904_22 -> line_3966_22 | GSO_142¦line_3966_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
225 | 10 | GSO_142 | line_4905_22 | S_nCCTT95 | 10.6074 | High | 12.47 | 13.5424 | 0.090581 | 13.4518 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 6 | 5 | 0 | 100 | 23.0833 | 0.26294 | -79.9585 | 36.036 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_4913_22 -> line_4904_22 -> line_4905_22 | GSO_142¦line_4905_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
226 | 11 | GSO_142 | line_4685_22 | S_nCCTT82 | 10.6074 | High | 12.47 | 13.5424 | 0.63973 | 12.9026 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 6 | 5 | 0 | 100 | 23.0833 | 0.26294 | -79.9609 | 36.0363 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 | GSO_142¦line_4685_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
227 | 12 | GSO_142 | line_4924_22 | S_nCCTT1483 | 10.6074 | High | 12.47 | 13.5424 | 0.08492 | 13.4574 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 7 | 6 | 0 | 100 | 23.0833 | 0.26294 | -79.9582 | 36.0361 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_4913_22 -> line_4904_22 -> line_4905_22 -> line_4924_22 | GSO_142¦line_4924_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
228 | 13 | GSO_142 | line_5427_22 | S_nCCTT244 | 10.6074 | High | 12.47 | 13.5424 | 0.63407 | 12.9083 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 7 | 6 | 0 | 100 | 23.0833 | 0.26294 | -79.9614 | 36.0363 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 | GSO_142¦line_5427_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
229 | 14 | GSO_142 | line_4528_22 | S_nCCTT1331 | 10.6074 | High | 12.47 | 13.5424 | 0.079259 | 13.4631 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 8 | 7 | 0 | 100 | 23.0833 | 0.26294 | -79.9583 | 36.0358 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_4913_22 -> line_4904_22 -> line_4905_22 -> line_4924_22 -> line_4528_22 | GSO_142¦line_4528_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
230 | 15 | GSO_142 | line_4889_22 | S_nCCTT1467 | 10.6074 | High | 12.47 | 13.5424 | 0.62841 | 12.914 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 8 | 7 | 0 | 100 | 23.0833 | 0.26294 | -79.9622 | 36.0363 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 | GSO_142¦line_4889_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
231 | 16 | GSO_142 | line_4527_22 | S_nCCTT1429 | 10.6074 | High | 12.47 | 13.5424 | 0.067936 | 13.4744 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 9 | 8 | 0 | 100 | 23.0833 | 0.26294 | -79.9582 | 36.0351 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_4913_22 -> line_4904_22 -> line_4905_22 -> line_4924_22 -> line_4528_22 -> line_4527_22 | GSO_142¦line_4527_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
232 | 17 | GSO_142 | line_3566_22 | S_nCCTT101 | 10.6074 | High | 12.47 | 13.5424 | 0.045291 | 13.4971 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 9 | 8 | 0 | 100 | 23.0833 | 0.26294 | -79.9628 | 36.0365 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_3566_22 | GSO_142¦line_3566_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
233 | 18 | GSO_142 | line_4608_22 | S_nCCTT136 | 10.6074 | High | 12.47 | 13.5424 | 0.57746 | 12.9649 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 9 | 8 | 0 | 100 | 23.0833 | 0.26294 | -79.9625 | 36.0361 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 | GSO_142¦line_4608_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
234 | 19 | GSO_142 | line_3565_22 | S_nCCTT1453 | 10.6074 | High | 12.47 | 13.5424 | 0.0056613 | 13.5367 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 10 | 9 | 0 | 100 | 23.0833 | 0.26294 | -79.9627 | 36.0372 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_3566_22 -> line_3565_22 | GSO_142¦line_3565_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
235 | 20 | GSO_142 | line_4439_22 | S_nCCTT1301 | 10.6074 | High | 12.47 | 13.5424 | 0.062275 | 13.4801 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 10 | 9 | 0 | 100 | 23.0833 | 0.26294 | -79.9588 | 36.0346 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_4913_22 -> line_4904_22 -> line_4905_22 -> line_4924_22 -> line_4528_22 -> line_4527_22 -> line_4439_22 | GSO_142¦line_4439_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
236 | 21 | GSO_142 | line_4609_22 | S_nCCTT1567 | 10.6074 | High | 12.47 | 13.5424 | 0.56613 | 12.9762 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 10 | 9 | 0 | 100 | 23.0833 | 0.26294 | -79.9631 | 36.0358 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 | GSO_142¦line_4609_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
237 | 22 | GSO_142 | line_4610_22 | S_nCCTT96 | 10.6074 | High | 12.47 | 13.5424 | 0.0056613 | 13.5367 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 10 | 9 | 0 | 100 | 23.0833 | 0.26294 | -79.9621 | 36.0357 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4610_22 | GSO_142¦line_4610_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
238 | 23 | GSO_142 | line_4440_22 | S_nCCTT1572 | 10.6074 | High | 12.47 | 13.5424 | 0.050952 | 13.4914 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 11 | 10 | 0 | 100 | 23.0833 | 0.26294 | -79.9591 | 36.0347 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_4913_22 -> line_4904_22 -> line_4905_22 -> line_4924_22 -> line_4528_22 -> line_4527_22 -> line_4439_22 -> line_4440_22 | GSO_142¦line_4440_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
239 | 24 | GSO_142 | line_4419_22 | S_nCCTT1295 | 10.6074 | High | 12.47 | 13.5424 | 0.0056613 | 13.5367 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 11 | 10 | 0 | 100 | 23.0833 | 0.26294 | -79.9584 | 36.0337 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_4913_22 -> line_4904_22 -> line_4905_22 -> line_4924_22 -> line_4528_22 -> line_4527_22 -> line_4439_22 -> line_4419_22 | GSO_142¦line_4419_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
240 | 25 | GSO_142 | line_4938_22 | S_nCCTT149 | 10.6074 | High | 12.47 | 13.5424 | 0.2491 | 13.2933 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 11 | 10 | 0 | 100 | 23.0833 | 0.26294 | -79.9642 | 36.0359 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_4938_22 | GSO_142¦line_4938_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
241 | 26 | GSO_142 | line_5129_22 | S_nCCTT256 | 10.6074 | High | 12.47 | 13.5424 | 0.31137 | 13.231 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 11 | 10 | 0 | 100 | 23.0833 | 0.26294 | -79.9635 | 36.0354 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_5129_22 | GSO_142¦line_5129_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
242 | 27 | GSO_142 | line_3988_22 | S_nCCTT115 | 10.6074 | High | 12.47 | 13.5424 | 0.045291 | 13.4971 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 12 | 11 | 0 | 100 | 23.0833 | 0.26294 | -79.9594 | 36.0349 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_4913_22 -> line_4904_22 -> line_4905_22 -> line_4924_22 -> line_4528_22 -> line_4527_22 -> line_4439_22 -> line_4440_22 -> line_3988_22 | GSO_142¦line_3988_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
243 | 28 | GSO_142 | line_4929_22 | S_nCCTT1486 | 10.6074 | High | 12.47 | 13.5424 | 0.011323 | 13.531 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 12 | 11 | 0 | 100 | 23.0833 | 0.26294 | -79.9657 | 36.0362 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_4938_22 -> line_4929_22 | GSO_142¦line_4929_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
244 | 29 | GSO_142 | line_4939_22 | S_nCCTT77 | 10.6074 | High | 12.47 | 13.5424 | 0.22645 | 13.3159 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 12 | 11 | 0 | 100 | 23.0833 | 0.26294 | -79.9649 | 36.0356 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_4938_22 -> line_4939_22 | GSO_142¦line_4939_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
245 | 30 | GSO_142 | line_5442_22 | S_nCCTT299 | 10.6074 | High | 12.47 | 13.5424 | 0.30571 | 13.2367 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 12 | 11 | 0 | 100 | 23.0833 | 0.26294 | -79.9634 | 36.035 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_5129_22 -> line_5442_22 | GSO_142¦line_5442_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
246 | 31 | GSO_142 | line_5463_22 | S_nCCTT269 | 10.6074 | High | 12.47 | 13.5424 | 0.30005 | 13.2423 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 13 | 12 | 0 | 100 | 23.0833 | 0.26294 | -79.9637 | 36.0345 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_5129_22 -> line_5442_22 -> line_5463_22 | GSO_142¦line_5463_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
247 | 32 | GSO_142 | line_4570_22 | S_nCCTT1346 | 10.6074 | High | 12.47 | 13.5424 | 0.0056613 | 13.5367 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 13 | 12 | 0 | 100 | 23.0833 | 0.26294 | -79.9665 | 36.0375 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_4938_22 -> line_4929_22 -> line_4570_22 | GSO_142¦line_4570_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
248 | 33 | GSO_142 | line_5117_22 | S_nCCTT1562 | 10.6074 | High | 12.47 | 13.5424 | 0.22079 | 13.3216 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 13 | 12 | 0 | 100 | 23.0833 | 0.26294 | -79.9653 | 36.0351 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_4938_22 -> line_4939_22 -> line_5117_22 | GSO_142¦line_5117_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
249 | 34 | GSO_142 | line_3913_22 | S_nCCTT112 | 10.6074 | High | 12.47 | 13.5424 | 0.29439 | 13.248 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 14 | 13 | 0 | 100 | 23.0833 | 0.26294 | -79.9639 | 36.034 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_5129_22 -> line_5442_22 -> line_5463_22 -> line_3913_22 | GSO_142¦line_3913_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
250 | 35 | GSO_142 | line_3989_22 | S_nCCTT250 | 10.6074 | High | 12.47 | 13.5424 | 0.039629 | 13.5027 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 14 | 12 | 0 | 100 | 23.0833 | 0.26294 | -79.9601 | 36.0347 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_4913_22 -> line_4904_22 -> line_4905_22 -> line_4924_22 -> line_4528_22 -> line_4527_22 -> line_4439_22 -> line_4440_22 -> line_3988_22 -> switch_291_22 -> line_3989_22 | GSO_142¦line_3989_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
251 | 36 | GSO_142 | line_4875_22 | S_nCCTT1462 | 10.6074 | High | 12.47 | 13.5424 | 0.21513 | 13.3272 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 14 | 13 | 0 | 100 | 23.0833 | 0.26294 | -79.9656 | 36.0348 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_4938_22 -> line_4939_22 -> line_5117_22 -> line_4875_22 | GSO_142¦line_4875_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
252 | 37 | GSO_142 | line_3912_22 | S_nCCTT158 | 10.6074 | High | 12.47 | 13.5424 | 0.28873 | 13.2536 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 15 | 14 | 0 | 100 | 23.0833 | 0.26294 | -79.9635 | 36.0337 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_5129_22 -> line_5442_22 -> line_5463_22 -> line_3913_22 -> line_3912_22 | GSO_142¦line_3912_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
253 | 38 | GSO_142 | line_4560_22 | S_nCCTT1343 | 10.6074 | High | 12.47 | 13.5424 | 0.033968 | 13.5084 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 15 | 13 | 0 | 100 | 23.0833 | 0.26294 | -79.9612 | 36.0344 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_4913_22 -> line_4904_22 -> line_4905_22 -> line_4924_22 -> line_4528_22 -> line_4527_22 -> line_4439_22 -> line_4440_22 -> line_3988_22 -> switch_291_22 -> line_3989_22 -> line_4560_22 | GSO_142¦line_4560_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
254 | 39 | GSO_142 | line_4876_22 | S_nCCTT419 | 10.6074 | High | 12.47 | 13.5424 | 0.20947 | 13.3329 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 15 | 14 | 0 | 100 | 23.0833 | 0.26294 | -79.9656 | 36.0344 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_4938_22 -> line_4939_22 -> line_5117_22 -> line_4875_22 -> line_4876_22 | GSO_142¦line_4876_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
255 | 40 | GSO_142 | line_5156_22 | S_nCCTT305 | 10.6074 | High | 12.47 | 13.5424 | 0 | 13.5424 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 16 | 14 | 0 | 100 | 23.0833 | 0.26294 | -79.9628 | 36.034 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_4913_22 -> line_4904_22 -> line_4905_22 -> line_4924_22 -> line_4528_22 -> line_4527_22 -> line_4439_22 -> line_4440_22 -> line_3988_22 -> switch_291_22 -> line_3989_22 -> line_4560_22 -> line_4561_22 | GSO_142¦line_5156_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
256 | 41 | GSO_142 | line_5157_22 | S_nCCTT158_B_S_nCCTT76 | 10.6074 | High | 12.47 | 12.3112 | 0.28307 | 12.0282 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 16 | 15 | 0 | 100 | 23.0833 | 0.26294 | -79.9631 | 36.0333 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_5129_22 -> line_5442_22 -> line_5463_22 -> line_3913_22 -> line_3912_22 -> line_5157_22 | GSO_142¦line_5157_22 | ACLineSegment | 600 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
257 | 42 | GSO_142 | line_4561_22 | S_nCCTT305 | 10.6074 | High | 12.47 | 13.5424 | 0.0056613 | 13.5367 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 16 | 14 | 0 | 100 | 23.0833 | 0.26294 | -79.9622 | 36.0343 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_4913_22 -> line_4904_22 -> line_4905_22 -> line_4924_22 -> line_4528_22 -> line_4527_22 -> line_4439_22 -> line_4440_22 -> line_3988_22 -> switch_291_22 -> line_3989_22 -> line_4560_22 -> line_4561_22 | GSO_142¦line_4561_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
258 | 43 | GSO_142 | line_4562_22 | S_nCCTT98 | 10.6074 | High | 12.47 | 13.5424 | 0.022645 | 13.5197 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 16 | 14 | 0 | 100 | 23.0833 | 0.26294 | -79.9616 | 36.0341 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_4913_22 -> line_4904_22 -> line_4905_22 -> line_4924_22 -> line_4528_22 -> line_4527_22 -> line_4439_22 -> line_4440_22 -> line_3988_22 -> switch_291_22 -> line_3989_22 -> line_4560_22 -> line_4562_22 | GSO_142¦line_4562_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
259 | 44 | GSO_142 | line_5777_22 | S_nCCTT93 | 10.6074 | High | 12.47 | 13.5424 | 0.20381 | 13.3386 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 16 | 15 | 0 | 100 | 23.0833 | 0.26294 | -79.9663 | 36.0341 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_4938_22 -> line_4939_22 -> line_5117_22 -> line_4875_22 -> line_4876_22 -> line_5777_22 | GSO_142¦line_5777_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
260 | 45 | GSO_142 | line_4717_22 | S_nCCTT140 | 10.6074 | High | 12.47 | 13.5424 | 0.016984 | 13.5254 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 17 | 15 | 0 | 100 | 23.0833 | 0.26294 | -79.9612 | 36.0336 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_4913_22 -> line_4904_22 -> line_4905_22 -> line_4924_22 -> line_4528_22 -> line_4527_22 -> line_4439_22 -> line_4440_22 -> line_3988_22 -> switch_291_22 -> line_3989_22 -> line_4560_22 -> line_4562_22 -> line_4717_22 | GSO_142¦line_4717_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
261 | 46 | GSO_142 | line_4716_22 | S_nCCTT1476 | 10.6074 | High | 12.47 | 13.5424 | 0.011323 | 13.531 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 18 | 16 | 0 | 100 | 23.0833 | 0.26294 | -79.9601 | 36.0328 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_4913_22 -> line_4904_22 -> line_4905_22 -> line_4924_22 -> line_4528_22 -> line_4527_22 -> line_4439_22 -> line_4440_22 -> line_3988_22 -> switch_291_22 -> line_3989_22 -> line_4560_22 -> line_4562_22 -> line_4717_22 -> line_4716_22 | GSO_142¦line_4716_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
262 | 47 | GSO_142 | line_4554_22 | S_nCCTT134 | 10.6074 | High | 12.47 | 12.3112 | 0.19249 | 12.1188 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 18 | 16 | 0 | 100 | 23.0833 | 0.26294 | -79.9675 | 36.0341 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_4938_22 -> line_4939_22 -> line_5117_22 -> line_4875_22 -> line_4876_22 -> line_5777_22 -> switch_450_22 -> line_4554_22 | GSO_142¦line_4554_22 | ACLineSegment | 600 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
263 | 48 | GSO_142 | line_6503_22 | S_nCCTT88 | 10.6074 | High | 12.47 | 12.3112 | 0.27741 | 12.0338 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 19 | 16 | 0 | 100 | 23.0833 | 0.26294 | -79.9633 | 36.0327 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_5129_22 -> line_5442_22 -> line_5463_22 -> line_3913_22 -> line_3912_22 -> line_5157_22 -> switch_582_22 -> switch_769_22 -> line_6503_22 | GSO_142¦line_6503_22 | ACLineSegment | 600 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
264 | 49 | GSO_142 | line_4545_22 | S_nCCTT134_B_S_nCCTT1338 | 10.6074 | High | 12.47 | 12.3112 | 0.1755 | 12.1357 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 19 | 17 | 0 | 100 | 23.0833 | 0.26294 | -79.9681 | 36.0343 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_4938_22 -> line_4939_22 -> line_5117_22 -> line_4875_22 -> line_4876_22 -> line_5777_22 -> switch_450_22 -> line_4554_22 -> line_4545_22 | GSO_142¦line_4545_22 | ACLineSegment | 600 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
265 | 50 | GSO_142 | line_4553_22 | S_nCCTT134_B_S_nCCTT1352 | 10.6074 | High | 12.47 | 12.3112 | 0.011323 | 12.2999 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 19 | 17 | 0 | 100 | 23.0833 | 0.26294 | -79.9676 | 36.0344 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_4938_22 -> line_4939_22 -> line_5117_22 -> line_4875_22 -> line_4876_22 -> line_5777_22 -> switch_450_22 -> line_4554_22 -> line_4553_22 | GSO_142¦line_4553_22 | ACLineSegment | 600 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
266 | 51 | GSO_142 | line_3663_22 | S_nCCTT88_B_S_nCCTT104 | 10.6074 | High | 12.47 | 12.3112 | 0.27174 | 12.0395 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 20 | 17 | 0 | 100 | 23.0833 | 0.26294 | -79.9628 | 36.0322 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_5129_22 -> line_5442_22 -> line_5463_22 -> line_3913_22 -> line_3912_22 -> line_5157_22 -> switch_582_22 -> switch_769_22 -> line_6503_22 -> line_3663_22 | GSO_142¦line_3663_22 | ACLineSegment | 600 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
267 | 52 | GSO_142 | line_4546_22 | S_nCCTT1338_B_S_nCCTT1350 | 10.6074 | High | 12.47 | 12.3112 | 0.16984 | 12.1414 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 21 | 18 | 0 | 100 | 23.0833 | 0.26294 | -79.9685 | 36.0344 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_4938_22 -> line_4939_22 -> line_5117_22 -> line_4875_22 -> line_4876_22 -> line_5777_22 -> switch_450_22 -> line_4554_22 -> line_4545_22 -> switch_445_22 -> line_4546_22 | GSO_142¦line_4546_22 | ACLineSegment | 600 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
268 | 53 | GSO_142 | line_3662_22 | S_nCCTT266 | 10.6074 | High | 12.47 | 12.3112 | 0.26042 | 12.0508 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 23 | 18 | 0 | 100 | 23.0833 | 0.26294 | -79.9624 | 36.0318 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_5129_22 -> line_5442_22 -> line_5463_22 -> line_3913_22 -> line_3912_22 -> line_5157_22 -> switch_582_22 -> switch_769_22 -> line_6503_22 -> line_3663_22 -> switch_229_22 -> switch_226_22 -> line_3662_22 | GSO_142¦line_3662_22 | ACLineSegment | 600 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
269 | 54 | GSO_142 | line_4584_22 | S_nCCTT1350_B_S_nCCTT1554 | 10.6074 | High | 12.47 | 12.3112 | 0.15852 | 12.1527 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 23 | 19 | 0 | 100 | 23.0833 | 0.26294 | -79.9689 | 36.0342 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_4938_22 -> line_4939_22 -> line_5117_22 -> line_4875_22 -> line_4876_22 -> line_5777_22 -> switch_450_22 -> line_4554_22 -> line_4545_22 -> switch_445_22 -> line_4546_22 -> switch_447_22 -> line_4584_22 | GSO_142¦line_4584_22 | ACLineSegment | 600 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
270 | 55 | GSO_142 | line_4864_22 | S_nCCTT1457 | 10.6074 | High | 12.47 | 12.3112 | 0.25476 | 12.0565 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 25 | 19 | 0 | 100 | 23.0833 | 0.26294 | -79.9625 | 36.0317 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_5129_22 -> line_5442_22 -> line_5463_22 -> line_3913_22 -> line_3912_22 -> line_5157_22 -> switch_582_22 -> switch_769_22 -> line_6503_22 -> line_3663_22 -> switch_229_22 -> switch_226_22 -> line_3662_22 -> switch_516_22 -> line_4864_22 | GSO_142¦line_4864_22 | ACLineSegment | 600 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
271 | 56 | GSO_142 | line_5099_22 | S_nCCTT1554_B_UCMV27 | 10.6074 | High | 12.47 | 12.3112 | 0.011323 | 12.2999 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 25 | 20 | 0 | 100 | 23.0833 | 0.26294 | -79.9693 | 36.0345 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_4938_22 -> line_4939_22 -> line_5117_22 -> line_4875_22 -> line_4876_22 -> line_5777_22 -> switch_450_22 -> line_4554_22 -> line_4545_22 -> switch_445_22 -> line_4546_22 -> switch_447_22 -> line_4584_22 -> switch_462_22 -> line_5099_22 | GSO_142¦line_5099_22 | ACLineSegment | 600 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
272 | 57 | GSO_142 | line_4908_22 | S_nCCTT1474 | 10.6074 | High | 12.47 | 12.3112 | 0.14153 | 12.1697 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 26 | 20 | 0 | 100 | 23.0833 | 0.26294 | -79.9691 | 36.0338 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_4938_22 -> line_4939_22 -> line_5117_22 -> line_4875_22 -> line_4876_22 -> line_5777_22 -> switch_450_22 -> line_4554_22 -> line_4545_22 -> switch_445_22 -> line_4546_22 -> switch_447_22 -> line_4584_22 -> switch_462_22 -> switch_532_22 -> line_4908_22 | GSO_142¦line_4908_22 | ACLineSegment | 600 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
273 | 58 | GSO_142 | line_4658_22 | S_nCCTT1377 | 10.6074 | High | 12.47 | 12.3112 | 0.24344 | 12.0678 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 27 | 20 | 0 | 100 | 23.0833 | 0.26294 | -79.963 | 36.0315 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_5129_22 -> line_5442_22 -> line_5463_22 -> line_3913_22 -> line_3912_22 -> line_5157_22 -> switch_582_22 -> switch_769_22 -> line_6503_22 -> line_3663_22 -> switch_229_22 -> switch_226_22 -> line_3662_22 -> switch_516_22 -> line_4864_22 -> switch_475_22 -> line_4658_22 | GSO_142¦line_4658_22 | ACLineSegment | 600 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
274 | 59 | GSO_142 | line_4907_22 | S_nCCTT1474_B_S_nCCTT155 | 10.6074 | High | 12.47 | 12.3112 | 0.13587 | 12.1754 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 27 | 21 | 0 | 100 | 23.0833 | 0.26294 | -79.9687 | 36.0336 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_4938_22 -> line_4939_22 -> line_5117_22 -> line_4875_22 -> line_4876_22 -> line_5777_22 -> switch_450_22 -> line_4554_22 -> line_4545_22 -> switch_445_22 -> line_4546_22 -> switch_447_22 -> line_4584_22 -> switch_462_22 -> switch_532_22 -> line_4908_22 -> line_4907_22 | GSO_142¦line_4907_22 | ACLineSegment | 600 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
275 | 60 | GSO_142 | line_4935_22 | S_nCCTT1489 | 10.6074 | High | 12.47 | 12.3112 | 0.0056613 | 12.3056 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 28 | 21 | 0 | 100 | 23.0833 | 0.26294 | -79.9691 | 36.0353 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_4938_22 -> line_4939_22 -> line_5117_22 -> line_4875_22 -> line_4876_22 -> line_5777_22 -> switch_450_22 -> line_4554_22 -> line_4545_22 -> switch_445_22 -> line_4546_22 -> switch_447_22 -> line_4584_22 -> switch_462_22 -> line_5099_22 -> switch_560_22 -> switch_534_22 -> line_4935_22 | GSO_142¦line_4935_22 | ACLineSegment | 600 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
276 | 61 | GSO_142 | line_3984_22 | S_nCCTT155_B_S_nCCTT1147 | 10.6074 | High | 12.47 | 12.3112 | 0.13021 | 12.181 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 29 | 22 | 0 | 100 | 23.0833 | 0.26294 | -79.9684 | 36.0334 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_4938_22 -> line_4939_22 -> line_5117_22 -> line_4875_22 -> line_4876_22 -> line_5777_22 -> switch_450_22 -> line_4554_22 -> line_4545_22 -> switch_445_22 -> line_4546_22 -> switch_447_22 -> line_4584_22 -> switch_462_22 -> switch_532_22 -> line_4908_22 -> line_4907_22 -> switch_531_22 -> line_3984_22 | GSO_142¦line_3984_22 | ACLineSegment | 600 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
277 | 62 | GSO_142 | line_4391_22 | S_nCCTT1286 | 10.6074 | High | 12.47 | 12.3112 | 0.23778 | 12.0735 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 29 | 21 | 0 | 100 | 23.0833 | 0.26294 | -79.9634 | 36.0304 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_5129_22 -> line_5442_22 -> line_5463_22 -> line_3913_22 -> line_3912_22 -> line_5157_22 -> switch_582_22 -> switch_769_22 -> line_6503_22 -> line_3663_22 -> switch_229_22 -> switch_226_22 -> line_3662_22 -> switch_516_22 -> line_4864_22 -> switch_475_22 -> line_4658_22 -> switch_411_22 -> line_4391_22 | GSO_142¦line_4391_22 | ACLineSegment | 600 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
278 | 63 | GSO_142 | line_4392_22 | S_nCCTT1443 | 10.6074 | High | 12.47 | 12.3112 | 0.22079 | 12.0905 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 31 | 22 | 0 | 100 | 23.0833 | 0.26294 | -79.9641 | 36.0292 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_5129_22 -> line_5442_22 -> line_5463_22 -> line_3913_22 -> line_3912_22 -> line_5157_22 -> switch_582_22 -> switch_769_22 -> line_6503_22 -> line_3663_22 -> switch_229_22 -> switch_226_22 -> line_3662_22 -> switch_516_22 -> line_4864_22 -> switch_475_22 -> line_4658_22 -> switch_411_22 -> line_4391_22 -> switch_413_22 -> line_4392_22 | GSO_142¦line_4392_22 | ACLineSegment | 600 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
279 | 64 | GSO_142 | line_4393_22 | S_nCCTT208 | 10.6074 | High | 12.47 | 12.3112 | 0.011323 | 12.2999 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 31 | 22 | 0 | 100 | 23.0833 | 0.26294 | -79.9633 | 36.0293 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_5129_22 -> line_5442_22 -> line_5463_22 -> line_3913_22 -> line_3912_22 -> line_5157_22 -> switch_582_22 -> switch_769_22 -> line_6503_22 -> line_3663_22 -> switch_229_22 -> switch_226_22 -> line_3662_22 -> switch_516_22 -> line_4864_22 -> switch_475_22 -> line_4658_22 -> switch_411_22 -> line_4391_22 -> switch_414_22 -> line_4393_22 | GSO_142¦line_4393_22 | ACLineSegment | 600 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
280 | 65 | GSO_142 | line_3983_22 | S_nCCTT143 | 10.6074 | High | 12.47 | 13.5424 | 0.11323 | 13.4291 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 32 | 23 | 0 | 100 | 23.0833 | 0.26294 | -79.9677 | 36.033 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_4938_22 -> line_4939_22 -> line_5117_22 -> line_4875_22 -> line_4876_22 -> line_5777_22 -> switch_450_22 -> line_4554_22 -> line_4545_22 -> switch_445_22 -> line_4546_22 -> switch_447_22 -> line_4584_22 -> switch_462_22 -> switch_532_22 -> line_4908_22 -> line_4907_22 -> switch_531_22 -> line_3984_22 -> switch_290_22 -> recloser_157_22 -> line_3983_22 | GSO_142¦line_3983_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
281 | 66 | GSO_142 | line_4830_22 | S_nCCTT315_A_S_nCCTT1443 | 10.6074 | High | 12.47 | 12.3112 | 0.21513 | 12.0961 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 32 | 23 | 0 | 100 | 23.0833 | 0.26294 | -79.9647 | 36.0293 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_5129_22 -> line_5442_22 -> line_5463_22 -> line_3913_22 -> line_3912_22 -> line_5157_22 -> switch_582_22 -> switch_769_22 -> line_6503_22 -> line_3663_22 -> switch_229_22 -> switch_226_22 -> line_3662_22 -> switch_516_22 -> line_4864_22 -> switch_475_22 -> line_4658_22 -> switch_411_22 -> line_4391_22 -> switch_413_22 -> line_4392_22 -> line_4830_22 | GSO_142¦line_4830_22 | ACLineSegment | 600 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
282 | 67 | GSO_142 | line_4796_22 | S_nCCTT70 | 10.6074 | High | 12.47 | 13.5424 | 0.011323 | 13.531 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 33 | 24 | 0 | 100 | 23.0833 | 0.26294 | -79.9673 | 36.0328 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_4938_22 -> line_4939_22 -> line_5117_22 -> line_4875_22 -> line_4876_22 -> line_5777_22 -> switch_450_22 -> line_4554_22 -> line_4545_22 -> switch_445_22 -> line_4546_22 -> switch_447_22 -> line_4584_22 -> switch_462_22 -> switch_532_22 -> line_4908_22 -> line_4907_22 -> switch_531_22 -> line_3984_22 -> switch_290_22 -> recloser_157_22 -> line_3983_22 -> line_4796_22 | GSO_142¦line_4796_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
283 | 68 | GSO_142 | line_3886_22 | S_nCCTT111 | 10.6074 | High | 12.47 | 13.5424 | 0.096243 | 13.4461 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 33 | 24 | 0 | 100 | 23.0833 | 0.26294 | -79.9675 | 36.0325 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_4938_22 -> line_4939_22 -> line_5117_22 -> line_4875_22 -> line_4876_22 -> line_5777_22 -> switch_450_22 -> line_4554_22 -> line_4545_22 -> switch_445_22 -> line_4546_22 -> switch_447_22 -> line_4584_22 -> switch_462_22 -> switch_532_22 -> line_4908_22 -> line_4907_22 -> switch_531_22 -> line_3984_22 -> switch_290_22 -> recloser_157_22 -> line_3983_22 -> line_3886_22 | GSO_142¦line_3886_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
284 | 69 | GSO_142 | line_5345_22 | S_nCCTT92 | 10.6074 | High | 12.47 | 12.3112 | 0.0056613 | 12.3056 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 33 | 23 | 0 | 100 | 23.0833 | 0.26294 | -79.9631 | 36.0289 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_5129_22 -> line_5442_22 -> line_5463_22 -> line_3913_22 -> line_3912_22 -> line_5157_22 -> switch_582_22 -> switch_769_22 -> line_6503_22 -> line_3663_22 -> switch_229_22 -> switch_226_22 -> line_3662_22 -> switch_516_22 -> line_4864_22 -> switch_475_22 -> line_4658_22 -> switch_411_22 -> line_4391_22 -> switch_414_22 -> line_4393_22 -> switch_614_22 -> line_5345_22 | GSO_142¦line_5345_22 | ACLineSegment | 600 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
285 | 70 | GSO_142 | line_5111_22 | S_nCCTT315_B_S_nCCTT1559 | 10.6074 | High | 12.47 | 12.3112 | 0.20381 | 12.1074 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 34 | 24 | 0 | 100 | 23.0833 | 0.26294 | -79.9657 | 36.0293 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_5129_22 -> line_5442_22 -> line_5463_22 -> line_3913_22 -> line_3912_22 -> line_5157_22 -> switch_582_22 -> switch_769_22 -> line_6503_22 -> line_3663_22 -> switch_229_22 -> switch_226_22 -> line_3662_22 -> switch_516_22 -> line_4864_22 -> switch_475_22 -> line_4658_22 -> switch_411_22 -> line_4391_22 -> switch_413_22 -> line_4392_22 -> line_4830_22 -> switch_504_22 -> line_5111_22 | GSO_142¦line_5111_22 | ACLineSegment | 600 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
286 | 71 | GSO_142 | line_3885_22 | S_nCCTT1242 | 10.6074 | High | 12.47 | 12.3112 | 0.011323 | 12.2999 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 35 | 25 | 0 | 100 | 23.0833 | 0.26294 | -79.9669 | 36.0316 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_4938_22 -> line_4939_22 -> line_5117_22 -> line_4875_22 -> line_4876_22 -> line_5777_22 -> switch_450_22 -> line_4554_22 -> line_4545_22 -> switch_445_22 -> line_4546_22 -> switch_447_22 -> line_4584_22 -> switch_462_22 -> switch_532_22 -> line_4908_22 -> line_4907_22 -> switch_531_22 -> line_3984_22 -> switch_290_22 -> recloser_157_22 -> line_3983_22 -> line_3886_22 -> switch_263_22 -> line_3885_22 | GSO_142¦line_3885_22 | ACLineSegment | 600 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
287 | 72 | GSO_142 | line_3887_22 | S_nCCTT395 | 10.6074 | High | 12.47 | 12.3112 | 0.079259 | 12.232 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 35 | 25 | 0 | 100 | 23.0833 | 0.26294 | -79.9679 | 36.032 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_4938_22 -> line_4939_22 -> line_5117_22 -> line_4875_22 -> line_4876_22 -> line_5777_22 -> switch_450_22 -> line_4554_22 -> line_4545_22 -> switch_445_22 -> line_4546_22 -> switch_447_22 -> line_4584_22 -> switch_462_22 -> switch_532_22 -> line_4908_22 -> line_4907_22 -> switch_531_22 -> line_3984_22 -> switch_290_22 -> recloser_157_22 -> line_3983_22 -> line_3886_22 -> switch_265_22 -> line_3887_22 | GSO_142¦line_3887_22 | ACLineSegment | 600 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
288 | 73 | GSO_142 | line_5168_22 | S_nCCTT1584 | 10.6074 | High | 12.47 | 12.3112 | 0.0056613 | 12.3056 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 35 | 24 | 0 | 100 | 23.0833 | 0.26294 | -79.9653 | 36.0303 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_5129_22 -> line_5442_22 -> line_5463_22 -> line_3913_22 -> line_3912_22 -> line_5157_22 -> switch_582_22 -> switch_769_22 -> line_6503_22 -> line_3663_22 -> switch_229_22 -> switch_226_22 -> line_3662_22 -> switch_516_22 -> line_4864_22 -> switch_475_22 -> line_4658_22 -> switch_411_22 -> line_4391_22 -> switch_413_22 -> line_4392_22 -> line_4830_22 -> switch_504_22 -> switch_586_22 -> line_5168_22 | GSO_142¦line_5168_22 | ACLineSegment | 600 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
289 | 74 | GSO_142 | line_4582_22 | S_nCCTT395_B_S_nCCTT135 | 10.6074 | High | 12.47 | 12.3112 | 0.073597 | 12.2376 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 36 | 26 | 0 | 100 | 23.0833 | 0.26294 | -79.9684 | 36.0316 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_4938_22 -> line_4939_22 -> line_5117_22 -> line_4875_22 -> line_4876_22 -> line_5777_22 -> switch_450_22 -> line_4554_22 -> line_4545_22 -> switch_445_22 -> line_4546_22 -> switch_447_22 -> line_4584_22 -> switch_462_22 -> switch_532_22 -> line_4908_22 -> line_4907_22 -> switch_531_22 -> line_3984_22 -> switch_290_22 -> recloser_157_22 -> line_3983_22 -> line_3886_22 -> switch_265_22 -> line_3887_22 -> line_4582_22 | GSO_142¦line_4582_22 | ACLineSegment | 600 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
290 | 75 | GSO_142 | line_4262_22 | S_nCCTT1242_A_S_nCCTT1584 | 10.6074 | High | 12.47 | 12.3112 | 0 | 12.3112 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 36 | 25 | 0 | 100 | 23.0833 | 0.26294 | -79.9658 | 36.0311 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_4938_22 -> line_4939_22 -> line_5117_22 -> line_4875_22 -> line_4876_22 -> line_5777_22 -> switch_450_22 -> line_4554_22 -> line_4545_22 -> switch_445_22 -> line_4546_22 -> switch_447_22 -> line_4584_22 -> switch_462_22 -> switch_532_22 -> line_4908_22 -> line_4907_22 -> switch_531_22 -> line_3984_22 -> switch_290_22 -> recloser_157_22 -> line_3983_22 -> line_3886_22 -> switch_263_22 -> line_3885_22 -> switch_380_22 | GSO_142¦line_4262_22 | ACLineSegment | 600 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
291 | 76 | GSO_142 | line_5109_22 | S_nCCTT1558 | 10.6074 | High | 12.47 | 12.3112 | 0.19815 | 12.1131 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 37 | 25 | 0 | 100 | 23.0833 | 0.26294 | -79.9663 | 36.0293 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_5129_22 -> line_5442_22 -> line_5463_22 -> line_3913_22 -> line_3912_22 -> line_5157_22 -> switch_582_22 -> switch_769_22 -> line_6503_22 -> line_3663_22 -> switch_229_22 -> switch_226_22 -> line_3662_22 -> switch_516_22 -> line_4864_22 -> switch_475_22 -> line_4658_22 -> switch_411_22 -> line_4391_22 -> switch_413_22 -> line_4392_22 -> line_4830_22 -> switch_504_22 -> line_5111_22 -> switch_564_22 -> switch_561_22 -> line_5109_22 | GSO_142¦line_5109_22 | ACLineSegment | 600 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
292 | 77 | GSO_142 | line_4477_22 | S_nCCTT1558_B_S_nCCTT1315 | 10.6074 | High | 12.47 | 12.3112 | 0.19249 | 12.1188 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 38 | 26 | 0 | 100 | 23.0833 | 0.26294 | -79.9664 | 36.029 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_5129_22 -> line_5442_22 -> line_5463_22 -> line_3913_22 -> line_3912_22 -> line_5157_22 -> switch_582_22 -> switch_769_22 -> line_6503_22 -> line_3663_22 -> switch_229_22 -> switch_226_22 -> line_3662_22 -> switch_516_22 -> line_4864_22 -> switch_475_22 -> line_4658_22 -> switch_411_22 -> line_4391_22 -> switch_413_22 -> line_4392_22 -> line_4830_22 -> switch_504_22 -> line_5111_22 -> switch_564_22 -> switch_561_22 -> line_5109_22 -> line_4477_22 | GSO_142¦line_4477_22 | ACLineSegment | 600 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
293 | 78 | GSO_142 | line_4583_22 | S_nCCTT421 | 10.6074 | High | 12.47 | 12.3112 | 0.067936 | 12.2433 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 39 | 27 | 0 | 100 | 23.0833 | 0.26294 | -79.9688 | 36.0314 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_4938_22 -> line_4939_22 -> line_5117_22 -> line_4875_22 -> line_4876_22 -> line_5777_22 -> switch_450_22 -> line_4554_22 -> line_4545_22 -> switch_445_22 -> line_4546_22 -> switch_447_22 -> line_4584_22 -> switch_462_22 -> switch_532_22 -> line_4908_22 -> line_4907_22 -> switch_531_22 -> line_3984_22 -> switch_290_22 -> recloser_157_22 -> line_3983_22 -> line_3886_22 -> switch_265_22 -> line_3887_22 -> line_4582_22 -> switch_458_22 -> switch_459_22 -> line_4583_22 | GSO_142¦line_4583_22 | ACLineSegment | 600 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
294 | 79 | GSO_142 | line_4823_22 | S_nCCTT144 | 10.6074 | High | 12.47 | 13.5424 | 0.062275 | 13.4801 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 40 | 28 | 0 | 100 | 23.0833 | 0.26294 | -79.9693 | 36.0318 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_4938_22 -> line_4939_22 -> line_5117_22 -> line_4875_22 -> line_4876_22 -> line_5777_22 -> switch_450_22 -> line_4554_22 -> line_4545_22 -> switch_445_22 -> line_4546_22 -> switch_447_22 -> line_4584_22 -> switch_462_22 -> switch_532_22 -> line_4908_22 -> line_4907_22 -> switch_531_22 -> line_3984_22 -> switch_290_22 -> recloser_157_22 -> line_3983_22 -> line_3886_22 -> switch_265_22 -> line_3887_22 -> line_4582_22 -> switch_458_22 -> switch_459_22 -> line_4583_22 -> line_4823_22 | GSO_142¦line_4823_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
295 | 80 | GSO_142 | line_4434_22 | S_nCCTT1315_B_S_nCCTT130 | 10.6074 | High | 12.47 | 12.3112 | 0.16418 | 12.1471 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 40 | 27 | 0 | 100 | 23.0833 | 0.26294 | -79.967 | 36.0288 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_5129_22 -> line_5442_22 -> line_5463_22 -> line_3913_22 -> line_3912_22 -> line_5157_22 -> switch_582_22 -> switch_769_22 -> line_6503_22 -> line_3663_22 -> switch_229_22 -> switch_226_22 -> line_3662_22 -> switch_516_22 -> line_4864_22 -> switch_475_22 -> line_4658_22 -> switch_411_22 -> line_4391_22 -> switch_413_22 -> line_4392_22 -> line_4830_22 -> switch_504_22 -> line_5111_22 -> switch_564_22 -> switch_561_22 -> line_5109_22 -> line_4477_22 -> switch_437_22 -> line_4434_22 | GSO_142¦line_4434_22 | ACLineSegment | 600 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
296 | 81 | GSO_142 | line_3723_22 | S_nCCTT106 | 10.6074 | High | 12.47 | 13.5424 | 0.056613 | 13.4858 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 41 | 29 | 0 | 100 | 23.0833 | 0.26294 | -79.97 | 36.0324 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_4938_22 -> line_4939_22 -> line_5117_22 -> line_4875_22 -> line_4876_22 -> line_5777_22 -> switch_450_22 -> line_4554_22 -> line_4545_22 -> switch_445_22 -> line_4546_22 -> switch_447_22 -> line_4584_22 -> switch_462_22 -> switch_532_22 -> line_4908_22 -> line_4907_22 -> switch_531_22 -> line_3984_22 -> switch_290_22 -> recloser_157_22 -> line_3983_22 -> line_3886_22 -> switch_265_22 -> line_3887_22 -> line_4582_22 -> switch_458_22 -> switch_459_22 -> line_4583_22 -> line_4823_22 -> line_3723_22 | GSO_142¦line_3723_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
297 | 82 | GSO_142 | line_4476_22 | S_nCCTT150 | 10.6074 | High | 12.47 | 12.3112 | 0.016984 | 12.2943 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 41 | 27 | 0 | 100 | 23.0833 | 0.26294 | -79.9664 | 36.0286 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_5129_22 -> line_5442_22 -> line_5463_22 -> line_3913_22 -> line_3912_22 -> line_5157_22 -> switch_582_22 -> switch_769_22 -> line_6503_22 -> line_3663_22 -> switch_229_22 -> switch_226_22 -> line_3662_22 -> switch_516_22 -> line_4864_22 -> switch_475_22 -> line_4658_22 -> switch_411_22 -> line_4391_22 -> switch_413_22 -> line_4392_22 -> line_4830_22 -> switch_504_22 -> line_5111_22 -> switch_564_22 -> switch_561_22 -> line_5109_22 -> line_4477_22 -> switch_437_22 -> switch_434_22 -> line_4476_22 | GSO_142¦line_4476_22 | ACLineSegment | 600 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
298 | 83 | GSO_142 | line_3724_22 | S_nCCTT91 | 10.6074 | High | 12.47 | 13.5424 | 0.033968 | 13.5084 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 42 | 30 | 0 | 100 | 23.0833 | 0.26294 | -79.9709 | 36.0327 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_4938_22 -> line_4939_22 -> line_5117_22 -> line_4875_22 -> line_4876_22 -> line_5777_22 -> switch_450_22 -> line_4554_22 -> line_4545_22 -> switch_445_22 -> line_4546_22 -> switch_447_22 -> line_4584_22 -> switch_462_22 -> switch_532_22 -> line_4908_22 -> line_4907_22 -> switch_531_22 -> line_3984_22 -> switch_290_22 -> recloser_157_22 -> line_3983_22 -> line_3886_22 -> switch_265_22 -> line_3887_22 -> line_4582_22 -> switch_458_22 -> switch_459_22 -> line_4583_22 -> line_4823_22 -> line_3723_22 -> line_3724_22 | GSO_142¦line_3724_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
299 | 84 | GSO_142 | line_4435_22 | S_nCCTT1480 | 10.6074 | High | 12.47 | 13.5424 | 0.14153 | 13.4008 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 42 | 28 | 0 | 100 | 23.0833 | 0.26294 | -79.968 | 36.0287 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_5129_22 -> line_5442_22 -> line_5463_22 -> line_3913_22 -> line_3912_22 -> line_5157_22 -> switch_582_22 -> switch_769_22 -> line_6503_22 -> line_3663_22 -> switch_229_22 -> switch_226_22 -> line_3662_22 -> switch_516_22 -> line_4864_22 -> switch_475_22 -> line_4658_22 -> switch_411_22 -> line_4391_22 -> switch_413_22 -> line_4392_22 -> line_4830_22 -> switch_504_22 -> line_5111_22 -> switch_564_22 -> switch_561_22 -> line_5109_22 -> line_4477_22 -> switch_437_22 -> line_4434_22 -> switch_421_22 -> line_4435_22 | GSO_142¦line_4435_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
300 | 85 | GSO_142 | line_4436_22 | S_nCCTT130_B_S_nCCTT407 | 10.6074 | High | 12.47 | 12.3112 | 0.016984 | 12.2943 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 42 | 28 | 0 | 100 | 23.0833 | 0.26294 | -79.9679 | 36.0292 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_5129_22 -> line_5442_22 -> line_5463_22 -> line_3913_22 -> line_3912_22 -> line_5157_22 -> switch_582_22 -> switch_769_22 -> line_6503_22 -> line_3663_22 -> switch_229_22 -> switch_226_22 -> line_3662_22 -> switch_516_22 -> line_4864_22 -> switch_475_22 -> line_4658_22 -> switch_411_22 -> line_4391_22 -> switch_413_22 -> line_4392_22 -> line_4830_22 -> switch_504_22 -> line_5111_22 -> switch_564_22 -> switch_561_22 -> line_5109_22 -> line_4477_22 -> switch_437_22 -> line_4434_22 -> switch_421_22 -> line_4436_22 | GSO_142¦line_4436_22 | ACLineSegment | 600 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
301 | 86 | GSO_142 | line_4942_22 | S_nCCTT1491 | 10.6074 | High | 12.47 | 13.5424 | 0.0056613 | 13.5367 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 43 | 31 | 0 | 100 | 23.0833 | 0.26294 | -79.9716 | 36.0328 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_4938_22 -> line_4939_22 -> line_5117_22 -> line_4875_22 -> line_4876_22 -> line_5777_22 -> switch_450_22 -> line_4554_22 -> line_4545_22 -> switch_445_22 -> line_4546_22 -> switch_447_22 -> line_4584_22 -> switch_462_22 -> switch_532_22 -> line_4908_22 -> line_4907_22 -> switch_531_22 -> line_3984_22 -> switch_290_22 -> recloser_157_22 -> line_3983_22 -> line_3886_22 -> switch_265_22 -> line_3887_22 -> line_4582_22 -> switch_458_22 -> switch_459_22 -> line_4583_22 -> line_4823_22 -> line_3723_22 -> line_3724_22 -> line_4942_22 | GSO_142¦line_4942_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
302 | 87 | GSO_142 | line_4919_22 | S_nCCTT246 | 10.6074 | High | 12.47 | 13.5424 | 0.13587 | 13.4065 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 43 | 29 | 0 | 100 | 23.0833 | 0.26294 | -79.9686 | 36.0284 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_5129_22 -> line_5442_22 -> line_5463_22 -> line_3913_22 -> line_3912_22 -> line_5157_22 -> switch_582_22 -> switch_769_22 -> line_6503_22 -> line_3663_22 -> switch_229_22 -> switch_226_22 -> line_3662_22 -> switch_516_22 -> line_4864_22 -> switch_475_22 -> line_4658_22 -> switch_411_22 -> line_4391_22 -> switch_413_22 -> line_4392_22 -> line_4830_22 -> switch_504_22 -> line_5111_22 -> switch_564_22 -> switch_561_22 -> line_5109_22 -> line_4477_22 -> switch_437_22 -> line_4434_22 -> switch_421_22 -> line_4435_22 -> line_4919_22 | GSO_142¦line_4919_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
303 | 88 | GSO_142 | line_4891_22 | S_nCCTT1468 | 10.6074 | High | 12.47 | 12.3112 | 0.011323 | 12.2999 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 43 | 28 | 0 | 100 | 23.0833 | 0.26294 | -79.9661 | 36.0279 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_5129_22 -> line_5442_22 -> line_5463_22 -> line_3913_22 -> line_3912_22 -> line_5157_22 -> switch_582_22 -> switch_769_22 -> line_6503_22 -> line_3663_22 -> switch_229_22 -> switch_226_22 -> line_3662_22 -> switch_516_22 -> line_4864_22 -> switch_475_22 -> line_4658_22 -> switch_411_22 -> line_4391_22 -> switch_413_22 -> line_4392_22 -> line_4830_22 -> switch_504_22 -> line_5111_22 -> switch_564_22 -> switch_561_22 -> line_5109_22 -> line_4477_22 -> switch_437_22 -> switch_434_22 -> line_4476_22 -> switch_528_22 -> line_4891_22 | GSO_142¦line_4891_22 | ACLineSegment | 600 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
304 | 89 | GSO_142 | line_3596_22 | S_nCCTT102 | 10.6074 | High | 12.47 | 13.5424 | 0.011323 | 13.531 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 44 | 30 | 0 | 100 | 23.0833 | 0.26294 | -79.9692 | 36.0287 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_5129_22 -> line_5442_22 -> line_5463_22 -> line_3913_22 -> line_3912_22 -> line_5157_22 -> switch_582_22 -> switch_769_22 -> line_6503_22 -> line_3663_22 -> switch_229_22 -> switch_226_22 -> line_3662_22 -> switch_516_22 -> line_4864_22 -> switch_475_22 -> line_4658_22 -> switch_411_22 -> line_4391_22 -> switch_413_22 -> line_4392_22 -> line_4830_22 -> switch_504_22 -> line_5111_22 -> switch_564_22 -> switch_561_22 -> line_5109_22 -> line_4477_22 -> switch_437_22 -> line_4434_22 -> switch_421_22 -> line_4435_22 -> line_4919_22 -> line_3596_22 | GSO_142¦line_3596_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
305 | 90 | GSO_142 | line_4464_22 | S_nCCTT131 | 10.6074 | High | 12.47 | 13.5424 | 0.11889 | 13.4235 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 44 | 30 | 0 | 100 | 23.0833 | 0.26294 | -79.9688 | 36.0282 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_5129_22 -> line_5442_22 -> line_5463_22 -> line_3913_22 -> line_3912_22 -> line_5157_22 -> switch_582_22 -> switch_769_22 -> line_6503_22 -> line_3663_22 -> switch_229_22 -> switch_226_22 -> line_3662_22 -> switch_516_22 -> line_4864_22 -> switch_475_22 -> line_4658_22 -> switch_411_22 -> line_4391_22 -> switch_413_22 -> line_4392_22 -> line_4830_22 -> switch_504_22 -> line_5111_22 -> switch_564_22 -> switch_561_22 -> line_5109_22 -> line_4477_22 -> switch_437_22 -> line_4434_22 -> switch_421_22 -> line_4435_22 -> line_4919_22 -> line_4464_22 | GSO_142¦line_4464_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
306 | 91 | GSO_142 | line_4682_22 | S_nCCTT407_B_S_nCCTT1387 | 10.6074 | High | 12.47 | 12.3112 | 0.011323 | 12.2999 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 44 | 29 | 0 | 100 | 23.0833 | 0.26294 | -79.9685 | 36.0297 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_5129_22 -> line_5442_22 -> line_5463_22 -> line_3913_22 -> line_3912_22 -> line_5157_22 -> switch_582_22 -> switch_769_22 -> line_6503_22 -> line_3663_22 -> switch_229_22 -> switch_226_22 -> line_3662_22 -> switch_516_22 -> line_4864_22 -> switch_475_22 -> line_4658_22 -> switch_411_22 -> line_4391_22 -> switch_413_22 -> line_4392_22 -> line_4830_22 -> switch_504_22 -> line_5111_22 -> switch_564_22 -> switch_561_22 -> line_5109_22 -> line_4477_22 -> switch_437_22 -> line_4434_22 -> switch_421_22 -> line_4436_22 -> switch_423_22 -> line_4682_22 | GSO_142¦line_4682_22 | ACLineSegment | 600 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
307 | 92 | GSO_142 | line_4463_22 | S_nCCTT148 | 10.6074 | High | 12.47 | 13.5424 | 0.11323 | 13.4291 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 45 | 31 | 0 | 100 | 23.0833 | 0.26294 | -79.969 | 36.028 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_5129_22 -> line_5442_22 -> line_5463_22 -> line_3913_22 -> line_3912_22 -> line_5157_22 -> switch_582_22 -> switch_769_22 -> line_6503_22 -> line_3663_22 -> switch_229_22 -> switch_226_22 -> line_3662_22 -> switch_516_22 -> line_4864_22 -> switch_475_22 -> line_4658_22 -> switch_411_22 -> line_4391_22 -> switch_413_22 -> line_4392_22 -> line_4830_22 -> switch_504_22 -> line_5111_22 -> switch_564_22 -> switch_561_22 -> line_5109_22 -> line_4477_22 -> switch_437_22 -> line_4434_22 -> switch_421_22 -> line_4435_22 -> line_4919_22 -> line_4464_22 -> line_4463_22 | GSO_142¦line_4463_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
308 | 93 | GSO_142 | line_3782_22 | S_nCCTT1387_B_S_nCCTT108 | 10.6074 | High | 12.47 | 12.3112 | 0.0056613 | 12.3056 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 46 | 30 | 0 | 100 | 23.0833 | 0.26294 | -79.9691 | 36.0302 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_5129_22 -> line_5442_22 -> line_5463_22 -> line_3913_22 -> line_3912_22 -> line_5157_22 -> switch_582_22 -> switch_769_22 -> line_6503_22 -> line_3663_22 -> switch_229_22 -> switch_226_22 -> line_3662_22 -> switch_516_22 -> line_4864_22 -> switch_475_22 -> line_4658_22 -> switch_411_22 -> line_4391_22 -> switch_413_22 -> line_4392_22 -> line_4830_22 -> switch_504_22 -> line_5111_22 -> switch_564_22 -> switch_561_22 -> line_5109_22 -> line_4477_22 -> switch_437_22 -> line_4434_22 -> switch_421_22 -> line_4436_22 -> switch_423_22 -> line_4682_22 -> switch_484_22 -> line_3782_22 | GSO_142¦line_3782_22 | ACLineSegment | 600 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
309 | 94 | GSO_142 | line_4770_22 | S_nCCTT142 | 10.6074 | High | 12.47 | 13.5424 | 0.10757 | 13.4348 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 46 | 32 | 0 | 100 | 23.0833 | 0.26294 | -79.9693 | 36.0277 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_5129_22 -> line_5442_22 -> line_5463_22 -> line_3913_22 -> line_3912_22 -> line_5157_22 -> switch_582_22 -> switch_769_22 -> line_6503_22 -> line_3663_22 -> switch_229_22 -> switch_226_22 -> line_3662_22 -> switch_516_22 -> line_4864_22 -> switch_475_22 -> line_4658_22 -> switch_411_22 -> line_4391_22 -> switch_413_22 -> line_4392_22 -> line_4830_22 -> switch_504_22 -> line_5111_22 -> switch_564_22 -> switch_561_22 -> line_5109_22 -> line_4477_22 -> switch_437_22 -> line_4434_22 -> switch_421_22 -> line_4435_22 -> line_4919_22 -> line_4464_22 -> line_4463_22 -> line_4770_22 | GSO_142¦line_4770_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
310 | 95 | GSO_142 | line_4769_22 | S_nCCTT1434 | 10.6074 | High | 12.47 | 13.5424 | 0.1019 | 13.4405 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 47 | 33 | 0 | 100 | 23.0833 | 0.26294 | -79.9696 | 36.0273 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_5129_22 -> line_5442_22 -> line_5463_22 -> line_3913_22 -> line_3912_22 -> line_5157_22 -> switch_582_22 -> switch_769_22 -> line_6503_22 -> line_3663_22 -> switch_229_22 -> switch_226_22 -> line_3662_22 -> switch_516_22 -> line_4864_22 -> switch_475_22 -> line_4658_22 -> switch_411_22 -> line_4391_22 -> switch_413_22 -> line_4392_22 -> line_4830_22 -> switch_504_22 -> line_5111_22 -> switch_564_22 -> switch_561_22 -> line_5109_22 -> line_4477_22 -> switch_437_22 -> line_4434_22 -> switch_421_22 -> line_4435_22 -> line_4919_22 -> line_4464_22 -> line_4463_22 -> line_4770_22 -> line_4769_22 | GSO_142¦line_4769_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
311 | 96 | GSO_142 | line_4386_22 | S_nCCTT1284 | 10.6074 | High | 12.47 | 13.5424 | 0.079259 | 13.4631 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 48 | 34 | 0 | 100 | 23.0833 | 0.26294 | -79.97 | 36.0268 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_5129_22 -> line_5442_22 -> line_5463_22 -> line_3913_22 -> line_3912_22 -> line_5157_22 -> switch_582_22 -> switch_769_22 -> line_6503_22 -> line_3663_22 -> switch_229_22 -> switch_226_22 -> line_3662_22 -> switch_516_22 -> line_4864_22 -> switch_475_22 -> line_4658_22 -> switch_411_22 -> line_4391_22 -> switch_413_22 -> line_4392_22 -> line_4830_22 -> switch_504_22 -> line_5111_22 -> switch_564_22 -> switch_561_22 -> line_5109_22 -> line_4477_22 -> switch_437_22 -> line_4434_22 -> switch_421_22 -> line_4435_22 -> line_4919_22 -> line_4464_22 -> line_4463_22 -> line_4770_22 -> line_4769_22 -> line_4386_22 | GSO_142¦line_4386_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
312 | 97 | GSO_142 | line_4808_22 | S_nCCTT85 | 10.6074 | High | 12.47 | 13.5424 | 0.011323 | 13.531 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 48 | 34 | 0 | 100 | 23.0833 | 0.26294 | -79.9692 | 36.027 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_5129_22 -> line_5442_22 -> line_5463_22 -> line_3913_22 -> line_3912_22 -> line_5157_22 -> switch_582_22 -> switch_769_22 -> line_6503_22 -> line_3663_22 -> switch_229_22 -> switch_226_22 -> line_3662_22 -> switch_516_22 -> line_4864_22 -> switch_475_22 -> line_4658_22 -> switch_411_22 -> line_4391_22 -> switch_413_22 -> line_4392_22 -> line_4830_22 -> switch_504_22 -> line_5111_22 -> switch_564_22 -> switch_561_22 -> line_5109_22 -> line_4477_22 -> switch_437_22 -> line_4434_22 -> switch_421_22 -> line_4435_22 -> line_4919_22 -> line_4464_22 -> line_4463_22 -> line_4770_22 -> line_4769_22 -> line_4808_22 | GSO_142¦line_4808_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
313 | 98 | GSO_142 | line_4387_22 | S_nCCTT236 | 10.6074 | High | 12.47 | 13.5424 | 0.073597 | 13.4688 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 49 | 35 | 0 | 100 | 23.0833 | 0.26294 | -79.9705 | 36.0262 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_5129_22 -> line_5442_22 -> line_5463_22 -> line_3913_22 -> line_3912_22 -> line_5157_22 -> switch_582_22 -> switch_769_22 -> line_6503_22 -> line_3663_22 -> switch_229_22 -> switch_226_22 -> line_3662_22 -> switch_516_22 -> line_4864_22 -> switch_475_22 -> line_4658_22 -> switch_411_22 -> line_4391_22 -> switch_413_22 -> line_4392_22 -> line_4830_22 -> switch_504_22 -> line_5111_22 -> switch_564_22 -> switch_561_22 -> line_5109_22 -> line_4477_22 -> switch_437_22 -> line_4434_22 -> switch_421_22 -> line_4435_22 -> line_4919_22 -> line_4464_22 -> line_4463_22 -> line_4770_22 -> line_4769_22 -> line_4386_22 -> line_4387_22 | GSO_142¦line_4387_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
314 | 99 | GSO_142 | line_4792_22 | S_nCCTT1428 | 10.6074 | High | 12.47 | 13.5424 | 0.067936 | 13.4744 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 50 | 36 | 0 | 100 | 23.0833 | 0.26294 | -79.9709 | 36.0255 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_5129_22 -> line_5442_22 -> line_5463_22 -> line_3913_22 -> line_3912_22 -> line_5157_22 -> switch_582_22 -> switch_769_22 -> line_6503_22 -> line_3663_22 -> switch_229_22 -> switch_226_22 -> line_3662_22 -> switch_516_22 -> line_4864_22 -> switch_475_22 -> line_4658_22 -> switch_411_22 -> line_4391_22 -> switch_413_22 -> line_4392_22 -> line_4830_22 -> switch_504_22 -> line_5111_22 -> switch_564_22 -> switch_561_22 -> line_5109_22 -> line_4477_22 -> switch_437_22 -> line_4434_22 -> switch_421_22 -> line_4435_22 -> line_4919_22 -> line_4464_22 -> line_4463_22 -> line_4770_22 -> line_4769_22 -> line_4386_22 -> line_4387_22 -> line_4792_22 | GSO_142¦line_4792_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
315 | 100 | GSO_142 | line_4458_22 | S_nCCTT1308 | 10.6074 | High | 12.47 | 13.5424 | 0.022645 | 13.5197 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 51 | 37 | 0 | 100 | 23.0833 | 0.26294 | -79.9709 | 36.0249 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_5129_22 -> line_5442_22 -> line_5463_22 -> line_3913_22 -> line_3912_22 -> line_5157_22 -> switch_582_22 -> switch_769_22 -> line_6503_22 -> line_3663_22 -> switch_229_22 -> switch_226_22 -> line_3662_22 -> switch_516_22 -> line_4864_22 -> switch_475_22 -> line_4658_22 -> switch_411_22 -> line_4391_22 -> switch_413_22 -> line_4392_22 -> line_4830_22 -> switch_504_22 -> line_5111_22 -> switch_564_22 -> switch_561_22 -> line_5109_22 -> line_4477_22 -> switch_437_22 -> line_4434_22 -> switch_421_22 -> line_4435_22 -> line_4919_22 -> line_4464_22 -> line_4463_22 -> line_4770_22 -> line_4769_22 -> line_4386_22 -> line_4387_22 -> line_4792_22 -> line_4458_22 | GSO_142¦line_4458_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
316 | 101 | GSO_142 | line_4548_22 | S_nCCTT1339 | 10.6074 | High | 12.47 | 13.5424 | 0.039629 | 13.5027 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 51 | 37 | 0 | 100 | 23.0833 | 0.26294 | -79.9712 | 36.0251 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_5129_22 -> line_5442_22 -> line_5463_22 -> line_3913_22 -> line_3912_22 -> line_5157_22 -> switch_582_22 -> switch_769_22 -> line_6503_22 -> line_3663_22 -> switch_229_22 -> switch_226_22 -> line_3662_22 -> switch_516_22 -> line_4864_22 -> switch_475_22 -> line_4658_22 -> switch_411_22 -> line_4391_22 -> switch_413_22 -> line_4392_22 -> line_4830_22 -> switch_504_22 -> line_5111_22 -> switch_564_22 -> switch_561_22 -> line_5109_22 -> line_4477_22 -> switch_437_22 -> line_4434_22 -> switch_421_22 -> line_4435_22 -> line_4919_22 -> line_4464_22 -> line_4463_22 -> line_4770_22 -> line_4769_22 -> line_4386_22 -> line_4387_22 -> line_4792_22 -> line_4548_22 | GSO_142¦line_4548_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
317 | 102 | GSO_142 | line_4549_22 | S_nCCTT396 | 10.6074 | High | 12.47 | 13.5424 | 0.028307 | 13.5141 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 52 | 38 | 0 | 100 | 23.0833 | 0.26294 | -79.9715 | 36.0251 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_5129_22 -> line_5442_22 -> line_5463_22 -> line_3913_22 -> line_3912_22 -> line_5157_22 -> switch_582_22 -> switch_769_22 -> line_6503_22 -> line_3663_22 -> switch_229_22 -> switch_226_22 -> line_3662_22 -> switch_516_22 -> line_4864_22 -> switch_475_22 -> line_4658_22 -> switch_411_22 -> line_4391_22 -> switch_413_22 -> line_4392_22 -> line_4830_22 -> switch_504_22 -> line_5111_22 -> switch_564_22 -> switch_561_22 -> line_5109_22 -> line_4477_22 -> switch_437_22 -> line_4434_22 -> switch_421_22 -> line_4435_22 -> line_4919_22 -> line_4464_22 -> line_4463_22 -> line_4770_22 -> line_4769_22 -> line_4386_22 -> line_4387_22 -> line_4792_22 -> line_4548_22 -> line_4549_22 | GSO_142¦line_4549_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
318 | 103 | GSO_142 | line_4457_22 | S_nCCTT1385 | 10.6074 | High | 12.47 | 13.5424 | 0.016984 | 13.5254 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 52 | 38 | 0 | 100 | 23.0833 | 0.26294 | -79.9704 | 36.0248 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_5129_22 -> line_5442_22 -> line_5463_22 -> line_3913_22 -> line_3912_22 -> line_5157_22 -> switch_582_22 -> switch_769_22 -> line_6503_22 -> line_3663_22 -> switch_229_22 -> switch_226_22 -> line_3662_22 -> switch_516_22 -> line_4864_22 -> switch_475_22 -> line_4658_22 -> switch_411_22 -> line_4391_22 -> switch_413_22 -> line_4392_22 -> line_4830_22 -> switch_504_22 -> line_5111_22 -> switch_564_22 -> switch_561_22 -> line_5109_22 -> line_4477_22 -> switch_437_22 -> line_4434_22 -> switch_421_22 -> line_4435_22 -> line_4919_22 -> line_4464_22 -> line_4463_22 -> line_4770_22 -> line_4769_22 -> line_4386_22 -> line_4387_22 -> line_4792_22 -> line_4458_22 -> line_4457_22 | GSO_142¦line_4457_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
319 | 104 | GSO_142 | line_3873_22 | S_nCCTT1105 | 10.6074 | High | 12.47 | 13.5424 | 0.022645 | 13.5197 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 53 | 39 | 0 | 100 | 23.0833 | 0.26294 | -79.9716 | 36.025 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_5129_22 -> line_5442_22 -> line_5463_22 -> line_3913_22 -> line_3912_22 -> line_5157_22 -> switch_582_22 -> switch_769_22 -> line_6503_22 -> line_3663_22 -> switch_229_22 -> switch_226_22 -> line_3662_22 -> switch_516_22 -> line_4864_22 -> switch_475_22 -> line_4658_22 -> switch_411_22 -> line_4391_22 -> switch_413_22 -> line_4392_22 -> line_4830_22 -> switch_504_22 -> line_5111_22 -> switch_564_22 -> switch_561_22 -> line_5109_22 -> line_4477_22 -> switch_437_22 -> line_4434_22 -> switch_421_22 -> line_4435_22 -> line_4919_22 -> line_4464_22 -> line_4463_22 -> line_4770_22 -> line_4769_22 -> line_4386_22 -> line_4387_22 -> line_4792_22 -> line_4548_22 -> line_4549_22 -> line_3873_22 | GSO_142¦line_3873_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
320 | 105 | GSO_142 | line_4678_22 | S_nCCTT408 | 10.6074 | High | 12.47 | 13.5424 | 0.011323 | 13.531 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 53 | 39 | 0 | 100 | 23.0833 | 0.26294 | -79.9701 | 36.025 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_5129_22 -> line_5442_22 -> line_5463_22 -> line_3913_22 -> line_3912_22 -> line_5157_22 -> switch_582_22 -> switch_769_22 -> line_6503_22 -> line_3663_22 -> switch_229_22 -> switch_226_22 -> line_3662_22 -> switch_516_22 -> line_4864_22 -> switch_475_22 -> line_4658_22 -> switch_411_22 -> line_4391_22 -> switch_413_22 -> line_4392_22 -> line_4830_22 -> switch_504_22 -> line_5111_22 -> switch_564_22 -> switch_561_22 -> line_5109_22 -> line_4477_22 -> switch_437_22 -> line_4434_22 -> switch_421_22 -> line_4435_22 -> line_4919_22 -> line_4464_22 -> line_4463_22 -> line_4770_22 -> line_4769_22 -> line_4386_22 -> line_4387_22 -> line_4792_22 -> line_4458_22 -> line_4457_22 -> line_4678_22 | GSO_142¦line_4678_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
321 | 106 | GSO_142 | line_3872_22 | S_nCCTT1481 | 10.6074 | High | 12.47 | 13.5424 | 0.011323 | 13.531 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 54 | 40 | 0 | 100 | 23.0833 | 0.26294 | -79.9717 | 36.0247 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_5129_22 -> line_5442_22 -> line_5463_22 -> line_3913_22 -> line_3912_22 -> line_5157_22 -> switch_582_22 -> switch_769_22 -> line_6503_22 -> line_3663_22 -> switch_229_22 -> switch_226_22 -> line_3662_22 -> switch_516_22 -> line_4864_22 -> switch_475_22 -> line_4658_22 -> switch_411_22 -> line_4391_22 -> switch_413_22 -> line_4392_22 -> line_4830_22 -> switch_504_22 -> line_5111_22 -> switch_564_22 -> switch_561_22 -> line_5109_22 -> line_4477_22 -> switch_437_22 -> line_4434_22 -> switch_421_22 -> line_4435_22 -> line_4919_22 -> line_4464_22 -> line_4463_22 -> line_4770_22 -> line_4769_22 -> line_4386_22 -> line_4387_22 -> line_4792_22 -> line_4548_22 -> line_4549_22 -> line_3873_22 -> line_3872_22 | GSO_142¦line_3872_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
322 | 107 | GSO_142 | line_4910_22 | S_nCCTT1475 | 10.6074 | High | 12.47 | 13.5424 | 0.0056613 | 13.5367 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 54 | 40 | 0 | 100 | 23.0833 | 0.26294 | -79.9696 | 36.0252 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_5129_22 -> line_5442_22 -> line_5463_22 -> line_3913_22 -> line_3912_22 -> line_5157_22 -> switch_582_22 -> switch_769_22 -> line_6503_22 -> line_3663_22 -> switch_229_22 -> switch_226_22 -> line_3662_22 -> switch_516_22 -> line_4864_22 -> switch_475_22 -> line_4658_22 -> switch_411_22 -> line_4391_22 -> switch_413_22 -> line_4392_22 -> line_4830_22 -> switch_504_22 -> line_5111_22 -> switch_564_22 -> switch_561_22 -> line_5109_22 -> line_4477_22 -> switch_437_22 -> line_4434_22 -> switch_421_22 -> line_4435_22 -> line_4919_22 -> line_4464_22 -> line_4463_22 -> line_4770_22 -> line_4769_22 -> line_4386_22 -> line_4387_22 -> line_4792_22 -> line_4458_22 -> line_4457_22 -> line_4678_22 -> line_4910_22 | GSO_142¦line_4910_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
323 | 108 | GSO_142 | line_4921_22 | S_nCCTT329 | 10.6074 | High | 12.47 | 13.5424 | 0.0056613 | 13.5367 | 0.79259 | 11.4 | 10.6074 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.79259 | 10.6074 | 55 | 41 | 0 | 100 | 23.0833 | 0.26294 | -79.9713 | 36.0242 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_5129_22 -> line_5442_22 -> line_5463_22 -> line_3913_22 -> line_3912_22 -> line_5157_22 -> switch_582_22 -> switch_769_22 -> line_6503_22 -> line_3663_22 -> switch_229_22 -> switch_226_22 -> line_3662_22 -> switch_516_22 -> line_4864_22 -> switch_475_22 -> line_4658_22 -> switch_411_22 -> line_4391_22 -> switch_413_22 -> line_4392_22 -> line_4830_22 -> switch_504_22 -> line_5111_22 -> switch_564_22 -> switch_561_22 -> line_5109_22 -> line_4477_22 -> switch_437_22 -> line_4434_22 -> switch_421_22 -> line_4435_22 -> line_4919_22 -> line_4464_22 -> line_4463_22 -> line_4770_22 -> line_4769_22 -> line_4386_22 -> line_4387_22 -> line_4792_22 -> line_4548_22 -> line_4549_22 -> line_3873_22 -> line_3872_22 -> line_4921_22 | GSO_142¦line_4921_22 | ACLineSegment | 660 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved |  | 250
501 | 109 | GSO_142 | line_4122_22 | S_nCCTT1468_B_S_nCCTT120 | 7.1027 | High | 7.2 | 7.1083 | 0.0056613 | 7.1027 | 0.79259 | 11.4 | 10.6074 | line_4122_22 | ACLineSegment | Line | 7.1083 | 0.0056613 | 7.1027 | 44 | 29 | 0 | 100 | 23.0833 | 0.26294 | -79.9658 | 36.0273 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_5129_22 -> line_5442_22 -> line_5463_22 -> line_3913_22 -> line_3912_22 -> line_5157_22 -> switch_582_22 -> switch_769_22 -> line_6503_22 -> line_3663_22 -> switch_229_22 -> switch_226_22 -> line_3662_22 -> switch_516_22 -> line_4864_22 -> switch_475_22 -> line_4658_22 -> switch_411_22 -> line_4391_22 -> switch_413_22 -> line_4392_22 -> line_4830_22 -> switch_504_22 -> line_5111_22 -> switch_564_22 -> switch_561_22 -> line_5109_22 -> line_4477_22 -> switch_437_22 -> switch_434_22 -> line_4476_22 -> switch_528_22 -> line_4891_22 -> line_4122_22 | GSO_142¦line_4122_22 | ACLineSegment | 600 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 7.1027 | [6 empty] | SubstationCapacityUnresolved | line_4122_22 | Substation capacity unresolved |  | 250
505 | 110 | GSO_142 | line_3982_22 | S_nCCTT139 | 7.097 | High | 7.2 | 7.1083 | 0.011323 | 7.097 | 0.79259 | 11.4 | 10.6074 | line_3982_22 | ACLineSegment | Line | 7.1083 | 0.011323 | 7.097 | 32 | 23 | 0 | 100 | 23.0833 | 0.26294 | -79.968 | 36.0334 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_4938_22 -> line_4939_22 -> line_5117_22 -> line_4875_22 -> line_4876_22 -> line_5777_22 -> switch_450_22 -> line_4554_22 -> line_4545_22 -> switch_445_22 -> line_4546_22 -> switch_447_22 -> line_4584_22 -> switch_462_22 -> switch_532_22 -> line_4908_22 -> line_4907_22 -> switch_531_22 -> line_3984_22 -> switch_290_22 -> switch_287_22 -> line_3982_22 | GSO_142¦line_3982_22 | ACLineSegment | 600 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 7.097 | [6 empty] | SubstationCapacityUnresolved | line_3982_22 | Substation capacity unresolved |  | 250
536 | 111 | GSO_142 | line_4351_22 | S_nCCTT323 | 2.8377 | High | 7.2 | 2.8433 | 0.0056613 | 2.8377 | 0.79259 | 11.4 | 10.6074 | line_4351_22 | ACLineSegment | Line | 2.8433 | 0.0056613 | 2.8377 | 8 | 6 | 0 | 100 | 23.0833 | 0.26294 | -79.9605 | 36.037 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4350_22 -> fuse_54_22 -> line_4351_22 | GSO_142¦line_4351_22 | ACLineSegment | 240 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.8377 | [6 empty] | SubstationCapacityUnresolved | line_4351_22 | Substation capacity unresolved |  | 250
537 | 112 | GSO_142 | line_4899_22 | S_nCCTT1470 | 2.8377 | High | 7.2 | 2.8433 | 0.0056613 | 2.8377 | 0.79259 | 11.4 | 10.6074 | line_4899_22 | ACLineSegment | Line | 2.8433 | 0.0056613 | 2.8377 | 20 | 17 | 0 | 100 | 23.0833 | 0.26294 | -79.9595 | 36.0321 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_4913_22 -> line_4904_22 -> line_4905_22 -> line_4924_22 -> line_4528_22 -> line_4527_22 -> line_4439_22 -> line_4440_22 -> line_3988_22 -> switch_291_22 -> line_3989_22 -> line_4560_22 -> line_4562_22 -> line_4717_22 -> line_4716_22 -> fuse_83_22 -> line_4899_22 | GSO_142¦line_4899_22 | ACLineSegment | 240 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.8377 | [6 empty] | SubstationCapacityUnresolved | line_4899_22 | Substation capacity unresolved |  | 250
538 | 113 | GSO_142 | line_6343_22 | S_nCCTT67 | 2.8377 | High | 7.2 | 2.8433 | 0.0056613 | 2.8377 | 0.79259 | 11.4 | 10.6074 | line_6343_22 | ACLineSegment | Line | 2.8433 | 0.0056613 | 2.8377 | 35 | 25 | 0 | 100 | 23.0833 | 0.26294 | -79.9668 | 36.0331 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_4938_22 -> line_4939_22 -> line_5117_22 -> line_4875_22 -> line_4876_22 -> line_5777_22 -> switch_450_22 -> line_4554_22 -> line_4545_22 -> switch_445_22 -> line_4546_22 -> switch_447_22 -> line_4584_22 -> switch_462_22 -> switch_532_22 -> line_4908_22 -> line_4907_22 -> switch_531_22 -> line_3984_22 -> switch_290_22 -> recloser_157_22 -> line_3983_22 -> line_4796_22 -> fuse_147_22 -> line_6343_22 | GSO_142¦line_6343_22 | ACLineSegment | 240 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.8377 | [6 empty] | SubstationCapacityUnresolved | line_6343_22 | Substation capacity unresolved |  | 250
539 | 114 | GSO_142 | line_3595_22 | S_nCCTT1482 | 2.8377 | High | 7.2 | 2.8433 | 0.0056613 | 2.8377 | 0.79259 | 11.4 | 10.6074 | line_3595_22 | ACLineSegment | Line | 2.8433 | 0.0056613 | 2.8377 | 46 | 31 | 0 | 100 | 23.0833 | 0.26294 | -79.9699 | 36.0293 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_5129_22 -> line_5442_22 -> line_5463_22 -> line_3913_22 -> line_3912_22 -> line_5157_22 -> switch_582_22 -> switch_769_22 -> line_6503_22 -> line_3663_22 -> switch_229_22 -> switch_226_22 -> line_3662_22 -> switch_516_22 -> line_4864_22 -> switch_475_22 -> line_4658_22 -> switch_411_22 -> line_4391_22 -> switch_413_22 -> line_4392_22 -> line_4830_22 -> switch_504_22 -> line_5111_22 -> switch_564_22 -> switch_561_22 -> line_5109_22 -> line_4477_22 -> switch_437_22 -> line_4434_22 -> switch_421_22 -> line_4435_22 -> line_4919_22 -> line_3596_22 -> fuse_4_22 -> line_3595_22 | GSO_142¦line_3595_22 | ACLineSegment | 240 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.8377 | [6 empty] | SubstationCapacityUnresolved | line_3595_22 | Substation capacity unresolved |  | 250
540 | 115 | GSO_142 | line_3946_22 | S_nCCTT1132 | 2.8377 | High | 7.2 | 2.8433 | 0.0056613 | 2.8377 | 0.79259 | 11.4 | 10.6074 | line_3946_22 | ACLineSegment | Line | 2.8433 | 0.0056613 | 2.8377 | 49 | 34 | 0 | 100 | 23.0833 | 0.26294 | -79.9704 | 36.0271 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_5129_22 -> line_5442_22 -> line_5463_22 -> line_3913_22 -> line_3912_22 -> line_5157_22 -> switch_582_22 -> switch_769_22 -> line_6503_22 -> line_3663_22 -> switch_229_22 -> switch_226_22 -> line_3662_22 -> switch_516_22 -> line_4864_22 -> switch_475_22 -> line_4658_22 -> switch_411_22 -> line_4391_22 -> switch_413_22 -> line_4392_22 -> line_4830_22 -> switch_504_22 -> line_5111_22 -> switch_564_22 -> switch_561_22 -> line_5109_22 -> line_4477_22 -> switch_437_22 -> line_4434_22 -> switch_421_22 -> line_4435_22 -> line_4919_22 -> line_4464_22 -> line_4463_22 -> line_4770_22 -> line_4769_22 -> fuse_27_22 -> line_3946_22 | GSO_142¦line_3946_22 | ACLineSegment | 240 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.8377 | [6 empty] | SubstationCapacityUnresolved | line_3946_22 | Substation capacity unresolved |  | 250
541 | 116 | GSO_142 | line_5115_22 | S_nCCTT1561 | 2.8377 | High | 7.2 | 2.8433 | 0.0056613 | 2.8377 | 0.79259 | 11.4 | 10.6074 | line_5115_22 | ACLineSegment | Line | 2.8433 | 0.0056613 | 2.8377 | 50 | 35 | 0 | 100 | 23.0833 | 0.26294 | -79.9682 | 36.0266 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_5129_22 -> line_5442_22 -> line_5463_22 -> line_3913_22 -> line_3912_22 -> line_5157_22 -> switch_582_22 -> switch_769_22 -> line_6503_22 -> line_3663_22 -> switch_229_22 -> switch_226_22 -> line_3662_22 -> switch_516_22 -> line_4864_22 -> switch_475_22 -> line_4658_22 -> switch_411_22 -> line_4391_22 -> switch_413_22 -> line_4392_22 -> line_4830_22 -> switch_504_22 -> line_5111_22 -> switch_564_22 -> switch_561_22 -> line_5109_22 -> line_4477_22 -> switch_437_22 -> line_4434_22 -> switch_421_22 -> line_4435_22 -> line_4919_22 -> line_4464_22 -> line_4463_22 -> line_4770_22 -> line_4769_22 -> line_4808_22 -> fuse_92_22 -> line_5115_22 | GSO_142¦line_5115_22 | ACLineSegment | 240 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.8377 | [6 empty] | SubstationCapacityUnresolved | line_5115_22 | Substation capacity unresolved |  | 250
555 | 117 | GSO_142 | line_3690_22 | S_nCCTT105 | 2.8264 | High | 7.2 | 2.8433 | 0.016984 | 2.8264 | 0.79259 | 11.4 | 10.6074 | line_3690_22 | ACLineSegment | Line | 2.8433 | 0.016984 | 2.8264 | 43 | 30 | 0 | 100 | 23.0833 | 0.26294 | -79.9705 | 36.033 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_4938_22 -> line_4939_22 -> line_5117_22 -> line_4875_22 -> line_4876_22 -> line_5777_22 -> switch_450_22 -> line_4554_22 -> line_4545_22 -> switch_445_22 -> line_4546_22 -> switch_447_22 -> line_4584_22 -> switch_462_22 -> switch_532_22 -> line_4908_22 -> line_4907_22 -> switch_531_22 -> line_3984_22 -> switch_290_22 -> recloser_157_22 -> line_3983_22 -> line_3886_22 -> switch_265_22 -> line_3887_22 -> line_4582_22 -> switch_458_22 -> switch_459_22 -> line_4583_22 -> line_4823_22 -> line_3723_22 -> fuse_11_22 -> line_3690_22 | GSO_142¦line_3690_22 | ACLineSegment | 240 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.8264 | [6 empty] | SubstationCapacityUnresolved | line_3690_22 | Substation capacity unresolved |  | 250
556 | 118 | GSO_142 | line_5135_22 | S_nCCTT157 | 2.8264 | High | 7.2 | 2.8433 | 0.016984 | 2.8264 | 0.79259 | 11.4 | 10.6074 | line_5135_22 | ACLineSegment | Line | 2.8433 | 0.016984 | 2.8264 | 44 | 31 | 0 | 100 | 23.0833 | 0.26294 | -79.971 | 36.032 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_4938_22 -> line_4939_22 -> line_5117_22 -> line_4875_22 -> line_4876_22 -> line_5777_22 -> switch_450_22 -> line_4554_22 -> line_4545_22 -> switch_445_22 -> line_4546_22 -> switch_447_22 -> line_4584_22 -> switch_462_22 -> switch_532_22 -> line_4908_22 -> line_4907_22 -> switch_531_22 -> line_3984_22 -> switch_290_22 -> recloser_157_22 -> line_3983_22 -> line_3886_22 -> switch_265_22 -> line_3887_22 -> line_4582_22 -> switch_458_22 -> switch_459_22 -> line_4583_22 -> line_4823_22 -> line_3723_22 -> line_3724_22 -> fuse_93_22 -> line_5135_22 | GSO_142¦line_5135_22 | ACLineSegment | 240 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.8264 | [6 empty] | SubstationCapacityUnresolved | line_5135_22 | Substation capacity unresolved |  | 250
557 | 119 | GSO_142 | line_3857_22 | S_nCCTT110 | 2.8264 | High | 7.2 | 2.8433 | 0.0056613 | 2.8377 | 0.79259 | 11.4 | 10.6074 | line_5135_22 | ACLineSegment | Line | 2.8433 | 0.016984 | 2.8264 | 45 | 32 | 0 | 100 | 23.0833 | 0.26294 | -79.9719 | 36.0315 | recloser_177_22 -> line_5429_22 -> line_5428_22 -> line_5565_22 -> line_4684_22 -> line_4685_22 -> line_5427_22 -> line_4889_22 -> line_4608_22 -> line_4609_22 -> line_4938_22 -> line_4939_22 -> line_5117_22 -> line_4875_22 -> line_4876_22 -> line_5777_22 -> switch_450_22 -> line_4554_22 -> line_4545_22 -> switch_445_22 -> line_4546_22 -> switch_447_22 -> line_4584_22 -> switch_462_22 -> switch_532_22 -> line_4908_22 -> line_4907_22 -> switch_531_22 -> line_3984_22 -> switch_290_22 -> recloser_157_22 -> line_3983_22 -> line_3886_22 -> switch_265_22 -> line_3887_22 -> line_4582_22 -> switch_458_22 -> switch_459_22 -> line_4583_22 -> line_4823_22 -> line_3723_22 -> line_3724_22 -> fuse_93_22 -> line_5135_22 -> line_3857_22 | GSO_142¦line_3857_22 | ACLineSegment | 240 | 12000 | Meter | br_022_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.8264 | [6 empty] | SubstationCapacityUnresolved | line_5135_22 | Substation capacity unresolved |  | 250
102 | 1 | GSO_144 | line_5978_22 | S_nCCTT504 | 11.2671 | High | 12.47 | 12.3112 | 0.13286 | 12.1784 | 0.13286 | 11.4 | 11.2671 | br_024_22 | CircuitBreaker | Breaker | 11.4 | 0.13286 | 11.2671 | 2 | 1 | 0 | 100 | 5.6667 | 0.064548 | -79.9468 | 36.0459 | recloser_188_22 -> line_5978_22 | GSO_144¦line_5978_22 | ACLineSegment | 600 | 12000 | Meter | br_024_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 11.2671 | [6 empty] | SubstationCapacityUnresolved | br_024_22 | Substation capacity unresolved |  | 250
518 | 2 | GSO_144 | line_5977_22 | S_nCCTT505 | 6.9921 | High | 7.2 | 7.1083 | 0.11626 | 6.9921 | 0.13286 | 11.4 | 11.2671 | line_5977_22 | ACLineSegment | Line | 7.1083 | 0.11626 | 6.9921 | 4 | 2 | 0 | 100 | 5.6667 | 0.064548 | -79.9465 | 36.0458 | recloser_188_22 -> line_5978_22 -> fuse_139_22 -> line_5977_22 | GSO_144¦line_5977_22 | ACLineSegment | 600 | 12000 | Meter | br_024_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 6.9921 | [6 empty] | SubstationCapacityUnresolved | line_5977_22 | Substation capacity unresolved |  | 250
519 | 3 | GSO_144 | line_5982_22 | S_nCCTT505_B_S_nCCTT506 | 6.9921 | High | 7.2 | 7.1083 | 0.074736 | 7.0336 | 0.13286 | 11.4 | 11.2671 | line_5977_22 | ACLineSegment | Line | 7.1083 | 0.11626 | 6.9921 | 5 | 3 | 0 | 100 | 5.6667 | 0.064548 | -79.9462 | 36.0458 | recloser_188_22 -> line_5978_22 -> fuse_139_22 -> line_5977_22 -> line_5982_22 | GSO_144¦line_5982_22 | ACLineSegment | 600 | 12000 | Meter | br_024_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 6.9921 | [6 empty] | SubstationCapacityUnresolved | line_5977_22 | Substation capacity unresolved |  | 250
520 | 4 | GSO_144 | line_5973_22 | S_nCCTT503 | 6.9921 | High | 7.2 | 7.1083 | 0.053976 | 7.0544 | 0.13286 | 11.4 | 11.2671 | line_5977_22 | ACLineSegment | Line | 7.1083 | 0.11626 | 6.9921 | 8 | 4 | 0 | 100 | 5.6667 | 0.064548 | -79.9458 | 36.0459 | recloser_188_22 -> line_5978_22 -> fuse_139_22 -> line_5977_22 -> line_5982_22 -> switch_710_22 -> switch_703_22 -> line_5973_22 | GSO_144¦line_5973_22 | ACLineSegment | 600 | 12000 | Meter | br_024_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 6.9921 | [6 empty] | SubstationCapacityUnresolved | line_5977_22 | Substation capacity unresolved |  | 250
521 | 5 | GSO_144 | line_5974_22 | S_nCCTT503_B_S_nCCTT507 | 6.9921 | High | 7.2 | 7.1083 | 0.045672 | 7.0627 | 0.13286 | 11.4 | 11.2671 | line_5977_22 | ACLineSegment | Line | 7.1083 | 0.11626 | 6.9921 | 9 | 5 | 0 | 100 | 5.6667 | 0.064548 | -79.9454 | 36.0459 | recloser_188_22 -> line_5978_22 -> fuse_139_22 -> line_5977_22 -> line_5982_22 -> switch_710_22 -> switch_703_22 -> line_5973_22 -> line_5974_22 | GSO_144¦line_5974_22 | ACLineSegment | 600 | 12000 | Meter | br_024_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 6.9921 | [6 empty] | SubstationCapacityUnresolved | line_5977_22 | Substation capacity unresolved |  | 250
147 | 1 | GSO_145 | line_6170_22 | S_nCCTT59 | 10.6656 | Medium | 12.47 | 13.5424 | 0.73442 | 12.8079 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 2 | 1 | 0 | 90.9677 | 16.5 | 0.18795 | -79.943 | 36.0469 | recloser_192_22 -> line_6170_22 | GSO_145¦line_6170_22 | ACLineSegment | 660 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
148 | 2 | GSO_145 | line_5166_22 | S_nCCTT1583 | 10.6656 | Medium | 12.47 | 13.5424 | 0.67713 | 12.8652 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 3 | 2 | 0 | 90.9677 | 16.5 | 0.18795 | -79.9402 | 36.0491 | recloser_192_22 -> line_6170_22 -> line_5166_22 | GSO_145¦line_5166_22 | ACLineSegment | 660 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
149 | 3 | GSO_145 | line_5164_22 | S_nCCTT207 | 10.6656 | Medium | 12.47 | 13.5424 | 0.63546 | 12.9069 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 4 | 3 | 0 | 90.9677 | 16.5 | 0.18795 | -79.9399 | 36.0499 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 | GSO_145¦line_5164_22 | ACLineSegment | 660 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
150 | 4 | GSO_145 | line_5344_22 | S_nCCTT280 | 10.6656 | Medium | 12.47 | 13.5424 | 0.56254 | 12.9798 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 5 | 4 | 0 | 90.9677 | 16.5 | 0.18795 | -79.9401 | 36.0503 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 | GSO_145¦line_5344_22 | ACLineSegment | 660 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
151 | 5 | GSO_145 | line_5482_22 | S_nCCTT496 | 10.6656 | Medium | 12.47 | 13.5424 | 0.53649 | 13.0059 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 6 | 5 | 0 | 90.9677 | 16.5 | 0.18795 | -79.941 | 36.0507 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 | GSO_145¦line_5482_22 | ACLineSegment | 660 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
152 | 6 | GSO_145 | line_5955_22 | S_nCCTT757 | 10.6656 | Medium | 12.47 | 13.5424 | 0.53129 | 13.0111 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 7 | 6 | 0 | 90.9677 | 16.5 | 0.18795 | -79.9415 | 36.0513 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 | GSO_145¦line_5955_22 | ACLineSegment | 660 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
153 | 7 | GSO_145 | line_6070_22 | S_nCCTT547 | 10.6656 | Medium | 12.47 | 13.5424 | 0.52608 | 13.0163 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 8 | 7 | 0 | 90.9677 | 16.5 | 0.18795 | -79.9412 | 36.0523 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 | GSO_145¦line_6070_22 | ACLineSegment | 660 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
154 | 8 | GSO_145 | line_4633_22 | S_nCCTT1369 | 10.6656 | Medium | 12.47 | 13.5424 | 0.51566 | 13.0267 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 9 | 8 | 0 | 90.9677 | 16.5 | 0.18795 | -79.9408 | 36.0535 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 | GSO_145¦line_4633_22 | ACLineSegment | 660 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
155 | 9 | GSO_145 | line_6069_22 | S_nCCTT617 | 10.6656 | Medium | 12.47 | 13.5424 | 0.0052087 | 13.5372 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 9 | 8 | 0 | 90.9677 | 16.5 | 0.18795 | -79.9409 | 36.0529 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_6069_22 | GSO_145¦line_6069_22 | ACLineSegment | 660 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
156 | 10 | GSO_145 | line_4634_22 | S_nCCTT640 | 10.6656 | Medium | 12.47 | 13.5424 | 0.50524 | 13.0371 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 10 | 9 | 0 | 90.9677 | 16.5 | 0.18795 | -79.9418 | 36.0542 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 | GSO_145¦line_4634_22 | ACLineSegment | 660 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
157 | 11 | GSO_145 | line_4635_22 | S_nCCTT860 | 10.6656 | Medium | 12.47 | 13.5424 | 0.0052087 | 13.5372 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 10 | 9 | 0 | 90.9677 | 16.5 | 0.18795 | -79.9405 | 36.0537 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4635_22 | GSO_145¦line_4635_22 | ACLineSegment | 660 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
158 | 12 | GSO_145 | line_4279_22 | S_nCCTT1248 | 10.6656 | Medium | 12.47 | 12.3112 | 0.4792 | 11.832 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 12 | 10 | 0 | 90.9677 | 16.5 | 0.18795 | -79.9431 | 36.0543 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 -> switch_386_22 -> line_4279_22 | GSO_145¦line_4279_22 | ACLineSegment | 600 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
159 | 13 | GSO_145 | line_4718_22 | S_nCCTT1400 | 10.6656 | Medium | 12.47 | 12.3112 | 0.020835 | 12.2904 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 12 | 10 | 0 | 90.9677 | 16.5 | 0.18795 | -79.9428 | 36.0548 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 -> switch_491_22 -> line_4718_22 | GSO_145¦line_4718_22 | ACLineSegment | 600 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
160 | 14 | GSO_145 | line_4225_22 | S_nCCTT1232 | 10.6656 | Medium | 12.47 | 13.5424 | 0.47399 | 13.0684 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 13 | 11 | 0 | 90.9677 | 16.5 | 0.18795 | -79.9441 | 36.0536 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 -> switch_386_22 -> line_4279_22 -> line_4225_22 | GSO_145¦line_4225_22 | ACLineSegment | 660 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
161 | 15 | GSO_145 | line_4719_22 | S_nCCTT1400_B_S_nCCTT766 | 10.6656 | Medium | 12.47 | 12.3112 | 0.015626 | 12.2956 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 13 | 11 | 0 | 90.9677 | 16.5 | 0.18795 | -79.9433 | 36.0552 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 -> switch_491_22 -> line_4718_22 -> line_4719_22 | GSO_145¦line_4719_22 | ACLineSegment | 600 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
162 | 16 | GSO_145 | line_4226_22 | S_nCCTT774 | 10.6656 | Medium | 12.47 | 13.5424 | 0.46357 | 13.0788 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 14 | 12 | 0 | 90.9677 | 16.5 | 0.18795 | -79.9453 | 36.0537 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 -> switch_386_22 -> line_4279_22 -> line_4225_22 -> line_4226_22 | GSO_145¦line_4226_22 | ACLineSegment | 660 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
163 | 17 | GSO_145 | line_5348_22 | S_nCCTT766_B_S_nCCTT209 | 10.6656 | Medium | 12.47 | 12.3112 | 0.010417 | 12.3008 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 15 | 12 | 0 | 90.9677 | 16.5 | 0.18795 | -79.9437 | 36.0553 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 -> switch_491_22 -> line_4718_22 -> line_4719_22 -> switch_494_22 -> line_5348_22 | GSO_145¦line_5348_22 | ACLineSegment | 600 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
164 | 18 | GSO_145 | line_6270_22 | S_nCCTT635 | 10.6656 | Medium | 12.47 | 12.3112 | 0.44274 | 11.8685 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 16 | 13 | 0 | 90.9677 | 16.5 | 0.18795 | -79.9457 | 36.0541 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 -> switch_386_22 -> line_4279_22 -> line_4225_22 -> line_4226_22 -> switch_755_22 -> line_6270_22 | GSO_145¦line_6270_22 | ACLineSegment | 600 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
165 | 19 | GSO_145 | line_5863_22 | S_nCCTT456 | 10.6656 | Medium | 12.47 | 12.3112 | 0.43753 | 11.8737 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 18 | 14 | 0 | 90.9677 | 16.5 | 0.18795 | -79.9454 | 36.0547 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 -> switch_386_22 -> line_4279_22 -> line_4225_22 -> line_4226_22 -> switch_755_22 -> line_6270_22 -> switch_679_22 -> line_5863_22 | GSO_145¦line_5863_22 | ACLineSegment | 600 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
166 | 20 | GSO_145 | line_5864_22 | S_nCCTT709 | 10.6656 | Medium | 12.47 | 12.3112 | 0.43232 | 11.8789 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 20 | 15 | 0 | 90.9677 | 16.5 | 0.18795 | -79.9453 | 36.0557 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 -> switch_386_22 -> line_4279_22 -> line_4225_22 -> line_4226_22 -> switch_755_22 -> line_6270_22 -> switch_679_22 -> line_5863_22 -> switch_681_22 -> line_5864_22 | GSO_145¦line_5864_22 | ACLineSegment | 600 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
167 | 21 | GSO_145 | line_4373_22 | S_nCCTT1279 | 10.6656 | Medium | 12.47 | 12.3112 | 0.4219 | 11.8893 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 22 | 16 | 0 | 90.9677 | 16.5 | 0.18795 | -79.9451 | 36.0562 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 -> switch_386_22 -> line_4279_22 -> line_4225_22 -> line_4226_22 -> switch_755_22 -> line_6270_22 -> switch_679_22 -> line_5863_22 -> switch_681_22 -> line_5864_22 -> switch_408_22 -> line_4373_22 | GSO_145¦line_4373_22 | ACLineSegment | 600 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
168 | 22 | GSO_145 | line_5477_22 | S_nCCTT278 | 10.6656 | Medium | 12.47 | 12.3112 | 0.0052087 | 12.306 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 22 | 16 | 0 | 90.9677 | 16.5 | 0.18795 | -79.9457 | 36.0562 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 -> switch_386_22 -> line_4279_22 -> line_4225_22 -> line_4226_22 -> switch_755_22 -> line_6270_22 -> switch_679_22 -> line_5863_22 -> switch_681_22 -> line_5864_22 -> switch_637_22 -> line_5477_22 | GSO_145¦line_5477_22 | ACLineSegment | 600 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
169 | 23 | GSO_145 | line_4372_22 | S_nCCTT1279_B_S_nCCTT485 | 10.6656 | Medium | 12.47 | 12.3112 | 0.41669 | 11.8945 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 23 | 17 | 0 | 90.9677 | 16.5 | 0.18795 | -79.9445 | 36.0571 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 -> switch_386_22 -> line_4279_22 -> line_4225_22 -> line_4226_22 -> switch_755_22 -> line_6270_22 -> switch_679_22 -> line_5863_22 -> switch_681_22 -> line_5864_22 -> switch_408_22 -> line_4373_22 -> line_4372_22 | GSO_145¦line_4372_22 | ACLineSegment | 600 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
170 | 24 | GSO_145 | line_5881_22 | S_nCCTT462 | 10.6656 | Medium | 12.47 | 12.3112 | 0.41149 | 11.8998 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 26 | 18 | 0 | 90.9677 | 16.5 | 0.18795 | -79.9437 | 36.0577 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 -> switch_386_22 -> line_4279_22 -> line_4225_22 -> line_4226_22 -> switch_755_22 -> line_6270_22 -> switch_679_22 -> line_5863_22 -> switch_681_22 -> line_5864_22 -> switch_408_22 -> line_4373_22 -> line_4372_22 -> switch_407_22 -> switch_685_22 -> line_5881_22 | GSO_145¦line_5881_22 | ACLineSegment | 600 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
171 | 25 | GSO_145 | line_5457_22 | S_nCCTT263 | 10.6656 | Medium | 12.47 | 12.3112 | 0.057295 | 12.2539 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 28 | 19 | 0 | 90.9677 | 16.5 | 0.18795 | -79.9436 | 36.0584 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 -> switch_386_22 -> line_4279_22 -> line_4225_22 -> line_4226_22 -> switch_755_22 -> line_6270_22 -> switch_679_22 -> line_5863_22 -> switch_681_22 -> line_5864_22 -> switch_408_22 -> line_4373_22 -> line_4372_22 -> switch_407_22 -> switch_685_22 -> line_5881_22 -> switch_632_22 -> line_5457_22 | GSO_145¦line_5457_22 | ACLineSegment | 600 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
172 | 26 | GSO_145 | line_5882_22 | S_nCCTT559 | 10.6656 | Medium | 12.47 | 12.3112 | 0.34898 | 11.9623 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 28 | 19 | 0 | 90.9677 | 16.5 | 0.18795 | -79.9428 | 36.0582 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 -> switch_386_22 -> line_4279_22 -> line_4225_22 -> line_4226_22 -> switch_755_22 -> line_6270_22 -> switch_679_22 -> line_5863_22 -> switch_681_22 -> line_5864_22 -> switch_408_22 -> line_4373_22 -> line_4372_22 -> switch_407_22 -> switch_685_22 -> line_5881_22 -> switch_687_22 -> line_5882_22 | GSO_145¦line_5882_22 | ACLineSegment | 600 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
173 | 27 | GSO_145 | line_5240_22 | S_nCCTT263_B_S_nCCTT169 | 10.6656 | Medium | 12.47 | 12.3112 | 0.052087 | 12.2592 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 29 | 20 | 0 | 90.9677 | 16.5 | 0.18795 | -79.9438 | 36.059 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 -> switch_386_22 -> line_4279_22 -> line_4225_22 -> line_4226_22 -> switch_755_22 -> line_6270_22 -> switch_679_22 -> line_5863_22 -> switch_681_22 -> line_5864_22 -> switch_408_22 -> line_4373_22 -> line_4372_22 -> switch_407_22 -> switch_685_22 -> line_5881_22 -> switch_632_22 -> line_5457_22 -> line_5240_22 | GSO_145¦line_5240_22 | ACLineSegment | 600 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
174 | 28 | GSO_145 | line_6098_22 | S_nCCTT559_B_S_nCCTT638 | 10.6656 | Medium | 12.47 | 12.3112 | 0.34377 | 11.9675 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 29 | 20 | 0 | 90.9677 | 16.5 | 0.18795 | -79.9412 | 36.0584 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 -> switch_386_22 -> line_4279_22 -> line_4225_22 -> line_4226_22 -> switch_755_22 -> line_6270_22 -> switch_679_22 -> line_5863_22 -> switch_681_22 -> line_5864_22 -> switch_408_22 -> line_4373_22 -> line_4372_22 -> switch_407_22 -> switch_685_22 -> line_5881_22 -> switch_687_22 -> line_5882_22 -> line_6098_22 | GSO_145¦line_6098_22 | ACLineSegment | 600 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
175 | 29 | GSO_145 | line_6277_22 | S_nCCTT638_B_UCMV122 | 10.6656 | Medium | 12.47 | 12.3112 | 0.33856 | 11.9727 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 31 | 21 | 0 | 90.9677 | 16.5 | 0.18795 | -79.9398 | 36.0586 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 -> switch_386_22 -> line_4279_22 -> line_4225_22 -> line_4226_22 -> switch_755_22 -> line_6270_22 -> switch_679_22 -> line_5863_22 -> switch_681_22 -> line_5864_22 -> switch_408_22 -> line_4373_22 -> line_4372_22 -> switch_407_22 -> switch_685_22 -> line_5881_22 -> switch_687_22 -> line_5882_22 -> line_6098_22 -> switch_734_22 -> line_6277_22 | GSO_145¦line_6277_22 | ACLineSegment | 600 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
176 | 30 | GSO_145 | line_5239_22 | S_nCCTT216 | 10.6656 | Medium | 12.47 | 12.3112 | 0.046878 | 12.2644 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 32 | 21 | 0 | 90.9677 | 16.5 | 0.18795 | -79.9436 | 36.0594 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 -> switch_386_22 -> line_4279_22 -> line_4225_22 -> line_4226_22 -> switch_755_22 -> line_6270_22 -> switch_679_22 -> line_5863_22 -> switch_681_22 -> line_5864_22 -> switch_408_22 -> line_4373_22 -> line_4372_22 -> switch_407_22 -> switch_685_22 -> line_5881_22 -> switch_632_22 -> line_5457_22 -> line_5240_22 -> switch_598_22 -> switch_595_22 -> line_5239_22 | GSO_145¦line_5239_22 | ACLineSegment | 600 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
177 | 31 | GSO_145 | line_5232_22 | S_nCCTT216_B_S_nCCTT164 | 10.6656 | Medium | 12.47 | 12.3112 | 0.036461 | 12.2748 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 33 | 22 | 0 | 90.9677 | 16.5 | 0.18795 | -79.9428 | 36.0604 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 -> switch_386_22 -> line_4279_22 -> line_4225_22 -> line_4226_22 -> switch_755_22 -> line_6270_22 -> switch_679_22 -> line_5863_22 -> switch_681_22 -> line_5864_22 -> switch_408_22 -> line_4373_22 -> line_4372_22 -> switch_407_22 -> switch_685_22 -> line_5881_22 -> switch_632_22 -> line_5457_22 -> line_5240_22 -> switch_598_22 -> switch_595_22 -> line_5239_22 -> line_5232_22 | GSO_145¦line_5232_22 | ACLineSegment | 600 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
178 | 32 | GSO_145 | line_6495_22 | UCMV122_B_S_nCCTT754 | 10.6656 | Medium | 12.47 | 12.3112 | 0.33336 | 11.9779 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 33 | 22 | 0 | 90.9677 | 16.5 | 0.18795 | -79.9386 | 36.0588 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 -> switch_386_22 -> line_4279_22 -> line_4225_22 -> line_4226_22 -> switch_755_22 -> line_6270_22 -> switch_679_22 -> line_5863_22 -> switch_681_22 -> line_5864_22 -> switch_408_22 -> line_4373_22 -> line_4372_22 -> switch_407_22 -> switch_685_22 -> line_5881_22 -> switch_687_22 -> line_5882_22 -> line_6098_22 -> switch_734_22 -> line_6277_22 -> switch_758_22 -> line_6495_22 | GSO_145¦line_6495_22 | ACLineSegment | 600 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
179 | 33 | GSO_145 | line_6040_22 | S_nCCTT754_B_S_nCCTT533 | 10.6656 | Medium | 12.47 | 12.3112 | 0.32815 | 11.9831 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 35 | 23 | 0 | 90.9677 | 16.5 | 0.18795 | -79.9387 | 36.0581 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 -> switch_386_22 -> line_4279_22 -> line_4225_22 -> line_4226_22 -> switch_755_22 -> line_6270_22 -> switch_679_22 -> line_5863_22 -> switch_681_22 -> line_5864_22 -> switch_408_22 -> line_4373_22 -> line_4372_22 -> switch_407_22 -> switch_685_22 -> line_5881_22 -> switch_687_22 -> line_5882_22 -> line_6098_22 -> switch_734_22 -> line_6277_22 -> switch_758_22 -> line_6495_22 -> switch_768_22 -> line_6040_22 | GSO_145¦line_6040_22 | ACLineSegment | 600 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
180 | 34 | GSO_145 | line_5609_22 | S_nCCTT346 | 10.6656 | Medium | 12.47 | 13.5424 | 0.30731 | 13.2351 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 38 | 24 | 0 | 90.9677 | 16.5 | 0.18795 | -79.9379 | 36.0578 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 -> switch_386_22 -> line_4279_22 -> line_4225_22 -> line_4226_22 -> switch_755_22 -> line_6270_22 -> switch_679_22 -> line_5863_22 -> switch_681_22 -> line_5864_22 -> switch_408_22 -> line_4373_22 -> line_4372_22 -> switch_407_22 -> switch_685_22 -> line_5881_22 -> switch_687_22 -> line_5882_22 -> line_6098_22 -> switch_734_22 -> line_6277_22 -> switch_758_22 -> line_6495_22 -> switch_768_22 -> line_6040_22 -> switch_719_22 -> recloser_181_22 -> line_5609_22 | GSO_145¦line_5609_22 | ACLineSegment | 660 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
181 | 35 | GSO_145 | line_4729_22 | S_nCCTT1404 | 10.6656 | Medium | 12.47 | 12.3112 | 0.010417 | 12.3008 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 38 | 24 | 0 | 90.9677 | 16.5 | 0.18795 | -79.9389 | 36.0575 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 -> switch_386_22 -> line_4279_22 -> line_4225_22 -> line_4226_22 -> switch_755_22 -> line_6270_22 -> switch_679_22 -> line_5863_22 -> switch_681_22 -> line_5864_22 -> switch_408_22 -> line_4373_22 -> line_4372_22 -> switch_407_22 -> switch_685_22 -> line_5881_22 -> switch_687_22 -> line_5882_22 -> line_6098_22 -> switch_734_22 -> line_6277_22 -> switch_758_22 -> line_6495_22 -> switch_768_22 -> line_6040_22 -> switch_719_22 -> switch_496_22 -> line_4729_22 | GSO_145¦line_4729_22 | ACLineSegment | 600 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
182 | 36 | GSO_145 | line_4243_22 | S_nCCTT1236 | 10.6656 | Medium | 12.47 | 13.5424 | 0.3021 | 13.2403 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 39 | 25 | 0 | 90.9677 | 16.5 | 0.18795 | -79.9371 | 36.0572 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 -> switch_386_22 -> line_4279_22 -> line_4225_22 -> line_4226_22 -> switch_755_22 -> line_6270_22 -> switch_679_22 -> line_5863_22 -> switch_681_22 -> line_5864_22 -> switch_408_22 -> line_4373_22 -> line_4372_22 -> switch_407_22 -> switch_685_22 -> line_5881_22 -> switch_687_22 -> line_5882_22 -> line_6098_22 -> switch_734_22 -> line_6277_22 -> switch_758_22 -> line_6495_22 -> switch_768_22 -> line_6040_22 -> switch_719_22 -> recloser_181_22 -> line_5609_22 -> line_4243_22 | GSO_145¦line_4243_22 | ACLineSegment | 660 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
183 | 37 | GSO_145 | line_4242_22 | S_nCCTT1288 | 10.6656 | Medium | 12.47 | 13.5424 | 0.27606 | 13.2663 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 40 | 26 | 0 | 90.9677 | 16.5 | 0.18795 | -79.9366 | 36.0568 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 -> switch_386_22 -> line_4279_22 -> line_4225_22 -> line_4226_22 -> switch_755_22 -> line_6270_22 -> switch_679_22 -> line_5863_22 -> switch_681_22 -> line_5864_22 -> switch_408_22 -> line_4373_22 -> line_4372_22 -> switch_407_22 -> switch_685_22 -> line_5881_22 -> switch_687_22 -> line_5882_22 -> line_6098_22 -> switch_734_22 -> line_6277_22 -> switch_758_22 -> line_6495_22 -> switch_768_22 -> line_6040_22 -> switch_719_22 -> recloser_181_22 -> line_5609_22 -> line_4243_22 -> line_4242_22 | GSO_145¦line_4242_22 | ACLineSegment | 660 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
184 | 38 | GSO_145 | line_4396_22 | S_nCCTT527 | 10.6656 | Medium | 12.47 | 13.5424 | 0.13022 | 13.4122 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 41 | 27 | 0 | 90.9677 | 16.5 | 0.18795 | -79.936 | 36.057 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 -> switch_386_22 -> line_4279_22 -> line_4225_22 -> line_4226_22 -> switch_755_22 -> line_6270_22 -> switch_679_22 -> line_5863_22 -> switch_681_22 -> line_5864_22 -> switch_408_22 -> line_4373_22 -> line_4372_22 -> switch_407_22 -> switch_685_22 -> line_5881_22 -> switch_687_22 -> line_5882_22 -> line_6098_22 -> switch_734_22 -> line_6277_22 -> switch_758_22 -> line_6495_22 -> switch_768_22 -> line_6040_22 -> switch_719_22 -> recloser_181_22 -> line_5609_22 -> line_4243_22 -> line_4242_22 -> line_4396_22 | GSO_145¦line_4396_22 | ACLineSegment | 660 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
185 | 39 | GSO_145 | line_4397_22 | S_nCCTT577 | 10.6656 | Medium | 12.47 | 13.5424 | 0.14063 | 13.4017 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 41 | 27 | 0 | 90.9677 | 16.5 | 0.18795 | -79.936 | 36.0567 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 -> switch_386_22 -> line_4279_22 -> line_4225_22 -> line_4226_22 -> switch_755_22 -> line_6270_22 -> switch_679_22 -> line_5863_22 -> switch_681_22 -> line_5864_22 -> switch_408_22 -> line_4373_22 -> line_4372_22 -> switch_407_22 -> switch_685_22 -> line_5881_22 -> switch_687_22 -> line_5882_22 -> line_6098_22 -> switch_734_22 -> line_6277_22 -> switch_758_22 -> line_6495_22 -> switch_768_22 -> line_6040_22 -> switch_719_22 -> recloser_181_22 -> line_5609_22 -> line_4243_22 -> line_4242_22 -> line_4397_22 | GSO_145¦line_4397_22 | ACLineSegment | 660 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
186 | 40 | GSO_145 | line_4244_22 | S_nCCTT453 | 10.6656 | Medium | 12.47 | 13.5424 | 0.020835 | 13.5215 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 41 | 26 | 0 | 90.9677 | 16.5 | 0.18795 | -79.9375 | 36.0561 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 -> switch_386_22 -> line_4279_22 -> line_4225_22 -> line_4226_22 -> switch_755_22 -> line_6270_22 -> switch_679_22 -> line_5863_22 -> switch_681_22 -> line_5864_22 -> switch_408_22 -> line_4373_22 -> line_4372_22 -> switch_407_22 -> switch_685_22 -> line_5881_22 -> switch_687_22 -> line_5882_22 -> line_6098_22 -> switch_734_22 -> line_6277_22 -> switch_758_22 -> line_6495_22 -> switch_768_22 -> line_6040_22 -> switch_719_22 -> recloser_181_22 -> line_5609_22 -> line_4243_22 -> switch_379_22 -> line_4244_22 | GSO_145¦line_4244_22 | ACLineSegment | 660 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
187 | 41 | GSO_145 | line_5671_22 | S_nCCTT373 | 10.6656 | Medium | 12.47 | 13.5424 | 0.010417 | 13.532 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 42 | 27 | 0 | 90.9677 | 16.5 | 0.18795 | -79.938 | 36.0547 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 -> switch_386_22 -> line_4279_22 -> line_4225_22 -> line_4226_22 -> switch_755_22 -> line_6270_22 -> switch_679_22 -> line_5863_22 -> switch_681_22 -> line_5864_22 -> switch_408_22 -> line_4373_22 -> line_4372_22 -> switch_407_22 -> switch_685_22 -> line_5881_22 -> switch_687_22 -> line_5882_22 -> line_6098_22 -> switch_734_22 -> line_6277_22 -> switch_758_22 -> line_6495_22 -> switch_768_22 -> line_6040_22 -> switch_719_22 -> recloser_181_22 -> line_5609_22 -> line_4243_22 -> switch_379_22 -> line_4244_22 -> line_5671_22 | GSO_145¦line_5671_22 | ACLineSegment | 660 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
188 | 42 | GSO_145 | line_6028_22 | S_nCCTT654 | 10.6656 | Medium | 12.47 | 13.5424 | 0.12501 | 13.4174 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 42 | 28 | 0 | 90.9677 | 16.5 | 0.18795 | -79.936 | 36.0572 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 -> switch_386_22 -> line_4279_22 -> line_4225_22 -> line_4226_22 -> switch_755_22 -> line_6270_22 -> switch_679_22 -> line_5863_22 -> switch_681_22 -> line_5864_22 -> switch_408_22 -> line_4373_22 -> line_4372_22 -> switch_407_22 -> switch_685_22 -> line_5881_22 -> switch_687_22 -> line_5882_22 -> line_6098_22 -> switch_734_22 -> line_6277_22 -> switch_758_22 -> line_6495_22 -> switch_768_22 -> line_6040_22 -> switch_719_22 -> recloser_181_22 -> line_5609_22 -> line_4243_22 -> line_4242_22 -> line_4396_22 -> line_6028_22 | GSO_145¦line_6028_22 | ACLineSegment | 660 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
189 | 43 | GSO_145 | line_6138_22 | S_nCCTT855 | 10.6656 | Medium | 12.47 | 13.5424 | 0.13543 | 13.4069 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 42 | 28 | 0 | 90.9677 | 16.5 | 0.18795 | -79.936 | 36.0563 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 -> switch_386_22 -> line_4279_22 -> line_4225_22 -> line_4226_22 -> switch_755_22 -> line_6270_22 -> switch_679_22 -> line_5863_22 -> switch_681_22 -> line_5864_22 -> switch_408_22 -> line_4373_22 -> line_4372_22 -> switch_407_22 -> switch_685_22 -> line_5881_22 -> switch_687_22 -> line_5882_22 -> line_6098_22 -> switch_734_22 -> line_6277_22 -> switch_758_22 -> line_6495_22 -> switch_768_22 -> line_6040_22 -> switch_719_22 -> recloser_181_22 -> line_5609_22 -> line_4243_22 -> line_4242_22 -> line_4397_22 -> line_6138_22 | GSO_145¦line_6138_22 | ACLineSegment | 660 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
190 | 44 | GSO_145 | line_5401_22 | S_nCCTT231 | 10.6656 | Medium | 12.47 | 13.5424 | 0.1198 | 13.4226 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 43 | 29 | 0 | 90.9677 | 16.5 | 0.18795 | -79.9359 | 36.0555 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 -> switch_386_22 -> line_4279_22 -> line_4225_22 -> line_4226_22 -> switch_755_22 -> line_6270_22 -> switch_679_22 -> line_5863_22 -> switch_681_22 -> line_5864_22 -> switch_408_22 -> line_4373_22 -> line_4372_22 -> switch_407_22 -> switch_685_22 -> line_5881_22 -> switch_687_22 -> line_5882_22 -> line_6098_22 -> switch_734_22 -> line_6277_22 -> switch_758_22 -> line_6495_22 -> switch_768_22 -> line_6040_22 -> switch_719_22 -> recloser_181_22 -> line_5609_22 -> line_4243_22 -> line_4242_22 -> line_4397_22 -> line_6138_22 -> line_5401_22 | GSO_145¦line_5401_22 | ACLineSegment | 660 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
191 | 45 | GSO_145 | line_5672_22 | S_nCCTT694 | 10.6656 | Medium | 12.47 | 13.5424 | 0.0052087 | 13.5372 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 43 | 28 | 0 | 90.9677 | 16.5 | 0.18795 | -79.9374 | 36.0542 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 -> switch_386_22 -> line_4279_22 -> line_4225_22 -> line_4226_22 -> switch_755_22 -> line_6270_22 -> switch_679_22 -> line_5863_22 -> switch_681_22 -> line_5864_22 -> switch_408_22 -> line_4373_22 -> line_4372_22 -> switch_407_22 -> switch_685_22 -> line_5881_22 -> switch_687_22 -> line_5882_22 -> line_6098_22 -> switch_734_22 -> line_6277_22 -> switch_758_22 -> line_6495_22 -> switch_768_22 -> line_6040_22 -> switch_719_22 -> recloser_181_22 -> line_5609_22 -> line_4243_22 -> switch_379_22 -> line_4244_22 -> line_5671_22 -> line_5672_22 | GSO_145¦line_5672_22 | ACLineSegment | 660 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
192 | 46 | GSO_145 | line_6309_22 | S_nCCTT747 | 10.6656 | Medium | 12.47 | 13.5424 | 0.1198 | 13.4226 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 43 | 29 | 0 | 90.9677 | 16.5 | 0.18795 | -79.936 | 36.0574 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 -> switch_386_22 -> line_4279_22 -> line_4225_22 -> line_4226_22 -> switch_755_22 -> line_6270_22 -> switch_679_22 -> line_5863_22 -> switch_681_22 -> line_5864_22 -> switch_408_22 -> line_4373_22 -> line_4372_22 -> switch_407_22 -> switch_685_22 -> line_5881_22 -> switch_687_22 -> line_5882_22 -> line_6098_22 -> switch_734_22 -> line_6277_22 -> switch_758_22 -> line_6495_22 -> switch_768_22 -> line_6040_22 -> switch_719_22 -> recloser_181_22 -> line_5609_22 -> line_4243_22 -> line_4242_22 -> line_4396_22 -> line_6028_22 -> line_6309_22 | GSO_145¦line_6309_22 | ACLineSegment | 660 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
193 | 47 | GSO_145 | line_6314_22 | S_nCCTT656 | 10.6656 | Medium | 12.47 | 13.5424 | 0.010417 | 13.532 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 43 | 29 | 0 | 90.9677 | 16.5 | 0.18795 | -79.9354 | 36.0562 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 -> switch_386_22 -> line_4279_22 -> line_4225_22 -> line_4226_22 -> switch_755_22 -> line_6270_22 -> switch_679_22 -> line_5863_22 -> switch_681_22 -> line_5864_22 -> switch_408_22 -> line_4373_22 -> line_4372_22 -> switch_407_22 -> switch_685_22 -> line_5881_22 -> switch_687_22 -> line_5882_22 -> line_6098_22 -> switch_734_22 -> line_6277_22 -> switch_758_22 -> line_6495_22 -> switch_768_22 -> line_6040_22 -> switch_719_22 -> recloser_181_22 -> line_5609_22 -> line_4243_22 -> line_4242_22 -> line_4397_22 -> line_6138_22 -> line_6314_22 | GSO_145¦line_6314_22 | ACLineSegment | 660 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
194 | 48 | GSO_145 | line_4785_22 | S_nCCTT1426 | 10.6656 | Medium | 12.47 | 13.5424 | 0.041669 | 13.5007 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 44 | 30 | 0 | 90.9677 | 16.5 | 0.18795 | -79.9355 | 36.0545 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 -> switch_386_22 -> line_4279_22 -> line_4225_22 -> line_4226_22 -> switch_755_22 -> line_6270_22 -> switch_679_22 -> line_5863_22 -> switch_681_22 -> line_5864_22 -> switch_408_22 -> line_4373_22 -> line_4372_22 -> switch_407_22 -> switch_685_22 -> line_5881_22 -> switch_687_22 -> line_5882_22 -> line_6098_22 -> switch_734_22 -> line_6277_22 -> switch_758_22 -> line_6495_22 -> switch_768_22 -> line_6040_22 -> switch_719_22 -> recloser_181_22 -> line_5609_22 -> line_4243_22 -> line_4242_22 -> line_4397_22 -> line_6138_22 -> line_5401_22 -> line_4785_22 | GSO_145¦line_4785_22 | ACLineSegment | 660 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
195 | 49 | GSO_145 | line_4788_22 | S_nCCTT1426 | 10.6656 | Medium | 12.47 | 13.5424 | 0 | 13.5424 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 44 | 30 | 0 | 90.9677 | 16.5 | 0.18795 | -79.9361 | 36.0542 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 -> switch_386_22 -> line_4279_22 -> line_4225_22 -> line_4226_22 -> switch_755_22 -> line_6270_22 -> switch_679_22 -> line_5863_22 -> switch_681_22 -> line_5864_22 -> switch_408_22 -> line_4373_22 -> line_4372_22 -> switch_407_22 -> switch_685_22 -> line_5881_22 -> switch_687_22 -> line_5882_22 -> line_6098_22 -> switch_734_22 -> line_6277_22 -> switch_758_22 -> line_6495_22 -> switch_768_22 -> line_6040_22 -> switch_719_22 -> recloser_181_22 -> line_5609_22 -> line_4243_22 -> line_4242_22 -> line_4397_22 -> line_6138_22 -> line_5401_22 -> line_4785_22 | GSO_145¦line_4788_22 | ACLineSegment | 660 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
196 | 50 | GSO_145 | line_5497_22 | S_nCCTT293 | 10.6656 | Medium | 12.47 | 13.5424 | 0.015626 | 13.5267 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 44 | 30 | 0 | 90.9677 | 16.5 | 0.18795 | -79.936 | 36.0577 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 -> switch_386_22 -> line_4279_22 -> line_4225_22 -> line_4226_22 -> switch_755_22 -> line_6270_22 -> switch_679_22 -> line_5863_22 -> switch_681_22 -> line_5864_22 -> switch_408_22 -> line_4373_22 -> line_4372_22 -> switch_407_22 -> switch_685_22 -> line_5881_22 -> switch_687_22 -> line_5882_22 -> line_6098_22 -> switch_734_22 -> line_6277_22 -> switch_758_22 -> line_6495_22 -> switch_768_22 -> line_6040_22 -> switch_719_22 -> recloser_181_22 -> line_5609_22 -> line_4243_22 -> line_4242_22 -> line_4396_22 -> line_6028_22 -> line_6309_22 -> line_5497_22 | GSO_145¦line_5497_22 | ACLineSegment | 660 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
197 | 51 | GSO_145 | line_4812_22 | S_nCCTT1436 | 10.6656 | Medium | 12.47 | 13.5424 | 0.098965 | 13.4434 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 44 | 30 | 0 | 90.9677 | 16.5 | 0.18795 | -79.9354 | 36.0575 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 -> switch_386_22 -> line_4279_22 -> line_4225_22 -> line_4226_22 -> switch_755_22 -> line_6270_22 -> switch_679_22 -> line_5863_22 -> switch_681_22 -> line_5864_22 -> switch_408_22 -> line_4373_22 -> line_4372_22 -> switch_407_22 -> switch_685_22 -> line_5881_22 -> switch_687_22 -> line_5882_22 -> line_6098_22 -> switch_734_22 -> line_6277_22 -> switch_758_22 -> line_6495_22 -> switch_768_22 -> line_6040_22 -> switch_719_22 -> recloser_181_22 -> line_5609_22 -> line_4243_22 -> line_4242_22 -> line_4396_22 -> line_6028_22 -> line_6309_22 -> line_4812_22 | GSO_145¦line_4812_22 | ACLineSegment | 660 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
198 | 52 | GSO_145 | line_5536_22 | S_nCCTT312 | 10.6656 | Medium | 12.47 | 13.5424 | 0.0052087 | 13.5372 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 44 | 30 | 0 | 90.9677 | 16.5 | 0.18795 | -79.9347 | 36.0559 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 -> switch_386_22 -> line_4279_22 -> line_4225_22 -> line_4226_22 -> switch_755_22 -> line_6270_22 -> switch_679_22 -> line_5863_22 -> switch_681_22 -> line_5864_22 -> switch_408_22 -> line_4373_22 -> line_4372_22 -> switch_407_22 -> switch_685_22 -> line_5881_22 -> switch_687_22 -> line_5882_22 -> line_6098_22 -> switch_734_22 -> line_6277_22 -> switch_758_22 -> line_6495_22 -> switch_768_22 -> line_6040_22 -> switch_719_22 -> recloser_181_22 -> line_5609_22 -> line_4243_22 -> line_4242_22 -> line_4397_22 -> line_6138_22 -> line_6314_22 -> line_5536_22 | GSO_145¦line_5536_22 | ACLineSegment | 660 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
199 | 53 | GSO_145 | line_4787_22 | S_nCCTT437 | 10.6656 | Medium | 12.47 | 13.5424 | 0.031252 | 13.5111 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 45 | 31 | 0 | 90.9677 | 16.5 | 0.18795 | -79.9355 | 36.0538 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 -> switch_386_22 -> line_4279_22 -> line_4225_22 -> line_4226_22 -> switch_755_22 -> line_6270_22 -> switch_679_22 -> line_5863_22 -> switch_681_22 -> line_5864_22 -> switch_408_22 -> line_4373_22 -> line_4372_22 -> switch_407_22 -> switch_685_22 -> line_5881_22 -> switch_687_22 -> line_5882_22 -> line_6098_22 -> switch_734_22 -> line_6277_22 -> switch_758_22 -> line_6495_22 -> switch_768_22 -> line_6040_22 -> switch_719_22 -> recloser_181_22 -> line_5609_22 -> line_4243_22 -> line_4242_22 -> line_4397_22 -> line_6138_22 -> line_5401_22 -> line_4785_22 -> line_4787_22 | GSO_145¦line_4787_22 | ACLineSegment | 660 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
200 | 54 | GSO_145 | line_4733_22 | S_nCCTT1406 | 10.6656 | Medium | 12.47 | 13.5424 | 0.0052087 | 13.5372 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 45 | 31 | 0 | 90.9677 | 16.5 | 0.18795 | -79.936 | 36.0578 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 -> switch_386_22 -> line_4279_22 -> line_4225_22 -> line_4226_22 -> switch_755_22 -> line_6270_22 -> switch_679_22 -> line_5863_22 -> switch_681_22 -> line_5864_22 -> switch_408_22 -> line_4373_22 -> line_4372_22 -> switch_407_22 -> switch_685_22 -> line_5881_22 -> switch_687_22 -> line_5882_22 -> line_6098_22 -> switch_734_22 -> line_6277_22 -> switch_758_22 -> line_6495_22 -> switch_768_22 -> line_6040_22 -> switch_719_22 -> recloser_181_22 -> line_5609_22 -> line_4243_22 -> line_4242_22 -> line_4396_22 -> line_6028_22 -> line_6309_22 -> line_5497_22 -> line_4733_22 | GSO_145¦line_4733_22 | ACLineSegment | 660 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
201 | 55 | GSO_145 | line_5247_22 | S_nCCTT172 | 10.6656 | Medium | 12.47 | 13.5424 | 0.0052087 | 13.5372 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 45 | 31 | 0 | 90.9677 | 16.5 | 0.18795 | -79.9359 | 36.0582 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 -> switch_386_22 -> line_4279_22 -> line_4225_22 -> line_4226_22 -> switch_755_22 -> line_6270_22 -> switch_679_22 -> line_5863_22 -> switch_681_22 -> line_5864_22 -> switch_408_22 -> line_4373_22 -> line_4372_22 -> switch_407_22 -> switch_685_22 -> line_5881_22 -> switch_687_22 -> line_5882_22 -> line_6098_22 -> switch_734_22 -> line_6277_22 -> switch_758_22 -> line_6495_22 -> switch_768_22 -> line_6040_22 -> switch_719_22 -> recloser_181_22 -> line_5609_22 -> line_4243_22 -> line_4242_22 -> line_4396_22 -> line_6028_22 -> line_6309_22 -> line_5497_22 -> line_5247_22 | GSO_145¦line_5247_22 | ACLineSegment | 660 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
202 | 56 | GSO_145 | line_4813_22 | S_nCCTT829 | 10.6656 | Medium | 12.47 | 13.5424 | 0.093756 | 13.4486 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 45 | 31 | 0 | 90.9677 | 16.5 | 0.18795 | -79.9346 | 36.0581 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 -> switch_386_22 -> line_4279_22 -> line_4225_22 -> line_4226_22 -> switch_755_22 -> line_6270_22 -> switch_679_22 -> line_5863_22 -> switch_681_22 -> line_5864_22 -> switch_408_22 -> line_4373_22 -> line_4372_22 -> switch_407_22 -> switch_685_22 -> line_5881_22 -> switch_687_22 -> line_5882_22 -> line_6098_22 -> switch_734_22 -> line_6277_22 -> switch_758_22 -> line_6495_22 -> switch_768_22 -> line_6040_22 -> switch_719_22 -> recloser_181_22 -> line_5609_22 -> line_4243_22 -> line_4242_22 -> line_4396_22 -> line_6028_22 -> line_6309_22 -> line_4812_22 -> line_4813_22 | GSO_145¦line_4813_22 | ACLineSegment | 660 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
203 | 57 | GSO_145 | line_5816_22 | S_nCCTT830 | 10.6656 | Medium | 12.47 | 13.5424 | 0.026043 | 13.5163 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 46 | 32 | 0 | 90.9677 | 16.5 | 0.18795 | -79.9355 | 36.0531 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 -> switch_386_22 -> line_4279_22 -> line_4225_22 -> line_4226_22 -> switch_755_22 -> line_6270_22 -> switch_679_22 -> line_5863_22 -> switch_681_22 -> line_5864_22 -> switch_408_22 -> line_4373_22 -> line_4372_22 -> switch_407_22 -> switch_685_22 -> line_5881_22 -> switch_687_22 -> line_5882_22 -> line_6098_22 -> switch_734_22 -> line_6277_22 -> switch_758_22 -> line_6495_22 -> switch_768_22 -> line_6040_22 -> switch_719_22 -> recloser_181_22 -> line_5609_22 -> line_4243_22 -> line_4242_22 -> line_4397_22 -> line_6138_22 -> line_5401_22 -> line_4785_22 -> line_4787_22 -> line_5816_22 | GSO_145¦line_5816_22 | ACLineSegment | 660 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
204 | 58 | GSO_145 | line_5367_22 | S_nCCTT217 | 10.6656 | Medium | 12.47 | 13.5424 | 0.088548 | 13.4538 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 46 | 32 | 0 | 90.9677 | 16.5 | 0.18795 | -79.9344 | 36.0596 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 -> switch_386_22 -> line_4279_22 -> line_4225_22 -> line_4226_22 -> switch_755_22 -> line_6270_22 -> switch_679_22 -> line_5863_22 -> switch_681_22 -> line_5864_22 -> switch_408_22 -> line_4373_22 -> line_4372_22 -> switch_407_22 -> switch_685_22 -> line_5881_22 -> switch_687_22 -> line_5882_22 -> line_6098_22 -> switch_734_22 -> line_6277_22 -> switch_758_22 -> line_6495_22 -> switch_768_22 -> line_6040_22 -> switch_719_22 -> recloser_181_22 -> line_5609_22 -> line_4243_22 -> line_4242_22 -> line_4396_22 -> line_6028_22 -> line_6309_22 -> line_4812_22 -> line_4813_22 -> line_5367_22 | GSO_145¦line_5367_22 | ACLineSegment | 660 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
205 | 59 | GSO_145 | line_6370_22 | S_nCCTT686 | 10.6656 | Medium | 12.47 | 13.5424 | 0.015626 | 13.5267 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 47 | 33 | 0 | 90.9677 | 16.5 | 0.18795 | -79.9351 | 36.0523 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 -> switch_386_22 -> line_4279_22 -> line_4225_22 -> line_4226_22 -> switch_755_22 -> line_6270_22 -> switch_679_22 -> line_5863_22 -> switch_681_22 -> line_5864_22 -> switch_408_22 -> line_4373_22 -> line_4372_22 -> switch_407_22 -> switch_685_22 -> line_5881_22 -> switch_687_22 -> line_5882_22 -> line_6098_22 -> switch_734_22 -> line_6277_22 -> switch_758_22 -> line_6495_22 -> switch_768_22 -> line_6040_22 -> switch_719_22 -> recloser_181_22 -> line_5609_22 -> line_4243_22 -> line_4242_22 -> line_4397_22 -> line_6138_22 -> line_5401_22 -> line_4785_22 -> line_4787_22 -> line_5816_22 -> line_6370_22 | GSO_145¦line_6370_22 | ACLineSegment | 660 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
206 | 60 | GSO_145 | line_5366_22 | S_nCCTT790 | 10.6656 | Medium | 12.47 | 13.5424 | 0.026043 | 13.5163 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 47 | 33 | 0 | 90.9677 | 16.5 | 0.18795 | -79.9341 | 36.0604 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 -> switch_386_22 -> line_4279_22 -> line_4225_22 -> line_4226_22 -> switch_755_22 -> line_6270_22 -> switch_679_22 -> line_5863_22 -> switch_681_22 -> line_5864_22 -> switch_408_22 -> line_4373_22 -> line_4372_22 -> switch_407_22 -> switch_685_22 -> line_5881_22 -> switch_687_22 -> line_5882_22 -> line_6098_22 -> switch_734_22 -> line_6277_22 -> switch_758_22 -> line_6495_22 -> switch_768_22 -> line_6040_22 -> switch_719_22 -> recloser_181_22 -> line_5609_22 -> line_4243_22 -> line_4242_22 -> line_4396_22 -> line_6028_22 -> line_6309_22 -> line_4812_22 -> line_4813_22 -> line_5367_22 -> line_5366_22 | GSO_145¦line_5366_22 | ACLineSegment | 660 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
207 | 61 | GSO_145 | line_5268_22 | S_nCCTT180 | 10.6656 | Medium | 12.47 | 13.5424 | 0.057295 | 13.4851 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 47 | 33 | 0 | 90.9677 | 16.5 | 0.18795 | -79.9353 | 36.0603 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 -> switch_386_22 -> line_4279_22 -> line_4225_22 -> line_4226_22 -> switch_755_22 -> line_6270_22 -> switch_679_22 -> line_5863_22 -> switch_681_22 -> line_5864_22 -> switch_408_22 -> line_4373_22 -> line_4372_22 -> switch_407_22 -> switch_685_22 -> line_5881_22 -> switch_687_22 -> line_5882_22 -> line_6098_22 -> switch_734_22 -> line_6277_22 -> switch_758_22 -> line_6495_22 -> switch_768_22 -> line_6040_22 -> switch_719_22 -> recloser_181_22 -> line_5609_22 -> line_4243_22 -> line_4242_22 -> line_4396_22 -> line_6028_22 -> line_6309_22 -> line_4812_22 -> line_4813_22 -> line_5367_22 -> line_5268_22 | GSO_145¦line_5268_22 | ACLineSegment | 660 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
208 | 62 | GSO_145 | line_5834_22 | S_nCCTT444 | 10.6656 | Medium | 12.47 | 13.5424 | 0.010417 | 13.532 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 48 | 34 | 0 | 90.9677 | 16.5 | 0.18795 | -79.9345 | 36.0516 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 -> switch_386_22 -> line_4279_22 -> line_4225_22 -> line_4226_22 -> switch_755_22 -> line_6270_22 -> switch_679_22 -> line_5863_22 -> switch_681_22 -> line_5864_22 -> switch_408_22 -> line_4373_22 -> line_4372_22 -> switch_407_22 -> switch_685_22 -> line_5881_22 -> switch_687_22 -> line_5882_22 -> line_6098_22 -> switch_734_22 -> line_6277_22 -> switch_758_22 -> line_6495_22 -> switch_768_22 -> line_6040_22 -> switch_719_22 -> recloser_181_22 -> line_5609_22 -> line_4243_22 -> line_4242_22 -> line_4397_22 -> line_6138_22 -> line_5401_22 -> line_4785_22 -> line_4787_22 -> line_5816_22 -> line_6370_22 -> line_5834_22 | GSO_145¦line_5834_22 | ACLineSegment | 660 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
209 | 63 | GSO_145 | line_6492_22 | S_nCCTT752 | 10.6656 | Medium | 12.47 | 13.5424 | 0.015626 | 13.5267 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 48 | 34 | 0 | 90.9677 | 16.5 | 0.18795 | -79.9333 | 36.0607 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 -> switch_386_22 -> line_4279_22 -> line_4225_22 -> line_4226_22 -> switch_755_22 -> line_6270_22 -> switch_679_22 -> line_5863_22 -> switch_681_22 -> line_5864_22 -> switch_408_22 -> line_4373_22 -> line_4372_22 -> switch_407_22 -> switch_685_22 -> line_5881_22 -> switch_687_22 -> line_5882_22 -> line_6098_22 -> switch_734_22 -> line_6277_22 -> switch_758_22 -> line_6495_22 -> switch_768_22 -> line_6040_22 -> switch_719_22 -> recloser_181_22 -> line_5609_22 -> line_4243_22 -> line_4242_22 -> line_4396_22 -> line_6028_22 -> line_6309_22 -> line_4812_22 -> line_4813_22 -> line_5367_22 -> line_5366_22 -> line_6492_22 | GSO_145¦line_6492_22 | ACLineSegment | 660 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
210 | 64 | GSO_145 | line_4471_22 | S_nCCTT1313 | 10.6656 | Medium | 12.47 | 13.5424 | 0.0052087 | 13.5372 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 48 | 34 | 0 | 90.9677 | 16.5 | 0.18795 | -79.9338 | 36.0605 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 -> switch_386_22 -> line_4279_22 -> line_4225_22 -> line_4226_22 -> switch_755_22 -> line_6270_22 -> switch_679_22 -> line_5863_22 -> switch_681_22 -> line_5864_22 -> switch_408_22 -> line_4373_22 -> line_4372_22 -> switch_407_22 -> switch_685_22 -> line_5881_22 -> switch_687_22 -> line_5882_22 -> line_6098_22 -> switch_734_22 -> line_6277_22 -> switch_758_22 -> line_6495_22 -> switch_768_22 -> line_6040_22 -> switch_719_22 -> recloser_181_22 -> line_5609_22 -> line_4243_22 -> line_4242_22 -> line_4396_22 -> line_6028_22 -> line_6309_22 -> line_4812_22 -> line_4813_22 -> line_5367_22 -> line_5366_22 -> line_4471_22 | GSO_145¦line_4471_22 | ACLineSegment | 660 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
211 | 65 | GSO_145 | line_5267_22 | S_nCCTT181 | 10.6656 | Medium | 12.47 | 13.5424 | 0.031252 | 13.5111 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 48 | 34 | 0 | 90.9677 | 16.5 | 0.18795 | -79.9367 | 36.0605 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 -> switch_386_22 -> line_4279_22 -> line_4225_22 -> line_4226_22 -> switch_755_22 -> line_6270_22 -> switch_679_22 -> line_5863_22 -> switch_681_22 -> line_5864_22 -> switch_408_22 -> line_4373_22 -> line_4372_22 -> switch_407_22 -> switch_685_22 -> line_5881_22 -> switch_687_22 -> line_5882_22 -> line_6098_22 -> switch_734_22 -> line_6277_22 -> switch_758_22 -> line_6495_22 -> switch_768_22 -> line_6040_22 -> switch_719_22 -> recloser_181_22 -> line_5609_22 -> line_4243_22 -> line_4242_22 -> line_4396_22 -> line_6028_22 -> line_6309_22 -> line_4812_22 -> line_4813_22 -> line_5367_22 -> line_5268_22 -> line_5267_22 | GSO_145¦line_5267_22 | ACLineSegment | 660 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
212 | 66 | GSO_145 | line_5269_22 | S_nCCTT631 | 10.6656 | Medium | 12.47 | 13.5424 | 0.0052087 | 13.5372 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 48 | 34 | 0 | 90.9677 | 16.5 | 0.18795 | -79.936 | 36.0604 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 -> switch_386_22 -> line_4279_22 -> line_4225_22 -> line_4226_22 -> switch_755_22 -> line_6270_22 -> switch_679_22 -> line_5863_22 -> switch_681_22 -> line_5864_22 -> switch_408_22 -> line_4373_22 -> line_4372_22 -> switch_407_22 -> switch_685_22 -> line_5881_22 -> switch_687_22 -> line_5882_22 -> line_6098_22 -> switch_734_22 -> line_6277_22 -> switch_758_22 -> line_6495_22 -> switch_768_22 -> line_6040_22 -> switch_719_22 -> recloser_181_22 -> line_5609_22 -> line_4243_22 -> line_4242_22 -> line_4396_22 -> line_6028_22 -> line_6309_22 -> line_4812_22 -> line_4813_22 -> line_5367_22 -> line_5268_22 -> line_5269_22 | GSO_145¦line_5269_22 | ACLineSegment | 660 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
213 | 67 | GSO_145 | line_5474_22 | S_nCCTT276 | 10.6656 | Medium | 12.47 | 13.5424 | 0.0052087 | 13.5372 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 49 | 35 | 0 | 90.9677 | 16.5 | 0.18795 | -79.9326 | 36.061 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 -> switch_386_22 -> line_4279_22 -> line_4225_22 -> line_4226_22 -> switch_755_22 -> line_6270_22 -> switch_679_22 -> line_5863_22 -> switch_681_22 -> line_5864_22 -> switch_408_22 -> line_4373_22 -> line_4372_22 -> switch_407_22 -> switch_685_22 -> line_5881_22 -> switch_687_22 -> line_5882_22 -> line_6098_22 -> switch_734_22 -> line_6277_22 -> switch_758_22 -> line_6495_22 -> switch_768_22 -> line_6040_22 -> switch_719_22 -> recloser_181_22 -> line_5609_22 -> line_4243_22 -> line_4242_22 -> line_4396_22 -> line_6028_22 -> line_6309_22 -> line_4812_22 -> line_4813_22 -> line_5367_22 -> line_5366_22 -> line_6492_22 -> line_5474_22 | GSO_145¦line_5474_22 | ACLineSegment | 660 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
214 | 68 | GSO_145 | line_5273_22 | S_nCCTT746 | 10.6656 | Medium | 12.47 | 13.5424 | 0.015626 | 13.5267 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 49 | 35 | 0 | 90.9677 | 16.5 | 0.18795 | -79.9371 | 36.0615 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 -> switch_386_22 -> line_4279_22 -> line_4225_22 -> line_4226_22 -> switch_755_22 -> line_6270_22 -> switch_679_22 -> line_5863_22 -> switch_681_22 -> line_5864_22 -> switch_408_22 -> line_4373_22 -> line_4372_22 -> switch_407_22 -> switch_685_22 -> line_5881_22 -> switch_687_22 -> line_5882_22 -> line_6098_22 -> switch_734_22 -> line_6277_22 -> switch_758_22 -> line_6495_22 -> switch_768_22 -> line_6040_22 -> switch_719_22 -> recloser_181_22 -> line_5609_22 -> line_4243_22 -> line_4242_22 -> line_4396_22 -> line_6028_22 -> line_6309_22 -> line_4812_22 -> line_4813_22 -> line_5367_22 -> line_5268_22 -> line_5267_22 -> line_5273_22 | GSO_145¦line_5273_22 | ACLineSegment | 660 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
215 | 69 | GSO_145 | line_6194_22 | S_nCCTT602 | 10.6656 | Medium | 12.47 | 13.5424 | 0.0052087 | 13.5372 | 0.73442 | 11.4 | 10.6656 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.73442 | 10.6656 | 50 | 36 | 0 | 90.9677 | 16.5 | 0.18795 | -79.9367 | 36.0624 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 -> switch_386_22 -> line_4279_22 -> line_4225_22 -> line_4226_22 -> switch_755_22 -> line_6270_22 -> switch_679_22 -> line_5863_22 -> switch_681_22 -> line_5864_22 -> switch_408_22 -> line_4373_22 -> line_4372_22 -> switch_407_22 -> switch_685_22 -> line_5881_22 -> switch_687_22 -> line_5882_22 -> line_6098_22 -> switch_734_22 -> line_6277_22 -> switch_758_22 -> line_6495_22 -> switch_768_22 -> line_6040_22 -> switch_719_22 -> recloser_181_22 -> line_5609_22 -> line_4243_22 -> line_4242_22 -> line_4396_22 -> line_6028_22 -> line_6309_22 -> line_4812_22 -> line_4813_22 -> line_5367_22 -> line_5268_22 -> line_5267_22 -> line_5273_22 -> line_6194_22 | GSO_145¦line_6194_22 | ACLineSegment | 660 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved |  | 250
499 | 70 | GSO_145 | line_5347_22 | S_nCCTT422 | 7.1031 | Medium | 7.2 | 7.1083 | 0.0052087 | 7.1031 | 0.73442 | 11.4 | 10.6656 | line_5347_22 | ACLineSegment | Line | 7.1083 | 0.0052087 | 7.1031 | 18 | 13 | 0 | 90.9677 | 16.5 | 0.18795 | -79.944 | 36.0555 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 -> switch_491_22 -> line_4718_22 -> line_4719_22 -> switch_494_22 -> line_5348_22 -> switch_619_22 -> switch_616_22 -> line_5347_22 | GSO_145¦line_5347_22 | ACLineSegment | 600 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 7.1031 | [6 empty] | SubstationCapacityUnresolved | line_5347_22 | Substation capacity unresolved |  | 250
532 | 71 | GSO_145 | line_4219_22 | S_nCCTT1230 | 2.8381 | Medium | 7.2 | 2.8433 | 0.0052087 | 2.8381 | 0.73442 | 11.4 | 10.6656 | line_4219_22 | ACLineSegment | Line | 2.8433 | 0.0052087 | 2.8381 | 15 | 12 | 0 | 90.9677 | 16.5 | 0.18795 | -79.9441 | 36.0527 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 -> switch_386_22 -> line_4279_22 -> line_4225_22 -> fuse_43_22 -> line_4219_22 | GSO_145¦line_4219_22 | ACLineSegment | 240 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.8381 | [6 empty] | SubstationCapacityUnresolved | line_4219_22 | Substation capacity unresolved |  | 250
533 | 72 | GSO_145 | line_4786_22 | S_nCCTT398 | 2.8381 | Medium | 7.2 | 2.8433 | 0.0052087 | 2.8381 | 0.73442 | 11.4 | 10.6656 | line_4786_22 | ACLineSegment | Line | 2.8433 | 0.0052087 | 2.8381 | 46 | 31 | 0 | 90.9677 | 16.5 | 0.18795 | -79.935 | 36.0542 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 -> switch_386_22 -> line_4279_22 -> line_4225_22 -> line_4226_22 -> switch_755_22 -> line_6270_22 -> switch_679_22 -> line_5863_22 -> switch_681_22 -> line_5864_22 -> switch_408_22 -> line_4373_22 -> line_4372_22 -> switch_407_22 -> switch_685_22 -> line_5881_22 -> switch_687_22 -> line_5882_22 -> line_6098_22 -> switch_734_22 -> line_6277_22 -> switch_758_22 -> line_6495_22 -> switch_768_22 -> line_6040_22 -> switch_719_22 -> recloser_181_22 -> line_5609_22 -> line_4243_22 -> line_4242_22 -> line_4397_22 -> line_6138_22 -> line_5401_22 -> line_4785_22 -> fuse_78_22 -> line_4786_22 | GSO_145¦line_4786_22 | ACLineSegment | 240 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.8381 | [6 empty] | SubstationCapacityUnresolved | line_4786_22 | Substation capacity unresolved |  | 250
534 | 73 | GSO_145 | line_5835_22 | S_nCCTT792 | 2.8381 | Medium | 7.2 | 2.8433 | 0.0052087 | 2.8381 | 0.73442 | 11.4 | 10.6656 | line_5835_22 | ACLineSegment | Line | 2.8433 | 0.0052087 | 2.8381 | 50 | 35 | 0 | 90.9677 | 16.5 | 0.18795 | -79.9343 | 36.0512 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 -> switch_386_22 -> line_4279_22 -> line_4225_22 -> line_4226_22 -> switch_755_22 -> line_6270_22 -> switch_679_22 -> line_5863_22 -> switch_681_22 -> line_5864_22 -> switch_408_22 -> line_4373_22 -> line_4372_22 -> switch_407_22 -> switch_685_22 -> line_5881_22 -> switch_687_22 -> line_5882_22 -> line_6098_22 -> switch_734_22 -> line_6277_22 -> switch_758_22 -> line_6495_22 -> switch_768_22 -> line_6040_22 -> switch_719_22 -> recloser_181_22 -> line_5609_22 -> line_4243_22 -> line_4242_22 -> line_4397_22 -> line_6138_22 -> line_5401_22 -> line_4785_22 -> line_4787_22 -> line_5816_22 -> line_6370_22 -> line_5834_22 -> fuse_134_22 -> line_5835_22 | GSO_145¦line_5835_22 | ACLineSegment | 240 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.8381 | [6 empty] | SubstationCapacityUnresolved | line_5835_22 | Substation capacity unresolved |  | 250
553 | 74 | GSO_145 | line_5362_22 | S_nCCTT215 | 2.8277 | Medium | 7.2 | 2.8433 | 0.015626 | 2.8277 | 0.73442 | 11.4 | 10.6656 | line_5362_22 | ACLineSegment | Line | 2.8433 | 0.015626 | 2.8277 | 16 | 13 | 0 | 90.9677 | 16.5 | 0.18795 | -79.9463 | 36.0531 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 -> switch_386_22 -> line_4279_22 -> line_4225_22 -> line_4226_22 -> fuse_110_22 -> line_5362_22 | GSO_145¦line_5362_22 | ACLineSegment | 240 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.8277 | [6 empty] | SubstationCapacityUnresolved | line_5362_22 | Substation capacity unresolved |  | 250
554 | 75 | GSO_145 | line_4319_22 | S_nCCTT1262 | 2.8277 | Medium | 7.2 | 2.8433 | 0.0052087 | 2.8381 | 0.73442 | 11.4 | 10.6656 | line_5362_22 | ACLineSegment | Line | 2.8433 | 0.015626 | 2.8277 | 17 | 14 | 0 | 90.9677 | 16.5 | 0.18795 | -79.9471 | 36.0514 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 -> switch_386_22 -> line_4279_22 -> line_4225_22 -> line_4226_22 -> fuse_110_22 -> line_5362_22 -> line_4319_22 | GSO_145¦line_4319_22 | ACLineSegment | 240 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.8277 | [6 empty] | SubstationCapacityUnresolved | line_5362_22 | Substation capacity unresolved |  | 250
564 | 76 | GSO_145 | line_4287_22 | S_nCCTT1250 | 2.8225 | Medium | 7.2 | 2.8433 | 0.020835 | 2.8225 | 0.73442 | 11.4 | 10.6656 | line_4287_22 | ACLineSegment | Line | 2.8433 | 0.020835 | 2.8225 | 36 | 23 | 0 | 90.9677 | 16.5 | 0.18795 | -79.9414 | 36.0613 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 -> switch_386_22 -> line_4279_22 -> line_4225_22 -> line_4226_22 -> switch_755_22 -> line_6270_22 -> switch_679_22 -> line_5863_22 -> switch_681_22 -> line_5864_22 -> switch_408_22 -> line_4373_22 -> line_4372_22 -> switch_407_22 -> switch_685_22 -> line_5881_22 -> switch_632_22 -> line_5457_22 -> line_5240_22 -> switch_598_22 -> switch_595_22 -> line_5239_22 -> line_5232_22 -> switch_588_22 -> fuse_48_22 -> line_4287_22 | GSO_145¦line_4287_22 | ACLineSegment | 240 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.8225 | [6 empty] | SubstationCapacityUnresolved | line_4287_22 | Substation capacity unresolved |  | 250
565 | 77 | GSO_145 | line_4288_22 | S_nCCTT167 | 2.8225 | Medium | 7.2 | 2.8433 | 0.010417 | 2.8329 | 0.73442 | 11.4 | 10.6656 | line_4287_22 | ACLineSegment | Line | 2.8433 | 0.020835 | 2.8225 | 37 | 24 | 0 | 90.9677 | 16.5 | 0.18795 | -79.9407 | 36.0617 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> line_5164_22 -> line_5344_22 -> line_5482_22 -> line_5955_22 -> line_6070_22 -> line_4633_22 -> line_4634_22 -> switch_386_22 -> line_4279_22 -> line_4225_22 -> line_4226_22 -> switch_755_22 -> line_6270_22 -> switch_679_22 -> line_5863_22 -> switch_681_22 -> line_5864_22 -> switch_408_22 -> line_4373_22 -> line_4372_22 -> switch_407_22 -> switch_685_22 -> line_5881_22 -> switch_632_22 -> line_5457_22 -> line_5240_22 -> switch_598_22 -> switch_595_22 -> line_5239_22 -> line_5232_22 -> switch_588_22 -> fuse_48_22 -> line_4287_22 -> line_4288_22 | GSO_145¦line_4288_22 | ACLineSegment | 240 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.8225 | [6 empty] | SubstationCapacityUnresolved | line_4287_22 | Substation capacity unresolved |  | 250
578 | 78 | GSO_145 | line_5165_22 | S_nCCTT369 | 2.8069 | Medium | 7.2 | 2.8433 | 0.036461 | 2.8069 | 0.73442 | 11.4 | 10.6656 | line_5165_22 | ACLineSegment | Line | 2.8433 | 0.036461 | 2.8069 | 5 | 3 | 0 | 90.9677 | 16.5 | 0.18795 | -79.9404 | 36.0493 | recloser_192_22 -> line_6170_22 -> line_5166_22 -> fuse_98_22 -> line_5165_22 | GSO_145¦line_5165_22 | ACLineSegment | 240 | 12000 | Meter | br_025_22 | hvmv_5_22 | 12000.0 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.8069 | [6 empty] | SubstationCapacityUnresolved | line_5165_22 | Substation capacity unresolved |  | 250
324 | 1 | GSO_18 | line_108323_21 | S_nCCTT10746 | 10.3769 | High | 12.47 | 13.5424 | 2.2897 | 11.2526 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 2 | 1 | 0 | 100 | 27 | 0.30755 | -79.8258 | 36.0207 | recloser_1790_21 -> line_108323_21 | GSO_18¦line_108323_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
325 | 2 | GSO_18 | line_108322_21 | S_nCCTT4838 | 10.3769 | High | 12.47 | 13.5424 | 1.9016 | 11.6408 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 3 | 2 | 0 | 100 | 27 | 0.30755 | -79.8233 | 36.0134 | recloser_1790_21 -> line_108323_21 -> line_108322_21 | GSO_18¦line_108322_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
326 | 3 | GSO_18 | line_122867_21 | S_nCCTT8098 | 10.3769 | High | 12.47 | 13.5424 | 1.878 | 11.6643 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 4 | 3 | 0 | 100 | 27 | 0.30755 | -79.8241 | 36.0127 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 | GSO_18¦line_122867_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
327 | 4 | GSO_18 | line_129230_21 | S_nCCTT8100 | 10.3769 | High | 12.47 | 13.5424 | 0.023525 | 13.5188 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 5 | 4 | 0 | 100 | 27 | 0.30755 | -79.8244 | 36.012 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129230_21 | GSO_18¦line_129230_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
328 | 5 | GSO_18 | line_129223_21 | S_nCCTT8094 | 10.3769 | High | 12.47 | 13.5424 | 1.8506 | 11.6918 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 5 | 4 | 0 | 100 | 27 | 0.30755 | -79.8246 | 36.0125 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 | GSO_18¦line_129223_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
329 | 6 | GSO_18 | line_107810_21 | S_nCCTT10590 | 10.3769 | High | 12.47 | 13.5424 | 1.8467 | 11.6957 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 6 | 5 | 0 | 100 | 27 | 0.30755 | -79.8252 | 36.0129 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 | GSO_18¦line_107810_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
330 | 7 | GSO_18 | line_107809_21 | S_nCCTT8091 | 10.3769 | High | 12.47 | 13.5424 | 1.7839 | 11.7584 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 7 | 6 | 0 | 100 | 27 | 0.30755 | -79.8258 | 36.0129 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 | GSO_18¦line_107809_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
331 | 8 | GSO_18 | line_110795_21 | S_nCCTT11534 | 10.3769 | High | 12.47 | 13.5424 | 1.78 | 11.7623 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 8 | 7 | 0 | 100 | 27 | 0.30755 | -79.8268 | 36.0123 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 | GSO_18¦line_110795_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
332 | 9 | GSO_18 | line_110794_21 | S_nCCTT11870 | 10.3769 | High | 12.47 | 13.5424 | 1.7643 | 11.778 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 9 | 8 | 0 | 100 | 27 | 0.30755 | -79.8273 | 36.0119 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 | GSO_18¦line_110794_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
333 | 10 | GSO_18 | line_111728_21 | S_nCCTT12184 | 10.3769 | High | 12.47 | 13.5424 | 1.682 | 11.8604 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 10 | 9 | 0 | 100 | 27 | 0.30755 | -79.828 | 36.0117 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 | GSO_18¦line_111728_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
334 | 11 | GSO_18 | line_110281_21 | S_nCCTT11364 | 10.3769 | High | 12.47 | 13.5424 | 1.2272 | 12.3152 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 11 | 10 | 0 | 100 | 27 | 0.30755 | -79.8287 | 36.0122 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 | GSO_18¦line_110281_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
335 | 12 | GSO_18 | line_108303_21 | S_nCCTT10741 | 10.3769 | High | 12.47 | 13.5424 | 0.80375 | 12.7386 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 12 | 11 | 0 | 100 | 27 | 0.30755 | -79.8292 | 36.0125 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 | GSO_18¦line_108303_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
336 | 13 | GSO_18 | line_108304_21 | S_nCCTT6705 | 10.3769 | High | 12.47 | 13.5424 | 0.47441 | 13.068 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 13 | 12 | 0 | 100 | 27 | 0.30755 | -79.8306 | 36.0124 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108304_21 | GSO_18¦line_108304_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
337 | 14 | GSO_18 | line_108305_21 | S_nCCTT6824 | 10.3769 | High | 12.47 | 13.5424 | 0.27445 | 13.2679 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 13 | 12 | 0 | 100 | 27 | 0.30755 | -79.8305 | 36.013 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108305_21 | GSO_18¦line_108305_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
338 | 15 | GSO_18 | line_108117_21 | S_nCCTT10687 | 10.3769 | High | 12.47 | 13.5424 | 0.46265 | 13.0797 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 14 | 13 | 0 | 100 | 27 | 0.30755 | -79.8313 | 36.0119 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108304_21 -> line_108117_21 | GSO_18¦line_108117_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
339 | 16 | GSO_18 | line_109744_21 | S_nCCTT11189 | 10.3769 | High | 12.47 | 13.5424 | 0.1882 | 13.3542 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 14 | 13 | 0 | 100 | 27 | 0.30755 | -79.8312 | 36.0139 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108305_21 -> line_109744_21 | GSO_18¦line_109744_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
340 | 17 | GSO_18 | line_109743_21 | S_nCCTT11341 | 10.3769 | High | 12.47 | 13.5424 | 0.18035 | 13.362 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 15 | 14 | 0 | 100 | 27 | 0.30755 | -79.8313 | 36.0148 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108305_21 -> line_109744_21 -> line_109743_21 | GSO_18¦line_109743_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
341 | 18 | GSO_18 | line_108116_21 | S_nCCTT2058 | 10.3769 | High | 12.47 | 13.5424 | 0.42736 | 13.115 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 15 | 14 | 0 | 100 | 27 | 0.30755 | -79.8319 | 36.0118 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108304_21 -> line_108117_21 -> line_108116_21 | GSO_18¦line_108116_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
342 | 19 | GSO_18 | line_116127_21 | S_nCCTT8115 | 10.3769 | High | 12.47 | 13.5424 | 0.33326 | 13.2091 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 16 | 15 | 0 | 100 | 27 | 0.30755 | -79.8325 | 36.0113 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108304_21 -> line_108117_21 -> line_108116_21 -> line_116127_21 | GSO_18¦line_116127_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
343 | 20 | GSO_18 | line_110125_21 | S_nCCTT11312 | 10.3769 | High | 12.47 | 13.5424 | 0.039208 | 13.5032 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 16 | 15 | 0 | 100 | 27 | 0.30755 | -79.8322 | 36.0151 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108305_21 -> line_109744_21 -> line_109743_21 -> line_110125_21 | GSO_18¦line_110125_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
344 | 21 | GSO_18 | line_116128_21 | S_nCCTT9222 | 10.3769 | High | 12.47 | 13.5424 | 0.0078415 | 13.5345 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 16 | 15 | 0 | 100 | 27 | 0.30755 | -79.8324 | 36.0124 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108304_21 -> line_108117_21 -> line_108116_21 -> line_116128_21 | GSO_18¦line_116128_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
345 | 22 | GSO_18 | line_128625_21 | S_nCCTT7751 | 10.3769 | High | 12.47 | 13.5424 | 0.29798 | 13.2444 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 17 | 16 | 0 | 100 | 27 | 0.30755 | -79.8327 | 36.0108 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108304_21 -> line_108117_21 -> line_108116_21 -> line_116127_21 -> line_128625_21 | GSO_18¦line_128625_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
346 | 23 | GSO_18 | line_110126_21 | S_nCCTT6610 | 10.3769 | High | 12.47 | 13.5424 | 0.035287 | 13.5071 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 17 | 16 | 0 | 100 | 27 | 0.30755 | -79.8333 | 36.0153 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108305_21 -> line_109744_21 -> line_109743_21 -> line_110125_21 -> line_110126_21 | GSO_18¦line_110126_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
347 | 24 | GSO_18 | line_113231_21 | S_nCCTT12475 | 10.3769 | High | 12.47 | 13.5424 | 0.031366 | 13.511 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 18 | 17 | 0 | 100 | 27 | 0.30755 | -79.8339 | 36.0149 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108305_21 -> line_109744_21 -> line_109743_21 -> line_110125_21 -> line_110126_21 -> line_113231_21 | GSO_18¦line_113231_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
348 | 25 | GSO_18 | line_128626_21 | S_nCCTT9228 | 10.3769 | High | 12.47 | 13.5424 | 0.29406 | 13.2483 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 18 | 17 | 0 | 100 | 27 | 0.30755 | -79.8332 | 36.0108 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108304_21 -> line_108117_21 -> line_108116_21 -> line_116127_21 -> line_128625_21 -> line_128626_21 | GSO_18¦line_128626_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
349 | 26 | GSO_18 | line_112666_21 | S_nCCTT12242 | 10.3769 | High | 12.47 | 13.5424 | 0.027445 | 13.5149 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 19 | 18 | 0 | 100 | 27 | 0.30755 | -79.8341 | 36.0145 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108305_21 -> line_109744_21 -> line_109743_21 -> line_110125_21 -> line_110126_21 -> line_113231_21 -> line_112666_21 | GSO_18¦line_112666_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
350 | 27 | GSO_18 | line_131276_21 | UCMV21 | 10.3769 | High | 12.47 | 13.5424 | 0.29014 | 13.2522 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 19 | 18 | 0 | 100 | 27 | 0.30755 | -79.8339 | 36.0108 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108304_21 -> line_108117_21 -> line_108116_21 -> line_116127_21 -> line_128625_21 -> line_128626_21 -> line_131276_21 | GSO_18¦line_131276_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
351 | 28 | GSO_18 | line_106219_21 | S_nCCTT10108 | 10.3769 | High | 12.47 | 13.5424 | 0.023525 | 13.5188 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 20 | 19 | 0 | 100 | 27 | 0.30755 | -79.8349 | 36.0143 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108305_21 -> line_109744_21 -> line_109743_21 -> line_110125_21 -> line_110126_21 -> line_113231_21 -> line_112666_21 -> line_106219_21 | GSO_18¦line_106219_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
352 | 29 | GSO_18 | line_116038_21 | S_nCCTT2016 | 10.3769 | High | 12.47 | 13.5424 | 0.28621 | 13.2562 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 20 | 19 | 0 | 100 | 27 | 0.30755 | -79.8343 | 36.0108 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108304_21 -> line_108117_21 -> line_108116_21 -> line_116127_21 -> line_128625_21 -> line_128626_21 -> line_131276_21 -> line_116038_21 | GSO_18¦line_116038_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
353 | 30 | GSO_18 | line_106218_21 | S_nCCTT10607 | 10.3769 | High | 12.47 | 13.5424 | 0.019604 | 13.5228 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 21 | 20 | 0 | 100 | 27 | 0.30755 | -79.836 | 36.0139 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108305_21 -> line_109744_21 -> line_109743_21 -> line_110125_21 -> line_110126_21 -> line_113231_21 -> line_112666_21 -> line_106219_21 -> line_106218_21 | GSO_18¦line_106218_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
354 | 31 | GSO_18 | line_116037_21 | S_nCCTT2126 | 10.3769 | High | 12.47 | 13.5424 | 0.27053 | 13.2718 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 21 | 20 | 0 | 100 | 27 | 0.30755 | -79.8347 | 36.0108 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108304_21 -> line_108117_21 -> line_108116_21 -> line_116127_21 -> line_128625_21 -> line_128626_21 -> line_131276_21 -> line_116038_21 -> line_116037_21 | GSO_18¦line_116037_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
355 | 32 | GSO_18 | line_107862_21 | S_nCCTT10927 | 10.3769 | High | 12.47 | 13.5424 | 0.0078415 | 13.5345 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 22 | 21 | 0 | 100 | 27 | 0.30755 | -79.8362 | 36.0133 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108305_21 -> line_109744_21 -> line_109743_21 -> line_110125_21 -> line_110126_21 -> line_113231_21 -> line_112666_21 -> line_106219_21 -> line_106218_21 -> line_107862_21 | GSO_18¦line_107862_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
356 | 33 | GSO_18 | line_107863_21 | S_nCCTT6562 | 10.3769 | High | 12.47 | 13.5424 | 0.0078415 | 13.5345 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 22 | 21 | 0 | 100 | 27 | 0.30755 | -79.8369 | 36.0134 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108305_21 -> line_109744_21 -> line_109743_21 -> line_110125_21 -> line_110126_21 -> line_113231_21 -> line_112666_21 -> line_106219_21 -> line_106218_21 -> line_107863_21 | GSO_18¦line_107863_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
357 | 34 | GSO_18 | line_112560_21 | S_nCCTT12196 | 10.3769 | High | 12.47 | 13.5424 | 0.26269 | 13.2797 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 22 | 21 | 0 | 100 | 27 | 0.30755 | -79.8351 | 36.0108 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108304_21 -> line_108117_21 -> line_108116_21 -> line_116127_21 -> line_128625_21 -> line_128626_21 -> line_131276_21 -> line_116038_21 -> line_116037_21 -> line_112560_21 | GSO_18¦line_112560_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
358 | 35 | GSO_18 | line_113658_21 | S_nCCTT12664 | 10.3769 | High | 12.47 | 13.5424 | 0.0039208 | 13.5384 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 23 | 22 | 0 | 100 | 27 | 0.30755 | -79.8371 | 36.0127 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108305_21 -> line_109744_21 -> line_109743_21 -> line_110125_21 -> line_110126_21 -> line_113231_21 -> line_112666_21 -> line_106219_21 -> line_106218_21 -> line_107863_21 -> line_113658_21 | GSO_18¦line_113658_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
359 | 36 | GSO_18 | line_112561_21 | S_nCCTT6762 | 10.3769 | High | 12.47 | 13.5424 | 0.25877 | 13.2836 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 23 | 22 | 0 | 100 | 27 | 0.30755 | -79.8354 | 36.0108 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108304_21 -> line_108117_21 -> line_108116_21 -> line_116127_21 -> line_128625_21 -> line_128626_21 -> line_131276_21 -> line_116038_21 -> line_116037_21 -> line_112560_21 -> line_112561_21 | GSO_18¦line_112561_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
360 | 37 | GSO_18 | line_111905_21 | S_nCCTT11937_A_S_nCCTT12664 | 10.3769 | High | 12.47 | 13.5424 | 0 | 13.5424 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 24 | 23 | 0 | 100 | 27 | 0.30755 | -79.8363 | 36.0115 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108305_21 -> line_109744_21 -> line_109743_21 -> line_110125_21 -> line_110126_21 -> line_113231_21 -> line_112666_21 -> line_106219_21 -> line_106218_21 -> line_107863_21 -> line_113658_21 -> line_111905_21 | GSO_18¦line_111905_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
361 | 38 | GSO_18 | line_111906_21 | S_nCCTT11937 | 10.3769 | High | 12.47 | 13.5424 | 0.25485 | 13.2875 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 24 | 23 | 0 | 100 | 27 | 0.30755 | -79.8356 | 36.0108 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108304_21 -> line_108117_21 -> line_108116_21 -> line_116127_21 -> line_128625_21 -> line_128626_21 -> line_131276_21 -> line_116038_21 -> line_116037_21 -> line_112560_21 -> line_112561_21 -> line_111906_21 | GSO_18¦line_111906_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
362 | 39 | GSO_18 | line_111907_21 | S_nCCTT9220 | 10.3769 | High | 12.47 | 13.5424 | 0.25093 | 13.2914 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 25 | 24 | 0 | 100 | 27 | 0.30755 | -79.8362 | 36.0107 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108304_21 -> line_108117_21 -> line_108116_21 -> line_116127_21 -> line_128625_21 -> line_128626_21 -> line_131276_21 -> line_116038_21 -> line_116037_21 -> line_112560_21 -> line_112561_21 -> line_111906_21 -> line_111907_21 | GSO_18¦line_111907_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
363 | 40 | GSO_18 | line_113500_21 | S_nCCTT12595 | 10.3769 | High | 12.47 | 13.5424 | 0.24701 | 13.2954 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 26 | 25 | 0 | 100 | 27 | 0.30755 | -79.837 | 36.0103 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108304_21 -> line_108117_21 -> line_108116_21 -> line_116127_21 -> line_128625_21 -> line_128626_21 -> line_131276_21 -> line_116038_21 -> line_116037_21 -> line_112560_21 -> line_112561_21 -> line_111906_21 -> line_111907_21 -> line_113500_21 | GSO_18¦line_113500_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
364 | 41 | GSO_18 | line_113501_21 | UCMV22 | 10.3769 | High | 12.47 | 13.5424 | 0.0039208 | 13.5384 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 27 | 26 | 0 | 100 | 27 | 0.30755 | -79.8372 | 36.0101 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108304_21 -> line_108117_21 -> line_108116_21 -> line_116127_21 -> line_128625_21 -> line_128626_21 -> line_131276_21 -> line_116038_21 -> line_116037_21 -> line_112560_21 -> line_112561_21 -> line_111906_21 -> line_111907_21 -> line_113500_21 -> line_113501_21 | GSO_18¦line_113501_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
365 | 42 | GSO_18 | line_113499_21 | S_nCCTT8114 | 10.3769 | High | 12.47 | 13.5424 | 0.23917 | 13.3032 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 28 | 26 | 0 | 100 | 27 | 0.30755 | -79.8374 | 36.01 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108304_21 -> line_108117_21 -> line_108116_21 -> line_116127_21 -> line_128625_21 -> line_128626_21 -> line_131276_21 -> line_116038_21 -> line_116037_21 -> line_112560_21 -> line_112561_21 -> line_111906_21 -> line_111907_21 -> line_113500_21 -> recloser_1836_21 -> line_113499_21 | GSO_18¦line_113499_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
366 | 43 | GSO_18 | line_112222_21 | S_nCCTT12055 | 10.3769 | High | 12.47 | 13.5424 | 0.23132 | 13.311 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 29 | 27 | 0 | 100 | 27 | 0.30755 | -79.838 | 36.0096 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108304_21 -> line_108117_21 -> line_108116_21 -> line_116127_21 -> line_128625_21 -> line_128626_21 -> line_131276_21 -> line_116038_21 -> line_116037_21 -> line_112560_21 -> line_112561_21 -> line_111906_21 -> line_111907_21 -> line_113500_21 -> recloser_1836_21 -> line_113499_21 -> line_112222_21 | GSO_18¦line_112222_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
367 | 44 | GSO_18 | line_112221_21 | S_nCCTT3900 | 10.3769 | High | 12.47 | 13.5424 | 0.2274 | 13.315 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 30 | 28 | 0 | 100 | 27 | 0.30755 | -79.8387 | 36.0089 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108304_21 -> line_108117_21 -> line_108116_21 -> line_116127_21 -> line_128625_21 -> line_128626_21 -> line_131276_21 -> line_116038_21 -> line_116037_21 -> line_112560_21 -> line_112561_21 -> line_111906_21 -> line_111907_21 -> line_113500_21 -> recloser_1836_21 -> line_113499_21 -> line_112222_21 -> line_112221_21 | GSO_18¦line_112221_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
368 | 45 | GSO_18 | line_111623_21 | S_nCCTT11828 | 10.3769 | High | 12.47 | 13.5424 | 0.0039208 | 13.5384 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 31 | 29 | 0 | 100 | 27 | 0.30755 | -79.8395 | 36.0086 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108304_21 -> line_108117_21 -> line_108116_21 -> line_116127_21 -> line_128625_21 -> line_128626_21 -> line_131276_21 -> line_116038_21 -> line_116037_21 -> line_112560_21 -> line_112561_21 -> line_111906_21 -> line_111907_21 -> line_113500_21 -> recloser_1836_21 -> line_113499_21 -> line_112222_21 -> line_112221_21 -> line_111623_21 | GSO_18¦line_111623_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
369 | 46 | GSO_18 | line_112166_21 | S_nCCTT12034 | 10.3769 | High | 12.47 | 13.5424 | 0.21956 | 13.3228 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 31 | 29 | 0 | 100 | 27 | 0.30755 | -79.8384 | 36.0086 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108304_21 -> line_108117_21 -> line_108116_21 -> line_116127_21 -> line_128625_21 -> line_128626_21 -> line_131276_21 -> line_116038_21 -> line_116037_21 -> line_112560_21 -> line_112561_21 -> line_111906_21 -> line_111907_21 -> line_113500_21 -> recloser_1836_21 -> line_113499_21 -> line_112222_21 -> line_112221_21 -> line_112166_21 | GSO_18¦line_112166_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
370 | 47 | GSO_18 | line_112168_21 | S_nCCTT8121 | 10.3769 | High | 12.47 | 13.5424 | 0.074494 | 13.4679 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 32 | 30 | 0 | 100 | 27 | 0.30755 | -79.8373 | 36.0087 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108304_21 -> line_108117_21 -> line_108116_21 -> line_116127_21 -> line_128625_21 -> line_128626_21 -> line_131276_21 -> line_116038_21 -> line_116037_21 -> line_112560_21 -> line_112561_21 -> line_111906_21 -> line_111907_21 -> line_113500_21 -> recloser_1836_21 -> line_113499_21 -> line_112222_21 -> line_112221_21 -> line_112166_21 -> line_112168_21 | GSO_18¦line_112168_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
371 | 48 | GSO_18 | line_112167_21 | S_nCCTT3902 | 10.3769 | High | 12.47 | 13.5424 | 0.14115 | 13.4012 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 32 | 30 | 0 | 100 | 27 | 0.30755 | -79.8376 | 36.0084 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108304_21 -> line_108117_21 -> line_108116_21 -> line_116127_21 -> line_128625_21 -> line_128626_21 -> line_131276_21 -> line_116038_21 -> line_116037_21 -> line_112560_21 -> line_112561_21 -> line_111906_21 -> line_111907_21 -> line_113500_21 -> recloser_1836_21 -> line_113499_21 -> line_112222_21 -> line_112221_21 -> line_112166_21 -> line_112167_21 | GSO_18¦line_112167_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
372 | 49 | GSO_18 | line_111343_21 | S_nCCTT11726 | 10.3769 | High | 12.47 | 13.5424 | 0.070574 | 13.4718 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 33 | 31 | 0 | 100 | 27 | 0.30755 | -79.8364 | 36.0087 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108304_21 -> line_108117_21 -> line_108116_21 -> line_116127_21 -> line_128625_21 -> line_128626_21 -> line_131276_21 -> line_116038_21 -> line_116037_21 -> line_112560_21 -> line_112561_21 -> line_111906_21 -> line_111907_21 -> line_113500_21 -> recloser_1836_21 -> line_113499_21 -> line_112222_21 -> line_112221_21 -> line_112166_21 -> line_112168_21 -> line_111343_21 | GSO_18¦line_111343_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
373 | 50 | GSO_18 | line_120823_21 | S_nCCTT6740 | 10.3769 | High | 12.47 | 13.5424 | 0.13723 | 13.4051 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 33 | 31 | 0 | 100 | 27 | 0.30755 | -79.8378 | 36.0076 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108304_21 -> line_108117_21 -> line_108116_21 -> line_116127_21 -> line_128625_21 -> line_128626_21 -> line_131276_21 -> line_116038_21 -> line_116037_21 -> line_112560_21 -> line_112561_21 -> line_111906_21 -> line_111907_21 -> line_113500_21 -> recloser_1836_21 -> line_113499_21 -> line_112222_21 -> line_112221_21 -> line_112166_21 -> line_112167_21 -> line_120823_21 | GSO_18¦line_120823_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
374 | 51 | GSO_18 | line_106649_21 | S_nCCTT10238 | 10.3769 | High | 12.47 | 13.5424 | 0.0078415 | 13.5345 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 34 | 32 | 0 | 100 | 27 | 0.30755 | -79.8362 | 36.0085 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108304_21 -> line_108117_21 -> line_108116_21 -> line_116127_21 -> line_128625_21 -> line_128626_21 -> line_131276_21 -> line_116038_21 -> line_116037_21 -> line_112560_21 -> line_112561_21 -> line_111906_21 -> line_111907_21 -> line_113500_21 -> recloser_1836_21 -> line_113499_21 -> line_112222_21 -> line_112221_21 -> line_112166_21 -> line_112168_21 -> line_111343_21 -> line_106649_21 | GSO_18¦line_106649_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
375 | 52 | GSO_18 | line_111342_21 | S_nCCTT8111 | 10.3769 | High | 12.47 | 13.5424 | 0.058811 | 13.4836 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 34 | 32 | 0 | 100 | 27 | 0.30755 | -79.8354 | 36.0088 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108304_21 -> line_108117_21 -> line_108116_21 -> line_116127_21 -> line_128625_21 -> line_128626_21 -> line_131276_21 -> line_116038_21 -> line_116037_21 -> line_112560_21 -> line_112561_21 -> line_111906_21 -> line_111907_21 -> line_113500_21 -> recloser_1836_21 -> line_113499_21 -> line_112222_21 -> line_112221_21 -> line_112166_21 -> line_112168_21 -> line_111343_21 -> line_111342_21 | GSO_18¦line_111342_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
376 | 53 | GSO_18 | line_112965_21 | S_nCCTT12360 | 10.3769 | High | 12.47 | 13.5424 | 0.13331 | 13.4091 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 34 | 32 | 0 | 100 | 27 | 0.30755 | -79.8381 | 36.0069 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108304_21 -> line_108117_21 -> line_108116_21 -> line_116127_21 -> line_128625_21 -> line_128626_21 -> line_131276_21 -> line_116038_21 -> line_116037_21 -> line_112560_21 -> line_112561_21 -> line_111906_21 -> line_111907_21 -> line_113500_21 -> recloser_1836_21 -> line_113499_21 -> line_112222_21 -> line_112221_21 -> line_112166_21 -> line_112167_21 -> line_120823_21 -> line_112965_21 | GSO_18¦line_112965_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
377 | 54 | GSO_18 | line_106648_21 | S_nCCTT11486 | 10.3769 | High | 12.47 | 13.5424 | 0.0039208 | 13.5384 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 35 | 33 | 0 | 100 | 27 | 0.30755 | -79.836 | 36.0083 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108304_21 -> line_108117_21 -> line_108116_21 -> line_116127_21 -> line_128625_21 -> line_128626_21 -> line_131276_21 -> line_116038_21 -> line_116037_21 -> line_112560_21 -> line_112561_21 -> line_111906_21 -> line_111907_21 -> line_113500_21 -> recloser_1836_21 -> line_113499_21 -> line_112222_21 -> line_112221_21 -> line_112166_21 -> line_112168_21 -> line_111343_21 -> line_106649_21 -> line_106648_21 | GSO_18¦line_106648_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
378 | 55 | GSO_18 | line_110779_21 | S_nCCTT11528 | 10.3769 | High | 12.47 | 13.5424 | 0.12938 | 13.413 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 35 | 33 | 0 | 100 | 27 | 0.30755 | -79.8382 | 36.0066 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108304_21 -> line_108117_21 -> line_108116_21 -> line_116127_21 -> line_128625_21 -> line_128626_21 -> line_131276_21 -> line_116038_21 -> line_116037_21 -> line_112560_21 -> line_112561_21 -> line_111906_21 -> line_111907_21 -> line_113500_21 -> recloser_1836_21 -> line_113499_21 -> line_112222_21 -> line_112221_21 -> line_112166_21 -> line_112167_21 -> line_120823_21 -> line_112965_21 -> line_110779_21 | GSO_18¦line_110779_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
379 | 56 | GSO_18 | line_129249_21 | S_nCCTT8119 | 10.3769 | High | 12.47 | 13.5424 | 0.054891 | 13.4875 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 35 | 33 | 0 | 100 | 27 | 0.30755 | -79.8347 | 36.0089 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108304_21 -> line_108117_21 -> line_108116_21 -> line_116127_21 -> line_128625_21 -> line_128626_21 -> line_131276_21 -> line_116038_21 -> line_116037_21 -> line_112560_21 -> line_112561_21 -> line_111906_21 -> line_111907_21 -> line_113500_21 -> recloser_1836_21 -> line_113499_21 -> line_112222_21 -> line_112221_21 -> line_112166_21 -> line_112168_21 -> line_111343_21 -> line_111342_21 -> line_129249_21 | GSO_18¦line_129249_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
380 | 57 | GSO_18 | line_108245_21 | S_nCCTT10727 | 10.3769 | High | 12.47 | 13.5424 | 0.031366 | 13.511 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 36 | 34 | 0 | 100 | 27 | 0.30755 | -79.8386 | 36.0068 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108304_21 -> line_108117_21 -> line_108116_21 -> line_116127_21 -> line_128625_21 -> line_128626_21 -> line_131276_21 -> line_116038_21 -> line_116037_21 -> line_112560_21 -> line_112561_21 -> line_111906_21 -> line_111907_21 -> line_113500_21 -> recloser_1836_21 -> line_113499_21 -> line_112222_21 -> line_112221_21 -> line_112166_21 -> line_112167_21 -> line_120823_21 -> line_112965_21 -> line_110779_21 -> line_108245_21 | GSO_18¦line_108245_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
381 | 58 | GSO_18 | line_110780_21 | S_nCCTT9628 | 10.3769 | High | 12.47 | 13.5424 | 0.094098 | 13.4483 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 36 | 34 | 0 | 100 | 27 | 0.30755 | -79.8385 | 36.0064 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108304_21 -> line_108117_21 -> line_108116_21 -> line_116127_21 -> line_128625_21 -> line_128626_21 -> line_131276_21 -> line_116038_21 -> line_116037_21 -> line_112560_21 -> line_112561_21 -> line_111906_21 -> line_111907_21 -> line_113500_21 -> recloser_1836_21 -> line_113499_21 -> line_112222_21 -> line_112221_21 -> line_112166_21 -> line_112167_21 -> line_120823_21 -> line_112965_21 -> line_110779_21 -> line_110780_21 | GSO_18¦line_110780_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
382 | 59 | GSO_18 | line_111485_21 | S_nCCTT11779 | 10.3769 | High | 12.47 | 13.5424 | 0.05097 | 13.4914 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 36 | 34 | 0 | 100 | 27 | 0.30755 | -79.834 | 36.009 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108304_21 -> line_108117_21 -> line_108116_21 -> line_116127_21 -> line_128625_21 -> line_128626_21 -> line_131276_21 -> line_116038_21 -> line_116037_21 -> line_112560_21 -> line_112561_21 -> line_111906_21 -> line_111907_21 -> line_113500_21 -> recloser_1836_21 -> line_113499_21 -> line_112222_21 -> line_112221_21 -> line_112166_21 -> line_112168_21 -> line_111343_21 -> line_111342_21 -> line_129249_21 -> line_111485_21 | GSO_18¦line_111485_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
383 | 60 | GSO_18 | line_108246_21 | S_nCCTT7541 | 10.3769 | High | 12.47 | 13.5424 | 0.023525 | 13.5188 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 37 | 35 | 0 | 100 | 27 | 0.30755 | -79.8389 | 36.0071 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108304_21 -> line_108117_21 -> line_108116_21 -> line_116127_21 -> line_128625_21 -> line_128626_21 -> line_131276_21 -> line_116038_21 -> line_116037_21 -> line_112560_21 -> line_112561_21 -> line_111906_21 -> line_111907_21 -> line_113500_21 -> recloser_1836_21 -> line_113499_21 -> line_112222_21 -> line_112221_21 -> line_112166_21 -> line_112167_21 -> line_120823_21 -> line_112965_21 -> line_110779_21 -> line_108245_21 -> line_108246_21 | GSO_18¦line_108246_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
384 | 61 | GSO_18 | line_111484_21 | S_nCCTT6871 | 10.3769 | High | 12.47 | 13.5424 | 0.047049 | 13.4953 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 37 | 35 | 0 | 100 | 27 | 0.30755 | -79.8335 | 36.0083 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108304_21 -> line_108117_21 -> line_108116_21 -> line_116127_21 -> line_128625_21 -> line_128626_21 -> line_131276_21 -> line_116038_21 -> line_116037_21 -> line_112560_21 -> line_112561_21 -> line_111906_21 -> line_111907_21 -> line_113500_21 -> recloser_1836_21 -> line_113499_21 -> line_112222_21 -> line_112221_21 -> line_112166_21 -> line_112168_21 -> line_111343_21 -> line_111342_21 -> line_129249_21 -> line_111485_21 -> line_111484_21 | GSO_18¦line_111484_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
385 | 62 | GSO_18 | line_112972_21 | S_nCCTT12363 | 10.3769 | High | 12.47 | 13.5424 | 0.019604 | 13.5228 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 37 | 35 | 0 | 100 | 27 | 0.30755 | -79.8388 | 36.0063 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108304_21 -> line_108117_21 -> line_108116_21 -> line_116127_21 -> line_128625_21 -> line_128626_21 -> line_131276_21 -> line_116038_21 -> line_116037_21 -> line_112560_21 -> line_112561_21 -> line_111906_21 -> line_111907_21 -> line_113500_21 -> recloser_1836_21 -> line_113499_21 -> line_112222_21 -> line_112221_21 -> line_112166_21 -> line_112167_21 -> line_120823_21 -> line_112965_21 -> line_110779_21 -> line_110780_21 -> line_112972_21 | GSO_18¦line_112972_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
386 | 63 | GSO_18 | line_131950_21 | S_nCCTT9622 | 10.3769 | High | 12.47 | 13.5424 | 0.062732 | 13.4796 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 37 | 35 | 0 | 100 | 27 | 0.30755 | -79.8387 | 36.0052 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108304_21 -> line_108117_21 -> line_108116_21 -> line_116127_21 -> line_128625_21 -> line_128626_21 -> line_131276_21 -> line_116038_21 -> line_116037_21 -> line_112560_21 -> line_112561_21 -> line_111906_21 -> line_111907_21 -> line_113500_21 -> recloser_1836_21 -> line_113499_21 -> line_112222_21 -> line_112221_21 -> line_112166_21 -> line_112167_21 -> line_120823_21 -> line_112965_21 -> line_110779_21 -> line_110780_21 -> line_131950_21 | GSO_18¦line_131950_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
387 | 64 | GSO_18 | line_112973_21 | S_nCCTT9634 | 10.3769 | High | 12.47 | 13.5424 | 0.015683 | 13.5267 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 38 | 36 | 0 | 100 | 27 | 0.30755 | -79.8393 | 36.0063 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108304_21 -> line_108117_21 -> line_108116_21 -> line_116127_21 -> line_128625_21 -> line_128626_21 -> line_131276_21 -> line_116038_21 -> line_116037_21 -> line_112560_21 -> line_112561_21 -> line_111906_21 -> line_111907_21 -> line_113500_21 -> recloser_1836_21 -> line_113499_21 -> line_112222_21 -> line_112221_21 -> line_112166_21 -> line_112167_21 -> line_120823_21 -> line_112965_21 -> line_110779_21 -> line_110780_21 -> line_112972_21 -> line_112973_21 | GSO_18¦line_112973_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
388 | 65 | GSO_18 | line_106466_21 | S_nCCTT10183 | 10.3769 | High | 12.47 | 13.5424 | 0.039208 | 13.5032 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 38 | 36 | 0 | 100 | 27 | 0.30755 | -79.8344 | 36.0069 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108304_21 -> line_108117_21 -> line_108116_21 -> line_116127_21 -> line_128625_21 -> line_128626_21 -> line_131276_21 -> line_116038_21 -> line_116037_21 -> line_112560_21 -> line_112561_21 -> line_111906_21 -> line_111907_21 -> line_113500_21 -> recloser_1836_21 -> line_113499_21 -> line_112222_21 -> line_112221_21 -> line_112166_21 -> line_112168_21 -> line_111343_21 -> line_111342_21 -> line_129249_21 -> line_111485_21 -> line_111484_21 -> line_106466_21 | GSO_18¦line_106466_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
389 | 66 | GSO_18 | line_128347_21 | S_nCCTT7601 | 10.3769 | High | 12.47 | 13.5424 | 0.047049 | 13.4953 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 38 | 36 | 0 | 100 | 27 | 0.30755 | -79.8374 | 36.0042 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108304_21 -> line_108117_21 -> line_108116_21 -> line_116127_21 -> line_128625_21 -> line_128626_21 -> line_131276_21 -> line_116038_21 -> line_116037_21 -> line_112560_21 -> line_112561_21 -> line_111906_21 -> line_111907_21 -> line_113500_21 -> recloser_1836_21 -> line_113499_21 -> line_112222_21 -> line_112221_21 -> line_112166_21 -> line_112167_21 -> line_120823_21 -> line_112965_21 -> line_110779_21 -> line_110780_21 -> line_131950_21 -> line_128347_21 | GSO_18¦line_128347_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
390 | 67 | GSO_18 | line_106465_21 | S_nCCTT6861 | 10.3769 | High | 12.47 | 13.5424 | 0.031366 | 13.511 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 39 | 37 | 0 | 100 | 27 | 0.30755 | -79.8342 | 36.0059 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108304_21 -> line_108117_21 -> line_108116_21 -> line_116127_21 -> line_128625_21 -> line_128626_21 -> line_131276_21 -> line_116038_21 -> line_116037_21 -> line_112560_21 -> line_112561_21 -> line_111906_21 -> line_111907_21 -> line_113500_21 -> recloser_1836_21 -> line_113499_21 -> line_112222_21 -> line_112221_21 -> line_112166_21 -> line_112168_21 -> line_111343_21 -> line_111342_21 -> line_129249_21 -> line_111485_21 -> line_111484_21 -> line_106466_21 -> line_106465_21 | GSO_18¦line_106465_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
391 | 68 | GSO_18 | line_115816_21 | S_nCCTT1942 | 10.3769 | High | 12.47 | 13.5424 | 0.043128 | 13.4992 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 39 | 37 | 0 | 100 | 27 | 0.30755 | -79.8358 | 36.0029 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108304_21 -> line_108117_21 -> line_108116_21 -> line_116127_21 -> line_128625_21 -> line_128626_21 -> line_131276_21 -> line_116038_21 -> line_116037_21 -> line_112560_21 -> line_112561_21 -> line_111906_21 -> line_111907_21 -> line_113500_21 -> recloser_1836_21 -> line_113499_21 -> line_112222_21 -> line_112221_21 -> line_112166_21 -> line_112167_21 -> line_120823_21 -> line_112965_21 -> line_110779_21 -> line_110780_21 -> line_131950_21 -> line_128347_21 -> line_115816_21 | GSO_18¦line_115816_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
392 | 69 | GSO_18 | line_108372_21 | S_nCCTT1942_L_S_nCCTT10761 | 10.3769 | High | 12.47 | 13.5424 | 0.015683 | 13.5267 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 40 | 38 | 0 | 100 | 27 | 0.30755 | -79.8353 | 36.0021 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108304_21 -> line_108117_21 -> line_108116_21 -> line_116127_21 -> line_128625_21 -> line_128626_21 -> line_131276_21 -> line_116038_21 -> line_116037_21 -> line_112560_21 -> line_112561_21 -> line_111906_21 -> line_111907_21 -> line_113500_21 -> recloser_1836_21 -> line_113499_21 -> line_112222_21 -> line_112221_21 -> line_112166_21 -> line_112167_21 -> line_120823_21 -> line_112965_21 -> line_110779_21 -> line_110780_21 -> line_131950_21 -> line_128347_21 -> line_115816_21 -> line_108372_21 | GSO_18¦line_108372_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
393 | 70 | GSO_18 | line_108373_21 | S_nCCTT10761 | 10.3769 | High | 12.47 | 13.5424 | 0.015683 | 13.5267 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 41 | 39 | 0 | 100 | 27 | 0.30755 | -79.8343 | 36.0023 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108304_21 -> line_108117_21 -> line_108116_21 -> line_116127_21 -> line_128625_21 -> line_128626_21 -> line_131276_21 -> line_116038_21 -> line_116037_21 -> line_112560_21 -> line_112561_21 -> line_111906_21 -> line_111907_21 -> line_113500_21 -> recloser_1836_21 -> line_113499_21 -> line_112222_21 -> line_112221_21 -> line_112166_21 -> line_112167_21 -> line_120823_21 -> line_112965_21 -> line_110779_21 -> line_110780_21 -> line_131950_21 -> line_128347_21 -> line_115816_21 -> line_108372_21 -> line_108373_21 | GSO_18¦line_108373_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
394 | 71 | GSO_18 | line_108371_21 | S_nCCTT12351 | 10.3769 | High | 12.47 | 13.5424 | 0.011762 | 13.5306 | 2.2897 | 12.6666 | 10.3769 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2897 | 10.3769 | 42 | 40 | 0 | 100 | 27 | 0.30755 | -79.8338 | 36.0022 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108304_21 -> line_108117_21 -> line_108116_21 -> line_116127_21 -> line_128625_21 -> line_128626_21 -> line_131276_21 -> line_116038_21 -> line_116037_21 -> line_112560_21 -> line_112561_21 -> line_111906_21 -> line_111907_21 -> line_113500_21 -> recloser_1836_21 -> line_113499_21 -> line_112222_21 -> line_112221_21 -> line_112166_21 -> line_112167_21 -> line_120823_21 -> line_112965_21 -> line_110779_21 -> line_110780_21 -> line_131950_21 -> line_128347_21 -> line_115816_21 -> line_108372_21 -> line_108373_21 -> line_108371_21 | GSO_18¦line_108371_21 | ACLineSegment | 660 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved |  | 132
531 | 72 | GSO_18 | line_106670_21 | S_nCCTT10244 | 2.8394 | High | 7.2 | 2.8433 | 0.0039208 | 2.8394 | 2.2897 | 12.6666 | 10.3769 | line_106670_21 | ACLineSegment | Line | 2.8433 | 0.0039208 | 2.8394 | 30 | 27 | 0 | 100 | 27 | 0.30755 | -79.8378 | 36.0102 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108304_21 -> line_108117_21 -> line_108116_21 -> line_116127_21 -> line_128625_21 -> line_128626_21 -> line_131276_21 -> line_116038_21 -> line_116037_21 -> line_112560_21 -> line_112561_21 -> line_111906_21 -> line_111907_21 -> line_113500_21 -> recloser_1836_21 -> line_113499_21 -> fuse_79_21 -> line_106670_21 | GSO_18¦line_106670_21 | ACLineSegment | 240 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.8394 | [6 empty] | SubstationCapacityUnresolved | line_106670_21 | Substation capacity unresolved |  | 132
543 | 73 | GSO_18 | line_111503_21 | S_nCCTT12351_L_S_nCCTT11783 | 2.8355 | High | 7.2 | 2.8433 | 0.0078415 | 2.8355 | 2.2897 | 12.6666 | 10.3769 | line_111503_21 | ACLineSegment | Line | 2.8433 | 0.0078415 | 2.8355 | 43 | 41 | 0 | 100 | 27 | 0.30755 | -79.8333 | 36.0017 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108304_21 -> line_108117_21 -> line_108116_21 -> line_116127_21 -> line_128625_21 -> line_128626_21 -> line_131276_21 -> line_116038_21 -> line_116037_21 -> line_112560_21 -> line_112561_21 -> line_111906_21 -> line_111907_21 -> line_113500_21 -> recloser_1836_21 -> line_113499_21 -> line_112222_21 -> line_112221_21 -> line_112166_21 -> line_112167_21 -> line_120823_21 -> line_112965_21 -> line_110779_21 -> line_110780_21 -> line_131950_21 -> line_128347_21 -> line_115816_21 -> line_108372_21 -> line_108373_21 -> line_108371_21 -> line_111503_21 | GSO_18¦line_111503_21 | ACLineSegment | 240 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.8355 | [6 empty] | SubstationCapacityUnresolved | line_111503_21 | Substation capacity unresolved |  | 132
544 | 74 | GSO_18 | line_111504_21 | S_nCCTT12351_B_S_nCCTT11783 | 2.8355 | High | 7.2 | 2.8433 | 0.0078415 | 2.8355 | 2.2897 | 12.6666 | 10.3769 | line_111503_21 | ACLineSegment | Line | 2.8433 | 0.0078415 | 2.8355 | 44 | 42 | 0 | 100 | 27 | 0.30755 | -79.8337 | 36.0019 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108304_21 -> line_108117_21 -> line_108116_21 -> line_116127_21 -> line_128625_21 -> line_128626_21 -> line_131276_21 -> line_116038_21 -> line_116037_21 -> line_112560_21 -> line_112561_21 -> line_111906_21 -> line_111907_21 -> line_113500_21 -> recloser_1836_21 -> line_113499_21 -> line_112222_21 -> line_112221_21 -> line_112166_21 -> line_112167_21 -> line_120823_21 -> line_112965_21 -> line_110779_21 -> line_110780_21 -> line_131950_21 -> line_128347_21 -> line_115816_21 -> line_108372_21 -> line_108373_21 -> line_108371_21 -> line_111503_21 -> line_111504_21 | GSO_18¦line_111504_21 | ACLineSegment | 240 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.8355 | [6 empty] | SubstationCapacityUnresolved | line_111503_21 | Substation capacity unresolved |  | 132
545 | 75 | GSO_18 | line_111505_21 | S_nCCTT12385 | 2.8355 | High | 7.2 | 2.8433 | 0.0039208 | 2.8394 | 2.2897 | 12.6666 | 10.3769 | line_111503_21 | ACLineSegment | Line | 2.8433 | 0.0078415 | 2.8355 | 46 | 43 | 0 | 100 | 27 | 0.30755 | -79.8331 | 36.0012 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108304_21 -> line_108117_21 -> line_108116_21 -> line_116127_21 -> line_128625_21 -> line_128626_21 -> line_131276_21 -> line_116038_21 -> line_116037_21 -> line_112560_21 -> line_112561_21 -> line_111906_21 -> line_111907_21 -> line_113500_21 -> recloser_1836_21 -> line_113499_21 -> line_112222_21 -> line_112221_21 -> line_112166_21 -> line_112167_21 -> line_120823_21 -> line_112965_21 -> line_110779_21 -> line_110780_21 -> line_131950_21 -> line_128347_21 -> line_115816_21 -> line_108372_21 -> line_108373_21 -> line_108371_21 -> line_111503_21 -> line_111504_21 -> fuse_470_21 -> line_111505_21 | GSO_18¦line_111505_21 | ACLineSegment | 240 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.8355 | [6 empty] | SubstationCapacityUnresolved | line_111503_21 | Substation capacity unresolved |  | 132
551 | 76 | GSO_18 | line_112861_21 | S_nCCTT12319 | 2.8316 | High | 7.2 | 2.8433 | 0.011762 | 2.8316 | 2.2897 | 12.6666 | 10.3769 | line_112861_21 | ACLineSegment | Line | 2.8433 | 0.011762 | 2.8316 | 40 | 37 | 0 | 100 | 27 | 0.30755 | -79.84 | 36.0058 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108304_21 -> line_108117_21 -> line_108116_21 -> line_116127_21 -> line_128625_21 -> line_128626_21 -> line_131276_21 -> line_116038_21 -> line_116037_21 -> line_112560_21 -> line_112561_21 -> line_111906_21 -> line_111907_21 -> line_113500_21 -> recloser_1836_21 -> line_113499_21 -> line_112222_21 -> line_112221_21 -> line_112166_21 -> line_112167_21 -> line_120823_21 -> line_112965_21 -> line_110779_21 -> line_110780_21 -> line_112972_21 -> line_112973_21 -> fuse_575_21 -> line_112861_21 | GSO_18¦line_112861_21 | ACLineSegment | 240 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.8316 | [6 empty] | SubstationCapacityUnresolved | line_112861_21 | Substation capacity unresolved |  | 132
558 | 77 | GSO_18 | line_106690_21 | S_nCCTT10251 | 2.8237 | High | 7.2 | 2.8433 | 0.019604 | 2.8237 | 2.2897 | 12.6666 | 10.3769 | line_106690_21 | ACLineSegment | Line | 2.8433 | 0.019604 | 2.8237 | 7 | 5 | 0 | 100 | 27 | 0.30755 | -79.8234 | 36.011 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129230_21 -> fuse_83_21 -> line_106690_21 | GSO_18¦line_106690_21 | ACLineSegment | 240 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.8237 | [6 empty] | SubstationCapacityUnresolved | line_106690_21 | Substation capacity unresolved |  | 132
559 | 78 | GSO_18 | line_106886_21 | S_nCCTT10306 | 2.8237 | High | 7.2 | 2.8433 | 0.019604 | 2.8237 | 2.2897 | 12.6666 | 10.3769 | line_106886_21 | ACLineSegment | Line | 2.8433 | 0.019604 | 2.8237 | 39 | 36 | 0 | 100 | 27 | 0.30755 | -79.8394 | 36.0073 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108304_21 -> line_108117_21 -> line_108116_21 -> line_116127_21 -> line_128625_21 -> line_128626_21 -> line_131276_21 -> line_116038_21 -> line_116037_21 -> line_112560_21 -> line_112561_21 -> line_111906_21 -> line_111907_21 -> line_113500_21 -> recloser_1836_21 -> line_113499_21 -> line_112222_21 -> line_112221_21 -> line_112166_21 -> line_112167_21 -> line_120823_21 -> line_112965_21 -> line_110779_21 -> line_108245_21 -> line_108246_21 -> fuse_99_21 -> line_106886_21 | GSO_18¦line_106886_21 | ACLineSegment | 240 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.8237 | [6 empty] | SubstationCapacityUnresolved | line_106886_21 | Substation capacity unresolved |  | 132
560 | 79 | GSO_18 | line_106885_21 | S_nCCTT11505 | 2.8237 | High | 7.2 | 2.8433 | 0.0078415 | 2.8355 | 2.2897 | 12.6666 | 10.3769 | line_106886_21 | ACLineSegment | Line | 2.8433 | 0.019604 | 2.8237 | 40 | 37 | 0 | 100 | 27 | 0.30755 | -79.8401 | 36.0073 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108304_21 -> line_108117_21 -> line_108116_21 -> line_116127_21 -> line_128625_21 -> line_128626_21 -> line_131276_21 -> line_116038_21 -> line_116037_21 -> line_112560_21 -> line_112561_21 -> line_111906_21 -> line_111907_21 -> line_113500_21 -> recloser_1836_21 -> line_113499_21 -> line_112222_21 -> line_112221_21 -> line_112166_21 -> line_112167_21 -> line_120823_21 -> line_112965_21 -> line_110779_21 -> line_108245_21 -> line_108246_21 -> fuse_99_21 -> line_106886_21 -> line_106885_21 | GSO_18¦line_106885_21 | ACLineSegment | 240 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.8237 | [6 empty] | SubstationCapacityUnresolved | line_106886_21 | Substation capacity unresolved |  | 132
561 | 80 | GSO_18 | line_112325_21 | S_nCCTT12096 | 2.8237 | High | 7.2 | 2.8433 | 0.019604 | 2.8237 | 2.2897 | 12.6666 | 10.3769 | line_112325_21 | ACLineSegment | Line | 2.8433 | 0.019604 | 2.8237 | 41 | 38 | 0 | 100 | 27 | 0.30755 | -79.836 | 36.0012 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108304_21 -> line_108117_21 -> line_108116_21 -> line_116127_21 -> line_128625_21 -> line_128626_21 -> line_131276_21 -> line_116038_21 -> line_116037_21 -> line_112560_21 -> line_112561_21 -> line_111906_21 -> line_111907_21 -> line_113500_21 -> recloser_1836_21 -> line_113499_21 -> line_112222_21 -> line_112221_21 -> line_112166_21 -> line_112167_21 -> line_120823_21 -> line_112965_21 -> line_110779_21 -> line_110780_21 -> line_131950_21 -> line_128347_21 -> line_115816_21 -> fuse_536_21 -> line_112325_21 | GSO_18¦line_112325_21 | ACLineSegment | 240 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.8237 | [6 empty] | SubstationCapacityUnresolved | line_112325_21 | Substation capacity unresolved |  | 132
562 | 81 | GSO_18 | line_110709_21 | S_nCCTT9629 | 2.8237 | High | 7.2 | 2.8433 | 0.0039208 | 2.8394 | 2.2897 | 12.6666 | 10.3769 | line_106886_21 | ACLineSegment | Line | 2.8433 | 0.019604 | 2.8237 | 41 | 38 | 0 | 100 | 27 | 0.30755 | -79.8406 | 36.0076 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108304_21 -> line_108117_21 -> line_108116_21 -> line_116127_21 -> line_128625_21 -> line_128626_21 -> line_131276_21 -> line_116038_21 -> line_116037_21 -> line_112560_21 -> line_112561_21 -> line_111906_21 -> line_111907_21 -> line_113500_21 -> recloser_1836_21 -> line_113499_21 -> line_112222_21 -> line_112221_21 -> line_112166_21 -> line_112167_21 -> line_120823_21 -> line_112965_21 -> line_110779_21 -> line_108245_21 -> line_108246_21 -> fuse_99_21 -> line_106886_21 -> line_106885_21 -> line_110709_21 | GSO_18¦line_110709_21 | ACLineSegment | 240 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.8237 | [6 empty] | SubstationCapacityUnresolved | line_106886_21 | Substation capacity unresolved |  | 132
563 | 82 | GSO_18 | line_112326_21 | S_nCCTT7565 | 2.8237 | High | 7.2 | 2.8433 | 0.011762 | 2.8316 | 2.2897 | 12.6666 | 10.3769 | line_112325_21 | ACLineSegment | Line | 2.8433 | 0.019604 | 2.8237 | 42 | 39 | 0 | 100 | 27 | 0.30755 | -79.8371 | 36.0005 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108304_21 -> line_108117_21 -> line_108116_21 -> line_116127_21 -> line_128625_21 -> line_128626_21 -> line_131276_21 -> line_116038_21 -> line_116037_21 -> line_112560_21 -> line_112561_21 -> line_111906_21 -> line_111907_21 -> line_113500_21 -> recloser_1836_21 -> line_113499_21 -> line_112222_21 -> line_112221_21 -> line_112166_21 -> line_112167_21 -> line_120823_21 -> line_112965_21 -> line_110779_21 -> line_110780_21 -> line_131950_21 -> line_128347_21 -> line_115816_21 -> fuse_536_21 -> line_112325_21 -> line_112326_21 | GSO_18¦line_112326_21 | ACLineSegment | 240 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.8237 | [6 empty] | SubstationCapacityUnresolved | line_112325_21 | Substation capacity unresolved |  | 132
570 | 83 | GSO_18 | line_108159_21 | S_nCCTT10700 | 2.8159 | High | 7.2 | 2.8433 | 0.027445 | 2.8159 | 2.2897 | 12.6666 | 10.3769 | line_108159_21 | ACLineSegment | Line | 2.8433 | 0.027445 | 2.8159 | 41 | 38 | 0 | 100 | 27 | 0.30755 | -79.834 | 36.0056 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108304_21 -> line_108117_21 -> line_108116_21 -> line_116127_21 -> line_128625_21 -> line_128626_21 -> line_131276_21 -> line_116038_21 -> line_116037_21 -> line_112560_21 -> line_112561_21 -> line_111906_21 -> line_111907_21 -> line_113500_21 -> recloser_1836_21 -> line_113499_21 -> line_112222_21 -> line_112221_21 -> line_112166_21 -> line_112168_21 -> line_111343_21 -> line_111342_21 -> line_129249_21 -> line_111485_21 -> line_111484_21 -> line_106466_21 -> line_106465_21 -> fuse_203_21 -> line_108159_21 | GSO_18¦line_108159_21 | ACLineSegment | 240 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.8159 | [6 empty] | SubstationCapacityUnresolved | line_108159_21 | Substation capacity unresolved |  | 132
571 | 84 | GSO_18 | line_107001_21 | S_nCCTT10341 | 2.8159 | High | 7.2 | 2.8433 | 0.023525 | 2.8198 | 2.2897 | 12.6666 | 10.3769 | line_108159_21 | ACLineSegment | Line | 2.8433 | 0.027445 | 2.8159 | 42 | 39 | 0 | 100 | 27 | 0.30755 | -79.8332 | 36.0051 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108304_21 -> line_108117_21 -> line_108116_21 -> line_116127_21 -> line_128625_21 -> line_128626_21 -> line_131276_21 -> line_116038_21 -> line_116037_21 -> line_112560_21 -> line_112561_21 -> line_111906_21 -> line_111907_21 -> line_113500_21 -> recloser_1836_21 -> line_113499_21 -> line_112222_21 -> line_112221_21 -> line_112166_21 -> line_112168_21 -> line_111343_21 -> line_111342_21 -> line_129249_21 -> line_111485_21 -> line_111484_21 -> line_106466_21 -> line_106465_21 -> fuse_203_21 -> line_108159_21 -> line_107001_21 | GSO_18¦line_107001_21 | ACLineSegment | 240 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.8159 | [6 empty] | SubstationCapacityUnresolved | line_108159_21 | Substation capacity unresolved |  | 132
572 | 85 | GSO_18 | line_106839_21 | S_nCCTT10341_B_S_nCCTT10292 | 2.8159 | High | 7.2 | 7.1083 | 0.0078415 | 7.1005 | 2.2897 | 12.6666 | 10.3769 | line_108159_21 | ACLineSegment | Line | 2.8433 | 0.027445 | 2.8159 | 43 | 40 | 0 | 100 | 27 | 0.30755 | -79.832 | 36.0044 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108304_21 -> line_108117_21 -> line_108116_21 -> line_116127_21 -> line_128625_21 -> line_128626_21 -> line_131276_21 -> line_116038_21 -> line_116037_21 -> line_112560_21 -> line_112561_21 -> line_111906_21 -> line_111907_21 -> line_113500_21 -> recloser_1836_21 -> line_113499_21 -> line_112222_21 -> line_112221_21 -> line_112166_21 -> line_112168_21 -> line_111343_21 -> line_111342_21 -> line_129249_21 -> line_111485_21 -> line_111484_21 -> line_106466_21 -> line_106465_21 -> fuse_203_21 -> line_108159_21 -> line_107001_21 -> line_106839_21 | GSO_18¦line_106839_21 | ACLineSegment | 600 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.8159 | [6 empty] | SubstationCapacityUnresolved | line_108159_21 | Substation capacity unresolved |  | 132
577 | 86 | GSO_18 | line_126656_21 | S_nCCTT6639 | 2.812 | High | 7.2 | 2.8433 | 0.031366 | 2.812 | 2.2897 | 12.6666 | 10.3769 | line_126656_21 | ACLineSegment | Line | 2.8433 | 0.031366 | 2.812 | 18 | 16 | 0 | 100 | 27 | 0.30755 | -79.8323 | 36.0108 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108304_21 -> line_108117_21 -> line_108116_21 -> line_116127_21 -> fuse_1577_21 -> line_126656_21 | GSO_18¦line_126656_21 | ACLineSegment | 240 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.812 | [6 empty] | SubstationCapacityUnresolved | line_126656_21 | Substation capacity unresolved |  | 132
579 | 87 | GSO_18 | line_107808_21 | S_nCCTT6750 | 2.7884 | High | 7.2 | 2.8433 | 0.054891 | 2.7884 | 2.2897 | 12.6666 | 10.3769 | line_107808_21 | ACLineSegment | Line | 2.8433 | 0.054891 | 2.7884 | 8 | 6 | 0 | 100 | 27 | 0.30755 | -79.8254 | 36.0137 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> fuse_173_21 -> line_107808_21 | GSO_18¦line_107808_21 | ACLineSegment | 240 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.7884 | [6 empty] | SubstationCapacityUnresolved | line_107808_21 | Substation capacity unresolved |  | 132
580 | 88 | GSO_18 | line_106801_21 | S_nCCTT10280 | 2.7806 | High | 7.2 | 2.8433 | 0.062732 | 2.7806 | 2.2897 | 12.6666 | 10.3769 | line_106801_21 | ACLineSegment | Line | 2.8433 | 0.062732 | 2.7806 | 17 | 15 | 0 | 100 | 27 | 0.30755 | -79.8313 | 36.0151 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108305_21 -> line_109744_21 -> line_109743_21 -> fuse_93_21 -> line_106801_21 | GSO_18¦line_106801_21 | ACLineSegment | 240 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.7806 | [6 empty] | SubstationCapacityUnresolved | line_106801_21 | Substation capacity unresolved |  | 132
581 | 89 | GSO_18 | line_106802_21 | S_nCCTT7482 | 2.7806 | High | 7.2 | 2.8433 | 0.031366 | 2.812 | 2.2897 | 12.6666 | 10.3769 | line_106801_21 | ACLineSegment | Line | 2.8433 | 0.062732 | 2.7806 | 18 | 16 | 0 | 100 | 27 | 0.30755 | -79.8306 | 36.0153 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108305_21 -> line_109744_21 -> line_109743_21 -> fuse_93_21 -> line_106801_21 -> line_106802_21 | GSO_18¦line_106802_21 | ACLineSegment | 240 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.7806 | [6 empty] | SubstationCapacityUnresolved | line_106801_21 | Substation capacity unresolved |  | 132
582 | 90 | GSO_18 | line_110213_21 | S_nCCTT1988 | 2.7688 | High | 7.2 | 2.8433 | 0.074494 | 2.7688 | 2.2897 | 12.6666 | 10.3769 | line_110213_21 | ACLineSegment | Line | 2.8433 | 0.074494 | 2.7688 | 17 | 15 | 0 | 100 | 27 | 0.30755 | -79.832 | 36.0147 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> line_108303_21 -> line_108305_21 -> line_109744_21 -> line_109743_21 -> fuse_369_21 -> line_110213_21 | GSO_18¦line_110213_21 | ACLineSegment | 240 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.7688 | [6 empty] | SubstationCapacityUnresolved | line_110213_21 | Substation capacity unresolved |  | 132
583 | 91 | GSO_18 | line_111729_21 | S_nCCTT7533 | 2.7649 | High | 7.2 | 2.8433 | 0.078415 | 2.7649 | 2.2897 | 12.6666 | 10.3769 | line_111729_21 | ACLineSegment | Line | 2.8433 | 0.078415 | 2.7649 | 11 | 9 | 0 | 100 | 27 | 0.30755 | -79.8273 | 36.0115 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> fuse_494_21 -> line_111729_21 | GSO_18¦line_111729_21 | ACLineSegment | 240 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.7649 | [6 empty] | SubstationCapacityUnresolved | line_111729_21 | Substation capacity unresolved |  | 132
584 | 92 | GSO_18 | line_108321_21 | S_nCCTT10848 | 2.4826 | High | 7.2 | 2.8433 | 0.36071 | 2.4826 | 2.2897 | 12.6666 | 10.3769 | line_108321_21 | ACLineSegment | Line | 2.8433 | 0.36071 | 2.4826 | 4 | 2 | 0 | 100 | 27 | 0.30755 | -79.8232 | 36.0142 | recloser_1790_21 -> line_108323_21 -> fuse_219_21 -> line_108321_21 | GSO_18¦line_108321_21 | ACLineSegment | 240 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.4826 | [6 empty] | SubstationCapacityUnresolved | line_108321_21 | Substation capacity unresolved |  | 132
585 | 93 | GSO_18 | line_108642_21 | S_nCCTT1941 | 2.4826 | High | 7.2 | 2.8433 | 0.32934 | 2.514 | 2.2897 | 12.6666 | 10.3769 | line_108321_21 | ACLineSegment | Line | 2.8433 | 0.36071 | 2.4826 | 5 | 3 | 0 | 100 | 27 | 0.30755 | -79.8242 | 36.0149 | recloser_1790_21 -> line_108323_21 -> fuse_219_21 -> line_108321_21 -> line_108642_21 | GSO_18¦line_108642_21 | ACLineSegment | 240 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.4826 | [6 empty] | SubstationCapacityUnresolved | line_108321_21 | Substation capacity unresolved |  | 132
586 | 94 | GSO_18 | line_115810_21 | S_nCCTT6860 | 2.4826 | High | 7.2 | 2.8433 | 0.26661 | 2.5767 | 2.2897 | 12.6666 | 10.3769 | line_108321_21 | ACLineSegment | Line | 2.8433 | 0.36071 | 2.4826 | 6 | 4 | 0 | 100 | 27 | 0.30755 | -79.8252 | 36.0152 | recloser_1790_21 -> line_108323_21 -> fuse_219_21 -> line_108321_21 -> line_108642_21 -> line_115810_21 | GSO_18¦line_115810_21 | ACLineSegment | 240 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.4826 | [6 empty] | SubstationCapacityUnresolved | line_108321_21 | Substation capacity unresolved |  | 132
587 | 95 | GSO_18 | line_116051_21 | S_nCCTT2022 | 2.4826 | High | 7.2 | 2.8433 | 0.25093 | 2.5924 | 2.2897 | 12.6666 | 10.3769 | line_108321_21 | ACLineSegment | Line | 2.8433 | 0.36071 | 2.4826 | 7 | 5 | 0 | 100 | 27 | 0.30755 | -79.8252 | 36.0158 | recloser_1790_21 -> line_108323_21 -> fuse_219_21 -> line_108321_21 -> line_108642_21 -> line_115810_21 -> line_116051_21 | GSO_18¦line_116051_21 | ACLineSegment | 240 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.4826 | [6 empty] | SubstationCapacityUnresolved | line_108321_21 | Substation capacity unresolved |  | 132
588 | 96 | GSO_18 | line_109051_21 | S_nCCTT10976 | 2.4826 | High | 7.2 | 2.8433 | 0.19604 | 2.6473 | 2.2897 | 12.6666 | 10.3769 | line_108321_21 | ACLineSegment | Line | 2.8433 | 0.36071 | 2.4826 | 8 | 6 | 0 | 100 | 27 | 0.30755 | -79.8242 | 36.0162 | recloser_1790_21 -> line_108323_21 -> fuse_219_21 -> line_108321_21 -> line_108642_21 -> line_115810_21 -> line_116051_21 -> line_109051_21 | GSO_18¦line_109051_21 | ACLineSegment | 240 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.4826 | [6 empty] | SubstationCapacityUnresolved | line_108321_21 | Substation capacity unresolved |  | 132
589 | 97 | GSO_18 | line_106608_21 | S_nCCTT10226 | 2.4826 | High | 7.2 | 2.8433 | 0.05097 | 2.7924 | 2.2897 | 12.6666 | 10.3769 | line_108321_21 | ACLineSegment | Line | 2.8433 | 0.36071 | 2.4826 | 9 | 7 | 0 | 100 | 27 | 0.30755 | -79.8237 | 36.0161 | recloser_1790_21 -> line_108323_21 -> fuse_219_21 -> line_108321_21 -> line_108642_21 -> line_115810_21 -> line_116051_21 -> line_109051_21 -> line_106608_21 | GSO_18¦line_106608_21 | ACLineSegment | 240 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.4826 | [6 empty] | SubstationCapacityUnresolved | line_108321_21 | Substation capacity unresolved |  | 132
590 | 98 | GSO_18 | line_109050_21 | S_nCCTT11181 | 2.4826 | High | 7.2 | 2.8433 | 0.14115 | 2.7022 | 2.2897 | 12.6666 | 10.3769 | line_108321_21 | ACLineSegment | Line | 2.8433 | 0.36071 | 2.4826 | 9 | 7 | 0 | 100 | 27 | 0.30755 | -79.8239 | 36.0167 | recloser_1790_21 -> line_108323_21 -> fuse_219_21 -> line_108321_21 -> line_108642_21 -> line_115810_21 -> line_116051_21 -> line_109051_21 -> line_109050_21 | GSO_18¦line_109050_21 | ACLineSegment | 240 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.4826 | [6 empty] | SubstationCapacityUnresolved | line_108321_21 | Substation capacity unresolved |  | 132
591 | 99 | GSO_18 | line_109719_21 | S_nCCTT11187 | 2.4826 | High | 7.2 | 2.8433 | 0.12938 | 2.7139 | 2.2897 | 12.6666 | 10.3769 | line_108321_21 | ACLineSegment | Line | 2.8433 | 0.36071 | 2.4826 | 10 | 8 | 0 | 100 | 27 | 0.30755 | -79.824 | 36.0174 | recloser_1790_21 -> line_108323_21 -> fuse_219_21 -> line_108321_21 -> line_108642_21 -> line_115810_21 -> line_116051_21 -> line_109051_21 -> line_109050_21 -> line_109719_21 | GSO_18¦line_109719_21 | ACLineSegment | 240 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.4826 | [6 empty] | SubstationCapacityUnresolved | line_108321_21 | Substation capacity unresolved |  | 132
592 | 100 | GSO_18 | line_108954_21 | S_nCCTT10947 | 2.4826 | High | 7.2 | 2.8433 | 0.11762 | 2.7257 | 2.2897 | 12.6666 | 10.3769 | line_108321_21 | ACLineSegment | Line | 2.8433 | 0.36071 | 2.4826 | 11 | 9 | 0 | 100 | 27 | 0.30755 | -79.8237 | 36.0181 | recloser_1790_21 -> line_108323_21 -> fuse_219_21 -> line_108321_21 -> line_108642_21 -> line_115810_21 -> line_116051_21 -> line_109051_21 -> line_109050_21 -> line_109719_21 -> line_108954_21 | GSO_18¦line_108954_21 | ACLineSegment | 240 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.4826 | [6 empty] | SubstationCapacityUnresolved | line_108321_21 | Substation capacity unresolved |  | 132
593 | 101 | GSO_18 | line_108953_21 | S_nCCTT11179 | 2.4826 | High | 7.2 | 2.8433 | 0.0039208 | 2.8394 | 2.2897 | 12.6666 | 10.3769 | line_108321_21 | ACLineSegment | Line | 2.8433 | 0.36071 | 2.4826 | 12 | 10 | 0 | 100 | 27 | 0.30755 | -79.8241 | 36.0185 | recloser_1790_21 -> line_108323_21 -> fuse_219_21 -> line_108321_21 -> line_108642_21 -> line_115810_21 -> line_116051_21 -> line_109051_21 -> line_109050_21 -> line_109719_21 -> line_108954_21 -> line_108953_21 | GSO_18¦line_108953_21 | ACLineSegment | 240 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.4826 | [6 empty] | SubstationCapacityUnresolved | line_108321_21 | Substation capacity unresolved |  | 132
594 | 102 | GSO_18 | line_108955_21 | S_nCCTT9935 | 2.4826 | High | 7.2 | 2.8433 | 0.10586 | 2.7375 | 2.2897 | 12.6666 | 10.3769 | line_108321_21 | ACLineSegment | Line | 2.8433 | 0.36071 | 2.4826 | 12 | 10 | 0 | 100 | 27 | 0.30755 | -79.8231 | 36.0183 | recloser_1790_21 -> line_108323_21 -> fuse_219_21 -> line_108321_21 -> line_108642_21 -> line_115810_21 -> line_116051_21 -> line_109051_21 -> line_109050_21 -> line_109719_21 -> line_108954_21 -> line_108955_21 | GSO_18¦line_108955_21 | ACLineSegment | 240 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.4826 | [6 empty] | SubstationCapacityUnresolved | line_108321_21 | Substation capacity unresolved |  | 132
595 | 103 | GSO_18 | line_126719_21 | S_nCCTT6665 | 2.4826 | High | 7.2 | 2.8433 | 0.0078415 | 2.8355 | 2.2897 | 12.6666 | 10.3769 | line_108321_21 | ACLineSegment | Line | 2.8433 | 0.36071 | 2.4826 | 13 | 11 | 0 | 100 | 27 | 0.30755 | -79.8221 | 36.0187 | recloser_1790_21 -> line_108323_21 -> fuse_219_21 -> line_108321_21 -> line_108642_21 -> line_115810_21 -> line_116051_21 -> line_109051_21 -> line_109050_21 -> line_109719_21 -> line_108954_21 -> line_108955_21 -> line_126719_21 | GSO_18¦line_126719_21 | ACLineSegment | 240 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.4826 | [6 empty] | SubstationCapacityUnresolved | line_108321_21 | Substation capacity unresolved |  | 132
596 | 104 | GSO_18 | line_127045_21 | S_nCCTT6829 | 2.4826 | High | 7.2 | 2.8433 | 0.05097 | 2.7924 | 2.2897 | 12.6666 | 10.3769 | line_108321_21 | ACLineSegment | Line | 2.8433 | 0.36071 | 2.4826 | 13 | 11 | 0 | 100 | 27 | 0.30755 | -79.8222 | 36.018 | recloser_1790_21 -> line_108323_21 -> fuse_219_21 -> line_108321_21 -> line_108642_21 -> line_115810_21 -> line_116051_21 -> line_109051_21 -> line_109050_21 -> line_109719_21 -> line_108954_21 -> line_108955_21 -> line_127045_21 | GSO_18¦line_127045_21 | ACLineSegment | 240 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.4826 | [6 empty] | SubstationCapacityUnresolved | line_108321_21 | Substation capacity unresolved |  | 132
597 | 105 | GSO_18 | line_110282_21 | S_nCCTT12516 | 2.4395 | High | 7.2 | 2.8433 | 0.40384 | 2.4395 | 2.2897 | 12.6666 | 10.3769 | line_110282_21 | ACLineSegment | Line | 2.8433 | 0.40384 | 2.4395 | 13 | 11 | 0 | 100 | 27 | 0.30755 | -79.8285 | 36.013 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> fuse_377_21 -> line_110282_21 | GSO_18¦line_110282_21 | ACLineSegment | 240 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.4395 | [6 empty] | SubstationCapacityUnresolved | line_110282_21 | Substation capacity unresolved |  | 132
598 | 106 | GSO_18 | line_109986_21 | S_nCCTT11266 | 2.4395 | High | 7.2 | 2.8433 | 0.39992 | 2.4434 | 2.2897 | 12.6666 | 10.3769 | line_110282_21 | ACLineSegment | Line | 2.8433 | 0.40384 | 2.4395 | 14 | 12 | 0 | 100 | 27 | 0.30755 | -79.8285 | 36.0134 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> fuse_377_21 -> line_110282_21 -> line_109986_21 | GSO_18¦line_109986_21 | ACLineSegment | 240 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.4395 | [6 empty] | SubstationCapacityUnresolved | line_110282_21 | Substation capacity unresolved |  | 132
599 | 107 | GSO_18 | line_106073_21 | S_nCCTT10065 | 2.4395 | High | 7.2 | 2.8433 | 0.15683 | 2.6865 | 2.2897 | 12.6666 | 10.3769 | line_110282_21 | ACLineSegment | Line | 2.8433 | 0.40384 | 2.4395 | 15 | 13 | 0 | 100 | 27 | 0.30755 | -79.8279 | 36.0134 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> fuse_377_21 -> line_110282_21 -> line_109986_21 -> line_106073_21 | GSO_18¦line_106073_21 | ACLineSegment | 240 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.4395 | [6 empty] | SubstationCapacityUnresolved | line_110282_21 | Substation capacity unresolved |  | 132
600 | 108 | GSO_18 | line_109987_21 | S_nCCTT1954 | 2.4395 | High | 7.2 | 2.8433 | 0.066653 | 2.7767 | 2.2897 | 12.6666 | 10.3769 | line_110282_21 | ACLineSegment | Line | 2.8433 | 0.40384 | 2.4395 | 15 | 13 | 0 | 100 | 27 | 0.30755 | -79.829 | 36.0135 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> fuse_377_21 -> line_110282_21 -> line_109986_21 -> line_109987_21 | GSO_18¦line_109987_21 | ACLineSegment | 240 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.4395 | [6 empty] | SubstationCapacityUnresolved | line_110282_21 | Substation capacity unresolved |  | 132
601 | 109 | GSO_18 | line_109988_21 | S_nCCTT6867 | 2.4395 | High | 7.2 | 2.8433 | 0.16859 | 2.6747 | 2.2897 | 12.6666 | 10.3769 | line_110282_21 | ACLineSegment | Line | 2.8433 | 0.40384 | 2.4395 | 15 | 13 | 0 | 100 | 27 | 0.30755 | -79.8289 | 36.0139 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> fuse_377_21 -> line_110282_21 -> line_109986_21 -> line_109988_21 | GSO_18¦line_109988_21 | ACLineSegment | 240 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.4395 | [6 empty] | SubstationCapacityUnresolved | line_110282_21 | Substation capacity unresolved |  | 132
602 | 110 | GSO_18 | line_106074_21 | S_nCCTT1958 | 2.4395 | High | 7.2 | 2.8433 | 0.13723 | 2.7061 | 2.2897 | 12.6666 | 10.3769 | line_110282_21 | ACLineSegment | Line | 2.8433 | 0.40384 | 2.4395 | 16 | 14 | 0 | 100 | 27 | 0.30755 | -79.8273 | 36.0137 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> fuse_377_21 -> line_110282_21 -> line_109986_21 -> line_106073_21 -> line_106074_21 | GSO_18¦line_106074_21 | ACLineSegment | 240 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.4395 | [6 empty] | SubstationCapacityUnresolved | line_110282_21 | Substation capacity unresolved |  | 132
603 | 111 | GSO_18 | line_116237_21 | S_nCCTT2098 | 2.4395 | High | 7.2 | 2.8433 | 0.11762 | 2.7257 | 2.2897 | 12.6666 | 10.3769 | line_110282_21 | ACLineSegment | Line | 2.8433 | 0.40384 | 2.4395 | 16 | 14 | 0 | 100 | 27 | 0.30755 | -79.8291 | 36.0151 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> fuse_377_21 -> line_110282_21 -> line_109986_21 -> line_109988_21 -> line_116237_21 | GSO_18¦line_116237_21 | ACLineSegment | 240 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.4395 | [6 empty] | SubstationCapacityUnresolved | line_110282_21 | Substation capacity unresolved |  | 132
604 | 112 | GSO_18 | line_115874_21 | S_nCCTT7571 | 2.4395 | High | 7.2 | 2.8433 | 0.074494 | 2.7688 | 2.2897 | 12.6666 | 10.3769 | line_110282_21 | ACLineSegment | Line | 2.8433 | 0.40384 | 2.4395 | 17 | 15 | 0 | 100 | 27 | 0.30755 | -79.8273 | 36.0144 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> fuse_377_21 -> line_110282_21 -> line_109986_21 -> line_106073_21 -> line_106074_21 -> line_115874_21 | GSO_18¦line_115874_21 | ACLineSegment | 240 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.4395 | [6 empty] | SubstationCapacityUnresolved | line_110282_21 | Substation capacity unresolved |  | 132
605 | 113 | GSO_18 | line_106668_21 | S_nCCTT10243 | 2.4395 | High | 7.2 | 2.8433 | 0.047049 | 2.7963 | 2.2897 | 12.6666 | 10.3769 | line_110282_21 | ACLineSegment | Line | 2.8433 | 0.40384 | 2.4395 | 17 | 15 | 0 | 100 | 27 | 0.30755 | -79.829 | 36.0158 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> fuse_377_21 -> line_110282_21 -> line_109986_21 -> line_109988_21 -> line_116237_21 -> line_106668_21 | GSO_18¦line_106668_21 | ACLineSegment | 240 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.4395 | [6 empty] | SubstationCapacityUnresolved | line_110282_21 | Substation capacity unresolved |  | 132
606 | 114 | GSO_18 | line_106669_21 | S_nCCTT2115 | 2.4395 | High | 7.2 | 2.8433 | 0.039208 | 2.8041 | 2.2897 | 12.6666 | 10.3769 | line_110282_21 | ACLineSegment | Line | 2.8433 | 0.40384 | 2.4395 | 18 | 16 | 0 | 100 | 27 | 0.30755 | -79.8288 | 36.0163 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> fuse_377_21 -> line_110282_21 -> line_109986_21 -> line_109988_21 -> line_116237_21 -> line_106668_21 -> line_106669_21 | GSO_18¦line_106669_21 | ACLineSegment | 240 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.4395 | [6 empty] | SubstationCapacityUnresolved | line_110282_21 | Substation capacity unresolved |  | 132
607 | 115 | GSO_18 | line_127903_21 | S_nCCTT7335 | 2.4395 | High | 7.2 | 2.8433 | 0.070574 | 2.7728 | 2.2897 | 12.6666 | 10.3769 | line_110282_21 | ACLineSegment | Line | 2.8433 | 0.40384 | 2.4395 | 18 | 16 | 0 | 100 | 27 | 0.30755 | -79.8273 | 36.0151 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> line_110281_21 -> fuse_377_21 -> line_110282_21 -> line_109986_21 -> line_106073_21 -> line_106074_21 -> line_115874_21 -> line_127903_21 | GSO_18¦line_127903_21 | ACLineSegment | 240 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.4395 | [6 empty] | SubstationCapacityUnresolved | line_110282_21 | Substation capacity unresolved |  | 132
608 | 116 | GSO_18 | line_106667_21 | S_nCCTT10242 | 2.3964 | High | 7.2 | 2.8433 | 0.44697 | 2.3964 | 2.2897 | 12.6666 | 10.3769 | line_106667_21 | ACLineSegment | Line | 2.8433 | 0.44697 | 2.3964 | 12 | 10 | 0 | 100 | 27 | 0.30755 | -79.8285 | 36.0114 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> fuse_78_21 -> line_106667_21 | GSO_18¦line_106667_21 | ACLineSegment | 240 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.3964 | [6 empty] | SubstationCapacityUnresolved | line_106667_21 | Substation capacity unresolved |  | 132
609 | 117 | GSO_18 | line_106666_21 | S_nCCTT12041 | 2.3964 | High | 7.2 | 2.8433 | 0.42344 | 2.4199 | 2.2897 | 12.6666 | 10.3769 | line_106667_21 | ACLineSegment | Line | 2.8433 | 0.44697 | 2.3964 | 13 | 11 | 0 | 100 | 27 | 0.30755 | -79.8285 | 36.0107 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> fuse_78_21 -> line_106667_21 -> line_106666_21 | GSO_18¦line_106666_21 | ACLineSegment | 240 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.3964 | [6 empty] | SubstationCapacityUnresolved | line_106667_21 | Substation capacity unresolved |  | 132
610 | 118 | GSO_18 | line_106064_21 | S_nCCTT10062 | 2.3964 | High | 7.2 | 2.8433 | 0.0039208 | 2.8394 | 2.2897 | 12.6666 | 10.3769 | line_106667_21 | ACLineSegment | Line | 2.8433 | 0.44697 | 2.3964 | 14 | 12 | 0 | 100 | 27 | 0.30755 | -79.8283 | 36.0102 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> fuse_78_21 -> line_106667_21 -> line_106666_21 -> line_106064_21 | GSO_18¦line_106064_21 | ACLineSegment | 240 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.3964 | [6 empty] | SubstationCapacityUnresolved | line_106667_21 | Substation capacity unresolved |  | 132
611 | 119 | GSO_18 | line_112184_21 | S_nCCTT2028 | 2.3964 | High | 7.2 | 2.8433 | 0.40776 | 2.4356 | 2.2897 | 12.6666 | 10.3769 | line_106667_21 | ACLineSegment | Line | 2.8433 | 0.44697 | 2.3964 | 14 | 12 | 0 | 100 | 27 | 0.30755 | -79.8288 | 36.0102 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> fuse_78_21 -> line_106667_21 -> line_106666_21 -> line_112184_21 | GSO_18¦line_112184_21 | ACLineSegment | 240 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.3964 | [6 empty] | SubstationCapacityUnresolved | line_106667_21 | Substation capacity unresolved |  | 132
612 | 120 | GSO_18 | line_108380_21 | S_nCCTT10764 | 2.3964 | High | 7.2 | 2.8433 | 0.10978 | 2.7336 | 2.2897 | 12.6666 | 10.3769 | line_106667_21 | ACLineSegment | Line | 2.8433 | 0.44697 | 2.3964 | 15 | 13 | 0 | 100 | 27 | 0.30755 | -79.8295 | 36.0102 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> fuse_78_21 -> line_106667_21 -> line_106666_21 -> line_112184_21 -> line_108380_21 | GSO_18¦line_108380_21 | ACLineSegment | 240 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.3964 | [6 empty] | SubstationCapacityUnresolved | line_106667_21 | Substation capacity unresolved |  | 132
613 | 121 | GSO_18 | line_112251_21 | S_nCCTT12066 | 2.3964 | High | 7.2 | 2.8433 | 0.23525 | 2.6081 | 2.2897 | 12.6666 | 10.3769 | line_106667_21 | ACLineSegment | Line | 2.8433 | 0.44697 | 2.3964 | 15 | 13 | 0 | 100 | 27 | 0.30755 | -79.8289 | 36.0097 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> fuse_78_21 -> line_106667_21 -> line_106666_21 -> line_112184_21 -> line_112251_21 | GSO_18¦line_112251_21 | ACLineSegment | 240 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.3964 | [6 empty] | SubstationCapacityUnresolved | line_106667_21 | Substation capacity unresolved |  | 132
614 | 122 | GSO_18 | line_108379_21 | S_nCCTT12425 | 2.3964 | High | 7.2 | 2.8433 | 0.031366 | 2.812 | 2.2897 | 12.6666 | 10.3769 | line_106667_21 | ACLineSegment | Line | 2.8433 | 0.44697 | 2.3964 | 16 | 14 | 0 | 100 | 27 | 0.30755 | -79.8302 | 36.01 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> fuse_78_21 -> line_106667_21 -> line_106666_21 -> line_112184_21 -> line_108380_21 -> line_108379_21 | GSO_18¦line_108379_21 | ACLineSegment | 240 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.3964 | [6 empty] | SubstationCapacityUnresolved | line_106667_21 | Substation capacity unresolved |  | 132
615 | 123 | GSO_18 | line_108381_21 | S_nCCTT8101 | 2.3964 | High | 7.2 | 2.8433 | 0.070574 | 2.7728 | 2.2897 | 12.6666 | 10.3769 | line_106667_21 | ACLineSegment | Line | 2.8433 | 0.44697 | 2.3964 | 16 | 14 | 0 | 100 | 27 | 0.30755 | -79.8303 | 36.0105 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> fuse_78_21 -> line_106667_21 -> line_106666_21 -> line_112184_21 -> line_108380_21 -> line_108381_21 | GSO_18¦line_108381_21 | ACLineSegment | 240 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.3964 | [6 empty] | SubstationCapacityUnresolved | line_106667_21 | Substation capacity unresolved |  | 132
616 | 124 | GSO_18 | line_112250_21 | S_nCCTT12159 | 2.3964 | High | 7.2 | 2.8433 | 0.23132 | 2.612 | 2.2897 | 12.6666 | 10.3769 | line_106667_21 | ACLineSegment | Line | 2.8433 | 0.44697 | 2.3964 | 16 | 14 | 0 | 100 | 27 | 0.30755 | -79.828 | 36.0091 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> fuse_78_21 -> line_106667_21 -> line_106666_21 -> line_112184_21 -> line_112251_21 -> line_112250_21 | GSO_18¦line_112250_21 | ACLineSegment | 240 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.3964 | [6 empty] | SubstationCapacityUnresolved | line_106667_21 | Substation capacity unresolved |  | 132
617 | 125 | GSO_18 | line_111444_21 | S_nCCTT11763 | 2.3964 | High | 7.2 | 2.8433 | 0.023525 | 2.8198 | 2.2897 | 12.6666 | 10.3769 | line_106667_21 | ACLineSegment | Line | 2.8433 | 0.44697 | 2.3964 | 17 | 15 | 0 | 100 | 27 | 0.30755 | -79.8308 | 36.0093 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> fuse_78_21 -> line_106667_21 -> line_106666_21 -> line_112184_21 -> line_108380_21 -> line_108379_21 -> line_111444_21 | GSO_18¦line_111444_21 | ACLineSegment | 240 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.3964 | [6 empty] | SubstationCapacityUnresolved | line_106667_21 | Substation capacity unresolved |  | 132
618 | 126 | GSO_18 | line_112171_21 | S_nCCTT12036 | 2.3964 | High | 7.2 | 2.8433 | 0.2274 | 2.6159 | 2.2897 | 12.6666 | 10.3769 | line_106667_21 | ACLineSegment | Line | 2.8433 | 0.44697 | 2.3964 | 17 | 15 | 0 | 100 | 27 | 0.30755 | -79.8268 | 36.0091 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> fuse_78_21 -> line_106667_21 -> line_106666_21 -> line_112184_21 -> line_112251_21 -> line_112250_21 -> line_112171_21 | GSO_18¦line_112171_21 | ACLineSegment | 240 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.3964 | [6 empty] | SubstationCapacityUnresolved | line_106667_21 | Substation capacity unresolved |  | 132
619 | 127 | GSO_18 | line_112172_21 | S_nCCTT3890 | 2.3964 | High | 7.2 | 2.8433 | 0.22348 | 2.6199 | 2.2897 | 12.6666 | 10.3769 | line_106667_21 | ACLineSegment | Line | 2.8433 | 0.44697 | 2.3964 | 18 | 16 | 0 | 100 | 27 | 0.30755 | -79.8259 | 36.0091 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> fuse_78_21 -> line_106667_21 -> line_106666_21 -> line_112184_21 -> line_112251_21 -> line_112250_21 -> line_112171_21 -> line_112172_21 | GSO_18¦line_112172_21 | ACLineSegment | 240 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.3964 | [6 empty] | SubstationCapacityUnresolved | line_106667_21 | Substation capacity unresolved |  | 132
620 | 128 | GSO_18 | line_113593_21 | S_nCCTT12635 | 2.3964 | High | 7.2 | 2.8433 | 0.0039208 | 2.8394 | 2.2897 | 12.6666 | 10.3769 | line_106667_21 | ACLineSegment | Line | 2.8433 | 0.44697 | 2.3964 | 19 | 17 | 0 | 100 | 27 | 0.30755 | -79.8251 | 36.009 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> fuse_78_21 -> line_106667_21 -> line_106666_21 -> line_112184_21 -> line_112251_21 -> line_112250_21 -> line_112171_21 -> line_112172_21 -> line_113593_21 | GSO_18¦line_113593_21 | ACLineSegment | 240 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.3964 | [6 empty] | SubstationCapacityUnresolved | line_106667_21 | Substation capacity unresolved |  | 132
621 | 129 | GSO_18 | line_120790_21 | S_nCCTT9644 | 2.3964 | High | 7.2 | 2.8433 | 0.13723 | 2.7061 | 2.2897 | 12.6666 | 10.3769 | line_106667_21 | ACLineSegment | Line | 2.8433 | 0.44697 | 2.3964 | 19 | 17 | 0 | 100 | 27 | 0.30755 | -79.8243 | 36.0089 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> fuse_78_21 -> line_106667_21 -> line_106666_21 -> line_112184_21 -> line_112251_21 -> line_112250_21 -> line_112171_21 -> line_112172_21 -> line_120790_21 | GSO_18¦line_120790_21 | ACLineSegment | 240 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.3964 | [6 empty] | SubstationCapacityUnresolved | line_106667_21 | Substation capacity unresolved |  | 132
622 | 130 | GSO_18 | line_122817_21 | S_nCCTT4815 | 2.3964 | High | 7.2 | 2.8433 | 0.11762 | 2.7257 | 2.2897 | 12.6666 | 10.3769 | line_106667_21 | ACLineSegment | Line | 2.8433 | 0.44697 | 2.3964 | 20 | 18 | 0 | 100 | 27 | 0.30755 | -79.8234 | 36.0089 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> fuse_78_21 -> line_106667_21 -> line_106666_21 -> line_112184_21 -> line_112251_21 -> line_112250_21 -> line_112171_21 -> line_112172_21 -> line_120790_21 -> line_122817_21 | GSO_18¦line_122817_21 | ACLineSegment | 240 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.3964 | [6 empty] | SubstationCapacityUnresolved | line_106667_21 | Substation capacity unresolved |  | 132
623 | 131 | GSO_18 | line_122816_21 | S_nCCTT4817 | 2.3964 | High | 7.2 | 2.8433 | 0.031366 | 2.812 | 2.2897 | 12.6666 | 10.3769 | line_106667_21 | ACLineSegment | Line | 2.8433 | 0.44697 | 2.3964 | 21 | 19 | 0 | 100 | 27 | 0.30755 | -79.8232 | 36.0089 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> fuse_78_21 -> line_106667_21 -> line_106666_21 -> line_112184_21 -> line_112251_21 -> line_112250_21 -> line_112171_21 -> line_112172_21 -> line_120790_21 -> line_122817_21 -> line_122816_21 | GSO_18¦line_122816_21 | ACLineSegment | 240 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.3964 | [6 empty] | SubstationCapacityUnresolved | line_106667_21 | Substation capacity unresolved |  | 132
624 | 132 | GSO_18 | line_122824_21 | S_nCCTT4822 | 2.3964 | High | 7.2 | 2.8433 | 0.0078415 | 2.8355 | 2.2897 | 12.6666 | 10.3769 | line_106667_21 | ACLineSegment | Line | 2.8433 | 0.44697 | 2.3964 | 22 | 20 | 0 | 100 | 27 | 0.30755 | -79.8228 | 36.0088 | recloser_1790_21 -> line_108323_21 -> line_108322_21 -> line_122867_21 -> line_129223_21 -> line_107810_21 -> line_107809_21 -> line_110795_21 -> line_110794_21 -> line_111728_21 -> fuse_78_21 -> line_106667_21 -> line_106666_21 -> line_112184_21 -> line_112251_21 -> line_112250_21 -> line_112171_21 -> line_112172_21 -> line_120790_21 -> line_122817_21 -> line_122816_21 -> line_122824_21 | GSO_18¦line_122824_21 | ACLineSegment | 240 | 13333.3 | Meter | br_025_21 | hvmv_4_21 | 13333.3 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.3964 | [6 empty] | SubstationCapacityUnresolved | line_106667_21 | Substation capacity unresolved |  | 132
451 | 1 | GSO_55 | line_128388_21 | S_nCCTT7620 | 9.2315 | High | 12.47 | 12.3112 | 0.26848 | 12.0428 | 0.26848 | 9.5 | 9.2315 | br_062_21 | CircuitBreaker | Breaker | 9.5 | 0.26848 | 9.2315 | 2 | 1 | 0 | 100 | 19.9167 | 0.22687 | -79.849 | 36.0126 | recloser_1928_21 -> line_128388_21 | GSO_55¦line_128388_21 | ACLineSegment | 600 | 10000 | Meter | br_062_21 | hvmv_10_21 | 10000.0 | 3 | 3 | TRUE | 3.0835 | 4.6008 | 6.1336 | 2024-01-21 04:00 | 6.1575 | 0.99612 | 1.0039 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.2315 | [6 empty] | SubstationCapacityUnresolved | br_062_21 | Substation capacity unresolved |  | 11
498 | 2 | GSO_55 | line_112967_21 | S_nCCTT7620_B_S_nCCTT12361 | 7.1047 | High | 7.2 | 7.1083 | 0.0036778 | 7.1047 | 0.26848 | 9.5 | 9.2315 | line_112967_21 | ACLineSegment | Line | 7.1083 | 0.0036778 | 7.1047 | 3 | 2 | 0 | 100 | 19.9167 | 0.22687 | -79.8493 | 36.0124 | recloser_1928_21 -> line_128388_21 -> line_112967_21 | GSO_55¦line_112967_21 | ACLineSegment | 600 | 10000 | Meter | br_062_21 | hvmv_10_21 | 10000.0 | 3 | 3 | TRUE | 3.0835 | 4.6008 | 6.1336 | 2024-01-21 04:00 | 6.1575 | 0.99612 | 1.0039 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 7.1047 | [6 empty] | SubstationCapacityUnresolved | line_112967_21 | Substation capacity unresolved |  | 11
522 | 3 | GSO_55 | line_112839_21 | S_nCCTT12310 | 6.9244 | High | 7.2 | 7.1083 | 0.18389 | 6.9244 | 0.26848 | 9.5 | 9.2315 | line_112839_21 | ACLineSegment | Line | 7.1083 | 0.18389 | 6.9244 | 4 | 2 | 0 | 100 | 19.9167 | 0.22687 | -79.8494 | 36.0121 | recloser_1928_21 -> line_128388_21 -> switch_4208_21 -> line_112839_21 | GSO_55¦line_112839_21 | ACLineSegment | 600 | 10000 | Meter | br_062_21 | hvmv_10_21 | 10000.0 | 3 | 3 | TRUE | 3.0835 | 4.6008 | 6.1336 | 2024-01-21 04:00 | 6.1575 | 0.99612 | 1.0039 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 6.9244 | [6 empty] | SubstationCapacityUnresolved | line_112839_21 | Substation capacity unresolved |  | 11
523 | 4 | GSO_55 | line_112837_21 | S_nCCTT12310_B_S_nCCTT12615 | 6.9244 | High | 7.2 | 7.1083 | 0.0073555 | 7.101 | 0.26848 | 9.5 | 9.2315 | line_112839_21 | ACLineSegment | Line | 7.1083 | 0.18389 | 6.9244 | 5 | 3 | 0 | 100 | 19.9167 | 0.22687 | -79.8497 | 36.0113 | recloser_1928_21 -> line_128388_21 -> switch_4208_21 -> line_112839_21 -> line_112837_21 | GSO_55¦line_112837_21 | ACLineSegment | 600 | 10000 | Meter | br_062_21 | hvmv_10_21 | 10000.0 | 3 | 3 | TRUE | 3.0835 | 4.6008 | 6.1336 | 2024-01-21 04:00 | 6.1575 | 0.99612 | 1.0039 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 6.9244 | [6 empty] | SubstationCapacityUnresolved | line_112839_21 | Substation capacity unresolved |  | 11
524 | 5 | GSO_55 | line_112838_21 | S_nCCTT1990 | 6.9244 | High | 7.2 | 7.1083 | 0.16918 | 6.9392 | 0.26848 | 9.5 | 9.2315 | line_112839_21 | ACLineSegment | Line | 7.1083 | 0.18389 | 6.9244 | 6 | 3 | 0 | 100 | 19.9167 | 0.22687 | -79.8501 | 36.0122 | recloser_1928_21 -> line_128388_21 -> switch_4208_21 -> line_112839_21 -> switch_4206_21 -> line_112838_21 | GSO_55¦line_112838_21 | ACLineSegment | 600 | 10000 | Meter | br_062_21 | hvmv_10_21 | 10000.0 | 3 | 3 | TRUE | 3.0835 | 4.6008 | 6.1336 | 2024-01-21 04:00 | 6.1575 | 0.99612 | 1.0039 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 6.9244 | [6 empty] | SubstationCapacityUnresolved | line_112839_21 | Substation capacity unresolved |  | 11
525 | 6 | GSO_55 | line_109004_21 | S_nCCTT1990_B_S_nCCTT10962 | 6.9244 | High | 7.2 | 7.1083 | 0.084588 | 7.0237 | 0.26848 | 9.5 | 9.2315 | line_112839_21 | ACLineSegment | Line | 7.1083 | 0.18389 | 6.9244 | 7 | 4 | 0 | 100 | 19.9167 | 0.22687 | -79.8508 | 36.0122 | recloser_1928_21 -> line_128388_21 -> switch_4208_21 -> line_112839_21 -> switch_4206_21 -> line_112838_21 -> line_109004_21 | GSO_55¦line_109004_21 | ACLineSegment | 600 | 10000 | Meter | br_062_21 | hvmv_10_21 | 10000.0 | 3 | 3 | TRUE | 3.0835 | 4.6008 | 6.1336 | 2024-01-21 04:00 | 6.1575 | 0.99612 | 1.0039 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 6.9244 | [6 empty] | SubstationCapacityUnresolved | line_112839_21 | Substation capacity unresolved |  | 11
526 | 7 | GSO_55 | line_111366_21 | S_nCCTT12615_B_S_nCCTT11736 | 6.9244 | High | 7.2 | 7.1083 | 0.0036778 | 7.1047 | 0.26848 | 9.5 | 9.2315 | line_112839_21 | ACLineSegment | Line | 7.1083 | 0.18389 | 6.9244 | 7 | 4 | 0 | 100 | 19.9167 | 0.22687 | -79.8493 | 36.0106 | recloser_1928_21 -> line_128388_21 -> switch_4208_21 -> line_112839_21 -> line_112837_21 -> switch_4205_21 -> line_111366_21 | GSO_55¦line_111366_21 | ACLineSegment | 600 | 10000 | Meter | br_062_21 | hvmv_10_21 | 10000.0 | 3 | 3 | TRUE | 3.0835 | 4.6008 | 6.1336 | 2024-01-21 04:00 | 6.1575 | 0.99612 | 1.0039 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 6.9244 | [6 empty] | SubstationCapacityUnresolved | line_112839_21 | Substation capacity unresolved |  | 11
527 | 8 | GSO_55 | line_109005_21 | S_nCCTT10962_B_S_nCCTT6628 | 6.9244 | High | 7.2 | 7.1083 | 0.077233 | 7.0311 | 0.26848 | 9.5 | 9.2315 | line_112839_21 | ACLineSegment | Line | 7.1083 | 0.18389 | 6.9244 | 9 | 5 | 0 | 100 | 19.9167 | 0.22687 | -79.8511 | 36.0123 | recloser_1928_21 -> line_128388_21 -> switch_4208_21 -> line_112839_21 -> switch_4206_21 -> line_112838_21 -> line_109004_21 -> switch_2996_21 -> line_109005_21 | GSO_55¦line_109005_21 | ACLineSegment | 600 | 10000 | Meter | br_062_21 | hvmv_10_21 | 10000.0 | 3 | 3 | TRUE | 3.0835 | 4.6008 | 6.1336 | 2024-01-21 04:00 | 6.1575 | 0.99612 | 1.0039 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 6.9244 | [6 empty] | SubstationCapacityUnresolved | line_112839_21 | Substation capacity unresolved |  | 11
528 | 9 | GSO_55 | line_113552_21 | S_nCCTT12614 | 6.9244 | High | 7.2 | 7.1083 | 0.0036778 | 7.1047 | 0.26848 | 9.5 | 9.2315 | line_112839_21 | ACLineSegment | Line | 7.1083 | 0.18389 | 6.9244 | 12 | 6 | 0 | 100 | 19.9167 | 0.22687 | -79.851 | 36.0125 | recloser_1928_21 -> line_128388_21 -> switch_4208_21 -> line_112839_21 -> switch_4206_21 -> line_112838_21 -> line_109004_21 -> switch_2996_21 -> line_109005_21 -> switch_2998_21 -> switch_4459_21 -> line_113552_21 | GSO_55¦line_113552_21 | ACLineSegment | 600 | 10000 | Meter | br_062_21 | hvmv_10_21 | 10000.0 | 3 | 3 | TRUE | 3.0835 | 4.6008 | 6.1336 | 2024-01-21 04:00 | 6.1575 | 0.99612 | 1.0039 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 6.9244 | [6 empty] | SubstationCapacityUnresolved | line_112839_21 | Substation capacity unresolved |  | 11
529 | 10 | GSO_55 | line_126626_21 | S_nCCTT9948 | 6.9244 | High | 7.2 | 7.1083 | 0.055166 | 7.0532 | 0.26848 | 9.5 | 9.2315 | line_112839_21 | ACLineSegment | Line | 7.1083 | 0.18389 | 6.9244 | 12 | 6 | 0 | 100 | 19.9167 | 0.22687 | -79.8515 | 36.0125 | recloser_1928_21 -> line_128388_21 -> switch_4208_21 -> line_112839_21 -> switch_4206_21 -> line_112838_21 -> line_109004_21 -> switch_2996_21 -> line_109005_21 -> switch_2998_21 -> switch_7181_21 -> line_126626_21 | GSO_55¦line_126626_21 | ACLineSegment | 600 | 10000 | Meter | br_062_21 | hvmv_10_21 | 10000.0 | 3 | 3 | TRUE | 3.0835 | 4.6008 | 6.1336 | 2024-01-21 04:00 | 6.1575 | 0.99612 | 1.0039 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 6.9244 | [6 empty] | SubstationCapacityUnresolved | line_112839_21 | Substation capacity unresolved |  | 11
530 | 11 | GSO_55 | line_131955_21 | S_nCCTT9948_B_S_nCCTT9624 | 6.9244 | High | 7.2 | 7.1083 | 0.040455 | 7.0679 | 0.26848 | 9.5 | 9.2315 | line_112839_21 | ACLineSegment | Line | 7.1083 | 0.18389 | 6.9244 | 13 | 7 | 0 | 100 | 19.9167 | 0.22687 | -79.8519 | 36.0124 | recloser_1928_21 -> line_128388_21 -> switch_4208_21 -> line_112839_21 -> switch_4206_21 -> line_112838_21 -> line_109004_21 -> switch_2996_21 -> line_109005_21 -> switch_2998_21 -> switch_7181_21 -> line_126626_21 -> line_131955_21 | GSO_55¦line_131955_21 | ACLineSegment | 600 | 10000 | Meter | br_062_21 | hvmv_10_21 | 10000.0 | 3 | 3 | TRUE | 3.0835 | 4.6008 | 6.1336 | 2024-01-21 04:00 | 6.1575 | 0.99612 | 1.0039 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 6.9244 | [6 empty] | SubstationCapacityUnresolved | line_112839_21 | Substation capacity unresolved |  | 11
396 | 1 | GSO_73 | line_129349_21 | S_nCCTT8151 | 9.4021 | High | 12.47 | 12.3112 | 0.097896 | 12.2133 | 0.097896 | 9.5 | 9.4021 | br_073_21 | CircuitBreaker | Breaker | 9.5 | 0.097896 | 9.4021 | 2 | 1 | 0 | 100 | 1.6667 | 0.018985 | -79.7704 | 36.0826 | recloser_1941_21 -> line_129349_21 | GSO_73¦line_129349_21 | ACLineSegment | 600 | 10000 | Meter | br_073_21 | hvmv_12_21 | 10000.0 | 5 | 5 | TRUE | 4.926 | 7.0139 | 9.0553 | 2024-01-18 04:00 | 9.2034 | 0.98391 | 1.0164 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.4021 | [6 empty] | SubstationCapacityUnresolved | br_073_21 | Substation capacity unresolved |  | 14
397 | 2 | GSO_73 | line_129085_21 | S_nCCTT8004 | 9.4021 | High | 12.47 | 12.3112 | 0.08062 | 12.2306 | 0.097896 | 9.5 | 9.4021 | br_073_21 | CircuitBreaker | Breaker | 9.5 | 0.097896 | 9.4021 | 4 | 2 | 0 | 100 | 1.6667 | 0.018985 | -79.7699 | 36.0831 | recloser_1941_21 -> line_129349_21 -> switch_7535_21 -> line_129085_21 | GSO_73¦line_129085_21 | ACLineSegment | 600 | 10000 | Meter | br_073_21 | hvmv_12_21 | 10000.0 | 5 | 5 | TRUE | 4.926 | 7.0139 | 9.0553 | 2024-01-18 04:00 | 9.2034 | 0.98391 | 1.0164 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.4021 | [6 empty] | SubstationCapacityUnresolved | br_073_21 | Substation capacity unresolved |  | 14
398 | 3 | GSO_73 | line_109902_21 | S_nCCTT8004_B_S_nCCTT11236 | 9.4021 | High | 12.47 | 12.3112 | 0.074862 | 12.2364 | 0.097896 | 9.5 | 9.4021 | br_073_21 | CircuitBreaker | Breaker | 9.5 | 0.097896 | 9.4021 | 5 | 3 | 0 | 100 | 1.6667 | 0.018985 | -79.7699 | 36.0838 | recloser_1941_21 -> line_129349_21 -> switch_7535_21 -> line_129085_21 -> line_109902_21 | GSO_73¦line_109902_21 | ACLineSegment | 600 | 10000 | Meter | br_073_21 | hvmv_12_21 | 10000.0 | 5 | 5 | TRUE | 4.926 | 7.0139 | 9.0553 | 2024-01-18 04:00 | 9.2034 | 0.98391 | 1.0164 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.4021 | [6 empty] | SubstationCapacityUnresolved | br_073_21 | Substation capacity unresolved |  | 14
399 | 4 | GSO_73 | line_109903_21 | S_nCCTT8162 | 9.4021 | High | 12.47 | 12.3112 | 0.069103 | 12.2421 | 0.097896 | 9.5 | 9.4021 | br_073_21 | CircuitBreaker | Breaker | 9.5 | 0.097896 | 9.4021 | 8 | 4 | 0 | 100 | 1.6667 | 0.018985 | -79.7696 | 36.0841 | recloser_1941_21 -> line_129349_21 -> switch_7535_21 -> line_129085_21 -> line_109902_21 -> switch_3259_21 -> switch_3260_21 -> line_109903_21 | GSO_73¦line_109903_21 | ACLineSegment | 600 | 10000 | Meter | br_073_21 | hvmv_12_21 | 10000.0 | 5 | 5 | TRUE | 4.926 | 7.0139 | 9.0553 | 2024-01-18 04:00 | 9.2034 | 0.98391 | 1.0164 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.4021 | [6 empty] | SubstationCapacityUnresolved | br_073_21 | Substation capacity unresolved |  | 14
400 | 5 | GSO_73 | line_129368_21 | S_nCCTT8172 | 9.4021 | High | 12.47 | 12.3112 | 0.063344 | 12.2479 | 0.097896 | 9.5 | 9.4021 | br_073_21 | CircuitBreaker | Breaker | 9.5 | 0.097896 | 9.4021 | 10 | 5 | 0 | 100 | 1.6667 | 0.018985 | -79.7692 | 36.0841 | recloser_1941_21 -> line_129349_21 -> switch_7535_21 -> line_129085_21 -> line_109902_21 -> switch_3259_21 -> switch_3260_21 -> line_109903_21 -> switch_7555_21 -> line_129368_21 | GSO_73¦line_129368_21 | ACLineSegment | 600 | 10000 | Meter | br_073_21 | hvmv_12_21 | 10000.0 | 5 | 5 | TRUE | 4.926 | 7.0139 | 9.0553 | 2024-01-18 04:00 | 9.2034 | 0.98391 | 1.0164 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.4021 | [6 empty] | SubstationCapacityUnresolved | br_073_21 | Substation capacity unresolved |  | 14
401 | 6 | GSO_73 | line_117011_21 | S_nCCTT8172_B_S_nCCTT2356 | 9.4021 | High | 12.47 | 12.3112 | 0.051827 | 12.2594 | 0.097896 | 9.5 | 9.4021 | br_073_21 | CircuitBreaker | Breaker | 9.5 | 0.097896 | 9.4021 | 11 | 6 | 0 | 100 | 1.6667 | 0.018985 | -79.7688 | 36.0841 | recloser_1941_21 -> line_129349_21 -> switch_7535_21 -> line_129085_21 -> line_109902_21 -> switch_3259_21 -> switch_3260_21 -> line_109903_21 -> switch_7555_21 -> line_129368_21 -> line_117011_21 | GSO_73¦line_117011_21 | ACLineSegment | 600 | 10000 | Meter | br_073_21 | hvmv_12_21 | 10000.0 | 5 | 5 | TRUE | 4.926 | 7.0139 | 9.0553 | 2024-01-18 04:00 | 9.2034 | 0.98391 | 1.0164 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.4021 | [6 empty] | SubstationCapacityUnresolved | br_073_21 | Substation capacity unresolved |  | 14
402 | 7 | GSO_73 | line_117010_21 | S_nCCTT3893 | 9.4021 | High | 12.47 | 13.5424 | 0.04031 | 13.5021 | 0.097896 | 9.5 | 9.4021 | br_073_21 | CircuitBreaker | Breaker | 9.5 | 0.097896 | 9.4021 | 13 | 7 | 0 | 100 | 1.6667 | 0.018985 | -79.7685 | 36.0842 | recloser_1941_21 -> line_129349_21 -> switch_7535_21 -> line_129085_21 -> line_109902_21 -> switch_3259_21 -> switch_3260_21 -> line_109903_21 -> switch_7555_21 -> line_129368_21 -> line_117011_21 -> switch_5174_21 -> line_117010_21 | GSO_73¦line_117010_21 | ACLineSegment | 660 | 10000 | Meter | br_073_21 | hvmv_12_21 | 10000.0 | 5 | 5 | TRUE | 4.926 | 7.0139 | 9.0553 | 2024-01-18 04:00 | 9.2034 | 0.98391 | 1.0164 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.4021 | [6 empty] | SubstationCapacityUnresolved | br_073_21 | Substation capacity unresolved |  | 14
403 | 8 | GSO_73 | line_120795_21 | S_nCCTT516 | 9.4021 | High | 12.47 | 13.5424 | 0.023034 | 13.5193 | 0.097896 | 9.5 | 9.4021 | br_073_21 | CircuitBreaker | Breaker | 9.5 | 0.097896 | 9.4021 | 14 | 8 | 0 | 100 | 1.6667 | 0.018985 | -79.7682 | 36.0843 | recloser_1941_21 -> line_129349_21 -> switch_7535_21 -> line_129085_21 -> line_109902_21 -> switch_3259_21 -> switch_3260_21 -> line_109903_21 -> switch_7555_21 -> line_129368_21 -> line_117011_21 -> switch_5174_21 -> line_117010_21 -> line_120795_21 | GSO_73¦line_120795_21 | ACLineSegment | 660 | 10000 | Meter | br_073_21 | hvmv_12_21 | 10000.0 | 5 | 5 | TRUE | 4.926 | 7.0139 | 9.0553 | 2024-01-18 04:00 | 9.2034 | 0.98391 | 1.0164 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.4021 | [6 empty] | SubstationCapacityUnresolved | br_073_21 | Substation capacity unresolved |  | 14
404 | 9 | GSO_73 | line_110416_21 | S_nCCTT11408 | 9.4021 | High | 12.47 | 13.5424 | 0.0057586 | 13.5366 | 0.097896 | 9.5 | 9.4021 | br_073_21 | CircuitBreaker | Breaker | 9.5 | 0.097896 | 9.4021 | 14 | 8 | 0 | 100 | 1.6667 | 0.018985 | -79.7684 | 36.0842 | recloser_1941_21 -> line_129349_21 -> switch_7535_21 -> line_129085_21 -> line_109902_21 -> switch_3259_21 -> switch_3260_21 -> line_109903_21 -> switch_7555_21 -> line_129368_21 -> line_117011_21 -> switch_5174_21 -> line_117010_21 -> line_110416_21 | GSO_73¦line_110416_21 | ACLineSegment | 660 | 10000 | Meter | br_073_21 | hvmv_12_21 | 10000.0 | 5 | 5 | TRUE | 4.926 | 7.0139 | 9.0553 | 2024-01-18 04:00 | 9.2034 | 0.98391 | 1.0164 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.4021 | [6 empty] | SubstationCapacityUnresolved | br_073_21 | Substation capacity unresolved |  | 14
405 | 10 | GSO_73 | line_107924_21 | S_nCCTT10628 | 9.4021 | High | 12.47 | 13.5424 | 0.0057586 | 13.5366 | 0.097896 | 9.5 | 9.4021 | br_073_21 | CircuitBreaker | Breaker | 9.5 | 0.097896 | 9.4021 | 15 | 9 | 0 | 100 | 1.6667 | 0.018985 | -79.768 | 36.0843 | recloser_1941_21 -> line_129349_21 -> switch_7535_21 -> line_129085_21 -> line_109902_21 -> switch_3259_21 -> switch_3260_21 -> line_109903_21 -> switch_7555_21 -> line_129368_21 -> line_117011_21 -> switch_5174_21 -> line_117010_21 -> line_120795_21 -> line_107924_21 | GSO_73¦line_107924_21 | ACLineSegment | 660 | 10000 | Meter | br_073_21 | hvmv_12_21 | 10000.0 | 5 | 5 | TRUE | 4.926 | 7.0139 | 9.0553 | 2024-01-18 04:00 | 9.2034 | 0.98391 | 1.0164 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 9.4021 | [6 empty] | SubstationCapacityUnresolved | br_073_21 | Substation capacity unresolved |  | 14
502 | 11 | GSO_73 | line_117012_21 | S_nCCTT9896 | 7.1026 | High | 7.2 | 7.1083 | 0.0057586 | 7.1026 | 0.097896 | 9.5 | 9.4021 | line_117012_21 | ACLineSegment | Line | 7.1083 | 0.0057586 | 7.1026 | 14 | 7 | 0 | 100 | 1.6667 | 0.018985 | -79.7684 | 36.0836 | recloser_1941_21 -> line_129349_21 -> switch_7535_21 -> line_129085_21 -> line_109902_21 -> switch_3259_21 -> switch_3260_21 -> line_109903_21 -> switch_7555_21 -> line_129368_21 -> line_117011_21 -> switch_5174_21 -> switch_5175_21 -> line_117012_21 | GSO_73¦line_117012_21 | ACLineSegment | 600 | 10000 | Meter | br_073_21 | hvmv_12_21 | 10000.0 | 5 | 5 | TRUE | 4.926 | 7.0139 | 9.0553 | 2024-01-18 04:00 | 9.2034 | 0.98391 | 1.0164 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 7.1026 | [6 empty] | SubstationCapacityUnresolved | line_117012_21 | Substation capacity unresolved |  | 14
506 | 12 | GSO_73 | line_123517_21 | S_nCCTT5093 | 7.0968 | High | 7.2 | 7.1083 | 0.011517 | 7.0968 | 0.097896 | 9.5 | 9.4021 | line_123517_21 | ACLineSegment | Line | 7.1083 | 0.011517 | 7.0968 | 4 | 2 | 0 | 100 | 1.6667 | 0.018985 | -79.7694 | 36.0826 | recloser_1941_21 -> line_129349_21 -> fuse_1407_21 -> line_123517_21 | GSO_73¦line_123517_21 | ACLineSegment | 600 | 10000 | Meter | br_073_21 | hvmv_12_21 | 10000.0 | 5 | 5 | TRUE | 4.926 | 7.0139 | 9.0553 | 2024-01-18 04:00 | 9.2034 | 0.98391 | 1.0164 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 7.0968 | [6 empty] | SubstationCapacityUnresolved | line_123517_21 | Substation capacity unresolved |  | 14
542 | 13 | GSO_73 | line_123518_21 | S_nCCTT9825 | 2.8376 | High | 7.2 | 2.8433 | 0.0057586 | 2.8376 | 0.097896 | 9.5 | 9.4021 | line_123518_21 | ACLineSegment | Line | 2.8433 | 0.0057586 | 2.8376 | 5 | 3 | 0 | 100 | 1.6667 | 0.018985 | -79.7691 | 36.0815 | recloser_1941_21 -> line_129349_21 -> fuse_1407_21 -> line_123517_21 -> line_123518_21 | GSO_73¦line_123518_21 | ACLineSegment | 240 | 10000 | Meter | br_073_21 | hvmv_12_21 | 10000.0 | 5 | 5 | TRUE | 4.926 | 7.0139 | 9.0553 | 2024-01-18 04:00 | 9.2034 | 0.98391 | 1.0164 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.8376 | [6 empty] | SubstationCapacityUnresolved | line_123518_21 | Substation capacity unresolved |  | 14
550 | 14 | GSO_73 | line_123681_21 | S_nCCTT7307 | 2.8318 | High | 7.2 | 2.8433 | 0.011517 | 2.8318 | 0.097896 | 9.5 | 9.4021 | line_123681_21 | ACLineSegment | Line | 2.8433 | 0.011517 | 2.8318 | 16 | 9 | 0 | 100 | 1.6667 | 0.018985 | -79.7676 | 36.0843 | recloser_1941_21 -> line_129349_21 -> switch_7535_21 -> line_129085_21 -> line_109902_21 -> switch_3259_21 -> switch_3260_21 -> line_109903_21 -> switch_7555_21 -> line_129368_21 -> line_117011_21 -> switch_5174_21 -> line_117010_21 -> line_120795_21 -> fuse_1420_21 -> line_123681_21 | GSO_73¦line_123681_21 | ACLineSegment | 240 | 10000 | Meter | br_073_21 | hvmv_12_21 | 10000.0 | 5 | 5 | TRUE | 4.926 | 7.0139 | 9.0553 | 2024-01-18 04:00 | 9.2034 | 0.98391 | 1.0164 | 99.9431 | High |  | Unresolved | No recognized explicit capacity value | [13 empty] | 2.8318 | [6 empty] | SubstationCapacityUnresolved | line_123681_21 | Substation capacity unresolved |  | 14

## Global_Top_Locations
GlobalRank | RankWithinFeeder | GridID | CandidateLineID | CandidateNode | EstimatedBaseHostingMW | CandidateConfidence | NominalVoltageKV | CandidateLineCapacityMW | CandidateLineExistingLoadMW | CandidateLineResidualMW | FeederPeakMW | BreakerCapacityMW | BreakerResidualMW | LimitingElementID | LimitingElementType | LimitingElementClass | LimitingElementCapacityMW | LimitingElementExistingLoadMW | LimitingElementResidualMW | ElectricalDistanceHops | PathLineCount | PathTransformerCount | LoadPointReachabilityPct | HoursWithin10PctOfPeak | PctTimeWithin10PctOfPeak | CentroidX | CentroidY | PathElementIDs | CandidateKey | CandidateLineType | CandidateLineRatingA | BreakerRatingKVA_x | LoadAllocationMethod | BreakerID | SubstationID | BreakerRatingKVA_y | Substation_ExpectedFeederCount | Substation_LoadedFeederCount | Substation_AllMappedFeedersLoaded | Substation_AverageLoadMW | Substation_P95LoadMW | Substation_PeakLoadMW | Substation_PeakTimestampUTC | Substation_SumIndividualFeederPeaksMW | Substation_CoincidenceFactor | Substation_DiversityFactor | Substation_DataCoveragePct | Substation_LoadProfileConfidence | Substation_AvailableCapacityMW | Substation_CapacityResolutionStatus | Substation_CapacitySource | Substation_CapacitySourceKey | Substation_CapacitySourceUnit | Substation_Preferred80PctLimitMW | Substation_Preferred90PctLimitMW | Substation_Hard100PctLimitMW | Substation_Preferred80PctHeadroomMW | Substation_Preferred90PctHeadroomMW | Substation_Hard100PctHeadroomMW | Substation_PeakSubstationUtilizationPct | Substation_OverloadLimitPct | Substation_OverloadDurationHours | Substation_OverloadLimitMW | Substation_OverloadHeadroomMW | FeederPathHostingMW | SubstationHardHeadroomMW | SubstationPreferred90HeadroomMW | SubstationPreferred80HeadroomMW | FinalBaseHostingMW | Preferred90HostingMW | Preferred80HostingMW | FinalConstraintClass | FinalConstraintID | FinalRankingStatus | FinalRank | CandidateCountOnSharedSubstation

## Best_By_Feeder
GlobalRank | RankWithinFeeder | GridID | CandidateLineID | CandidateNode | EstimatedBaseHostingMW | CandidateConfidence | NominalVoltageKV | CandidateLineCapacityMW | CandidateLineExistingLoadMW | CandidateLineResidualMW | FeederPeakMW | BreakerCapacityMW | BreakerResidualMW | LimitingElementID | LimitingElementType | LimitingElementClass | LimitingElementCapacityMW | LimitingElementExistingLoadMW | LimitingElementResidualMW | ElectricalDistanceHops | PathLineCount | PathTransformerCount | LoadPointReachabilityPct | HoursWithin10PctOfPeak | PctTimeWithin10PctOfPeak | CentroidX | CentroidY | PathElementIDs | CandidateKey | CandidateLineType | CandidateLineRatingA | BreakerRatingKVA_x | LoadAllocationMethod | BreakerID | SubstationID | BreakerRatingKVA_y | Substation_ExpectedFeederCount | Substation_LoadedFeederCount | Substation_AllMappedFeedersLoaded | Substation_AverageLoadMW | Substation_P95LoadMW | Substation_PeakLoadMW | Substation_PeakTimestampUTC | Substation_SumIndividualFeederPeaksMW | Substation_CoincidenceFactor | Substation_DiversityFactor | Substation_DataCoveragePct | Substation_LoadProfileConfidence | Substation_AvailableCapacityMW | Substation_CapacityResolutionStatus | Substation_CapacitySource | Substation_CapacitySourceKey | Substation_CapacitySourceUnit | Substation_Preferred80PctLimitMW | Substation_Preferred90PctLimitMW | Substation_Hard100PctLimitMW | Substation_Preferred80PctHeadroomMW | Substation_Preferred90PctHeadroomMW | Substation_Hard100PctHeadroomMW | Substation_PeakSubstationUtilizationPct | Substation_OverloadLimitPct | Substation_OverloadDurationHours | Substation_OverloadLimitMW | Substation_OverloadHeadroomMW | FeederPathHostingMW | SubstationHardHeadroomMW | SubstationPreferred90HeadroomMW | SubstationPreferred80HeadroomMW | FinalBaseHostingMW | Preferred90HostingMW | Preferred80HostingMW | FinalConstraintClass | FinalConstraintID | FinalRankingStatus | FinalRank | CandidateCountOnSharedSubstation

## Best_By_Substation
GlobalRank | RankWithinFeeder | GridID | CandidateLineID | CandidateNode | EstimatedBaseHostingMW | CandidateConfidence | NominalVoltageKV | CandidateLineCapacityMW | CandidateLineExistingLoadMW | CandidateLineResidualMW | FeederPeakMW | BreakerCapacityMW | BreakerResidualMW | LimitingElementID | LimitingElementType | LimitingElementClass | LimitingElementCapacityMW | LimitingElementExistingLoadMW | LimitingElementResidualMW | ElectricalDistanceHops | PathLineCount | PathTransformerCount | LoadPointReachabilityPct | HoursWithin10PctOfPeak | PctTimeWithin10PctOfPeak | CentroidX | CentroidY | PathElementIDs | CandidateKey | CandidateLineType | CandidateLineRatingA | BreakerRatingKVA_x | LoadAllocationMethod | BreakerID | SubstationID | BreakerRatingKVA_y | Substation_ExpectedFeederCount | Substation_LoadedFeederCount | Substation_AllMappedFeedersLoaded | Substation_AverageLoadMW | Substation_P95LoadMW | Substation_PeakLoadMW | Substation_PeakTimestampUTC | Substation_SumIndividualFeederPeaksMW | Substation_CoincidenceFactor | Substation_DiversityFactor | Substation_DataCoveragePct | Substation_LoadProfileConfidence | Substation_AvailableCapacityMW | Substation_CapacityResolutionStatus | Substation_CapacitySource | Substation_CapacitySourceKey | Substation_CapacitySourceUnit | Substation_Preferred80PctLimitMW | Substation_Preferred90PctLimitMW | Substation_Hard100PctLimitMW | Substation_Preferred80PctHeadroomMW | Substation_Preferred90PctHeadroomMW | Substation_Hard100PctHeadroomMW | Substation_PeakSubstationUtilizationPct | Substation_OverloadLimitPct | Substation_OverloadDurationHours | Substation_OverloadLimitMW | Substation_OverloadHeadroomMW | FeederPathHostingMW | SubstationHardHeadroomMW | SubstationPreferred90HeadroomMW | SubstationPreferred80HeadroomMW | FinalBaseHostingMW | Preferred90HostingMW | Preferred80HostingMW | FinalConstraintClass | FinalConstraintID | FinalRankingStatus | FinalRank | CandidateCountOnSharedSubstation

## Constraint_Audit
FinalRank | GridID | CandidateLineID | SubstationID | FeederPathHostingMW | SubstationPreferred80HeadroomMW | SubstationPreferred90HeadroomMW | SubstationHardHeadroomMW | Preferred80HostingMW | Preferred90HostingMW | FinalBaseHostingMW | FinalConstraintClass | FinalConstraintID | FinalRankingStatus | CandidateConfidence | LoadPointReachabilityPct | Substation_PeakLoadMW | Substation_AvailableCapacityMW | Substation_PeakSubstationUtilizationPct | Substation_CoincidenceFactor | Substation_LoadProfileConfidence | Substation_CapacityResolutionStatus
| GSO_121 | line_3530_22 | hvmv_1_22 | 13.1607 | [6 empty] | SubstationCapacityUnresolved | line_3530_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_121 | line_3529_22 | hvmv_1_22 | 13.1607 | [6 empty] | SubstationCapacityUnresolved | line_3530_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_121 | line_5665_22 | hvmv_1_22 | 13.1607 | [6 empty] | SubstationCapacityUnresolved | line_3530_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_121 | line_6422_22 | hvmv_1_22 | 13.1607 | [6 empty] | SubstationCapacityUnresolved | line_3530_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_121 | line_6234_22 | hvmv_1_22 | 13.1607 | [6 empty] | SubstationCapacityUnresolved | line_3530_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_121 | line_6474_22 | hvmv_1_22 | 13.1607 | [6 empty] | SubstationCapacityUnresolved | line_3530_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_121 | line_6235_22 | hvmv_1_22 | 13.1607 | [6 empty] | SubstationCapacityUnresolved | line_3530_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_121 | line_6144_22 | hvmv_1_22 | 13.1607 | [6 empty] | SubstationCapacityUnresolved | line_3530_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_121 | line_6249_22 | hvmv_1_22 | 13.1607 | [6 empty] | SubstationCapacityUnresolved | line_3530_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_121 | line_5800_22 | hvmv_1_22 | 13.1607 | [6 empty] | SubstationCapacityUnresolved | line_3530_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_121 | line_5825_22 | hvmv_1_22 | 13.1607 | [6 empty] | SubstationCapacityUnresolved | line_3530_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_121 | line_5826_22 | hvmv_1_22 | 13.1607 | [6 empty] | SubstationCapacityUnresolved | line_3530_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_121 | line_5618_22 | hvmv_1_22 | 13.1607 | [6 empty] | SubstationCapacityUnresolved | line_3530_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_121 | line_5801_22 | hvmv_1_22 | 13.1607 | [6 empty] | SubstationCapacityUnresolved | line_3530_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_121 | line_5619_22 | hvmv_1_22 | 13.1607 | [6 empty] | SubstationCapacityUnresolved | line_3530_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_121 | line_5525_22 | hvmv_1_22 | 13.1607 | [6 empty] | SubstationCapacityUnresolved | line_3530_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_121 | line_6085_22 | hvmv_1_22 | 13.1607 | [6 empty] | SubstationCapacityUnresolved | line_3530_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_121 | line_5524_22 | hvmv_1_22 | 13.1607 | [6 empty] | SubstationCapacityUnresolved | line_3530_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_121 | line_5872_22 | hvmv_1_22 | 13.1607 | [6 empty] | SubstationCapacityUnresolved | line_3530_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_121 | line_6088_22 | hvmv_1_22 | 13.1607 | [6 empty] | SubstationCapacityUnresolved | line_3530_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_121 | line_6016_22 | hvmv_1_22 | 12.3059 | [6 empty] | SubstationCapacityUnresolved | line_6016_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_121 | line_5873_22 | hvmv_1_22 | 12.3006 | [6 empty] | SubstationCapacityUnresolved | line_5873_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_121 | line_6017_22 | hvmv_1_22 | 12.3006 | [6 empty] | SubstationCapacityUnresolved | line_5873_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_121 | line_6250_22 | hvmv_1_22 | 12.1999 | [6 empty] | SubstationCapacityUnresolved | line_6250_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_121 | line_5901_22 | hvmv_1_22 | 12.1999 | [6 empty] | SubstationCapacityUnresolved | line_6250_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_121 | line_4707_22 | hvmv_1_22 | 12.1999 | [6 empty] | SubstationCapacityUnresolved | line_6250_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_121 | line_4513_22 | hvmv_1_22 | 12.1999 | [6 empty] | SubstationCapacityUnresolved | line_6250_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_121 | line_4512_22 | hvmv_1_22 | 12.1999 | [6 empty] | SubstationCapacityUnresolved | line_6250_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_121 | line_4639_22 | hvmv_1_22 | 12.1999 | [6 empty] | SubstationCapacityUnresolved | line_6250_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_121 | line_5483_22 | hvmv_1_22 | 12.1999 | [6 empty] | SubstationCapacityUnresolved | line_6250_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_121 | line_6051_22 | hvmv_1_22 | 12.1999 | [6 empty] | SubstationCapacityUnresolved | line_6250_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_121 | line_5372_22 | hvmv_1_22 | 12.1999 | [6 empty] | SubstationCapacityUnresolved | line_6250_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_121 | line_4865_22 | hvmv_1_22 | 12.1999 | [6 empty] | SubstationCapacityUnresolved | line_6250_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_121 | line_4866_22 | hvmv_1_22 | 12.1999 | [6 empty] | SubstationCapacityUnresolved | line_6250_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_121 | line_4473_22 | hvmv_1_22 | 12.1999 | [6 empty] | SubstationCapacityUnresolved | line_6250_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_121 | line_4474_22 | hvmv_1_22 | 12.1999 | [6 empty] | SubstationCapacityUnresolved | line_6250_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_121 | line_4573_22 | hvmv_1_22 | 12.1999 | [6 empty] | SubstationCapacityUnresolved | line_6250_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_121 | line_4572_22 | hvmv_1_22 | 12.1999 | [6 empty] | SubstationCapacityUnresolved | line_6250_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_121 | line_5479_22 | hvmv_1_22 | 12.1999 | [6 empty] | SubstationCapacityUnresolved | line_6250_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_121 | line_5900_22 | hvmv_1_22 | 7.103 | [6 empty] | SubstationCapacityUnresolved | line_5900_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_121 | line_4867_22 | hvmv_1_22 | 7.0977 | [6 empty] | SubstationCapacityUnresolved | line_4867_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_121 | line_5478_22 | hvmv_1_22 | 7.0977 | [6 empty] | SubstationCapacityUnresolved | line_5478_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_121 | line_5634_22 | hvmv_1_22 | 6.997 | [6 empty] | SubstationCapacityUnresolved | line_5634_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_121 | line_5635_22 | hvmv_1_22 | 6.997 | [6 empty] | SubstationCapacityUnresolved | line_5634_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_121 | line_4701_22 | hvmv_1_22 | 6.997 | [6 empty] | SubstationCapacityUnresolved | line_5634_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_121 | line_4838_22 | hvmv_1_22 | 6.997 | [6 empty] | SubstationCapacityUnresolved | line_5634_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_121 | line_4700_22 | hvmv_1_22 | 6.997 | [6 empty] | SubstationCapacityUnresolved | line_5634_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_121 | line_4836_22 | hvmv_1_22 | 6.997 | [6 empty] | SubstationCapacityUnresolved | line_5634_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_121 | line_4837_22 | hvmv_1_22 | 6.997 | [6 empty] | SubstationCapacityUnresolved | line_5634_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_121 | line_5553_22 | hvmv_1_22 | 6.997 | [6 empty] | SubstationCapacityUnresolved | line_5634_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_121 | line_5690_22 | hvmv_1_22 | 6.997 | [6 empty] | SubstationCapacityUnresolved | line_5634_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_121 | line_4618_22 | hvmv_1_22 | 6.997 | [6 empty] | SubstationCapacityUnresolved | line_5634_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_121 | line_4619_22 | hvmv_1_22 | 6.997 | [6 empty] | SubstationCapacityUnresolved | line_5634_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_121 | line_6086_22 | hvmv_1_22 | 2.8327 | [6 empty] | SubstationCapacityUnresolved | line_6086_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_122 | line_5852_22 | hvmv_1_22 | 13.5096 | [6 empty] | SubstationCapacityUnresolved | line_5852_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_122 | line_5376_22 | hvmv_1_22 | 13.5096 | [6 empty] | SubstationCapacityUnresolved | line_5852_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_122 | line_5377_22 | hvmv_1_22 | 13.5096 | [6 empty] | SubstationCapacityUnresolved | line_5852_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_123 | line_6019_22 | hvmv_1_22 | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_123 | line_3606_22 | hvmv_1_22 | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_123 | line_4780_22 | hvmv_1_22 | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_123 | line_3605_22 | hvmv_1_22 | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_123 | line_5721_22 | hvmv_1_22 | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_123 | line_4425_22 | hvmv_1_22 | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_123 | line_4627_22 | hvmv_1_22 | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_123 | line_4628_22 | hvmv_1_22 | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_123 | line_5588_22 | hvmv_1_22 | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_123 | line_5587_22 | hvmv_1_22 | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_123 | line_5430_22 | hvmv_1_22 | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_123 | line_3954_22 | hvmv_1_22 | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_123 | line_3953_22 | hvmv_1_22 | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_123 | line_4022_22 | hvmv_1_22 | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_123 | line_4389_22 | hvmv_1_22 | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_123 | line_4507_22 | hvmv_1_22 | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_123 | line_5492_22 | hvmv_1_22 | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_123 | line_4185_22 | hvmv_1_22 | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_123 | line_5491_22 | hvmv_1_22 | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_123 | line_3591_22 | hvmv_1_22 | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_123 | line_6329_22 | hvmv_1_22 | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_123 | line_3592_22 | hvmv_1_22 | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_123 | line_6642_22 | hvmv_1_22 | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_123 | line_6181_22 | hvmv_1_22 | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_123 | line_4033_22 | hvmv_1_22 | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_123 | line_4142_22 | hvmv_1_22 | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_123 | line_4032_22 | hvmv_1_22 | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_123 | line_6691_22 | hvmv_1_22 | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_123 | line_3742_22 | hvmv_1_22 | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_123 | line_3743_22 | hvmv_1_22 | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_123 | line_6670_22 | hvmv_1_22 | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_123 | line_3745_22 | hvmv_1_22 | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_123 | line_6357_22 | hvmv_1_22 | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_123 | line_5692_22 | hvmv_1_22 | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_123 | line_5844_22 | hvmv_1_22 | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_123 | line_3731_22 | hvmv_1_22 | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_123 | line_5843_22 | hvmv_1_22 | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_123 | line_6075_22 | hvmv_1_22 | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_123 | line_5158_22 | hvmv_1_22 | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_123 | line_6628_22 | hvmv_1_22 | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_123 | line_6584_22 | hvmv_1_22 | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_123 | line_6463_22 | hvmv_1_22 | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_123 | line_4047_22 | hvmv_1_22 | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_123 | line_6585_22 | hvmv_1_22 | 13.1777 | [6 empty] | SubstationCapacityUnresolved | line_6019_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_123 | line_4141_22 | hvmv_1_22 | 12.2957 | [6 empty] | SubstationCapacityUnresolved | line_4141_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_123 | line_3878_22 | hvmv_1_22 | 12.2957 | [6 empty] | SubstationCapacityUnresolved | line_4141_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_124 | line_6716_22 | hvmv_1_22 | 13.4085 | [6 empty] | SubstationCapacityUnresolved | line_6716_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_124 | line_3831_22 | hvmv_1_22 | 13.4085 | [6 empty] | SubstationCapacityUnresolved | line_6716_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_124 | line_3830_22 | hvmv_1_22 | 13.4085 | [6 empty] | SubstationCapacityUnresolved | line_6716_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_124 | line_3829_22 | hvmv_1_22 | 13.4085 | [6 empty] | SubstationCapacityUnresolved | line_6716_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_124 | line_3767_22 | hvmv_1_22 | 13.4085 | [6 empty] | SubstationCapacityUnresolved | line_6716_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_124 | line_4130_22 | hvmv_1_22 | 13.4085 | [6 empty] | SubstationCapacityUnresolved | line_6716_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_124 | line_3766_22 | hvmv_1_22 | 13.4085 | [6 empty] | SubstationCapacityUnresolved | line_6716_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_124 | line_3773_22 | hvmv_1_22 | 13.4085 | [6 empty] | SubstationCapacityUnresolved | line_6716_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_124 | line_5663_22 | hvmv_1_22 | 13.4085 | [6 empty] | SubstationCapacityUnresolved | line_6716_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_124 | line_5515_22 | hvmv_1_22 | 13.4085 | [6 empty] | SubstationCapacityUnresolved | line_6716_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_124 | line_3772_22 | hvmv_1_22 | 13.4085 | [6 empty] | SubstationCapacityUnresolved | line_6716_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_124 | line_5664_22 | hvmv_1_22 | 13.4085 | [6 empty] | SubstationCapacityUnresolved | line_6716_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_124 | line_5514_22 | hvmv_1_22 | 12.3029 | [6 empty] | SubstationCapacityUnresolved | line_5514_22 | Substation capacity unresolved | High | 100 | 0.87823 |  |  | 0.96202 | High | Unresolved
| GSO_125 | line_3656_22 | hvmv_2_22 | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_125 | line_3654_22 | hvmv_2_22 | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_125 | line_3655_22 | hvmv_2_22 | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_125 | line_6571_22 | hvmv_2_22 | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_125 | line_4139_22 | hvmv_2_22 | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_125 | line_6701_22 | hvmv_2_22 | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_125 | line_5656_22 | hvmv_2_22 | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_125 | line_5655_22 | hvmv_2_22 | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_125 | line_4056_22 | hvmv_2_22 | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_125 | line_3995_22 | hvmv_2_22 | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_125 | line_4027_22 | hvmv_2_22 | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_125 | line_3996_22 | hvmv_2_22 | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_125 | line_3787_22 | hvmv_2_22 | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_125 | line_3786_22 | hvmv_2_22 | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_125 | line_6150_22 | hvmv_2_22 | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_125 | line_4087_22 | hvmv_2_22 | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_125 | line_6149_22 | hvmv_2_22 | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_125 | line_4086_22 | hvmv_2_22 | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_125 | line_3770_22 | hvmv_2_22 | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_125 | line_4137_22 | hvmv_2_22 | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_125 | line_3769_22 | hvmv_2_22 | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_125 | line_5122_22 | hvmv_2_22 | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_125 | line_6578_22 | hvmv_2_22 | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_125 | line_4108_22 | hvmv_2_22 | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_125 | line_3842_22 | hvmv_2_22 | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_125 | line_3698_22 | hvmv_2_22 | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_125 | line_3696_22 | hvmv_2_22 | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_125 | line_3697_22 | hvmv_2_22 | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_125 | line_3843_22 | hvmv_2_22 | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_125 | line_3681_22 | hvmv_2_22 | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_125 | line_3963_22 | hvmv_2_22 | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_125 | line_6288_22 | hvmv_2_22 | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_125 | line_3682_22 | hvmv_2_22 | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_125 | line_3967_22 | hvmv_2_22 | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_125 | line_4025_22 | hvmv_2_22 | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_125 | line_4187_22 | hvmv_2_22 | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_125 | line_3737_22 | hvmv_2_22 | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_125 | line_4188_22 | hvmv_2_22 | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_125 | line_4024_22 | hvmv_2_22 | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_125 | line_3736_22 | hvmv_2_22 | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_125 | line_4147_22 | hvmv_2_22 | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_125 | line_3978_22 | hvmv_2_22 | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_125 | line_4097_22 | hvmv_2_22 | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_125 | line_4098_22 | hvmv_2_22 | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_125 | line_5101_22 | hvmv_2_22 | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_125 | line_6324_22 | hvmv_2_22 | 9.1759 | [6 empty] | SubstationCapacityUnresolved | br_05_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_125 | line_5647_22 | hvmv_2_22 | 2.8381 | [6 empty] | SubstationCapacityUnresolved | line_5647_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_125 | line_5915_22 | hvmv_2_22 | 2.8329 | [6 empty] | SubstationCapacityUnresolved | line_5915_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_125 | line_6131_22 | hvmv_2_22 | 2.8329 | [6 empty] | SubstationCapacityUnresolved | line_6131_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_125 | line_3761_22 | hvmv_2_22 | 2.8224 | [6 empty] | SubstationCapacityUnresolved | line_3761_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_125 | line_3762_22 | hvmv_2_22 | 2.8224 | [6 empty] | SubstationCapacityUnresolved | line_3761_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_125 | line_6490_22 | hvmv_2_22 | 2.8224 | [6 empty] | SubstationCapacityUnresolved | line_3761_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_125 | line_6438_22 | hvmv_2_22 | 2.8224 | [6 empty] | SubstationCapacityUnresolved | line_3761_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_126 | line_6387_22 | hvmv_2_22 | 9.2578 | [6 empty] | SubstationCapacityUnresolved | br_06_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_126 | line_6386_22 | hvmv_2_22 | 9.2578 | [6 empty] | SubstationCapacityUnresolved | br_06_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_126 | line_6613_22 | hvmv_2_22 | 9.2578 | [6 empty] | SubstationCapacityUnresolved | br_06_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_126 | line_6580_22 | hvmv_2_22 | 9.2578 | [6 empty] | SubstationCapacityUnresolved | br_06_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_126 | line_3859_22 | hvmv_2_22 | 9.2578 | [6 empty] | SubstationCapacityUnresolved | br_06_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_126 | line_6337_22 | hvmv_2_22 | 9.2578 | [6 empty] | SubstationCapacityUnresolved | br_06_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_126 | line_3858_22 | hvmv_2_22 | 9.2578 | [6 empty] | SubstationCapacityUnresolved | br_06_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_126 | line_3784_22 | hvmv_2_22 | 9.2578 | [6 empty] | SubstationCapacityUnresolved | br_06_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_126 | line_3783_22 | hvmv_2_22 | 9.2578 | [6 empty] | SubstationCapacityUnresolved | br_06_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_126 | line_5621_22 | hvmv_2_22 | 9.2578 | [6 empty] | SubstationCapacityUnresolved | br_06_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_126 | line_4081_22 | hvmv_2_22 | 9.2578 | [6 empty] | SubstationCapacityUnresolved | br_06_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_126 | line_4082_22 | hvmv_2_22 | 9.2578 | [6 empty] | SubstationCapacityUnresolved | br_06_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_126 | line_6424_22 | hvmv_2_22 | 9.2578 | [6 empty] | SubstationCapacityUnresolved | br_06_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_126 | line_5819_22 | hvmv_2_22 | 9.2578 | [6 empty] | SubstationCapacityUnresolved | br_06_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_126 | line_5818_22 | hvmv_2_22 | 9.2578 | [6 empty] | SubstationCapacityUnresolved | br_06_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_126 | line_6196_22 | hvmv_2_22 | 9.2578 | [6 empty] | SubstationCapacityUnresolved | br_06_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_126 | line_6013_22 | hvmv_2_22 | 9.2578 | [6 empty] | SubstationCapacityUnresolved | br_06_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_126 | line_6012_22 | hvmv_2_22 | 9.2578 | [6 empty] | SubstationCapacityUnresolved | br_06_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_126 | line_6014_22 | hvmv_2_22 | 9.2578 | [6 empty] | SubstationCapacityUnresolved | br_06_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_126 | line_3794_22 | hvmv_2_22 | 9.2578 | [6 empty] | SubstationCapacityUnresolved | br_06_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_126 | line_3998_22 | hvmv_2_22 | 9.2578 | [6 empty] | SubstationCapacityUnresolved | br_06_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_126 | line_6171_22 | hvmv_2_22 | 9.2578 | [6 empty] | SubstationCapacityUnresolved | br_06_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_126 | line_6172_22 | hvmv_2_22 | 9.2578 | [6 empty] | SubstationCapacityUnresolved | br_06_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_126 | line_3930_22 | hvmv_2_22 | 9.2578 | [6 empty] | SubstationCapacityUnresolved | br_06_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_126 | line_6399_22 | hvmv_2_22 | 9.2578 | [6 empty] | SubstationCapacityUnresolved | br_06_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_126 | line_6154_22 | hvmv_2_22 | 9.2578 | [6 empty] | SubstationCapacityUnresolved | br_06_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_126 | line_3793_22 | hvmv_2_22 | 9.2578 | [6 empty] | SubstationCapacityUnresolved | br_06_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_126 | line_3795_22 | hvmv_2_22 | 9.2578 | [6 empty] | SubstationCapacityUnresolved | br_06_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_126 | line_4199_22 | hvmv_2_22 | 9.2578 | [6 empty] | SubstationCapacityUnresolved | br_06_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_126 | line_4078_22 | hvmv_2_22 | 9.2578 | [6 empty] | SubstationCapacityUnresolved | br_06_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_126 | line_3802_22 | hvmv_2_22 | 9.2578 | [6 empty] | SubstationCapacityUnresolved | br_06_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_126 | line_6461_22 | hvmv_2_22 | 2.8302 | [6 empty] | SubstationCapacityUnresolved | line_6461_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_127 | line_6871_22 | hvmv_2_22 | 9.4748 | [6 empty] | SubstationCapacityUnresolved | br_07_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_128 | line_6872_22 | hvmv_2_22 | 9.3499 | [6 empty] | SubstationCapacityUnresolved | br_08_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_128 | line_6395_22 | hvmv_2_22 | 9.3499 | [6 empty] | SubstationCapacityUnresolved | br_08_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_128 | line_6394_22 | hvmv_2_22 | 9.3499 | [6 empty] | SubstationCapacityUnresolved | br_08_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_128 | line_3675_22 | hvmv_2_22 | 9.3499 | [6 empty] | SubstationCapacityUnresolved | br_08_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_128 | line_3674_22 | hvmv_2_22 | 9.3499 | [6 empty] | SubstationCapacityUnresolved | br_08_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_128 | line_3778_22 | hvmv_2_22 | 9.3499 | [6 empty] | SubstationCapacityUnresolved | br_08_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_128 | line_3861_22 | hvmv_2_22 | 9.3499 | [6 empty] | SubstationCapacityUnresolved | br_08_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_128 | line_3862_22 | hvmv_2_22 | 9.3499 | [6 empty] | SubstationCapacityUnresolved | br_08_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_128 | line_6830_22 | hvmv_2_22 | 9.3499 | [6 empty] | SubstationCapacityUnresolved | br_08_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_128 | line_6881_22 | hvmv_2_22 | 9.3499 | [6 empty] | SubstationCapacityUnresolved | br_08_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_128 | line_6884_22 | hvmv_2_22 | 9.3499 | [6 empty] | SubstationCapacityUnresolved | br_08_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_128 | line_6882_22 | hvmv_2_22 | 9.3499 | [6 empty] | SubstationCapacityUnresolved | br_08_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_128 | line_3810_22 | hvmv_2_22 | 9.3499 | [6 empty] | SubstationCapacityUnresolved | br_08_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_128 | line_3809_22 | hvmv_2_22 | 9.3499 | [6 empty] | SubstationCapacityUnresolved | br_08_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_128 | line_4124_22 | hvmv_2_22 | 2.834 | [6 empty] | SubstationCapacityUnresolved | line_4124_22 | Substation capacity unresolved | High | 100 | 0.69532 |  |  | 0.93756 | High | Unresolved
| GSO_141 | line_4565_22 | hvmv_5_22 | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_141 | line_4566_22 | hvmv_5_22 | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_141 | line_5449_22 | hvmv_5_22 | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_141 | line_6472_22 | hvmv_5_22 | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_141 | line_5448_22 | hvmv_5_22 | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_141 | line_6471_22 | hvmv_5_22 | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_141 | line_5658_22 | hvmv_5_22 | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_141 | line_6887_22 | hvmv_5_22 | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_141 | line_4878_22 | hvmv_5_22 | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_141 | line_4879_22 | hvmv_5_22 | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_141 | line_5743_22 | hvmv_5_22 | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_141 | line_4709_22 | hvmv_5_22 | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_141 | line_4710_22 | hvmv_5_22 | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_141 | line_4403_22 | hvmv_5_22 | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_141 | line_4401_22 | hvmv_5_22 | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_141 | line_4250_22 | hvmv_5_22 | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_141 | line_4803_22 | hvmv_5_22 | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_141 | line_4251_22 | hvmv_5_22 | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_141 | line_4361_22 | hvmv_5_22 | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_141 | line_4360_22 | hvmv_5_22 | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_141 | line_4095_22 | hvmv_5_22 | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_141 | line_4815_22 | hvmv_5_22 | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_141 | line_4094_22 | hvmv_5_22 | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_141 | line_4096_22 | hvmv_5_22 | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_141 | line_4523_22 | hvmv_5_22 | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_141 | line_4887_22 | hvmv_5_22 | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_141 | line_4522_22 | hvmv_5_22 | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_141 | line_4602_22 | hvmv_5_22 | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_141 | line_4300_22 | hvmv_5_22 | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_141 | line_6118_22 | hvmv_5_22 | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_141 | line_4370_22 | hvmv_5_22 | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_141 | line_5677_22 | hvmv_5_22 | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_141 | line_5676_22 | hvmv_5_22 | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_141 | line_6007_22 | hvmv_5_22 | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_141 | line_6175_22 | hvmv_5_22 | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_141 | line_6241_22 | hvmv_5_22 | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_141 | line_5932_22 | hvmv_5_22 | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_141 | line_6174_22 | hvmv_5_22 | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_141 | line_6294_22 | hvmv_5_22 | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_141 | line_6060_22 | hvmv_5_22 | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_141 | line_4849_22 | hvmv_5_22 | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_141 | line_6059_22 | hvmv_5_22 | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_141 | line_4502_22 | hvmv_5_22 | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_141 | line_4758_22 | hvmv_5_22 | 11.02 | [6 empty] | SubstationCapacityUnresolved | br_021_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_141 | line_4258_22 | hvmv_5_22 | 2.8154 | [6 empty] | SubstationCapacityUnresolved | line_4258_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_141 | line_4257_22 | hvmv_5_22 | 2.8154 | [6 empty] | SubstationCapacityUnresolved | line_4258_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_141 | line_4268_22 | hvmv_5_22 | 2.8154 | [6 empty] | SubstationCapacityUnresolved | line_4258_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_141 | line_4437_22 | hvmv_5_22 | 2.8154 | [6 empty] | SubstationCapacityUnresolved | line_4258_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_5429_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_5428_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_5565_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4913_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_5566_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4904_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4684_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4350_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_3966_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4905_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4685_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4924_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_5427_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4528_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4889_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4527_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_3566_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4608_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_3565_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4439_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4609_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4610_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4440_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4419_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4938_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_5129_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_3988_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4929_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4939_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_5442_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_5463_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4570_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_5117_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_3913_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_3989_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4875_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_3912_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4560_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4876_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_5156_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_5157_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4561_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4562_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_5777_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4717_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4716_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4554_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_6503_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4545_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4553_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_3663_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4546_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_3662_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4584_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4864_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_5099_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4908_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4658_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4907_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4935_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_3984_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4391_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4392_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4393_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_3983_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4830_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4796_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_3886_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_5345_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_5111_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_3885_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_3887_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_5168_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4582_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4262_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_5109_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4477_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4583_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4823_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4434_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_3723_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4476_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_3724_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4435_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4436_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4942_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4919_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4891_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_3596_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4464_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4682_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4463_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_3782_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4770_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4769_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4386_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4808_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4387_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4792_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4458_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4548_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4549_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4457_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_3873_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4678_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_3872_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4910_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4921_22 | hvmv_5_22 | 10.6074 | [6 empty] | SubstationCapacityUnresolved | br_022_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4122_22 | hvmv_5_22 | 7.1027 | [6 empty] | SubstationCapacityUnresolved | line_4122_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_3982_22 | hvmv_5_22 | 7.097 | [6 empty] | SubstationCapacityUnresolved | line_3982_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4351_22 | hvmv_5_22 | 2.8377 | [6 empty] | SubstationCapacityUnresolved | line_4351_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_4899_22 | hvmv_5_22 | 2.8377 | [6 empty] | SubstationCapacityUnresolved | line_4899_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_6343_22 | hvmv_5_22 | 2.8377 | [6 empty] | SubstationCapacityUnresolved | line_6343_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_3595_22 | hvmv_5_22 | 2.8377 | [6 empty] | SubstationCapacityUnresolved | line_3595_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_3946_22 | hvmv_5_22 | 2.8377 | [6 empty] | SubstationCapacityUnresolved | line_3946_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_5115_22 | hvmv_5_22 | 2.8377 | [6 empty] | SubstationCapacityUnresolved | line_5115_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_3690_22 | hvmv_5_22 | 2.8264 | [6 empty] | SubstationCapacityUnresolved | line_3690_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_5135_22 | hvmv_5_22 | 2.8264 | [6 empty] | SubstationCapacityUnresolved | line_5135_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_142 | line_3857_22 | hvmv_5_22 | 2.8264 | [6 empty] | SubstationCapacityUnresolved | line_5135_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_144 | line_5978_22 | hvmv_5_22 | 11.2671 | [6 empty] | SubstationCapacityUnresolved | br_024_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_144 | line_5977_22 | hvmv_5_22 | 6.9921 | [6 empty] | SubstationCapacityUnresolved | line_5977_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_144 | line_5982_22 | hvmv_5_22 | 6.9921 | [6 empty] | SubstationCapacityUnresolved | line_5977_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_144 | line_5973_22 | hvmv_5_22 | 6.9921 | [6 empty] | SubstationCapacityUnresolved | line_5977_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_144 | line_5974_22 | hvmv_5_22 | 6.9921 | [6 empty] | SubstationCapacityUnresolved | line_5977_22 | Substation capacity unresolved | High | 100 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_6170_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_5166_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_5164_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_5344_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_5482_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_5955_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_6070_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_4633_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_6069_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_4634_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_4635_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_4279_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_4718_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_4225_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_4719_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_4226_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_5348_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_6270_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_5863_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_5864_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_4373_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_5477_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_4372_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_5881_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_5457_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_5882_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_5240_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_6098_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_6277_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_5239_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_5232_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_6495_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_6040_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_5609_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_4729_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_4243_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_4242_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_4396_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_4397_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_4244_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_5671_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_6028_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_6138_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_5401_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_5672_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_6309_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_6314_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_4785_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_4788_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_5497_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_4812_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_5536_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_4787_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_4733_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_5247_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_4813_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_5816_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_5367_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_6370_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_5366_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_5268_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_5834_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_6492_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_4471_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_5267_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_5269_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_5474_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_5273_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_6194_22 | hvmv_5_22 | 10.6656 | [6 empty] | SubstationCapacityUnresolved | br_025_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_5347_22 | hvmv_5_22 | 7.1031 | [6 empty] | SubstationCapacityUnresolved | line_5347_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_4219_22 | hvmv_5_22 | 2.8381 | [6 empty] | SubstationCapacityUnresolved | line_4219_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_4786_22 | hvmv_5_22 | 2.8381 | [6 empty] | SubstationCapacityUnresolved | line_4786_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_5835_22 | hvmv_5_22 | 2.8381 | [6 empty] | SubstationCapacityUnresolved | line_5835_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_5362_22 | hvmv_5_22 | 2.8277 | [6 empty] | SubstationCapacityUnresolved | line_5362_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_4319_22 | hvmv_5_22 | 2.8277 | [6 empty] | SubstationCapacityUnresolved | line_5362_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_4287_22 | hvmv_5_22 | 2.8225 | [6 empty] | SubstationCapacityUnresolved | line_4287_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_4288_22 | hvmv_5_22 | 2.8225 | [6 empty] | SubstationCapacityUnresolved | line_4287_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_145 | line_5165_22 | hvmv_5_22 | 2.8069 | [6 empty] | SubstationCapacityUnresolved | line_5165_22 | Substation capacity unresolved | Medium | 90.9677 | 4.4648 |  |  | 0.97473 | High | Unresolved
| GSO_18 | line_108323_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_108322_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_122867_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_129230_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_129223_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_107810_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_107809_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_110795_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_110794_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_111728_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_110281_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_108303_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_108304_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_108305_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_108117_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_109744_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_109743_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_108116_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_116127_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_110125_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_116128_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_128625_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_110126_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_113231_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_128626_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_112666_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_131276_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_106219_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_116038_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_106218_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_116037_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_107862_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_107863_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_112560_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_113658_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_112561_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_111905_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_111906_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_111907_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_113500_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_113501_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_113499_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_112222_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_112221_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_111623_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_112166_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_112168_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_112167_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_111343_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_120823_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_106649_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_111342_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_112965_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_106648_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_110779_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_129249_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_108245_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_110780_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_111485_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_108246_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_111484_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_112972_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_131950_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_112973_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_106466_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_128347_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_106465_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_115816_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_108372_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_108373_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_108371_21 | hvmv_4_21 | 10.3769 | [6 empty] | SubstationCapacityUnresolved | br_025_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_106670_21 | hvmv_4_21 | 2.8394 | [6 empty] | SubstationCapacityUnresolved | line_106670_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_111503_21 | hvmv_4_21 | 2.8355 | [6 empty] | SubstationCapacityUnresolved | line_111503_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_111504_21 | hvmv_4_21 | 2.8355 | [6 empty] | SubstationCapacityUnresolved | line_111503_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_111505_21 | hvmv_4_21 | 2.8355 | [6 empty] | SubstationCapacityUnresolved | line_111503_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_112861_21 | hvmv_4_21 | 2.8316 | [6 empty] | SubstationCapacityUnresolved | line_112861_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_106690_21 | hvmv_4_21 | 2.8237 | [6 empty] | SubstationCapacityUnresolved | line_106690_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_106886_21 | hvmv_4_21 | 2.8237 | [6 empty] | SubstationCapacityUnresolved | line_106886_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_106885_21 | hvmv_4_21 | 2.8237 | [6 empty] | SubstationCapacityUnresolved | line_106886_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_112325_21 | hvmv_4_21 | 2.8237 | [6 empty] | SubstationCapacityUnresolved | line_112325_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_110709_21 | hvmv_4_21 | 2.8237 | [6 empty] | SubstationCapacityUnresolved | line_106886_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_112326_21 | hvmv_4_21 | 2.8237 | [6 empty] | SubstationCapacityUnresolved | line_112325_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_108159_21 | hvmv_4_21 | 2.8159 | [6 empty] | SubstationCapacityUnresolved | line_108159_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_107001_21 | hvmv_4_21 | 2.8159 | [6 empty] | SubstationCapacityUnresolved | line_108159_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_106839_21 | hvmv_4_21 | 2.8159 | [6 empty] | SubstationCapacityUnresolved | line_108159_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_126656_21 | hvmv_4_21 | 2.812 | [6 empty] | SubstationCapacityUnresolved | line_126656_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_107808_21 | hvmv_4_21 | 2.7884 | [6 empty] | SubstationCapacityUnresolved | line_107808_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_106801_21 | hvmv_4_21 | 2.7806 | [6 empty] | SubstationCapacityUnresolved | line_106801_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_106802_21 | hvmv_4_21 | 2.7806 | [6 empty] | SubstationCapacityUnresolved | line_106801_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_110213_21 | hvmv_4_21 | 2.7688 | [6 empty] | SubstationCapacityUnresolved | line_110213_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_111729_21 | hvmv_4_21 | 2.7649 | [6 empty] | SubstationCapacityUnresolved | line_111729_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_108321_21 | hvmv_4_21 | 2.4826 | [6 empty] | SubstationCapacityUnresolved | line_108321_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_108642_21 | hvmv_4_21 | 2.4826 | [6 empty] | SubstationCapacityUnresolved | line_108321_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_115810_21 | hvmv_4_21 | 2.4826 | [6 empty] | SubstationCapacityUnresolved | line_108321_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_116051_21 | hvmv_4_21 | 2.4826 | [6 empty] | SubstationCapacityUnresolved | line_108321_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_109051_21 | hvmv_4_21 | 2.4826 | [6 empty] | SubstationCapacityUnresolved | line_108321_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_106608_21 | hvmv_4_21 | 2.4826 | [6 empty] | SubstationCapacityUnresolved | line_108321_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_109050_21 | hvmv_4_21 | 2.4826 | [6 empty] | SubstationCapacityUnresolved | line_108321_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_109719_21 | hvmv_4_21 | 2.4826 | [6 empty] | SubstationCapacityUnresolved | line_108321_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_108954_21 | hvmv_4_21 | 2.4826 | [6 empty] | SubstationCapacityUnresolved | line_108321_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_108953_21 | hvmv_4_21 | 2.4826 | [6 empty] | SubstationCapacityUnresolved | line_108321_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_108955_21 | hvmv_4_21 | 2.4826 | [6 empty] | SubstationCapacityUnresolved | line_108321_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_126719_21 | hvmv_4_21 | 2.4826 | [6 empty] | SubstationCapacityUnresolved | line_108321_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_127045_21 | hvmv_4_21 | 2.4826 | [6 empty] | SubstationCapacityUnresolved | line_108321_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_110282_21 | hvmv_4_21 | 2.4395 | [6 empty] | SubstationCapacityUnresolved | line_110282_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_109986_21 | hvmv_4_21 | 2.4395 | [6 empty] | SubstationCapacityUnresolved | line_110282_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_106073_21 | hvmv_4_21 | 2.4395 | [6 empty] | SubstationCapacityUnresolved | line_110282_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_109987_21 | hvmv_4_21 | 2.4395 | [6 empty] | SubstationCapacityUnresolved | line_110282_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_109988_21 | hvmv_4_21 | 2.4395 | [6 empty] | SubstationCapacityUnresolved | line_110282_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_106074_21 | hvmv_4_21 | 2.4395 | [6 empty] | SubstationCapacityUnresolved | line_110282_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_116237_21 | hvmv_4_21 | 2.4395 | [6 empty] | SubstationCapacityUnresolved | line_110282_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_115874_21 | hvmv_4_21 | 2.4395 | [6 empty] | SubstationCapacityUnresolved | line_110282_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_106668_21 | hvmv_4_21 | 2.4395 | [6 empty] | SubstationCapacityUnresolved | line_110282_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_106669_21 | hvmv_4_21 | 2.4395 | [6 empty] | SubstationCapacityUnresolved | line_110282_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_127903_21 | hvmv_4_21 | 2.4395 | [6 empty] | SubstationCapacityUnresolved | line_110282_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_106667_21 | hvmv_4_21 | 2.3964 | [6 empty] | SubstationCapacityUnresolved | line_106667_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_106666_21 | hvmv_4_21 | 2.3964 | [6 empty] | SubstationCapacityUnresolved | line_106667_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_106064_21 | hvmv_4_21 | 2.3964 | [6 empty] | SubstationCapacityUnresolved | line_106667_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_112184_21 | hvmv_4_21 | 2.3964 | [6 empty] | SubstationCapacityUnresolved | line_106667_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_108380_21 | hvmv_4_21 | 2.3964 | [6 empty] | SubstationCapacityUnresolved | line_106667_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_112251_21 | hvmv_4_21 | 2.3964 | [6 empty] | SubstationCapacityUnresolved | line_106667_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_108379_21 | hvmv_4_21 | 2.3964 | [6 empty] | SubstationCapacityUnresolved | line_106667_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_108381_21 | hvmv_4_21 | 2.3964 | [6 empty] | SubstationCapacityUnresolved | line_106667_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_112250_21 | hvmv_4_21 | 2.3964 | [6 empty] | SubstationCapacityUnresolved | line_106667_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_111444_21 | hvmv_4_21 | 2.3964 | [6 empty] | SubstationCapacityUnresolved | line_106667_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_112171_21 | hvmv_4_21 | 2.3964 | [6 empty] | SubstationCapacityUnresolved | line_106667_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_112172_21 | hvmv_4_21 | 2.3964 | [6 empty] | SubstationCapacityUnresolved | line_106667_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_113593_21 | hvmv_4_21 | 2.3964 | [6 empty] | SubstationCapacityUnresolved | line_106667_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_120790_21 | hvmv_4_21 | 2.3964 | [6 empty] | SubstationCapacityUnresolved | line_106667_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_122817_21 | hvmv_4_21 | 2.3964 | [6 empty] | SubstationCapacityUnresolved | line_106667_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_122816_21 | hvmv_4_21 | 2.3964 | [6 empty] | SubstationCapacityUnresolved | line_106667_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_18 | line_122824_21 | hvmv_4_21 | 2.3964 | [6 empty] | SubstationCapacityUnresolved | line_106667_21 | Substation capacity unresolved | High | 100 | 10.9621 |  |  | 0.99756 | High | Unresolved
| GSO_55 | line_128388_21 | hvmv_10_21 | 9.2315 | [6 empty] | SubstationCapacityUnresolved | br_062_21 | Substation capacity unresolved | High | 100 | 6.1336 |  |  | 0.99612 | High | Unresolved
| GSO_55 | line_112967_21 | hvmv_10_21 | 7.1047 | [6 empty] | SubstationCapacityUnresolved | line_112967_21 | Substation capacity unresolved | High | 100 | 6.1336 |  |  | 0.99612 | High | Unresolved
| GSO_55 | line_112839_21 | hvmv_10_21 | 6.9244 | [6 empty] | SubstationCapacityUnresolved | line_112839_21 | Substation capacity unresolved | High | 100 | 6.1336 |  |  | 0.99612 | High | Unresolved
| GSO_55 | line_112837_21 | hvmv_10_21 | 6.9244 | [6 empty] | SubstationCapacityUnresolved | line_112839_21 | Substation capacity unresolved | High | 100 | 6.1336 |  |  | 0.99612 | High | Unresolved
| GSO_55 | line_112838_21 | hvmv_10_21 | 6.9244 | [6 empty] | SubstationCapacityUnresolved | line_112839_21 | Substation capacity unresolved | High | 100 | 6.1336 |  |  | 0.99612 | High | Unresolved
| GSO_55 | line_109004_21 | hvmv_10_21 | 6.9244 | [6 empty] | SubstationCapacityUnresolved | line_112839_21 | Substation capacity unresolved | High | 100 | 6.1336 |  |  | 0.99612 | High | Unresolved
| GSO_55 | line_111366_21 | hvmv_10_21 | 6.9244 | [6 empty] | SubstationCapacityUnresolved | line_112839_21 | Substation capacity unresolved | High | 100 | 6.1336 |  |  | 0.99612 | High | Unresolved
| GSO_55 | line_109005_21 | hvmv_10_21 | 6.9244 | [6 empty] | SubstationCapacityUnresolved | line_112839_21 | Substation capacity unresolved | High | 100 | 6.1336 |  |  | 0.99612 | High | Unresolved
| GSO_55 | line_113552_21 | hvmv_10_21 | 6.9244 | [6 empty] | SubstationCapacityUnresolved | line_112839_21 | Substation capacity unresolved | High | 100 | 6.1336 |  |  | 0.99612 | High | Unresolved
| GSO_55 | line_126626_21 | hvmv_10_21 | 6.9244 | [6 empty] | SubstationCapacityUnresolved | line_112839_21 | Substation capacity unresolved | High | 100 | 6.1336 |  |  | 0.99612 | High | Unresolved
| GSO_55 | line_131955_21 | hvmv_10_21 | 6.9244 | [6 empty] | SubstationCapacityUnresolved | line_112839_21 | Substation capacity unresolved | High | 100 | 6.1336 |  |  | 0.99612 | High | Unresolved
| GSO_73 | line_129349_21 | hvmv_12_21 | 9.4021 | [6 empty] | SubstationCapacityUnresolved | br_073_21 | Substation capacity unresolved | High | 100 | 9.0553 |  |  | 0.98391 | High | Unresolved
| GSO_73 | line_129085_21 | hvmv_12_21 | 9.4021 | [6 empty] | SubstationCapacityUnresolved | br_073_21 | Substation capacity unresolved | High | 100 | 9.0553 |  |  | 0.98391 | High | Unresolved
| GSO_73 | line_109902_21 | hvmv_12_21 | 9.4021 | [6 empty] | SubstationCapacityUnresolved | br_073_21 | Substation capacity unresolved | High | 100 | 9.0553 |  |  | 0.98391 | High | Unresolved
| GSO_73 | line_109903_21 | hvmv_12_21 | 9.4021 | [6 empty] | SubstationCapacityUnresolved | br_073_21 | Substation capacity unresolved | High | 100 | 9.0553 |  |  | 0.98391 | High | Unresolved
| GSO_73 | line_129368_21 | hvmv_12_21 | 9.4021 | [6 empty] | SubstationCapacityUnresolved | br_073_21 | Substation capacity unresolved | High | 100 | 9.0553 |  |  | 0.98391 | High | Unresolved
| GSO_73 | line_117011_21 | hvmv_12_21 | 9.4021 | [6 empty] | SubstationCapacityUnresolved | br_073_21 | Substation capacity unresolved | High | 100 | 9.0553 |  |  | 0.98391 | High | Unresolved
| GSO_73 | line_117010_21 | hvmv_12_21 | 9.4021 | [6 empty] | SubstationCapacityUnresolved | br_073_21 | Substation capacity unresolved | High | 100 | 9.0553 |  |  | 0.98391 | High | Unresolved
| GSO_73 | line_120795_21 | hvmv_12_21 | 9.4021 | [6 empty] | SubstationCapacityUnresolved | br_073_21 | Substation capacity unresolved | High | 100 | 9.0553 |  |  | 0.98391 | High | Unresolved
| GSO_73 | line_110416_21 | hvmv_12_21 | 9.4021 | [6 empty] | SubstationCapacityUnresolved | br_073_21 | Substation capacity unresolved | High | 100 | 9.0553 |  |  | 0.98391 | High | Unresolved
| GSO_73 | line_107924_21 | hvmv_12_21 | 9.4021 | [6 empty] | SubstationCapacityUnresolved | br_073_21 | Substation capacity unresolved | High | 100 | 9.0553 |  |  | 0.98391 | High | Unresolved
| GSO_73 | line_117012_21 | hvmv_12_21 | 7.1026 | [6 empty] | SubstationCapacityUnresolved | line_117012_21 | Substation capacity unresolved | High | 100 | 9.0553 |  |  | 0.98391 | High | Unresolved
| GSO_73 | line_123517_21 | hvmv_12_21 | 7.0968 | [6 empty] | SubstationCapacityUnresolved | line_123517_21 | Substation capacity unresolved | High | 100 | 9.0553 |  |  | 0.98391 | High | Unresolved
| GSO_73 | line_123518_21 | hvmv_12_21 | 2.8376 | [6 empty] | SubstationCapacityUnresolved | line_123518_21 | Substation capacity unresolved | High | 100 | 9.0553 |  |  | 0.98391 | High | Unresolved
| GSO_73 | line_123681_21 | hvmv_12_21 | 2.8318 | [6 empty] | SubstationCapacityUnresolved | line_123681_21 | Substation capacity unresolved | High | 100 | 9.0553 |  |  | 0.98391 | High | Unresolved

## Substation_Summary
SubstationID | ExpectedFeederCount | LoadedFeederCount | AllMappedFeedersLoaded | AverageLoadMW | P95LoadMW | PeakLoadMW | PeakTimestampUTC | SumIndividualFeederPeaksMW | CoincidenceFactor | DiversityFactor | LoadFactor_AvgDivPeak | SCADAIntervalMinutes | Observations | ObservedHours | DataCoveragePct | HoursWithin5PctOfPeak | PctTimeWithin5PctOfPeak | HoursWithin10PctOfPeak | PctTimeWithin10PctOfPeak | HoursWithin20PctOfPeak | PctTimeWithin20PctOfPeak | HoursWithin30PctOfPeak | PctTimeWithin30PctOfPeak | HoursWithin50PctOfPeak | PctTimeWithin50PctOfPeak | LoadProfileConfidence | AvailableCapacityMW | CapacityResolutionStatus | CapacitySource | CapacitySourceKey | CapacitySourceUnit | Preferred80PctLimitMW | Preferred90PctLimitMW | Hard100PctLimitMW | Preferred80PctHeadroomMW | Preferred90PctHeadroomMW | Hard100PctHeadroomMW | PeakSubstationUtilizationPct | OverloadLimitPct | OverloadDurationHours | OverloadLimitMW | OverloadHeadroomMW
hvmv_10_21 | 3 | 3 | TRUE | 3.0835 | 4.6008 | 6.1336 | 2024-01-21 04:00 | 6.1575 | 0.99612 | 1.0039 | 0.50272 | 5 | 105348 | 8779 | 99.9431 | 19.9167 | 0.22687 | 25.25 | 0.28762 | 180.25 | 2.0532 | 682.5 | 7.7742 | 3816.8333 | 43.4769 | High |  | Unresolved | No recognized explicit capacity value
hvmv_12_21 | 5 | 5 | TRUE | 4.926 | 7.0139 | 9.0553 | 2024-01-18 04:00 | 9.2034 | 0.98391 | 1.0164 | 0.54399 | 5 | 105348 | 8779 | 99.9431 | 22.4167 | 0.25534 | 35.6667 | 0.40627 | 262.1667 | 2.9863 | 824.5 | 9.3917 | 4912.5 | 55.9574 | High |  | Unresolved | No recognized explicit capacity value
hvmv_1_22 | 4 | 4 | TRUE | 0.59032 | 0.70412 | 0.87823 | 2024-01-22 04:00 | 0.9129 | 0.96202 | 1.0395 | 0.67216 | 5 | 105348 | 8779 | 99.9431 | 1.1667 | 0.013289 | 22.0833 | 0.25155 | 457.25 | 5.2085 | 2494 | 28.4087 | 8779 | 100 | High |  | Unresolved | No recognized explicit capacity value
hvmv_2_22 | 4 | 4 | TRUE | 0.47306 | 0.56262 | 0.69532 | 2024-01-20 15:00 | 0.74162 | 0.93756 | 1.0666 | 0.68035 | 5 | 105348 | 8779 | 99.9431 | 2.9167 | 0.033223 | 31.8333 | 0.36261 | 521.8333 | 5.9441 | 2846.6667 | 32.4259 | 8779 | 100 | High |  | Unresolved | No recognized explicit capacity value
hvmv_4_21 | 3 | 3 | TRUE | 5.5174 | 8.2443 | 10.9621 | 2024-01-18 04:00 | 10.9889 | 0.99756 | 1.0024 | 0.50332 | 5 | 105348 | 8779 | 99.9431 | 18.1667 | 0.20693 | 25.6667 | 0.29236 | 180.0833 | 2.0513 | 686.5833 | 7.8207 | 3841.8333 | 43.7616 | High |  | Unresolved | No recognized explicit capacity value
hvmv_5_22 | 5 | 5 | TRUE | 2.5068 | 3.4495 | 4.4648 | 2024-01-21 04:00 | 4.5806 | 0.97473 | 1.0259 | 0.56146 | 5 | 105348 | 8779 | 99.9431 | 8.8333 | 0.10062 | 34.6667 | 0.39488 | 252.25 | 2.8733 | 912.25 | 10.3913 | 5599.9167 | 63.7876 | High |  | Unresolved | No recognized explicit capacity value

## Substation_Peak_Contrib
SubstationID | PeakTimestampUTC | GridID | FeederLoadAtSubstationPeakMW | ContributionPct
hvmv_10_21 | 2024-01-21 04:00 | GSO_54 | 5.0799 | 82.8202
hvmv_10_21 | 2024-01-21 04:00 | GSO_55 | 0.24457 | 3.9874
hvmv_10_21 | 2024-01-21 04:00 | GSO_56 | 0.80917 | 13.1924
hvmv_12_21 | 2024-01-18 04:00 | GSO_71 | 5.4495 | 60.1802
hvmv_12_21 | 2024-01-18 04:00 | GSO_72 | 1.6873 | 18.6337
hvmv_12_21 | 2024-01-18 04:00 | GSO_73 | 0.073812 | 0.81512
hvmv_12_21 | 2024-01-18 04:00 | GSO_74 | 1.0341 | 11.42
hvmv_12_21 | 2024-01-18 04:00 | GSO_75 | 0.81054 | 8.951
hvmv_1_22 | 2024-01-22 04:00 | GSO_121 | 0.35251 | 40.1388
hvmv_1_22 | 2024-01-22 04:00 | GSO_122 | 0.027204 | 3.0976
hvmv_1_22 | 2024-01-22 04:00 | GSO_123 | 0.36464 | 41.5202
hvmv_1_22 | 2024-01-22 04:00 | GSO_124 | 0.13387 | 15.2434
hvmv_2_22 | 2024-01-20 15:00 | GSO_125 | 0.3094 | 44.4972
hvmv_2_22 | 2024-01-20 15:00 | GSO_126 | 0.23071 | 33.1809
hvmv_2_22 | 2024-01-20 15:00 | GSO_127 | 0.013764 | 1.9795
hvmv_2_22 | 2024-01-20 15:00 | GSO_128 | 0.14144 | 20.3424
hvmv_4_21 | 2024-01-18 04:00 | GSO_17 | 3.5261 | 32.1662
hvmv_4_21 | 2024-01-18 04:00 | GSO_18 | 2.2734 | 20.7386
hvmv_4_21 | 2024-01-18 04:00 | GSO_19 | 5.1626 | 47.0952
hvmv_5_22 | 2024-01-21 04:00 | GSO_141 | 0.33718 | 7.5518
hvmv_5_22 | 2024-01-21 04:00 | GSO_142 | 0.73967 | 16.5666
hvmv_5_22 | 2024-01-21 04:00 | GSO_143 | 2.5408 | 56.9061
hvmv_5_22 | 2024-01-21 04:00 | GSO_144 | 0.1128 | 2.5264
hvmv_5_22 | 2024-01-21 04:00 | GSO_145 | 0.73442 | 16.4491

## Feeder_Load_Summary
GridID | SubstationID | AverageLoadMW | P95LoadMW | PeakLoadMW | PeakTimestampUTC | SCADAIntervalMinutes | Observations | ObservedHours | DataCoveragePct
GSO_54 | hvmv_10_21 | 2.5084 | 3.7884 | 5.0799 | 2024-01-21 04:00 | 5 | 105348 | 8779 | 99.9431
GSO_55 | hvmv_10_21 | 0.12347 | 0.19112 | 0.26848 | 2024-01-20 10:00 | 5 | 105348 | 8779 | 99.9431
GSO_56 | hvmv_10_21 | 0.45164 | 0.62017 | 0.80917 | 2024-01-21 04:00 | 5 | 105348 | 8779 | 99.9431
GSO_71 | hvmv_12_21 | 2.7774 | 4.1681 | 5.5004 | 2024-01-21 02:00 | 5 | 105348 | 8779 | 99.9431
GSO_72 | hvmv_12_21 | 0.95133 | 1.3238 | 1.741 | 2024-01-21 04:00 | 5 | 105348 | 8779 | 99.9431
GSO_73 | hvmv_12_21 | 0.053536 | 0.06612 | 0.097896 | 2024-01-20 20:00 | 5 | 105348 | 8779 | 99.9431
GSO_74 | hvmv_12_21 | 0.71292 | 0.87569 | 1.0535 | 2024-01-20 23:25 | 5 | 105348 | 8779 | 99.9431
GSO_75 | hvmv_12_21 | 0.43085 | 0.58537 | 0.81054 | 2024-01-18 04:00 | 5 | 105348 | 8779 | 99.9431
GSO_121 | hvmv_1_22 | 0.24467 | 0.30456 | 0.38162 | 2024-01-17 23:00 | 5 | 105348 | 8779 | 99.9431
GSO_122 | hvmv_1_22 | 0.019727 | 0.024036 | 0.03276 | 2024-01-20 07:00 | 5 | 105348 | 8779 | 99.9431
GSO_123 | hvmv_1_22 | 0.24819 | 0.28877 | 0.36464 | 2024-01-22 04:00 | 5 | 105348 | 8779 | 99.9431
GSO_124 | hvmv_1_22 | 0.077728 | 0.0957 | 0.13387 | 2024-01-22 04:00 | 5 | 105348 | 8779 | 99.9431
GSO_125 | hvmv_2_22 | 0.20672 | 0.25126 | 0.3241 | 2024-01-20 11:00 | 5 | 105348 | 8779 | 99.9431
GSO_126 | hvmv_2_22 | 0.15702 | 0.18904 | 0.24218 | 2024-01-20 21:00 | 5 | 105348 | 8779 | 99.9431
GSO_127 | hvmv_2_22 | 0.012603 | 0.016656 | 0.025212 | 2024-01-20 21:00 | 5 | 105348 | 8779 | 99.9431
GSO_128 | hvmv_2_22 | 0.096715 | 0.11608 | 0.15013 | 2024-07-16 02:00 | 5 | 105348 | 8779 | 99.9431
GSO_17 | hvmv_4_21 | 1.8182 | 2.6953 | 3.5366 | 2024-01-21 04:05 | 5 | 105348 | 8779 | 99.9431
GSO_18 | hvmv_4_21 | 1.1891 | 1.713 | 2.2897 | 2024-01-21 | 5 | 105348 | 8779 | 99.9431
GSO_19 | hvmv_4_21 | 2.5101 | 3.8361 | 5.1626 | 2024-01-18 04:00 | 5 | 105348 | 8779 | 99.9431
GSO_141 | hvmv_5_22 | 0.23482 | 0.29074 | 0.37996 | 2024-01-21 01:00 | 5 | 105348 | 8779 | 99.9431
GSO_142 | hvmv_5_22 | 0.52512 | 0.62478 | 0.79259 | 2024-07-09 | 5 | 105348 | 8779 | 99.9431
GSO_143 | hvmv_5_22 | 1.249 | 1.8959 | 2.5408 | 2024-01-21 04:00 | 5 | 105348 | 8779 | 99.9431
GSO_144 | hvmv_5_22 | 0.057412 | 0.090084 | 0.13286 | 2024-01-20 21:00 | 5 | 105348 | 8779 | 99.9431
GSO_145 | hvmv_5_22 | 0.4405 | 0.56032 | 0.73442 | 2024-01-21 04:00 | 5 | 105348 | 8779 | 99.9431

## Feeder_Substation_Map
GridID | BreakerID | SubstationID | BreakerRatingKVA | BreakerVoltageLevel
GSO_121 | br_01_22 | hvmv_1_22 | 15000.0 | MV
GSO_122 | br_02_22 | hvmv_1_22 | 15000.0 | MV
GSO_123 | br_03_22 | hvmv_1_22 | 15000.0 | MV
GSO_124 | br_04_22 | hvmv_1_22 | 15000.0 | MV
GSO_125 | br_05_22 | hvmv_2_22 | 10000.0 | MV
GSO_126 | br_06_22 | hvmv_2_22 | 10000.0 | MV
GSO_127 | br_07_22 | hvmv_2_22 | 10000.0 | MV
GSO_128 | br_08_22 | hvmv_2_22 | 10000.0 | MV
GSO_141 | br_021_22 | hvmv_5_22 | 12000.0 | MV
GSO_142 | br_022_22 | hvmv_5_22 | 12000.0 | MV
GSO_143 | br_023_22 | hvmv_5_22 | 12000.0 | MV
GSO_144 | br_024_22 | hvmv_5_22 | 12000.0 | MV
GSO_145 | br_025_22 | hvmv_5_22 | 12000.0 | MV
GSO_17 | br_024_21 | hvmv_4_21 | 13333.3 | MV
GSO_18 | br_025_21 | hvmv_4_21 | 13333.3 | MV
GSO_19 | br_026_21 | hvmv_4_21 | 13333.3 | MV
GSO_54 | br_061_21 | hvmv_10_21 | 10000.0 | MV
GSO_55 | br_062_21 | hvmv_10_21 | 10000.0 | MV
GSO_56 | br_063_21 | hvmv_10_21 | 10000.0 | MV
GSO_71 | br_071_21 | hvmv_12_21 | 10000.0 | MV
GSO_72 | br_072_21 | hvmv_12_21 | 10000.0 | MV
GSO_73 | br_073_21 | hvmv_12_21 | 10000.0 | MV
GSO_74 | br_074_21 | hvmv_12_21 | 10000.0 | MV
GSO_75 | br_075_21 | hvmv_12_21 | 10000.0 | MV

## SCADA_Source_Audit
GridID | BreakerID | DataSourceID | Phase | Provider | FriendlyID | Observations | StartTimestamp | EndTimestamp | Status | SelectedForFeederProfile
GSO_54 | br_061_21 | 0c2d5da7-8b73-4e99-a2ec-e1bd371c44f1 | B | SMART_scada_data | br_061_21.B | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_54 | br_061_21 | b486465e-b5c3-4f46-9979-e961ceb9df52 | C | SMART_scada_data | br_061_21.C | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_54 | br_061_21 | c70624cc-3511-421e-bcd3-4f74ee43c80f | A | SMART_scada_data | br_061_21.A | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_55 | br_062_21 | 0d627f19-7146-43b0-9f7b-bac68e9966db | B | SMART_scada_data | br_062_21.B | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_55 | br_062_21 | 55b291eb-5761-4e7f-8635-63057f856791 | A | SMART_scada_data | br_062_21.A | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_55 | br_062_21 | efb7b851-1f6e-4084-9dd6-5a62049b7654 | C | SMART_scada_data | br_062_21.C | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_56 | br_063_21 | 620a8a0d-bcbd-4f44-be97-24244e308366 | C | SMART_scada_data | br_063_21.C | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_56 | br_063_21 | 748858e9-a0e0-4bc6-a0b7-f4e67d7c9ecd | B | SMART_scada_data | br_063_21.B | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_56 | br_063_21 | d5be6516-e14a-46ab-a02a-0650b74a5159 | A | SMART_scada_data | br_063_21.A | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_71 | br_071_21 | 4ff8b560-0d8d-46ca-aa4f-48e616d84a8c | B | SMART_scada_data | br_071_21.B | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_71 | br_071_21 | 7dec81b6-3b82-498d-bfaa-f44bf5d9581d | A | SMART_scada_data | br_071_21.A | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_71 | br_071_21 | 828a3353-455f-43cc-a9b0-71980deae8fd | C | SMART_scada_data | br_071_21.C | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_72 | br_072_21 | 2f6074d9-3367-424b-9912-3b54ba3842dc | A | SMART_scada_data | br_072_21.A | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_72 | br_072_21 | 5be2e72a-f9e3-4662-bcdd-f6914b127473 | B | SMART_scada_data | br_072_21.B | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_72 | br_072_21 | ceb3c16f-b2c1-4384-83e5-47eb8d9787a9 | C | SMART_scada_data | br_072_21.C | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_73 | br_073_21 | 0a5bd7a0-8dda-4ea9-8140-b43dcad4334a | C | SMART_scada_data | br_073_21.C | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_73 | br_073_21 | dc0e22aa-9b17-4812-81b9-805e6e2fcea4 | B | SMART_scada_data | br_073_21.B | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_73 | br_073_21 | dd7e3ea9-a097-46d9-ba3d-e976877c959f | A | SMART_scada_data | br_073_21.A | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_74 | br_074_21 | 2be1e40d-d971-44eb-9f8e-1f362b00491f | B | SMART_scada_data | br_074_21.B | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_74 | br_074_21 | 4cb9db9e-b9c3-473e-878d-2df2932f4dcf | A | SMART_scada_data | br_074_21.A | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_74 | br_074_21 | b4794b85-7397-40b2-a7b2-50c82c66983d | C | SMART_scada_data | br_074_21.C | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_75 | br_075_21 | 74ba07cb-a526-4618-b499-1a430d0286b7 | A | SMART_scada_data | br_075_21.A | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_75 | br_075_21 | 8cfdaf81-8e59-4486-ba2f-4e450a23c876 | C | SMART_scada_data | br_075_21.C | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_75 | br_075_21 | dc09ae69-e1ee-4c83-9c04-e09da568c6ab | B | SMART_scada_data | br_075_21.B | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_121 | br_01_22 | 0eb7ef08-0441-4661-84d4-63da9255ea41 | A | SMART_scada_data | br_01_22.A | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_121 | br_01_22 | 36cfcc10-f3c4-4989-ae21-5fdd2aa20962 | B | SMART_scada_data | br_01_22.B | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_121 | br_01_22 | 423b0798-4793-4a14-a787-72bb51fb4cef | C | SMART_scada_data | br_01_22.C | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_122 | br_02_22 | 4fa57e43-e6c7-4d4b-a312-3fb0e3337ffc | B | SMART_scada_data | br_02_22.B | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_122 | br_02_22 | abf746be-5de9-44ac-9f69-a717abe29437 | C | SMART_scada_data | br_02_22.C | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_122 | br_02_22 | e63f1c25-1cac-49ae-9929-f96fa015f74e | A | SMART_scada_data | br_02_22.A | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_123 | br_03_22 | 08fe15ea-b154-4270-ad96-7633898d9feb | C | SMART_scada_data | br_03_22.C | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_123 | br_03_22 | 22b46d3c-1104-4a6b-baf0-791554532cbe | A | SMART_scada_data | br_03_22.A | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_123 | br_03_22 | c84967ed-4e26-4447-aaec-39d0dba00695 | B | SMART_scada_data | br_03_22.B | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_124 | br_04_22 | cbbe0d2b-6245-4a4f-bcc2-e456b3e84669 | C | SMART_scada_data | br_04_22.C | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_124 | br_04_22 | e9588dba-e5c4-44a0-a87f-6d585846716c | A | SMART_scada_data | br_04_22.A | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_124 | br_04_22 | f9dd1e2c-0b53-4323-abbd-c79d2b87bf2e | B | SMART_scada_data | br_04_22.B | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_125 | br_05_22 | 16682194-aa4b-49e9-acf2-9c6562595352 | B | SMART_scada_data | br_05_22.B | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_125 | br_05_22 | 99cabfd6-b964-4658-8155-1699ad43459b | C | SMART_scada_data | br_05_22.C | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_125 | br_05_22 | cd7fbbb9-9a6f-4dd9-891c-e37a9557fa12 | A | SMART_scada_data | br_05_22.A | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_126 | br_06_22 | 12d09ac1-fdb6-467e-a1aa-f99f6eed49f6 | C | SMART_scada_data | br_06_22.C | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_126 | br_06_22 | 9006b8b1-eda0-485b-a8d0-426580b8950f | A | SMART_scada_data | br_06_22.A | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_126 | br_06_22 | bc3fda03-9c4b-412b-a5ef-6db07eeba8fc | B | SMART_scada_data | br_06_22.B | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_127 | br_07_22 | 1287cfdf-d61b-4b7d-9c56-4a67e583be03 | B | SMART_scada_data | br_07_22.B | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_127 | br_07_22 | 9962595a-e18a-4855-ab7a-6bcfb11262e4 | C | SMART_scada_data | br_07_22.C | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_127 | br_07_22 | a16d8ea2-fafa-4870-8bff-75e352b48100 | A | SMART_scada_data | br_07_22.A | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_128 | br_08_22 | 3d10e996-315d-4229-9b7c-a9b8e0697db8 | C | SMART_scada_data | br_08_22.C | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_128 | br_08_22 | 692be577-442c-4ab0-b1e1-5785854345e2 | A | SMART_scada_data | br_08_22.A | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_128 | br_08_22 | 6cff9753-e438-465f-8082-4b41468b4f8c | B | SMART_scada_data | br_08_22.B | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_17 | br_024_21 | 3a2af09c-baa8-4dbe-95ab-fb397036b19d | A | SMART_scada_data | br_024_21.A | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_17 | br_024_21 | 883c59a4-ab46-45e2-b36d-e1959b7c89b6 | B | SMART_scada_data | br_024_21.B | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_17 | br_024_21 | f0a67506-31bf-4b47-9614-f559c928646a | C | SMART_scada_data | br_024_21.C | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_18 | br_025_21 | 08eb7b30-b593-4a81-854f-d7a00d46db1e | C | SMART_scada_data | br_025_21.C | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_18 | br_025_21 | 34cac5e4-313a-4454-a92d-abc9047eadc8 | A | SMART_scada_data | br_025_21.A | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_18 | br_025_21 | 90d3f27c-2599-462f-8abb-58371a03ece5 | B | SMART_scada_data | br_025_21.B | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_19 | br_026_21 | a03bc8be-0c7b-4ca4-b625-79f7823155e9 | C | SMART_scada_data | br_026_21.C | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_19 | br_026_21 | cf54e8e6-a9a5-4011-b2be-1226fbdc86cb | B | SMART_scada_data | br_026_21.B | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_19 | br_026_21 | d5920248-7472-436e-b060-c7c2ff9ef29d | A | SMART_scada_data | br_026_21.A | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_141 | br_021_22 | 0b5869b0-b194-4a18-8593-e04336ade6ea | C | SMART_scada_data | br_021_22.C | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_141 | br_021_22 | 78f844cc-a5b4-4d9d-ba33-ef854d68bc8a | A | SMART_scada_data | br_021_22.A | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_141 | br_021_22 | b6f787f7-5117-4b48-81f4-ddbe099f96d7 | B | SMART_scada_data | br_021_22.B | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_142 | br_022_22 | 5c50320a-6541-43e1-a0eb-b3cc85335f92 | A | SMART_scada_data | br_022_22.A | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_142 | br_022_22 | aeed6de5-7aca-4fa3-a5ca-b1f32ee717c2 | C | SMART_scada_data | br_022_22.C | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_142 | br_022_22 | d8586197-7e6c-42e3-af81-89d0f76301f9 | B | SMART_scada_data | br_022_22.B | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_143 | br_023_22 | 15ee4200-f93f-4884-ab81-e52eb3d0b73c | B | SMART_scada_data | br_023_22.B | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_143 | br_023_22 | b2362459-63fa-42c8-b75d-cdff666f2190 | A | SMART_scada_data | br_023_22.A | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_143 | br_023_22 | ef7cab0d-e432-4fb1-aab4-46e5068286b4 | C | SMART_scada_data | br_023_22.C | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_144 | br_024_22 | 82536324-6f01-4e66-a011-7b067544a9ac | C | SMART_scada_data | br_024_22.C | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_144 | br_024_22 | bd7e1df8-2eb1-4167-bee8-930536ce0573 | B | SMART_scada_data | br_024_22.B | 0 |  |  | No observations | FALSE
GSO_144 | br_024_22 | cebe0434-4e95-4fd2-8e1e-22573f21abf5 | A | SMART_scada_data | br_024_22.A | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_145 | br_025_22 | 039cb766-152c-4467-9ec0-94180921a657 | C | SMART_scada_data | br_025_22.C | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_145 | br_025_22 | 5042bbb0-cc21-499d-9106-09bd8c86b439 | B | SMART_scada_data | br_025_22.B | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE
GSO_145 | br_025_22 | e8f52edb-11b6-4a01-8cb4-dde6abb481d7 | A | SMART_scada_data | br_025_22.A | 105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | Loaded | TRUE

## Substation_Capacity
SubstationID | AvailableCapacityMW | CapacityResolutionStatus | CapacitySource | CapacitySourceKey | CapacitySourceUnit
hvmv_10_21 |  | Unresolved | No recognized explicit capacity value
hvmv_1_22 |  | Unresolved | No recognized explicit capacity value
hvmv_12_21 |  | Unresolved | No recognized explicit capacity value
hvmv_2_22 |  | Unresolved | No recognized explicit capacity value
hvmv_4_21 |  | Unresolved | No recognized explicit capacity value
hvmv_5_22 |  | Unresolved | No recognized explicit capacity value

## Substation_Meta_Audit
SubstationID | MetaKey | MetaValue | NormalizedKey | NumericValue
hvmv_10_21 | name | hvmv_10_21 | name | 10
hvmv_10_21 | label | hvmv_10_21 | label | 10
hvmv_10_21 | latitude |  | latitude
hvmv_10_21 | longitude |  | longitude
hvmv_10_21 | ownership |  | ownership
hvmv_10_21 | original_id | S_nSSEE17 | originalid | 17
hvmv_10_21 | region_name |  | regionname
hvmv_10_21 | enclosure_type | substation | enclosuretype
hvmv_10_21 | is_operation_status |  | isoperationstatus
hvmv_1_22 | name | hvmv_1_22 | name | 1
hvmv_1_22 | label | hvmv_1_22 | label | 1
hvmv_1_22 | latitude |  | latitude
hvmv_1_22 | longitude |  | longitude
hvmv_1_22 | ownership |  | ownership
hvmv_1_22 | original_id | S_nSSEE0 | originalid | 0
hvmv_1_22 | region_name |  | regionname
hvmv_1_22 | enclosure_type | substation | enclosuretype
hvmv_1_22 | is_operation_status |  | isoperationstatus
hvmv_12_21 | name | hvmv_12_21 | name | 12
hvmv_12_21 | label | hvmv_12_21 | label | 12
hvmv_12_21 | latitude |  | latitude
hvmv_12_21 | longitude |  | longitude
hvmv_12_21 | ownership |  | ownership
hvmv_12_21 | original_id | S_nSSEE3 | originalid | 3
hvmv_12_21 | region_name |  | regionname
hvmv_12_21 | enclosure_type | substation | enclosuretype
hvmv_12_21 | is_operation_status |  | isoperationstatus
hvmv_2_22 | name | hvmv_2_22 | name | 2
hvmv_2_22 | label | hvmv_2_22 | label | 2
hvmv_2_22 | latitude |  | latitude
hvmv_2_22 | longitude |  | longitude
hvmv_2_22 | ownership |  | ownership
hvmv_2_22 | original_id | S_nSSEE1 | originalid | 1
hvmv_2_22 | region_name |  | regionname
hvmv_2_22 | enclosure_type | substation | enclosuretype
hvmv_2_22 | is_operation_status |  | isoperationstatus
hvmv_4_21 | name | hvmv_4_21 | name | 4
hvmv_4_21 | label | hvmv_4_21 | label | 4
hvmv_4_21 | latitude |  | latitude
hvmv_4_21 | longitude |  | longitude
hvmv_4_21 | ownership |  | ownership
hvmv_4_21 | original_id | S_nSSEE11 | originalid | 11
hvmv_4_21 | region_name |  | regionname
hvmv_4_21 | enclosure_type | substation | enclosuretype
hvmv_4_21 | is_operation_status |  | isoperationstatus
hvmv_5_22 | name | hvmv_5_22 | name | 5
hvmv_5_22 | label | hvmv_5_22 | label | 5
hvmv_5_22 | latitude |  | latitude
hvmv_5_22 | longitude |  | longitude
hvmv_5_22 | ownership |  | ownership
hvmv_5_22 | original_id | S_nSSEE4 | originalid | 4
hvmv_5_22 | region_name |  | regionname
hvmv_5_22 | enclosure_type | substation | enclosuretype
hvmv_5_22 | is_operation_status |  | isoperationstatus

## Assumptions
Item | Assumption
Substation mapping | Circuit breakers are mapped to substations through breaker meta enclosure_id
Shared substation load | Every feeder served by a relevant substation is included even if that feeder was not itself in the original top 15
Coincident demand | Substation demand is calculated by summing feeder breaker SCADA at matching timestamps
Power conversion | Interval kWh is converted to MW using interval energy divided by interval duration
Capacity source | Substation capacity must come from explicit metadata organizer supplied values or an external capacity file
Breaker ratings | Breaker ratings are not summed and treated as substation capacity
100 percent limit | 100 percent of stated substation available capacity is the normal hard planning limit
Preferred operating range | Substation transformers are considered preferable around 80 to 90 percent loading
Overload | Capacity above 100 percent is excluded from the base ranking and may only be evaluated separately with a documented overload range and duration
Service transformer assumption | Organizer guidance notes service transformers are most effective around 30 percent loading
Existing location hosting | EstimatedBaseHostingMW already represents the smallest thermal residual on the feeder breaker to candidate path
Final base hosting | FinalBaseHostingMW equals the smaller of feeder path hosting and remaining substation capacity at the 100 percent limit
Preferred hosting | Preferred80HostingMW and Preferred90HostingMW show additional capacity while keeping the substation below those utilization levels
Shared constraint | Locations on feeders belonging to the same substation share the same upstream capacity and cannot be added together independently
Ranking scope | This ranking evaluates each candidate independently and does not yet optimize simultaneous deployment across multiple sites
Next stage | Highest ranked electrically distinct locations proceed to voltage and power flow validation