## Capacity_Audit
CapacityRank | RankEligible | TopologyReadyFlag | FeederID | Description | BreakerElementID | Latitude | Longitude | CapacityConfidence | RatingValidationStatus | AuditFlag | StoredBreakerRatingKVA | BreakerRatingA | BreakerVoltageRaw | VoltageKV | VoltageInterpretation | CalculatedBreakerKVA | RatingDifferencePct | StoredBreakerCapacityMVA | CalculatedBreakerCapacityMVA | AuditedBreakerCapacityMVA | ConservativeBreakerCapacityMVA | AuditedBreakerCapacityMW | ConservativeBreakerCapacityMW | AverageLoadMW | P95LoadMW | PeakLoadMW | PeakLoadTimestamp | ValidatedHeadroomMW | ConservativeHeadroomMW | AverageUtilizationPct_Audited | P95UtilizationPct_Audited | PeakUtilizationPct_Audited | PeakUtilizationPct_Conservative | Observations | MedianIntervalMinutes | FirstTimestamp | LastTimestamp | SelectedSCADASourceCount | SelectedSCADASourceIDs | SelectedSCADAPhases | SCADAStatus | UpstreamElementID | SourceElementID | SourceElementType | SourceElementCustomerType | SourceIsProducer | UpstreamPathElementCount | UpstreamPathDepth | PathTerminatedAtNullUpstream | PathHitMaxDepth | UpstreamPathStatus | CapacityBasis | RecommendedNextStep | GridLastUpdated | ElementType | ElementCustomerType | BreakerPhases | IsProducer | IsConsumer | IsSwitchable | SwitchIsOpen | PowerFlowDirection | Terminal1CN | Terminal2CN | RawRatingKVA | RawRatingA | RawVoltageLevel | KWhSourceCount | UniquePhaseCount | DataSourceTypes | Providers | FriendlyIDs | BreakerSelectionScore | BreakerCandidateRank | AuditedBreakerCapacityKVA | ConservativeBreakerCapacityKVA | AverageIntervalKWh | P95IntervalKWh | PeakIntervalKWh
| FALSE | FALSE | GSO_1 | GSO_1 | br_01_21 | 36.0852 | -79.8827 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 5714.3 | [6 empty] | 5.7143 |  |  | 5.7143 |  | 5.4286 | 0.57147 | 0.69786 | 0.83644 | 2024-01-20 19:00 |  | 4.5921 |  |  |  | 15.408 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | b1e8c057-fded-4c70-8f86-a33db401b6d1, ba6970aa-af7f-428e-9a4f-7826618684b4, ea496fcb-6216-4db1-9885-1da5dbf70fa2 | A, B, C | OK |  | br_01_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE0 | S_nSSEE0_12.47 | 5714.3 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_01_21.A, br_01_21.B, br_01_21.C | 190 | 1 |  | 5714.3 | 47.6222 | 58.155 | 69.703
| FALSE | FALSE | GSO_10 | GSO_10 | br_015_21 | 36.1003 | -79.8075 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 5555.6 | [6 empty] | 5.5556 |  |  | 5.5556 |  | 5.2778 | 0.9939 | 1.3981 | 1.894 | 2024-01-21 04:00 |  | 3.3839 |  |  |  | 35.8853 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | d140ab36-31a8-40c7-820d-c3a2df82604a, b315ece6-7341-4cdf-a1c9-70a8dbfe93ff, 396f73e2-6041-46ac-90d5-a9439aef50d8 | A, B, C | OK |  | br_015_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE10 | S_nSSEE10_12.47 | 5555.6 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_015_21.A, br_015_21.B, br_015_21.C | 190 | 1 |  | 5555.6 | 82.8253 | 116.5043 | 157.83
| FALSE | FALSE | GSO_100 | GSO_100 | br_097_21 | 36.0611 | -79.7715 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 7500 | [6 empty] | 7.5 |  |  | 7.5 |  | 7.125 | 0.17463 | 0.26832 | 0.37085 | 2024-01-20 07:05 |  | 6.7542 |  |  |  | 5.2049 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 564551fe-ec45-4b6c-a7df-ebfa29a0a242, 3125b67a-cbd0-47b3-94b6-a60b38de7e8b, cc6f9a7e-ea1b-4cdb-9c85-6c672b845068 | A, B, C | OK |  | br_097_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE6 | S_nSSEE6_12.47 | 7500.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_097_21.A, br_097_21.B, br_097_21.C | 190 | 1 |  | 7500 | 14.5529 | 22.36 | 30.904
| FALSE | FALSE | GSO_101 | GSO_101 | br_0101_21 | 36.0872 | -79.897 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 5714.3 | [6 empty] | 5.7143 |  |  | 5.7143 |  | 5.4286 | 0.66936 | 0.87754 | 1.1216 | 2024-01-21 04:00 |  | 4.307 |  |  |  | 20.6613 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | f32aafa6-4f97-40b9-85a1-6516b7a34fb0, 8f1038a0-f3d5-4f15-bedf-b8f1215601f3, 6c559f06-b888-4a9d-ba0f-901b0b19b354 | A, B, C | OK |  | br_0101_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE7 | S_nSSEE7_12.47 | 5714.3 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_0101_21.A, br_0101_21.B, br_0101_21.C | 190 | 1 |  | 5714.3 | 55.7798 | 73.128 | 93.468
| FALSE | FALSE | GSO_102 | GSO_102 | br_0102_21 | 36.0872 | -79.897 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 5714.3 | [6 empty] | 5.7143 |  |  | 5.7143 |  | 5.4286 | 0.021543 | 0.0333 | 0.05448 | 2024-07-15 23:00 |  | 5.3741 |  |  |  | 1.0036 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | aaef163c-bdc4-464e-9864-b0c0ebdf8662, 3f11f59f-b6f2-44fe-8a16-f4a87144ca07, 58383f3b-39ee-41c1-9a45-f21c6b309b7c | A, B, C | OK |  | br_0102_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE7 | S_nSSEE7_12.47 | 5714.3 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_0102_21.A, br_0102_21.B, br_0102_21.C | 190 | 1 |  | 5714.3 | 1.7953 | 2.775 | 4.54
| FALSE | FALSE | GSO_103 | GSO_103 | br_0103_21 | 36.0872 | -79.897 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 5714.3 | [6 empty] | 5.7143 |  |  | 5.7143 |  | 5.4286 | 2.0181 | 3.1027 | 4.187 | 2024-01-21 04:00 |  | 1.2416 |  |  |  | 77.1282 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | d5fd099c-84d4-4965-91b3-bbc0c68d61d1, d53e58ae-230d-449a-b78d-6b5cfa60f56b, a3539c00-7186-4684-93db-03123790cf12 | A, B, C | OK |  | br_0103_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE7 | S_nSSEE7_12.47 | 5714.3 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_0103_21.A, br_0103_21.B, br_0103_21.C | 190 | 1 |  | 5714.3 | 168.1721 | 258.5616 | 348.914
| FALSE | FALSE | GSO_104 | GSO_104 | br_0104_21 | 36.0872 | -79.897 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 5714.3 | [6 empty] | 5.7143 |  |  | 5.7143 |  | 5.4286 | 1.917 | 2.8894 | 3.8614 | 2024-01-21 04:00 |  | 1.5672 |  |  |  | 71.1312 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | dbaf906f-b53b-4b15-bd48-42442608214a, 0256f17b-1fde-4e5f-aa42-6a293aa27e64, 4922eba1-a72a-4e22-8a37-912d5f9ac46b | A, B, C | OK |  | br_0104_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE7 | S_nSSEE7_12.47 | 5714.3 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_0104_21.A, br_0104_21.B, br_0104_21.C | 190 | 1 |  | 5714.3 | 159.7475 | 240.7818 | 321.785
| FALSE | FALSE | GSO_105 | GSO_105 | br_0105_21 | 36.0872 | -79.897 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 5714.3 | [6 empty] | 5.7143 |  |  | 5.7143 |  | 5.4286 | 1.8088 | 2.7735 | 3.66 | 2024-01-21 04:00 |  | 1.7686 |  |  |  | 67.4209 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 3943a935-55e7-44b5-a61e-08789763be18, 11bf4c6d-205c-4caf-b572-7246ab210632, 98dc0614-4560-469e-93e2-97b3c41b5000 | A, B, C | OK |  | br_0105_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE7 | S_nSSEE7_12.47 | 5714.3 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_0105_21.A, br_0105_21.B, br_0105_21.C | 190 | 1 |  | 5714.3 | 150.7342 | 231.125 | 305
| FALSE | FALSE | GSO_106 | GSO_106 | br_0106_21 | 36.0872 | -79.897 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 5714.3 | [6 empty] | 5.7143 |  |  | 5.7143 |  | 5.4286 | 0.041269 | 0.064536 | 0.09288 | 2024-01-20 10:00 |  | 5.3357 |  |  |  | 1.7109 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 1523bf59-c426-49d7-add2-e9b831978748, e37ebffe-ff65-4277-a7e0-2315cac8c267, f0643cc7-b03a-4328-82d5-2924a650f97f | A, B, C | OK |  | br_0106_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE7 | S_nSSEE7_12.47 | 5714.3 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_0106_21.A, br_0106_21.B, br_0106_21.C | 190 | 1 |  | 5714.3 | 3.439 | 5.378 | 7.74
| FALSE | FALSE | GSO_107 | GSO_107 | br_0107_21 | 36.0872 | -79.897 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 5714.3 | [6 empty] | 5.7143 |  |  | 5.7143 |  | 5.4286 | 0.068935 | 0.08376 | 0.11552 | 2024-07-16 01:00 |  | 5.3131 |  |  |  | 2.1281 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 4113937f-0ce2-415a-9249-ce7327d121f7, 5d59abb9-0bac-4fa7-a891-4e9d4e794c88, b1339292-267a-4146-8873-ecfc9cb1a82e | A, B, C | OK |  | br_0107_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE7 | S_nSSEE7_12.47 | 5714.3 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_0107_21.A, br_0107_21.B, br_0107_21.C | 190 | 1 |  | 5714.3 | 5.7446 | 6.98 | 9.627
| FALSE | FALSE | GSO_108 | GSO_108 | br_0108_21 | 36.0543 | -79.8942 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 7142.9 | [6 empty] | 7.1429 |  |  | 7.1429 |  | 6.7858 | 1.2795 | 1.9144 | 2.4922 | 2024-01-20 23:30 |  | 4.2935 |  |  |  | 36.7274 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | e867a5e4-d5f1-4fdf-98c8-da37424315a6, c0036365-6459-4cc7-b7b1-ed8933515338, 1886a888-6918-466c-929d-0c8f16370dda | A, B, C | OK |  | br_0108_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE8 | S_nSSEE8_12.47 | 7142.9 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_0108_21.A, br_0108_21.B, br_0108_21.C | 190 | 1 |  | 7142.9 | 106.625 | 159.5309 | 207.686
| FALSE | FALSE | GSO_109 | GSO_109 | br_0109_21 | 36.0543 | -79.8942 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 7142.9 | [6 empty] | 7.1429 |  |  | 7.1429 |  | 6.7858 | 1.16 | 1.6922 | 2.2226 | 2024-01-20 13:00 |  | 4.5632 |  |  |  | 32.754 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 0c75d1f1-8237-436b-a2c8-c9b6fdc7a116, ec8ad3c4-a39d-4acb-8788-e7435be58cb7, e6350d88-56d8-492b-bc1e-dcd90fcca31f | A, B, C | OK |  | br_0109_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE8 | S_nSSEE8_12.47 | 7142.9 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_0109_21.A, br_0109_21.B, br_0109_21.C | 190 | 1 |  | 7142.9 | 96.6701 | 141.014 | 185.217
| FALSE | FALSE | GSO_11 | GSO_11 | br_016_21 | 36.1003 | -79.8075 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 5555.6 | [6 empty] | 5.5556 |  |  | 5.5556 |  | 5.2778 | 1.2134 | 1.7004 | 2.1962 | 2024-01-21 04:00 |  | 3.0816 |  |  |  | 41.612 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 469868d0-2f60-42bd-aa67-be26d6eae0eb, 9cdbec33-569a-438b-ac44-23b272ad169b, dfea635f-2a86-40f1-9367-d78b6dd6c309 | A, B, C | OK |  | br_016_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE10 | S_nSSEE10_12.47 | 5555.6 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_016_21.A, br_016_21.B, br_016_21.C | 190 | 1 |  | 5555.6 | 101.1181 | 141.697 | 183.017
| FALSE | FALSE | GSO_110 | GSO_110 | br_0110_21 | 36.0543 | -79.8942 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 7142.9 | [6 empty] | 7.1429 |  |  | 7.1429 |  | 6.7858 | 2.1945 | 3.3579 | 4.5154 | 2024-01-21 04:00 |  | 2.2704 |  |  |  | 66.5421 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 1e111a58-963a-4906-b1f6-e2d03049b19a, 8a0dd243-2512-4f92-afd7-db6e79d7496e, ca02189c-f89b-417b-a469-ef0366d6da6e | A, B, C | OK |  | br_0110_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE8 | S_nSSEE8_12.47 | 7142.9 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_0110_21.A, br_0110_21.B, br_0110_21.C | 190 | 1 |  | 7142.9 | 182.8709 | 279.822 | 376.282
| FALSE | FALSE | GSO_111 | GSO_111 | br_0111_21 | 36.0543 | -79.8942 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 7142.9 | [6 empty] | 7.1429 |  |  | 7.1429 |  | 6.7858 | 0.65645 | 0.90895 | 1.156 | 2024-01-18 04:00 |  | 5.6297 |  |  |  | 17.0358 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | f8549391-d242-43a9-9a34-33f872443611, 3488e4fc-fa59-4bcf-b967-3b7a890f6c3c, e60c92cc-e283-4345-87b0-ba3a9fd78005 | A, B, C | OK |  | br_0111_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE8 | S_nSSEE8_12.47 | 7142.9 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_0111_21.A, br_0111_21.B, br_0111_21.C | 190 | 1 |  | 7142.9 | 54.7044 | 75.746 | 96.334
| FALSE | FALSE | GSO_112 | GSO_112 | br_0112_21 | 36.0543 | -79.8942 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 7142.9 | [6 empty] | 7.1429 |  |  | 7.1429 |  | 6.7858 | 0.47836 | 0.58066 | 0.77134 | 2024-01-21 04:00 |  | 6.0144 |  |  |  | 11.367 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 407ea9ca-a495-4119-a139-1d1233852fdc, 99fe4744-38fc-4467-902b-d97556b6d295, e1fd2b67-b072-4575-9f5d-c24af5f52b11 | A, B, C | OK |  | br_0112_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE8 | S_nSSEE8_12.47 | 7142.9 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_0112_21.A, br_0112_21.B, br_0112_21.C | 190 | 1 |  | 7142.9 | 39.8632 | 48.388 | 64.278
| FALSE | FALSE | GSO_113 | GSO_113 | br_0113_21 | 36.0543 | -79.8942 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 7142.9 | [6 empty] | 7.1429 |  |  | 7.1429 |  | 6.7858 | 0.053802 | 0.065088 | 0.091248 | 2024-01-20 20:00 |  | 6.6945 |  |  |  | 1.3447 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | f8ddca03-2f28-483b-97fe-a4538d6c4e2b, a9bc380c-ca71-4a2b-b314-0f03f9f76581, bdf27366-2b21-4e21-8946-86b299b81d14 | A, B, C | OK |  | br_0113_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE8 | S_nSSEE8_12.47 | 7142.9 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_0113_21.A, br_0113_21.B, br_0113_21.C | 190 | 1 |  | 7142.9 | 4.4835 | 5.424 | 7.604
| FALSE | FALSE | GSO_114 | GSO_114 | br_0114_21 | 36.0543 | -79.8942 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 7142.9 | [6 empty] | 7.1429 |  |  | 7.1429 |  | 6.7858 | 0.75285 | 1.0582 | 1.4064 | 2024-01-20 14:00 |  | 5.3794 |  |  |  | 20.7258 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 34c2c476-7801-4ae6-ba1f-ca1a602925b3, 156d4241-1525-4089-8367-effd61eb4969, 3128527e-a25b-4b2c-9d88-b40eb600580e | A, B, C | OK |  | br_0114_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE8 | S_nSSEE8_12.47 | 7142.9 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_0114_21.A, br_0114_21.B, br_0114_21.C | 190 | 1 |  | 7142.9 | 62.7375 | 88.1806 | 117.2
| FALSE | FALSE | GSO_115 | GSO_115 | br_0115_21 | 36.0426 | -79.8533 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 10000 | [6 empty] | 10 |  |  | 10 |  | 9.5 | 1.1974 | 1.7258 | 2.2713 | 2024-01-21 04:00 |  | 7.2287 |  |  |  | 23.908 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | d3645b59-a71d-4848-9deb-b044c307c52a, 820fcd78-48b0-467d-8925-554a0333f605, 58786ac1-7ac2-4287-bd8f-add68a4ea208 | A, B, C | OK |  | br_0115_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE9 | S_nSSEE9_12.47 | 10000.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_0115_21.A, br_0115_21.B, br_0115_21.C | 190 | 1 |  | 10000 | 99.7864 | 143.813 | 189.272
| FALSE | FALSE | GSO_116 | GSO_116 | br_0116_21 | 36.0426 | -79.8533 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 10000 | [6 empty] | 10 |  |  | 10 |  | 9.5 | 0.64103 | 0.8443 | 1.0806 | 2024-01-20 16:00 |  | 8.4194 |  |  |  | 11.3751 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 2a93f307-f837-4de0-9089-b308bde0f0fd, ba9bd088-fa13-4d76-ba16-6dba6a8b45de, e9542020-950f-403c-af95-965f8434a9f8 | A, B, C | OK |  | br_0116_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE9 | S_nSSEE9_12.47 | 10000.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_0116_21.A, br_0116_21.B, br_0116_21.C | 190 | 1 |  | 10000 | 53.4188 | 70.3586 | 90.053
| FALSE | FALSE | GSO_117 | GSO_117 | br_0117_21 | 36.0426 | -79.8533 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 10000 | [6 empty] | 10 |  |  | 10 |  | 9.5 | 1.821 | 2.682 | 3.528 | 2024-01-18 04:00 |  | 5.972 |  |  |  | 37.1373 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 20ca2ff7-1194-405d-9098-d4544944a36d, 127d58d0-da5d-47a0-a219-b8c1834a136a, 79b91384-9645-42ed-940d-37fdffcc31a0 | A, B, C | OK |  | br_0117_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE9 | S_nSSEE9_12.47 | 10000.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_0117_21.A, br_0117_21.B, br_0117_21.C | 190 | 1 |  | 10000 | 151.7502 | 223.4966 | 294.004
| FALSE | FALSE | GSO_118 | GSO_118 | br_0118_21 | 36.0426 | -79.8533 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 10000 | [6 empty] | 10 |  |  | 10 |  | 9.5 | 0.92656 | 1.2453 | 1.5724 | 2024-01-20 21:00 |  | 7.9276 |  |  |  | 16.5512 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | b2273af8-cb6e-4178-93e7-36fab6dbf2c0, cb23fba1-b5a8-477f-b388-dcbc14cf56b2, 7b9e37f6-9e61-405e-8bc5-9d79097397f4 | A, B, C | OK |  | br_0118_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE9 | S_nSSEE9_12.47 | 10000.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_0118_21.A, br_0118_21.B, br_0118_21.C | 190 | 1 |  | 10000 | 77.2137 | 103.7746 | 131.03
| FALSE | FALSE | GSO_119 | GSO_119 | br_0119_21 | 36.0426 | -79.8533 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 10000 | [6 empty] | 10 |  |  | 10 |  | 9.5 | 0.14971 | 0.23111 | 0.33516 | 2024-01-20 22:00 |  | 9.1648 |  |  |  | 3.528 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 1a46aa48-ac4e-4046-aa43-a61c07c816d6, faec1da7-65b2-4b86-be90-e4357dfde1ce, 3aad3364-ed36-4087-b7d0-6d3b3fa6f823 | A, B, C | OK |  | br_0119_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE9 | S_nSSEE9_12.47 | 10000.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_0119_21.A, br_0119_21.B, br_0119_21.C | 190 | 1 |  | 10000 | 12.4758 | 19.259 | 27.93
| FALSE | FALSE | GSO_12 | GSO_12 | br_017_21 | 36.1003 | -79.8075 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 5555.6 | [6 empty] | 5.5556 |  |  | 5.5556 |  | 5.2778 | 1.2344 | 1.896 | 2.4984 | 2024-01-18 04:00 |  | 2.7795 |  |  |  | 47.3368 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | e263a729-e360-4716-9561-679bf6b5d16a, ede6f7c6-f426-4d65-bfe0-7dac24a794c1, 4c1ed359-972e-4bdd-a0cd-1159d7a32c07 | A, B, C | OK |  | br_017_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE10 | S_nSSEE10_12.47 | 5555.6 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_017_21.A, br_017_21.B, br_017_21.C | 190 | 1 |  | 5555.6 | 102.8633 | 157.9969 | 208.196
| FALSE | FALSE | GSO_121 | GSO_121 | br_01_22 | 36.083 | -79.9727 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 15000 | [6 empty] | 15 |  |  | 15 |  | 14.25 | 0.24467 | 0.30456 | 0.38162 | 2024-01-17 23:00 |  | 13.8684 |  |  |  | 2.6781 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 0eb7ef08-0441-4661-84d4-63da9255ea41, 36cfcc10-f3c4-4989-ae21-5fdd2aa20962, 423b0798-4793-4a14-a787-72bb51fb4cef | A, B, C | OK |  | br_01_22 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE0 | S_nSSEE0_12.47 | 15000.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_01_22.A, br_01_22.B, br_01_22.C | 190 | 1 |  | 15000 | 20.3889 | 25.3796 | 31.802
| FALSE | FALSE | GSO_122 | GSO_122 | br_02_22 | 36.083 | -79.9727 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 15000 | [6 empty] | 15 |  |  | 15 |  | 14.25 | 0.019727 | 0.024036 | 0.03276 | 2024-01-20 07:00 |  | 14.2172 |  |  |  | 0.22989 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | e63f1c25-1cac-49ae-9929-f96fa015f74e, 4fa57e43-e6c7-4d4b-a312-3fb0e3337ffc, abf746be-5de9-44ac-9f69-a717abe29437 | A, B, C | OK |  | br_02_22 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE0 | S_nSSEE0_12.47 | 15000.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_02_22.A, br_02_22.B, br_02_22.C | 190 | 1 |  | 15000 | 1.6439 | 2.003 | 2.73
| FALSE | FALSE | GSO_123 | GSO_123 | br_03_22 | 36.083 | -79.9727 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 15000 | [6 empty] | 15 |  |  | 15 |  | 14.25 | 0.24819 | 0.28877 | 0.36464 | 2024-01-22 04:00 |  | 13.8854 |  |  |  | 2.5589 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 22b46d3c-1104-4a6b-baf0-791554532cbe, c84967ed-4e26-4447-aaec-39d0dba00695, 08fe15ea-b154-4270-ad96-7633898d9feb | A, B, C | OK |  | br_03_22 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE0 | S_nSSEE0_12.47 | 15000.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_03_22.A, br_03_22.B, br_03_22.C | 190 | 1 |  | 15000 | 20.6829 | 24.064 | 30.387
| FALSE | FALSE | GSO_124 | GSO_124 | br_04_22 | 36.083 | -79.9727 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 15000 | [6 empty] | 15 |  |  | 15 |  | 14.25 | 0.077728 | 0.0957 | 0.13387 | 2024-01-22 04:00 |  | 14.1161 |  |  |  | 0.93945 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | e9588dba-e5c4-44a0-a87f-6d585846716c, f9dd1e2c-0b53-4323-abbd-c79d2b87bf2e, cbbe0d2b-6245-4a4f-bcc2-e456b3e84669 | A, B, C | OK |  | br_04_22 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE0 | S_nSSEE0_12.47 | 15000.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_04_22.A, br_04_22.B, br_04_22.C | 190 | 1 |  | 15000 | 6.4773 | 7.975 | 11.156
| FALSE | FALSE | GSO_125 | GSO_125 | br_05_22 | 36.0974 | -79.9235 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 10000 | [6 empty] | 10 |  |  | 10 |  | 9.5 | 0.20672 | 0.25126 | 0.3241 | 2024-01-20 11:00 |  | 9.1759 |  |  |  | 3.4115 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | cd7fbbb9-9a6f-4dd9-891c-e37a9557fa12, 16682194-aa4b-49e9-acf2-9c6562595352, 99cabfd6-b964-4658-8155-1699ad43459b | A, B, C | OK |  | br_05_22 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE1 | S_nSSEE1_12.47 | 10000.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_05_22.A, br_05_22.B, br_05_22.C | 190 | 1 |  | 10000 | 17.2263 | 20.9386 | 27.008
| FALSE | FALSE | GSO_126 | GSO_126 | br_06_22 | 36.0974 | -79.9235 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 10000 | [6 empty] | 10 |  |  | 10 |  | 9.5 | 0.15702 | 0.18904 | 0.24218 | 2024-01-20 21:00 |  | 9.2578 |  |  |  | 2.5493 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 9006b8b1-eda0-485b-a8d0-426580b8950f, bc3fda03-9c4b-412b-a5ef-6db07eeba8fc, 12d09ac1-fdb6-467e-a1aa-f99f6eed49f6 | A, B, C | OK |  | br_06_22 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE1 | S_nSSEE1_12.47 | 10000.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_06_22.A, br_06_22.B, br_06_22.C | 190 | 1 |  | 10000 | 13.0851 | 15.753 | 20.182
| FALSE | FALSE | GSO_127 | GSO_127 | br_07_22 | 36.0974 | -79.9235 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 10000 | [6 empty] | 10 |  |  | 10 |  | 9.5 | 0.012603 | 0.016656 | 0.025212 | 2024-01-20 21:00 |  | 9.4748 |  |  |  | 0.26539 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | a16d8ea2-fafa-4870-8bff-75e352b48100, 1287cfdf-d61b-4b7d-9c56-4a67e583be03, 9962595a-e18a-4855-ab7a-6bcfb11262e4 | A, B, C | OK |  | br_07_22 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE1 | S_nSSEE1_12.47 | 10000.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_07_22.A, br_07_22.B, br_07_22.C | 190 | 1 |  | 10000 | 1.0502 | 1.388 | 2.101
| FALSE | FALSE | GSO_128 | GSO_128 | br_08_22 | 36.0974 | -79.9234 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 10000 | [6 empty] | 10 |  |  | 10 |  | 9.5 | 0.096715 | 0.11608 | 0.15013 | 2024-07-16 02:00 |  | 9.3499 |  |  |  | 1.5803 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 692be577-442c-4ab0-b1e1-5785854345e2, 6cff9753-e438-465f-8082-4b41468b4f8c, 3d10e996-315d-4229-9b7c-a9b8e0697db8 | A, B, C | OK |  | br_08_22 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE1 | S_nSSEE1_12.47 | 10000.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_08_22.A, br_08_22.B, br_08_22.C | 190 | 1 |  | 10000 | 8.0596 | 9.673 | 12.511
| FALSE | FALSE | GSO_129 | GSO_129 | br_09_22 | 36.0811 | -79.94 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 8571.4 | [6 empty] | 8.5714 |  |  | 8.5714 |  | 8.1428 | 0.17276 | 0.20905 | 0.26306 | 2024-01-22 04:00 |  | 7.8798 |  |  |  | 3.2306 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 686b2171-718b-454f-a63f-7a08af910b78, 066b1670-e5b9-40c9-bd97-907fe78b74e9, ca9fa130-fc7c-477e-8464-326c962a06af | A, B, C | OK |  | br_09_22 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE2 | S_nSSEE2_12.47 | 8571.4 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_09_22.A, br_09_22.B, br_09_22.C | 190 | 1 |  | 8571.4 | 14.3968 | 17.421 | 21.922
| FALSE | FALSE | GSO_13 | GSO_13 | br_018_21 | 36.1003 | -79.8075 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 5555.6 | [6 empty] | 5.5556 |  |  | 5.5556 |  | 5.2778 | 1.3096 | 1.9149 | 2.5309 | 2024-01-21 04:00 |  | 2.7469 |  |  |  | 47.9543 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 28993f84-c3b9-4382-b199-7eae1602f7b5, d4524dc1-a63b-454b-a0d9-1683a9db619b, 538bb977-c069-4a72-a1f5-79ade89be85e | A, B, C | OK |  | br_018_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE10 | S_nSSEE10_12.47 | 5555.6 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_018_21.A, br_018_21.B, br_018_21.C | 190 | 1 |  | 5555.6 | 109.1296 | 159.5763 | 210.912
| FALSE | FALSE | GSO_130 | GSO_130 | br_010_22 | 36.0811 | -79.94 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 8571.4 | [6 empty] | 8.5714 |  |  | 8.5714 |  | 8.1428 | 0.21103 | 0.24804 | 0.31823 | 2024-01-22 04:00 |  | 7.8246 |  |  |  | 3.9081 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | ec2f67d6-3e29-40e6-b3db-279de5aeb3e1, 0820aaeb-7057-4894-a6ba-7624e83ee1a7, cab2ab50-4b8d-4ecb-98f8-73c155d0b547 | A, B, C | OK |  | br_010_22 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE2 | S_nSSEE2_12.47 | 8571.4 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_010_22.A, br_010_22.B, br_010_22.C | 190 | 1 |  | 8571.4 | 17.5856 | 20.67 | 26.519
| FALSE | FALSE | GSO_131 | GSO_131 | br_011_22 | 36.0811 | -79.94 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 8571.4 | [6 empty] | 8.5714 |  |  | 8.5714 |  | 8.1428 | 0.04523 | 0.053576 | 0.073452 | 2024-01-20 18:00 |  | 8.0694 |  |  |  | 0.90205 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 434fff6c-2804-492a-a7e9-8c978d0dc8e3, 1a6f96c2-84f7-4c0d-b1a3-ee2364b2f450, 618c145a-b95c-4f8d-9e8d-9389861004d6 | A, B, C | OK |  | br_011_22 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE2 | S_nSSEE2_12.47 | 8571.4 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_011_22.A, br_011_22.B, br_011_22.C | 190 | 1 |  | 8571.4 | 3.7691 | 4.4646 | 6.121
| FALSE | FALSE | GSO_132 | GSO_132 | br_012_22 | 36.0811 | -79.94 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 8571.4 | [6 empty] | 8.5714 |  |  | 8.5714 |  | 8.1428 | 0.32331 | 0.37998 | 0.45876 | 2024-01-20 21:00 |  | 7.6841 |  |  |  | 5.6339 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 935c3854-ba34-4cf1-b241-c865be78d3bf, 0716ea38-77d5-4d34-bc24-820dc14d344a, 8eae3b99-7252-4faf-9a4e-4abe914bc30e | A, B, C | OK |  | br_012_22 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE2 | S_nSSEE2_12.47 | 8571.4 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_012_22.A, br_012_22.B, br_012_22.C | 190 | 1 |  | 8571.4 | 26.9423 | 31.6646 | 38.23
| FALSE | FALSE | GSO_133 | GSO_133 | br_013_22 | 36.0811 | -79.94 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 8571.4 | [6 empty] | 8.5714 |  |  | 8.5714 |  | 8.1428 | 0.44721 | 0.52895 | 0.6777 | 2024-01-20 11:00 |  | 7.4651 |  |  |  | 8.3227 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | dddfb629-b710-4a70-b13f-4f342bc8fe74, 4d344901-644b-4ea0-b7f1-b381d39a7879, c086c5c8-dc85-4746-8b0a-d8e23067358a | A, B, C | OK |  | br_013_22 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE2 | S_nSSEE2_12.47 | 8571.4 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_013_22.A, br_013_22.B, br_013_22.C | 190 | 1 |  | 8571.4 | 37.2676 | 44.079 | 56.475
| FALSE | FALSE | GSO_134 | GSO_134 | br_014_22 | 36.0811 | -79.94 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 8571.4 | [6 empty] | 8.5714 |  |  | 8.5714 |  | 8.1428 | 0.22056 | 0.26444 | 0.32862 | 2024-01-20 09:00 |  | 7.8142 |  |  |  | 4.0357 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 4091c3a2-55c3-4b7e-8d9d-a8e4affed314, 57c2fa84-53da-4153-9d01-3c3ac5b2144e, 7325e088-181d-4e0d-b15b-2dd1fbda83f0 | A, B, C | OK |  | br_014_22 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE2 | S_nSSEE2_12.47 | 8571.4 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_014_22.A, br_014_22.B, br_014_22.C | 190 | 1 |  | 8571.4 | 18.38 | 22.037 | 27.385
| FALSE | FALSE | GSO_135 | GSO_135 | br_015_22 | 36.0811 | -79.94 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 8571.4 | [6 empty] | 8.5714 |  |  | 8.5714 |  | 8.1428 | 0.36821 | 0.42978 | 0.52656 | 2024-01-20 23:05 |  | 7.6163 |  |  |  | 6.4665 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | c3ac0e33-1470-42fd-9a70-99015f289563, 306b628e-5350-43cc-bd44-5524b56eb0e1, cb036569-e3a3-4f9a-ab6b-ada0cfc7f7a2 | A, B, C | OK |  | br_015_22 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE2 | S_nSSEE2_12.47 | 8571.4 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_015_22.A, br_015_22.B, br_015_22.C | 190 | 1 |  | 8571.4 | 30.6842 | 35.815 | 43.88
| FALSE | FALSE | GSO_136 | GSO_136 | br_016_22 | 36.0705 | -79.9556 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 6000 | [6 empty] | 6 |  |  | 6 |  | 5.7 | 0.22044 | 0.26099 | 0.34441 | 2024-01-17 16:00 |  | 5.3556 |  |  |  | 6.0423 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 04ce7e89-fb0f-4fb3-9752-836af1c7ab9e, 1985324e-e67a-4d01-bf4e-cbc1776ba800, 66b785ca-af8e-4a6a-8af7-ff9241ec96a5 | A, B, C | OK |  | br_016_22 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE3 | S_nSSEE3_12.47 | 6000.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_016_22.A, br_016_22.B, br_016_22.C | 190 | 1 |  | 6000 | 18.3703 | 21.749 | 28.701
| FALSE | FALSE | GSO_137 | GSO_137 | br_017_22 | 36.0705 | -79.9557 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 6000 | [6 empty] | 6 |  |  | 6 |  | 5.7 | 0.21405 | 0.25138 | 0.30721 | 2024-01-20 18:00 |  | 5.3928 |  |  |  | 5.3897 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | cf094241-cd71-4a00-ae80-c341e78225f3, d0f42d15-cf63-4976-b310-0a7f21c9a7fc, bb261d99-e16f-41bf-90d2-05acc7b4f39c | A, B, C | OK |  | br_017_22 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE3 | S_nSSEE3_12.47 | 6000.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_017_22.A, br_017_22.B, br_017_22.C | 190 | 1 |  | 6000 | 17.8375 | 20.948 | 25.601
| FALSE | FALSE | GSO_138 | GSO_138 | br_018_22 | 36.0705 | -79.9556 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 6000 | [6 empty] | 6 |  |  | 6 |  | 5.7 | 0.22654 | 0.29495 | 0.38712 | 2024-01-21 04:00 |  | 5.3129 |  |  |  | 6.7916 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | c812a09e-5775-4fbc-93b7-37aa020f3a4a, b91b7108-02a6-4c8f-9294-9075747bf3d2, 8cf34f38-0fdb-4d44-9870-a7c9c5b5c3b4 | A, B, C | OK |  | br_018_22 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE3 | S_nSSEE3_12.47 | 6000.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_018_22.A, br_018_22.B, br_018_22.C | 190 | 1 |  | 6000 | 18.878 | 24.579 | 32.26
| FALSE | FALSE | GSO_139 | GSO_139 | br_019_22 | 36.0705 | -79.9557 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 6000 | [6 empty] | 6 |  |  | 6 |  | 5.7 | 0.30302 | 0.3653 | 0.50093 | 2024-01-21 04:00 |  | 5.1991 |  |  |  | 8.7882 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 8781de87-205d-4b90-963f-449d72c41e8c, 2a67f2a3-ad9e-4413-af20-999870d5694e, 6ec0fb64-8f9d-48b6-81ae-63048adca78a | A, B, C | OK |  | br_019_22 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE3 | S_nSSEE3_12.47 | 6000.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_019_22.A, br_019_22.B, br_019_22.C | 190 | 1 |  | 6000 | 25.2516 | 30.442 | 41.744
| FALSE | FALSE | GSO_14 | GSO_14 | br_019_21 | 36.1003 | -79.8075 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 5555.6 | [6 empty] | 5.5556 |  |  | 5.5556 |  | 5.2778 | 1.403 | 2.0384 | 2.6885 | 2024-01-21 04:00 |  | 2.5893 |  |  |  | 50.9392 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 9df35035-201c-43e2-9c0f-29f5652d20b6, 4f0a9de3-7d5d-4d74-841a-ad368a655ddc, 37a8aff5-f4d5-48d1-b094-f7ff7add641f | A, B, C | OK |  | br_019_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE10 | S_nSSEE10_12.47 | 5555.6 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_019_21.A, br_019_21.B, br_019_21.C | 190 | 1 |  | 5555.6 | 116.9126 | 169.864 | 224.04
| FALSE | FALSE | GSO_140 | GSO_140 | br_020_22 | 36.0705 | -79.9556 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 6000 | [6 empty] | 6 |  |  | 6 |  | 5.7 | 0.20816 | 0.2472 | 0.30924 | 2024-07-15 20:00 |  | 5.3908 |  |  |  | 5.4253 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | b6e43aeb-290f-443d-917c-933a0af02698, 7ac282db-535a-4cda-bcc4-f62230cc0be1, 52cf19cb-d2f9-48a0-a5d7-3d345a429c59 | A, B, C | OK |  | br_020_22 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE3 | S_nSSEE3_12.47 | 6000.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_020_22.A, br_020_22.B, br_020_22.C | 190 | 1 |  | 6000 | 17.3466 | 20.6 | 25.77
| FALSE | FALSE | GSO_141 | GSO_141 | br_021_22 | 36.0459 | -79.947 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 12000 | [6 empty] | 12 |  |  | 12 |  | 11.4 | 0.23482 | 0.29074 | 0.37996 | 2024-01-21 01:00 |  | 11.02 |  |  |  | 3.3329 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 78f844cc-a5b4-4d9d-ba33-ef854d68bc8a, b6f787f7-5117-4b48-81f4-ddbe099f96d7, 0b5869b0-b194-4a18-8593-e04336ade6ea | A, B, C | OK |  | br_021_22 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE4 | S_nSSEE4_12.47 | 12000.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_021_22.A, br_021_22.B, br_021_22.C | 190 | 1 |  | 12000 | 19.5682 | 24.2286 | 31.663
| FALSE | FALSE | GSO_142 | GSO_142 | br_022_22 | 36.0459 | -79.947 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 12000 | [6 empty] | 12 |  |  | 12 |  | 11.4 | 0.52512 | 0.62478 | 0.79259 | 2024-07-09 |  | 10.6074 |  |  |  | 6.9525 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 5c50320a-6541-43e1-a0eb-b3cc85335f92, d8586197-7e6c-42e3-af81-89d0f76301f9, aeed6de5-7aca-4fa3-a5ca-b1f32ee717c2 | A, B, C | OK |  | br_022_22 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE4 | S_nSSEE4_12.47 | 12000.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_022_22.A, br_022_22.B, br_022_22.C | 190 | 1 |  | 12000 | 43.7603 | 52.0646 | 66.049
| FALSE | FALSE | GSO_143 | GSO_143 | br_023_22 | 36.0459 | -79.947 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 12000 | [6 empty] | 12 |  |  | 12 |  | 11.4 | 1.249 | 1.8959 | 2.5408 | 2024-01-21 04:00 |  | 8.8592 |  |  |  | 22.2874 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | b2362459-63fa-42c8-b75d-cdff666f2190, 15ee4200-f93f-4884-ab81-e52eb3d0b73c, ef7cab0d-e432-4fb1-aab4-46e5068286b4 | A, B, C | OK |  | br_023_22 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE4 | S_nSSEE4_12.47 | 12000.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_023_22.A, br_023_22.B, br_023_22.C | 190 | 1 |  | 12000 | 104.0809 | 157.9957 | 211.73
| FALSE | FALSE | GSO_144 | GSO_144 | br_024_22 | 36.046 | -79.947 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 12000 | [6 empty] | 12 |  |  | 12 |  | 11.4 | 0.057412 | 0.090084 | 0.13286 | 2024-01-20 21:00 |  | 11.2671 |  |  |  | 1.1655 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | cebe0434-4e95-4fd2-8e1e-22573f21abf5, bd7e1df8-2eb1-4167-bee8-930536ce0573, 82536324-6f01-4e66-a011-7b067544a9ac | A, B, C | OK |  | br_024_22 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE4 | S_nSSEE4_12.47 | 12000.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_024_22.A, br_024_22.B, br_024_22.C | 190 | 1 |  | 12000 | 4.7843 | 7.507 | 11.072
| FALSE | FALSE | GSO_145 | GSO_145 | br_025_22 | 36.046 | -79.947 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 12000 | [6 empty] | 12 |  |  | 12 |  | 11.4 | 0.4405 | 0.56032 | 0.73442 | 2024-01-21 04:00 |  | 10.6656 |  |  |  | 6.4423 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | e8f52edb-11b6-4a01-8cb4-dde6abb481d7, 5042bbb0-cc21-499d-9106-09bd8c86b439, 039cb766-152c-4467-9ec0-94180921a657 | A, B, C | OK |  | br_025_22 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE4 | S_nSSEE4_12.47 | 12000.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_025_22.A, br_025_22.B, br_025_22.C | 190 | 1 |  | 12000 | 36.7087 | 46.6936 | 61.202
| FALSE | FALSE | GSO_146 | GSO_146 | br_026_22 | 36.114 | -79.9604 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 7500 | [6 empty] | 7.5 |  |  | 7.5 |  | 7.125 | 0.5382 | 0.72909 | 0.97618 | 2024-01-21 04:00 |  | 6.1488 |  |  |  | 13.7007 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 45141e3c-ee87-445b-a8cd-53eaf3cf8ac6, d4d03355-620e-4213-a24e-266e873f3f79, 9c3aa61d-fdd8-4e3a-a859-786b34331466 | A, B, C | OK |  | br_026_22 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE5 | S_nSSEE5_12.47 | 7500.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_026_22.A, br_026_22.B, br_026_22.C | 190 | 1 |  | 7500 | 44.8504 | 60.7569 | 81.348
| FALSE | FALSE | GSO_147 | GSO_147 | br_027_22 | 36.114 | -79.9604 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 7500 | [6 empty] | 7.5 |  |  | 7.5 |  | 7.125 | 0.16253 | 0.21618 | 0.29234 | 2024-01-21 04:00 |  | 6.8327 |  |  |  | 4.1031 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 783419bf-1c8f-4783-a364-729c4d25328a, b05dca4b-f167-46ba-b479-77fc9d306c98, a6c68db1-932a-455f-9961-2001628d137a | A, B, C | OK |  | br_027_22 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE5 | S_nSSEE5_12.47 | 7500.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_027_22.A, br_027_22.B, br_027_22.C | 190 | 1 |  | 7500 | 13.544 | 18.0146 | 24.362
| FALSE | FALSE | GSO_148 | GSO_148 | br_028_22 | 36.114 | -79.9604 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 7500 | [6 empty] | 7.5 |  |  | 7.5 |  | 7.125 | 0.29922 | 0.37366 | 0.49594 | 2024-01-21 01:00 |  | 6.6291 |  |  |  | 6.9605 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | f209db33-c63a-4eeb-9470-44a070b1f980, e51bd3d2-27db-4e8c-85b3-94bb36fdecb2, 9cb02ef5-7d31-4690-b5cc-1c8ff7465b94 | A, B, C | OK |  | br_028_22 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE5 | S_nSSEE5_12.47 | 7500.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_028_22.A, br_028_22.B, br_028_22.C | 190 | 1 |  | 7500 | 24.9351 | 31.138 | 41.328
| FALSE | FALSE | GSO_149 | GSO_149 | br_029_22 | 36.114 | -79.9604 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 7500 | [6 empty] | 7.5 |  |  | 7.5 |  | 7.125 | 0.056658 | 0.069716 | 0.091644 | 2024-01-17 05:00 |  | 7.0334 |  |  |  | 1.2862 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 54f22dd6-dae8-4d6f-8c00-4ee16cc1bce1, a7d55959-39f6-4006-8a75-2ac4375060d6, 22ef08a2-8b87-47bf-912f-a49f8dbe4e0e | A, B, C | OK |  | br_029_22 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE5 | S_nSSEE5_12.47 | 7500.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_029_22.A, br_029_22.B, br_029_22.C | 190 | 1 |  | 7500 | 4.7215 | 5.8096 | 7.637
| FALSE | FALSE | GSO_15 | GSO_15 | br_020_21 | 36.1003 | -79.8075 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 5555.6 | [6 empty] | 5.5556 |  |  | 5.5556 |  | 5.2778 | 1.6994 | 2.5284 | 3.3588 | 2024-01-21 04:00 |  | 1.919 |  |  |  | 63.6399 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 2dfc9022-cd2d-4071-a0ed-f7aa4dbf29b5, 34fb9785-294c-4580-94c1-92b57cb0e642, dd9e89fb-3f9a-4966-a494-c19ab9432a67 | A, B, C | OK |  | br_020_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE10 | S_nSSEE10_12.47 | 5555.6 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_020_21.A, br_020_21.B, br_020_21.C | 190 | 1 |  | 5555.6 | 141.6145 | 210.703 | 279.9
| FALSE | FALSE | GSO_150 | GSO_150 | br_030_22 | 36.0823 | -79.9238 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 6000 | [6 empty] | 6 |  |  | 6 |  | 5.7 | 0.13007 | 0.15808 | 0.22006 | 2024-01-20 11:00 |  | 5.4799 |  |  |  | 3.8606 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 99ca8035-36a9-410b-844c-06c1ddb4c66b, 97ae36fa-2e65-4c6d-8a11-b6c4ba921c0d, e18873a3-19e0-4c86-abaf-03f1ea49ef98 | A, B, C | OK |  | br_030_22 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE6 | S_nSSEE6_12.47 | 6000.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_030_22.A, br_030_22.B, br_030_22.C | 190 | 1 |  | 6000 | 10.8391 | 13.173 | 18.338
| FALSE | FALSE | GSO_151 | GSO_151 | br_031_22 | 36.0823 | -79.9238 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 6000 | [6 empty] | 6 |  |  | 6 |  | 5.7 | 0.42541 | 0.54888 | 0.73038 | 2024-01-21 04:00 |  | 4.9696 |  |  |  | 12.8137 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 5b53a681-1338-4fee-9587-71b3e65506cb, 051f7584-2010-41f8-9415-9183657a8ae0, 0542d836-ab02-49aa-a8b7-a4265443a1c4 | A, B, C | OK |  | br_031_22 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE6 | S_nSSEE6_12.47 | 6000.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_031_22.A, br_031_22.B, br_031_22.C | 190 | 1 |  | 6000 | 35.4508 | 45.74 | 60.865
| FALSE | FALSE | GSO_152 | GSO_152 | br_032_22 | 36.0823 | -79.9238 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 6000 | [6 empty] | 6 |  |  | 6 |  | 5.7 | 0.012 | 0.01728 | 0.0261 | 2024-01-20 16:00 |  | 5.6739 |  |  |  | 0.45789 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 3f75484a-66ad-416b-bdfc-429bf783f99d, ab723fc3-e0cb-4dbc-8181-5681e5ac3348, 3b38bb39-6b77-49e7-b0c7-d3c699da74dc | A, B, C | OK |  | br_032_22 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE6 | S_nSSEE6_12.47 | 6000.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_032_22.A, br_032_22.B, br_032_22.C | 190 | 1 |  | 6000 | 0.99999 | 1.44 | 2.175
| FALSE | FALSE | GSO_153 | GSO_153 | br_033_22 | 36.0823 | -79.9238 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 6000 | [6 empty] | 6 |  |  | 6 |  | 5.7 | 0.59934 | 0.69708 | 0.84121 | 2024-07-15 10:00 |  | 4.8588 |  |  |  | 14.7581 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 0d3f8e19-033b-4d8c-a34b-ff04747bd082, 5e1ed7ac-1e16-4c51-bb12-e8d8b8c244c4, 07ea0bf7-442d-4e77-b98a-b9e2c8d50114 | A, B, C | OK |  | br_033_22 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE6 | S_nSSEE6_12.47 | 6000.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_033_22.A, br_033_22.B, br_033_22.C | 190 | 1 |  | 6000 | 49.9449 | 58.09 | 70.101
| FALSE | FALSE | GSO_154 | GSO_154 | br_034_22 | 36.0823 | -79.9238 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 6000 | [6 empty] | 6 |  |  | 6 |  | 5.7 | 0.16112 | 0.19657 | 0.26084 | 2024-01-21 04:00 |  | 5.4392 |  |  |  | 4.5762 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 6eba73e4-418d-4cd1-96b6-60b826ae450c, 70369b74-10d7-4556-af26-c0ccb8f01935, 0840b23d-66b0-48cf-856c-1f62526c7d6e | A, B, C | OK |  | br_034_22 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE6 | S_nSSEE6_12.47 | 6000.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_034_22.A, br_034_22.B, br_034_22.C | 190 | 1 |  | 6000 | 13.4266 | 16.381 | 21.737
| FALSE | FALSE | GSO_155 | GSO_155 | br_01_23 | 36.1928 | -79.6069 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 7500 | [6 empty] | 7.5 |  |  | 7.5 |  | 7.125 | 0.64645 | 0.94631 | 1.2782 | 2024-01-21 04:00 |  | 5.8468 |  |  |  | 17.9392 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 033ba35a-0e88-44c7-ae68-9ef721532ab3, ecb9c3ef-513f-492a-821c-4bff92c1df9c, d1e45bf7-a00b-40dc-a6ec-c751080a13c9 | A, B, C | OK |  | br_01_23 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE0 | S_nSSEE0_12.47 | 7500.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_01_23.A, br_01_23.B, br_01_23.C | 190 | 1 |  | 7500 | 53.8705 | 78.859 | 106.514
| FALSE | FALSE | GSO_156 | GSO_156 | br_02_23 | 36.1929 | -79.6068 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 7500 | [6 empty] | 7.5 |  |  | 7.5 |  | 7.125 | 1.5909 | 2.3544 | 3.0797 | 2024-01-21 04:00 |  | 4.0453 |  |  |  | 43.2239 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 2ec12710-cbb3-4ac0-ae81-f21bc775b59d, 17343a92-f390-4c00-96dd-aa4c8e6f2cf5, 12b55d36-db8c-475f-838b-08caf84b6421 | A, B, C | OK |  | br_02_23 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE0 | S_nSSEE0_12.47 | 7500.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_02_23.A, br_02_23.B, br_02_23.C | 190 | 1 |  | 7500 | 132.5721 | 196.1993 | 256.642
| FALSE | FALSE | GSO_157 | GSO_157 | br_03_23 | 36.1929 | -79.6068 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 7500 | [6 empty] | 7.5 |  |  | 7.5 |  | 7.125 | 1.4377 | 2.1269 | 2.889 | 2024-01-21 04:00 |  | 4.236 |  |  |  | 40.5472 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | d76a1565-b995-4235-9508-12ae427ed548, b96622f9-34da-4d3a-a144-a82c9e2d84a9, 962e5ace-7f13-49d9-a1bd-65973f2adfac | A, B, C | OK |  | br_03_23 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE0 | S_nSSEE0_12.47 | 7500.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_03_23.A, br_03_23.B, br_03_23.C | 190 | 1 |  | 7500 | 119.8044 | 177.2403 | 240.749
| FALSE | FALSE | GSO_158 | GSO_158 | br_04_23 | 36.1929 | -79.6068 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 7500 | [6 empty] | 7.5 |  |  | 7.5 |  | 7.125 | 1.3735 | 2.0512 | 2.6914 | 2024-01-20 21:00 |  | 4.4336 |  |  |  | 37.7736 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 8e1d3060-4f17-4027-bb48-9326d72d1f5e, b84e6ee7-bc4b-467a-884d-e5dac0fbac0b, 5320e9a7-8d71-4f75-b9c9-3a6a37f707db | A, B, C | OK |  | br_04_23 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE0 | S_nSSEE0_12.47 | 7500.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_04_23.A, br_04_23.B, br_04_23.C | 190 | 1 |  | 7500 | 114.4589 | 170.9293 | 224.281
| FALSE | FALSE | GSO_159 | GSO_159 | br_05_23 | 36.2604 | -79.5886 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 5714.3 | [6 empty] | 5.7143 |  |  | 5.7143 |  | 5.4286 | 1.722 | 2.5527 | 3.469 | 2024-01-21 04:00 |  | 1.9596 |  |  |  | 63.9024 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 83f2cd36-180e-4d9a-9105-62a32f68ab85, 96fae847-ae01-4905-9884-47b324a88934, 2e882994-3bef-4961-988c-cd677efd6410 | A, B, C | OK |  | br_05_23 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE1 | S_nSSEE1_12.47 | 5714.3 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_05_23.A, br_05_23.B, br_05_23.C | 190 | 1 |  | 5714.3 | 143.5038 | 212.7262 | 289.083
| FALSE | FALSE | GSO_16 | GSO_16 | br_021_21 | 36.1003 | -79.8075 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 5555.6 | [6 empty] | 5.5556 |  |  | 5.5556 |  | 5.2778 | 0.91765 | 1.2917 | 1.7095 | 2024-01-21 |  | 3.5683 |  |  |  | 32.39 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | e4f24c66-81cd-48f4-b9a3-a8aaa9fe8c98, b5d738a6-79bd-43f6-b4e4-0fb4de70abfd, 2b3c0835-4f9e-453c-86b3-35847ab5af94 | A, B, C | OK |  | br_021_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE10 | S_nSSEE10_12.47 | 5555.6 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_021_21.A, br_021_21.B, br_021_21.C | 190 | 1 |  | 5555.6 | 76.4704 | 107.642 | 142.457
| FALSE | FALSE | GSO_160 | GSO_160 | br_06_23 | 36.2604 | -79.5886 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 5714.3 | [6 empty] | 5.7143 |  |  | 5.7143 |  | 5.4286 | 2.3408 | 3.4652 | 4.6476 | 2024-01-21 04:00 |  | 0.78094 |  |  |  | 85.6144 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | b9360429-edfb-4e59-a900-8a457dc83cba, c3e81296-2c1a-4ada-80c1-b847107d5cfb, 47f0ee8f-4288-4af4-b69a-10cebf43b645 | A, B, C | OK |  | br_06_23 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE1 | S_nSSEE1_12.47 | 5714.3 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_06_23.A, br_06_23.B, br_06_23.C | 190 | 1 |  | 5714.3 | 195.0631 | 288.77 | 387.304
| FALSE | FALSE | GSO_161 | GSO_161 | br_07_23 | 36.2604 | -79.5886 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 5714.3 | [6 empty] | 5.7143 |  |  | 5.7143 |  | 5.4286 | 0.028877 | 0.044532 | 0.06714 | 2024-01-20 21:00 |  | 5.3614 |  |  |  | 1.2368 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 89a3b24a-887f-4195-8344-51f18a00dbf7, c4eee589-eb1d-4947-bc9b-3f547ec858d4, e61fb2d3-e704-4d3f-bf86-8b04c3724fd7 | A, B, C | OK |  | br_07_23 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE1 | S_nSSEE1_12.47 | 5714.3 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_07_23.A, br_07_23.B, br_07_23.C | 190 | 1 |  | 5714.3 | 2.4064 | 3.711 | 5.595
| FALSE | FALSE | GSO_162 | GSO_162 | br_08_23 | 36.1644 | -79.7079 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 8000 | [6 empty] | 8 |  |  | 8 |  | 7.6 | 0.50804 | 0.75386 | 1.0057 | 2024-01-20 23:00 |  | 6.5943 |  |  |  | 13.2327 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | f620b838-2134-4f66-a112-15e5f46318b0, f4ffa257-f9a9-48e6-8ef7-945f8e687e83, 4bfd3a0a-1178-4983-b63c-76c387206a99 | A, B, C | OK |  | br_08_23 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE2 | S_nSSEE2_12.47 | 8000.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_08_23.A, br_08_23.B, br_08_23.C | 190 | 1 |  | 8000 | 42.3363 | 62.8216 | 83.807
| FALSE | FALSE | GSO_163 | GSO_163 | br_09_23 | 36.1644 | -79.708 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 8000 | [6 empty] | 8 |  |  | 8 |  | 7.6 | 1.6046 | 2.3743 | 3.1708 | 2024-01-18 04:00 |  | 4.4292 |  |  |  | 41.7216 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | d90170cc-5eec-43f7-a5d9-cb91dca851cb, 9018e821-338d-4aa5-bb0d-3e9aa19f5a3b, 0d2e0f05-d1e8-46f2-953d-daf9b517d3b5 | A, B, C | OK |  | br_09_23 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE2 | S_nSSEE2_12.47 | 8000.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_09_23.A, br_09_23.B, br_09_23.C | 190 | 1 |  | 8000 | 133.7168 | 197.8567 | 264.237
| FALSE | FALSE | GSO_17 | GSO_17 | br_024_21 | 36.0264 | -79.8286 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 13333.3 | [6 empty] | 13.3333 |  |  | 13.3333 |  | 12.6666 | 1.8182 | 2.6953 | 3.5366 | 2024-01-21 04:05 |  | 9.1301 |  |  |  | 27.9204 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 3a2af09c-baa8-4dbe-95ab-fb397036b19d, 883c59a4-ab46-45e2-b36d-e1959b7c89b6, f0a67506-31bf-4b47-9614-f559c928646a | A, B, C | OK |  | br_024_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE11 | S_nSSEE11_12.47 | 13333.3 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_024_21.A, br_024_21.B, br_024_21.C | 190 | 1 |  | 13333.3 | 151.5207 | 224.6077 | 294.715
| FALSE | FALSE | GSO_18 | GSO_18 | br_025_21 | 36.0264 | -79.8286 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 13333.3 | [6 empty] | 13.3333 |  |  | 13.3333 |  | 12.6666 | 1.1891 | 1.713 | 2.2897 | 2024-01-21 |  | 10.3769 |  |  |  | 18.0768 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 34cac5e4-313a-4454-a92d-abc9047eadc8, 90d3f27c-2599-462f-8abb-58371a03ece5, 08eb7b30-b593-4a81-854f-d7a00d46db1e | A, B, C | OK |  | br_025_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE11 | S_nSSEE11_12.47 | 13333.3 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_025_21.A, br_025_21.B, br_025_21.C | 190 | 1 |  | 13333.3 | 99.0903 | 142.754 | 190.81
| FALSE | FALSE | GSO_19 | GSO_19 | br_026_21 | 36.0264 | -79.8286 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 13333.3 | [6 empty] | 13.3333 |  |  | 13.3333 |  | 12.6666 | 2.5101 | 3.8361 | 5.1626 | 2024-01-18 04:00 |  | 7.504 |  |  |  | 40.7575 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | d5920248-7472-436e-b060-c7c2ff9ef29d, cf54e8e6-a9a5-4011-b2be-1226fbdc86cb, a03bc8be-0c7b-4ca4-b625-79f7823155e9 | A, B, C | OK |  | br_026_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE11 | S_nSSEE11_12.47 | 13333.3 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_026_21.A, br_026_21.B, br_026_21.C | 190 | 1 |  | 13333.3 | 209.1713 | 319.6785 | 430.217
| FALSE | FALSE | GSO_2 | GSO_2 | br_02_21 | 36.0852 | -79.8827 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 5714.3 | [6 empty] | 5.7143 |  |  | 5.7143 |  | 5.4286 | 1.2027 | 1.7331 | 2.2932 | 2024-01-20 08:10 |  | 3.1354 |  |  |  | 42.2426 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | e16fe26a-3331-4e10-bcda-3d5b4cfc42bc, f5b81547-937f-4c70-92ba-8a0fb6594394, a28c1752-7f45-48c2-b058-b7cdc091e5d6 | A, B, C | OK |  | br_02_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE0 | S_nSSEE0_12.47 | 5714.3 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_02_21.A, br_02_21.B, br_02_21.C | 190 | 1 |  | 5714.3 | 100.2277 | 144.422 | 191.098
| FALSE | FALSE | GSO_20 | GSO_20 | br_027_21 | 36.0604 | -79.8599 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 3750 | [6 empty] | 3.75 |  |  | 3.75 |  | 3.5625 | 0.0032747 | 0.004752 | 0.007668 | 2024-07-10 19:00 |  | 3.5548 |  |  |  | 0.21524 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 0367f0a8-b7e5-4ca5-94ae-d44fa9d00bfd, a602edca-8fde-46f7-8d51-40a5f85d6a1d, c9015052-da74-4877-bbf1-9a6c4275c44d | A, B, C | OK |  | br_027_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE12 | S_nSSEE12_12.47 | 3750.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_027_21.A, br_027_21.B, br_027_21.C | 190 | 1 |  | 3750 | 0.27289 | 0.396 | 0.639
| FALSE | FALSE | GSO_21 | GSO_21 | br_028_21 | 36.0604 | -79.8599 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 3750 | [6 empty] | 3.75 |  |  | 3.75 |  | 3.5625 | 0.9294 | 1.2838 | 1.6817 | 2024-01-18 04:00 |  | 1.8808 |  |  |  | 47.2064 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 6f7a2c02-ca5d-4d73-a76d-82f0fe3158c9, 39b0a939-9afe-4c84-bfda-5eec318bc35e, a49c303e-bacd-45af-8754-babfb2545a48 | A, B, C | OK |  | br_028_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE12 | S_nSSEE12_12.47 | 3750.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_028_21.A, br_028_21.B, br_028_21.C | 190 | 1 |  | 3750 | 77.4498 | 106.98 | 140.144
| FALSE | FALSE | GSO_22 | GSO_22 | br_029_21 | 36.0604 | -79.8599 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 3750 | [6 empty] | 3.75 |  |  | 3.75 |  | 3.5625 | 0.94167 | 1.3475 | 1.7494 | 2024-01-18 04:00 |  | 1.8131 |  |  |  | 49.1055 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | f1fcda72-2c9e-4219-9a68-e344865344e1, c13495f3-7436-4771-9d8e-028fe398e677, 60e175bd-dd8d-424f-b541-e6c27675c2ee | A, B, C | OK |  | br_029_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE12 | S_nSSEE12_12.47 | 3750.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_029_21.A, br_029_21.B, br_029_21.C | 190 | 1 |  | 3750 | 78.4727 | 112.2883 | 145.782
| FALSE | FALSE | GSO_23 | GSO_23 | br_030_21 | 36.0604 | -79.8599 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 3750 | [6 empty] | 3.75 |  |  | 3.75 |  | 3.5625 | 0.63701 | 0.87494 | 1.1484 | 2024-01-18 04:00 |  | 2.4141 |  |  |  | 32.2365 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 73114768-3396-46b2-8366-027d7f330c2a, 8896d2cc-f5f3-479a-9806-74f9830d0e65, 306a0179-6b1d-4c84-b7ad-c043978706f4 | A, B, C | OK |  | br_030_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE12 | S_nSSEE12_12.47 | 3750.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_030_21.A, br_030_21.B, br_030_21.C | 190 | 1 |  | 3750 | 53.0838 | 72.912 | 95.702
| FALSE | FALSE | GSO_24 | GSO_24 | br_031_21 | 36.0603 | -79.8599 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 3750 | [6 empty] | 3.75 |  |  | 3.75 |  | 3.5625 | 0.042273 | 0.050748 | 0.067452 | 2024-01-20 16:00 |  | 3.495 |  |  |  | 1.8934 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 8866ae0d-1645-4e1d-85a9-520a2b057093, 0e740376-b7d0-46f1-8238-50979ff53b86, 3abd341d-8629-4be0-888c-4405cbd18a68 | A, B, C | OK |  | br_031_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE12 | S_nSSEE12_12.47 | 3750.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_031_21.A, br_031_21.B, br_031_21.C | 190 | 1 |  | 3750 | 3.5228 | 4.229 | 5.621
| FALSE | FALSE | GSO_25 | GSO_25 | br_032_21 | 36.0603 | -79.8599 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 3750 | [6 empty] | 3.75 |  |  | 3.75 |  | 3.5625 | 0.406 | 0.49246 | 0.62447 | 2024-01-21 04:00 |  | 2.938 |  |  |  | 17.5289 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 8c0cf450-9297-450e-b468-8396988be79f, d4f80b32-222c-49ea-bb38-81080bcb0826, 6a2617f0-409e-448d-8ce4-c1175edcf36a | A, B, C | OK |  | br_032_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE12 | S_nSSEE12_12.47 | 3750.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_032_21.A, br_032_21.B, br_032_21.C | 190 | 1 |  | 3750 | 33.8332 | 41.038 | 52.039
| FALSE | FALSE | GSO_26 | GSO_26 | br_033_21 | 36.0603 | -79.8599 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 3750 | [6 empty] | 3.75 |  |  | 3.75 |  | 3.5625 | 1.0473 | 1.4436 | 1.89 | 2024-01-21 04:00 |  | 1.6725 |  |  |  | 53.054 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 2ded452d-d964-456f-bc61-891c5e02102b, 123d2e0f-6c7b-4b17-96d2-32d4328dde67, 06410d93-c578-4f9d-86d8-8eb333ba28c9 | A, B, C | OK |  | br_033_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE12 | S_nSSEE12_12.47 | 3750.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_033_21.A, br_033_21.B, br_033_21.C | 190 | 1 |  | 3750 | 87.2755 | 120.2986 | 157.504
| FALSE | FALSE | GSO_27 | GSO_27 | br_034_21 | 36.0604 | -79.8599 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 3750 | [6 empty] | 3.75 |  |  | 3.75 |  | 3.5625 | 1.2479 | 1.7988 | 2.4046 | 2024-01-21 04:00 |  | 1.1579 |  |  |  | 67.4968 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 6fdd1896-ad74-48a8-9816-85aa01d652d1, d428eae8-d228-4f79-b9ea-91e3a88bb229, 9dbd0f33-80b1-4155-96b0-ea2e0658e691 | A, B, C | OK |  | br_034_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE12 | S_nSSEE12_12.47 | 3750.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_034_21.A, br_034_21.B, br_034_21.C | 190 | 1 |  | 3750 | 103.9897 | 149.897 | 200.381
| FALSE | FALSE | GSO_28 | GSO_28 | br_035_21 | 36.1038 | -79.7639 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 7500 | [6 empty] | 7.5 |  |  | 7.5 |  | 7.125 | 0.062273 | 0.079944 | 0.11803 | 2024-01-20 11:00 |  | 7.007 |  |  |  | 1.6566 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | c3250712-a026-44dc-83b1-ab0b7bd1cef0, 4cc07d73-767d-4a92-aa56-8d6f6139433c, 4b1de06e-7ccd-42bd-ba7d-141a0d6eed10 | A, B, C | OK |  | br_035_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE13 | S_nSSEE13_12.47 | 7500.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_035_21.A, br_035_21.B, br_035_21.C | 190 | 1 |  | 7500 | 5.1894 | 6.662 | 9.836
| FALSE | FALSE | GSO_29 | GSO_29 | br_036_21 | 36.1038 | -79.7639 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 7500 | [6 empty] | 7.5 |  |  | 7.5 |  | 7.125 | 1.0643 | 1.5256 | 1.9875 | 2024-01-20 05:00 |  | 5.1375 |  |  |  | 27.8944 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 53ac9d88-ec7e-422c-9547-7b65d0e1b05c, bbdb1c8c-b61b-4af3-a00d-d34e99f936e8, 37be8bbe-3fc1-42ac-aa14-512831f011d9 | A, B, C | OK |  | br_036_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE13 | S_nSSEE13_12.47 | 7500.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_036_21.A, br_036_21.B, br_036_21.C | 190 | 1 |  | 7500 | 88.6911 | 127.1367 | 165.623
| FALSE | FALSE | GSO_3 | GSO_3 | br_03_21 | 36.0852 | -79.8826 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 5714.3 | [6 empty] | 5.7143 |  |  | 5.7143 |  | 5.4286 | 0.014119 | 0.021876 | 0.038244 | 2024-07-15 08:00 |  | 5.3903 |  |  |  | 0.70449 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | cabb02b4-86e3-4261-87ef-66f06902bb61, 262d1506-d23e-42d2-a938-f15cb2f35365, 861d3fe8-4f6d-46b5-bb00-6d79ddaf889d | A, B, C | OK |  | br_03_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE0 | S_nSSEE0_12.47 | 5714.3 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_03_21.A, br_03_21.B, br_03_21.C | 190 | 1 |  | 5714.3 | 1.1766 | 1.823 | 3.187
| FALSE | FALSE | GSO_30 | GSO_30 | br_037_21 | 36.1038 | -79.7639 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 7500 | [6 empty] | 7.5 |  |  | 7.5 |  | 7.125 | 0.94227 | 1.3691 | 1.8068 | 2024-01-20 09:05 |  | 5.3182 |  |  |  | 25.3585 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 80a38063-4b58-4c05-9631-c9f20eaae49f, 07afe75d-2efa-4a63-8500-f5eed954ebc4, 4339844d-f7f4-4af5-a7ce-ff1e206a4bfc | A, B, C | OK |  | br_037_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE13 | S_nSSEE13_12.47 | 7500.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_037_21.A, br_037_21.B, br_037_21.C | 190 | 1 |  | 7500 | 78.5223 | 114.0916 | 150.566
| FALSE | FALSE | GSO_31 | GSO_31 | br_038_21 | 36.1038 | -79.7639 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 7500 | [6 empty] | 7.5 |  |  | 7.5 |  | 7.125 | 0.014254 | 0.022212 | 0.036228 | 2024-07-15 08:00 |  | 7.0888 |  |  |  | 0.50846 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | dbd51660-93ed-49dc-b484-ac1a2ff93751, c4bbbd0b-e3cc-4312-b11b-48dca067f34f, f5f51af7-9112-4286-adaa-37e4589d054a | A, B, C | OK |  | br_038_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE13 | S_nSSEE13_12.47 | 7500.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_038_21.A, br_038_21.B, br_038_21.C | 190 | 1 |  | 7500 | 1.1878 | 1.851 | 3.019
| FALSE | FALSE | GSO_32 | GSO_32 | br_039_21 | 36.0466 | -79.7995 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 6666.7 | [6 empty] | 6.6667 |  |  | 6.6667 |  | 6.3334 | 0.70222 | 0.94806 | 1.2177 | 2024-01-21 |  | 5.1157 |  |  |  | 19.2262 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 049d0b94-e086-4825-b104-d454ffd3dc7c, 81e832b4-cd01-4844-b4d8-6ff81d95dbe4, 934aabc4-8b42-44e6-82dc-1b3261dc29d9 | A, B, C | OK |  | br_039_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE14 | S_nSSEE14_12.47 | 6666.7 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_039_21.A, br_039_21.B, br_039_21.C | 190 | 1 |  | 6666.7 | 58.5184 | 79.0046 | 101.472
| FALSE | FALSE | GSO_33 | GSO_33 | br_040_21 | 36.0466 | -79.7995 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 6666.7 | [6 empty] | 6.6667 |  |  | 6.6667 |  | 6.3334 | 0.5803 | 0.70153 | 0.88399 | 2024-01-20 15:00 |  | 5.4494 |  |  |  | 13.9577 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | ee1a565e-ae8b-4984-9f7a-cab15b5447c3, 2bcc2cc5-82f5-4040-ac32-a00d0d07de51, d858a33a-1b66-4073-aed2-4b1a30ad837b | A, B, C | OK |  | br_040_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE14 | S_nSSEE14_12.47 | 6666.7 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_040_21.A, br_040_21.B, br_040_21.C | 190 | 1 |  | 6666.7 | 48.3582 | 58.461 | 73.666
| FALSE | FALSE | GSO_34 | GSO_34 | br_041_21 | 36.0466 | -79.7995 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 6666.7 | [6 empty] | 6.6667 |  |  | 6.6667 |  | 6.3334 | 1.1591 | 1.6717 | 2.2167 | 2024-01-18 04:00 |  | 4.1167 |  |  |  | 35.0005 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | deb58541-2cca-43d5-86c5-55264c6041d3, 179024ab-8e49-42be-b943-761705fb5abd, 0cbf9200-98b4-43c7-934d-2cc30d8ab63b | A, B, C | OK |  | br_041_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE14 | S_nSSEE14_12.47 | 6666.7 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_041_21.A, br_041_21.B, br_041_21.C | 190 | 1 |  | 6666.7 | 96.588 | 139.3106 | 184.726
| FALSE | FALSE | GSO_35 | GSO_35 | br_042_21 | 36.0466 | -79.7995 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 6666.7 | [6 empty] | 6.6667 |  |  | 6.6667 |  | 6.3334 | 1.7539 | 2.6524 | 3.5443 | 2024-01-21 00:05 |  | 2.789 |  |  |  | 55.9627 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | efc37dec-e402-4c7d-81af-aa9cb2729757, d7ccdfd6-6a7d-4338-9666-e79b11f003a9, 6d4ede07-2601-4246-903b-56124df12172 | A, B, C | OK |  | br_042_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE14 | S_nSSEE14_12.47 | 6666.7 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_042_21.A, br_042_21.B, br_042_21.C | 190 | 1 |  | 6666.7 | 146.1585 | 221.035 | 295.36
| FALSE | FALSE | GSO_36 | GSO_36 | br_043_21 | 36.0466 | -79.7995 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 6666.7 | [6 empty] | 6.6667 |  |  | 6.6667 |  | 6.3334 | 0.34312 | 0.40406 | 0.4952 | 2024-01-20 05:00 |  | 5.8382 |  |  |  | 7.819 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | a492b914-7377-4047-b30b-90aa78dc94d3, c95edbeb-bfcc-48be-abeb-7c6ceba7bdae, 1ede274a-9246-4aec-acc0-17642c07af97 | A, B, C | OK |  | br_043_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE14 | S_nSSEE14_12.47 | 6666.7 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_043_21.A, br_043_21.B, br_043_21.C | 190 | 1 |  | 6666.7 | 28.5929 | 33.6716 | 41.267
| FALSE | FALSE | GSO_37 | GSO_37 | br_044_21 | 36.0466 | -79.7995 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 6666.7 | [6 empty] | 6.6667 |  |  | 6.6667 |  | 6.3334 | 2.635 | 3.9761 | 5.2542 | 2024-01-20 07:05 |  | 1.0792 |  |  |  | 82.9599 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | e72c363a-7373-4a30-a872-329d650d7569, 547c5604-b333-47b9-83ad-6f6fa1e88927, 53f8a349-7f61-440d-ad82-54a7f6d15d3a | A, B, C | OK |  | br_044_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE14 | S_nSSEE14_12.47 | 6666.7 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_044_21.A, br_044_21.B, br_044_21.C | 190 | 1 |  | 6666.7 | 219.5832 | 331.3441 | 437.846
| FALSE | FALSE | GSO_38 | GSO_38 | br_045_21 | 36.121 | -79.8612 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 6000 | [6 empty] | 6 |  |  | 6 |  | 5.7 | 0.015622 | 0.024204 | 0.042336 | 2024-01-20 09:00 |  | 5.6577 |  |  |  | 0.74274 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 9c1dc66a-d26b-42ae-9fa5-d4e46c87f492, 31c14863-6ede-40c4-86a5-41eadc729ac2, 15e8162e-962b-481f-923b-b2fe7c7ce432 | A, B, C | OK |  | br_045_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE15 | S_nSSEE15_12.47 | 6000.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_045_21.A, br_045_21.B, br_045_21.C | 190 | 1 |  | 6000 | 1.3018 | 2.017 | 3.528
| FALSE | FALSE | GSO_39 | GSO_39 | br_046_21 | 36.121 | -79.8612 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 6000 | [6 empty] | 6 |  |  | 6 |  | 5.7 | 1.194 | 1.7841 | 2.3656 | 2024-01-21 04:00 |  | 3.3344 |  |  |  | 41.5025 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 93658bef-4bd5-4300-8424-5c388155968b, 1ef359a3-1b23-4781-b7f6-73e5a4c4559f, 77ff5585-562a-45e7-a281-464e98737abb | A, B, C | OK |  | br_046_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE15 | S_nSSEE15_12.47 | 6000.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_046_21.A, br_046_21.B, br_046_21.C | 190 | 1 |  | 6000 | 99.4969 | 148.6783 | 197.137
| FALSE | FALSE | GSO_4 | GSO_4 | br_04_21 | 36.0852 | -79.8827 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 5714.3 | [6 empty] | 5.7143 |  |  | 5.7143 |  | 5.4286 | 2.4126 | 3.721 | 5.0234 | 2024-01-21 04:00 |  | 0.4052 |  |  |  | 92.5357 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | eda55f14-fedc-4eb6-a389-a51a43231405, 67c44f52-c49c-4993-940f-90408b4b9ae5, 1da22d5c-e6b3-4228-b327-ddf40f1f21b6 | A, B, C | OK |  | br_04_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE0 | S_nSSEE0_12.47 | 5714.3 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_04_21.A, br_04_21.B, br_04_21.C | 190 | 1 |  | 5714.3 | 201.0527 | 310.0799 | 418.615
| FALSE | FALSE | GSO_40 | GSO_40 | br_047_21 | 36.121 | -79.8612 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 6000 | [6 empty] | 6 |  |  | 6 |  | 5.7 | 1.0344 | 1.5401 | 2.0837 | 2024-01-20 20:00 |  | 3.6163 |  |  |  | 36.5566 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | ee7aaead-b8fb-40d3-8a03-8ab58a542fdc, 58cd6faf-3139-48ff-a9ef-b152b7ebf778, 79202d32-8dca-417a-9d59-fc14f3bcaf5f | A, B, C | OK |  | br_047_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE15 | S_nSSEE15_12.47 | 6000.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_047_21.A, br_047_21.B, br_047_21.C | 190 | 1 |  | 6000 | 86.2034 | 128.3382 | 173.644
| FALSE | FALSE | GSO_41 | GSO_41 | br_048_21 | 36.121 | -79.8612 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 6000 | [6 empty] | 6 |  |  | 6 |  | 5.7 | 0.89469 | 1.3503 | 1.859 | 2024-01-18 04:00 |  | 3.841 |  |  |  | 32.6147 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 4f3f10ee-748f-4c21-b9c3-8ac51c8d41f6, d7d6e014-1cd2-4cb5-84bb-a00b2cad42e3, e1cda877-0a5c-49b1-bd5f-ad8449fb0e0c | A, B, C | OK |  | br_048_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE15 | S_nSSEE15_12.47 | 6000.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_048_21.A, br_048_21.B, br_048_21.C | 190 | 1 |  | 6000 | 74.5573 | 112.5246 | 154.92
| FALSE | FALSE | GSO_42 | GSO_42 | br_049_21 | 36.121 | -79.8612 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 6000 | [6 empty] | 6 |  |  | 6 |  | 5.7 | 1.9506 | 3.0111 | 4.0752 | 2024-01-21 04:00 |  | 1.6248 |  |  |  | 71.4956 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 0b1099db-07b7-4a46-831f-0ab42e837cdd, 119ef0a4-9572-4988-9343-96cacd641d11, 0e80773a-a8cc-45a5-8095-4dc9d8b00215 | A, B, C | OK |  | br_049_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE15 | S_nSSEE15_12.47 | 6000.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_049_21.A, br_049_21.B, br_049_21.C | 190 | 1 |  | 6000 | 162.5501 | 250.9263 | 339.604
| FALSE | FALSE | GSO_43 | GSO_43 | br_050_21 | 36.0168 | -79.7965 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 5454.5 | [6 empty] | 5.4545 |  |  | 5.4545 |  | 5.1818 | 2.2069 | 3.2839 | 4.3723 | 2024-01-21 04:00 |  | 0.80947 |  |  |  | 84.3786 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 223df89f-b673-46b7-a74d-953aa3cadd02, d8ed1451-4cac-4c54-9238-07312269a3d5, d260c5dc-0f9a-4ff7-a347-cabc3421f531 | A, B, C | OK |  | br_050_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_050_21.A, br_050_21.B, br_050_21.C | 190 | 1 |  | 5454.5 | 183.9062 | 273.6613 | 364.359
| FALSE | FALSE | GSO_44 | GSO_44 | br_051_21 | 36.0168 | -79.7965 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 5454.5 | [6 empty] | 5.4545 |  |  | 5.4545 |  | 5.1818 | 0.026957 | 0.04086 | 0.065292 | 2024-01-21 |  | 5.1165 |  |  |  | 1.26 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | ae9708d6-58e3-48d8-b469-2b865749bda5, 9de5605e-2be3-4478-8321-ec1cfdb77d3e, c206a6a0-74a2-4aa0-b700-0397b158b47c | A, B, C | OK |  | br_051_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_051_21.A, br_051_21.B, br_051_21.C | 190 | 1 |  | 5454.5 | 2.2464 | 3.405 | 5.441
| FALSE | FALSE | GSO_45 | GSO_45 | br_052_21 | 36.0168 | -79.7965 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 5454.5 | [6 empty] | 5.4545 |  |  | 5.4545 |  | 5.1818 | 1.6229 | 2.498 | 3.3731 | 2024-01-18 04:00 |  | 1.8087 |  |  |  | 65.0955 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 0a36e22d-cb96-45c8-8d47-74ede8f433bd, ac9dddc3-7cae-427c-a129-87d3008b8362, 87af0485-ac3b-4ef1-bd8e-39742bb1311b | A, B, C | OK |  | br_052_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_052_21.A, br_052_21.B, br_052_21.C | 190 | 1 |  | 5454.5 | 135.2434 | 208.1636 | 281.092
| FALSE | FALSE | GSO_46 | GSO_46 | br_053_21 | 36.0168 | -79.7965 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 5454.5 | [6 empty] | 5.4545 |  |  | 5.4545 |  | 5.1818 | 1.4964 | 2.2132 | 2.9347 | 2024-01-21 04:00 |  | 2.247 |  |  |  | 56.6359 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 425e9895-3ec9-4ecf-a2de-00e847c9f5d0, e8d1fc00-bcf6-4d05-b6b9-7f38e6915ce5, 0b8f662d-5bc3-42fe-a24e-070da09bdd80 | A, B, C | OK |  | br_053_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_053_21.A, br_053_21.B, br_053_21.C | 190 | 1 |  | 5454.5 | 124.6999 | 184.4341 | 244.562
| FALSE | FALSE | GSO_47 | GSO_47 | br_054_21 | 36.0168 | -79.7965 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 5454.5 | [6 empty] | 5.4545 |  |  | 5.4545 |  | 5.1818 | 0.21699 | 0.27116 | 0.35389 | 2024-07-16 03:00 |  | 4.8279 |  |  |  | 6.8296 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 44d72b2b-4d39-442e-969c-28bfa609a6ca, df231f2b-7e74-4562-8026-e0248f99acb1, 73020989-8b85-4f2f-ae5e-b46034dccc36 | A, B, C | OK |  | br_054_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_054_21.A, br_054_21.B, br_054_21.C | 190 | 1 |  | 5454.5 | 18.0821 | 22.5966 | 29.491
| FALSE | FALSE | GSO_48 | GSO_48 | br_055_21 | 36.0168 | -79.7965 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 5454.5 | [6 empty] | 5.4545 |  |  | 5.4545 |  | 5.1818 | 0.34809 | 0.40578 | 0.50413 | 2024-01-17 21:00 |  | 4.6776 |  |  |  | 9.7289 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | caead5dd-6652-4002-9205-bf1f5d7841a2, 2756c12d-de33-427b-a20e-a7524bf8ba2a, d501232c-0e9b-4aed-b1c7-0711f51fd12c | A, B, C | OK |  | br_055_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_055_21.A, br_055_21.B, br_055_21.C | 190 | 1 |  | 5454.5 | 29.0078 | 33.8146 | 42.011
| FALSE | FALSE | GSO_49 | GSO_49 | br_056_21 | 36.0168 | -79.7965 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 5454.5 | [6 empty] | 5.4545 |  |  | 5.4545 |  | 5.1818 | 0.12927 | 0.15506 | 0.19782 | 2024-06-27 03:00 |  | 4.984 |  |  |  | 3.8176 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 904a534b-b4de-47cc-9111-a909cdd75ff6, cf17223b-5ef6-40ff-aa3f-7eaa71fa5ab1, 4e486c1d-6969-466b-bb85-e868d8c69d96 | A, B, C | OK |  | br_056_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_056_21.A, br_056_21.B, br_056_21.C | 190 | 1 |  | 5454.5 | 10.7723 | 12.922 | 16.485
| FALSE | FALSE | GSO_5 | GSO_5 | br_05_21 | 36.0852 | -79.8827 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 5714.3 | [6 empty] | 5.7143 |  |  | 5.7143 |  | 5.4286 | 0.6801 | 0.83893 | 1.0512 | 2024-01-20 15:00 |  | 4.3774 |  |  |  | 19.3644 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 1a7b2ce3-8ce4-43f0-822c-bae88f338574, fdea0e08-11f9-40c1-bd4a-4dfdb8ea2803, 921b5057-9802-4094-b921-551288ad3d2e | A, B, C | OK |  | br_05_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE0 | S_nSSEE0_12.47 | 5714.3 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_05_21.A, br_05_21.B, br_05_21.C | 190 | 1 |  | 5714.3 | 56.6751 | 69.911 | 87.601
| FALSE | FALSE | GSO_50 | GSO_50 | br_057_21 | 36.0168 | -79.7965 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 5454.5 | [6 empty] | 5.4545 |  |  | 5.4545 |  | 5.1818 | 0.027447 | 0.042684 | 0.06354 | 2024-01-21 |  | 5.1182 |  |  |  | 1.2262 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 4d9bb5e2-1e06-49ed-b322-273c65c7ea12, 02cb60eb-e56b-45c0-871a-7d5da5072e9a, ceeee8fb-13b1-43c7-9caf-4433648f6846 | A, B, C | OK |  | br_057_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_057_21.A, br_057_21.B, br_057_21.C | 190 | 1 |  | 5454.5 | 2.2873 | 3.557 | 5.295
| FALSE | FALSE | GSO_51 | GSO_51 | br_058_21 | 36.0168 | -79.7965 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 5454.5 | [6 empty] | 5.4545 |  |  | 5.4545 |  | 5.1818 | 0.24078 | 0.2792 | 0.35236 | 2024-01-20 15:00 |  | 4.8294 |  |  |  | 6.7999 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 2dabfa67-e633-42fb-88f8-b99c8c81ce3f, 40e658e9-710a-4f81-b823-ce3b23d76208, 100d5254-7678-4ba2-a678-ffa8ba0ac8ce | A, B, C | OK |  | br_058_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_058_21.A, br_058_21.B, br_058_21.C | 190 | 1 |  | 5454.5 | 20.0647 | 23.267 | 29.363
| FALSE | FALSE | GSO_52 | GSO_52 | br_059_21 | 36.0168 | -79.7965 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 5454.5 | [6 empty] | 5.4545 |  |  | 5.4545 |  | 5.1818 | 1.5455 | 2.3443 | 3.1697 | 2024-01-21 04:00 |  | 2.0121 |  |  |  | 61.17 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 148e241f-8dca-40c2-bc4c-9bba11acb600, 740ff96c-6171-4486-bb6a-904851da7f68, 54cc7298-372e-4f46-9c94-d78d3e7e3368 | A, B, C | OK |  | br_059_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_059_21.A, br_059_21.B, br_059_21.C | 190 | 1 |  | 5454.5 | 128.7905 | 195.3616 | 264.141
| FALSE | FALSE | GSO_53 | GSO_53 | br_060_21 | 36.0168 | -79.7965 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 5454.5 | [6 empty] | 5.4545 |  |  | 5.4545 |  | 5.1818 | 0.72043 | 0.99739 | 1.3206 | 2024-01-21 04:00 |  | 3.8612 |  |  |  | 25.4852 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 77c08208-993b-4559-b9e2-42c4c772997c, 4b800952-fa1b-4668-ba63-4244710bab3c, 3b012ead-fe04-4b66-8c50-59d42334a89c | A, B, C | OK |  | br_060_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_060_21.A, br_060_21.B, br_060_21.C | 190 | 1 |  | 5454.5 | 60.036 | 83.116 | 110.049
| FALSE | FALSE | GSO_54 | GSO_54 | br_061_21 | 36.0131 | -79.8489 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 10000 | [6 empty] | 10 |  |  | 10 |  | 9.5 | 2.5084 | 3.7884 | 5.0799 | 2024-01-21 04:00 |  | 4.4201 |  |  |  | 53.4723 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | c70624cc-3511-421e-bcd3-4f74ee43c80f, 0c2d5da7-8b73-4e99-a2ec-e1bd371c44f1, b486465e-b5c3-4f46-9979-e961ceb9df52 | A, B, C | OK |  | br_061_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE17 | S_nSSEE17_12.47 | 10000.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_061_21.A, br_061_21.B, br_061_21.C | 190 | 1 |  | 10000 | 209.0296 | 315.702 | 423.322
| FALSE | FALSE | GSO_55 | GSO_55 | br_062_21 | 36.0131 | -79.8489 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 10000 | [6 empty] | 10 |  |  | 10 |  | 9.5 | 0.12347 | 0.19112 | 0.26848 | 2024-01-20 10:00 |  | 9.2315 |  |  |  | 2.8261 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 55b291eb-5761-4e7f-8635-63057f856791, 0d627f19-7146-43b0-9f7b-bac68e9966db, efb7b851-1f6e-4084-9dd6-5a62049b7654 | A, B, C | OK |  | br_062_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE17 | S_nSSEE17_12.47 | 10000.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_062_21.A, br_062_21.B, br_062_21.C | 190 | 1 |  | 10000 | 10.2891 | 15.9266 | 22.373
| FALSE | FALSE | GSO_56 | GSO_56 | br_063_21 | 36.0131 | -79.8489 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 10000 | [6 empty] | 10 |  |  | 10 |  | 9.5 | 0.45164 | 0.62017 | 0.80917 | 2024-01-21 04:00 |  | 8.6908 |  |  |  | 8.5176 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | d5be6516-e14a-46ab-a02a-0650b74a5159, 748858e9-a0e0-4bc6-a0b7-f4e67d7c9ecd, 620a8a0d-bcbd-4f44-be97-24244e308366 | A, B, C | OK |  | br_063_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE17 | S_nSSEE17_12.47 | 10000.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_063_21.A, br_063_21.B, br_063_21.C | 190 | 1 |  | 10000 | 37.6367 | 51.681 | 67.431
| FALSE | FALSE | GSO_57 | GSO_57 | br_08_21 | 36.0872 | -79.8446 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 6122.4 | [6 empty] | 6.1224 |  |  | 6.1224 |  | 5.8163 | 0.53196 | 0.75041 | 1.0327 | 2024-01-20 10:05 |  | 4.7836 |  |  |  | 17.7546 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 27046833-12e1-4f55-aeb1-743d3fddc9b4, e2d61ac2-432e-446d-b560-32b75aebceed, 08dafb35-ef6e-48c6-89ef-1f3412fa5f7e | A, B, C | OK |  | br_08_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE1 | S_nSSEE1_12.47 | 6122.4 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_08_21.A, br_08_21.B, br_08_21.C | 190 | 1 |  | 6122.4 | 44.3296 | 62.5339 | 86.055
| FALSE | FALSE | GSO_58 | GSO_58 | br_09_21 | 36.0872 | -79.8446 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 6122.4 | [6 empty] | 6.1224 |  |  | 6.1224 |  | 5.8163 | 2.002 | 3.0619 | 4.1658 | 2024-01-21 04:00 |  | 1.6504 |  |  |  | 71.6239 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | cd71f269-7897-4746-9a77-c6bc730114fe, ff232009-b42f-4f71-a769-88a952701609, b8c6df33-b602-4d1c-9dda-e52dfeb41665 | A, B, C | OK |  | br_09_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE1 | S_nSSEE1_12.47 | 6122.4 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_09_21.A, br_09_21.B, br_09_21.C | 190 | 1 |  | 6122.4 | 166.8301 | 255.1588 | 347.154
| FALSE | FALSE | GSO_59 | GSO_59 | br_010_21 | 36.0873 | -79.8446 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 6122.4 | [6 empty] | 6.1224 |  |  | 6.1224 |  | 5.8163 | 1.5447 | 2.377 | 3.1957 | 2024-01-21 04:00 |  | 2.6206 |  |  |  | 54.9442 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 4529fb6d-421e-4f02-9b11-c956a4443f8e, 1231155d-ed13-4563-8801-fa08388d11cd, 1b822839-e89f-49f2-b2a9-69df27011548 | A, B, C | OK |  | br_010_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE1 | S_nSSEE1_12.47 | 6122.4 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_010_21.A, br_010_21.B, br_010_21.C | 190 | 1 |  | 6122.4 | 128.7271 | 198.0846 | 266.309
| FALSE | FALSE | GSO_6 | GSO_6 | br_06_21 | 36.0852 | -79.8827 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 5714.3 | [6 empty] | 5.7143 |  |  | 5.7143 |  | 5.4286 | 0.44327 | 0.637 | 0.82657 | 2024-01-18 04:00 |  | 4.602 |  |  |  | 15.2263 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 145f4423-0120-41c0-a961-6f6b453e91a7, 120599d7-eee0-4966-bd20-36d9e2e8b089, a5d804f2-bcf0-4e70-ad7f-9ffc889ca71a | A, B, C | OK |  | br_06_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE0 | S_nSSEE0_12.47 | 5714.3 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_06_21.A, br_06_21.B, br_06_21.C | 190 | 1 |  | 5714.3 | 36.9389 | 53.0836 | 68.881
| FALSE | FALSE | GSO_60 | GSO_60 | br_011_21 | 36.0873 | -79.8446 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 6122.4 | [6 empty] | 6.1224 |  |  | 6.1224 |  | 5.8163 | 1.3871 | 2.0963 | 2.859 | 2024-01-21 04:00 |  | 2.9573 |  |  |  | 49.1553 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 229fce16-0cb2-401d-957b-9d0d3c2ac1cc, fc187080-4278-4699-8d7f-ded10dc27448, 52980b4f-3c73-4c68-8631-e69ccc722a34 | A, B, C | OK |  | br_011_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE1 | S_nSSEE1_12.47 | 6122.4 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_011_21.A, br_011_21.B, br_011_21.C | 190 | 1 |  | 6122.4 | 115.5942 | 174.692 | 238.251
| FALSE | FALSE | GSO_61 | GSO_61 | br_012_21 | 36.0872 | -79.8446 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 6122.4 | [6 empty] | 6.1224 |  |  | 6.1224 |  | 5.8163 | 2.5424 | 3.922 | 5.2018 | 2024-01-20 09:00 |  | 0.61446 |  |  |  | 89.4355 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | bdb558af-9d90-4dcd-870e-28a86925b8cc, 192ef0e0-59f5-4932-a625-7e967573ec09, 69c0c6b0-aa07-4cdc-9789-b51b223584c4 | A, B, C | OK |  | br_012_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE1 | S_nSSEE1_12.47 | 6122.4 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_012_21.A, br_012_21.B, br_012_21.C | 190 | 1 |  | 6122.4 | 211.8673 | 326.8333 | 433.485
| FALSE | FALSE | GSO_62 | GSO_62 | br_013_21 | 36.0873 | -79.8446 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 6122.4 | [6 empty] | 6.1224 |  |  | 6.1224 |  | 5.8163 | 0.40929 | 0.62888 | 0.85519 | 2024-01-21 04:00 |  | 4.9611 |  |  |  | 14.7034 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 2c8910bb-0c41-4c36-8a5f-d8ffc5e65938, 3f59d58a-b780-49d5-86ae-b0b0f01c076d, decddce1-9f0e-44c6-a3bd-24fdb9cf1a60 | A, B, C | OK |  | br_013_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE1 | S_nSSEE1_12.47 | 6122.4 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_013_21.A, br_013_21.B, br_013_21.C | 190 | 1 |  | 6122.4 | 34.1079 | 52.4066 | 71.266
| FALSE | FALSE | GSO_63 | GSO_63 | br_014_21 | 36.0873 | -79.8446 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 6122.4 | [6 empty] | 6.1224 |  |  | 6.1224 |  | 5.8163 | 0.059226 | 0.090528 | 0.12385 | 2024-07-15 09:00 |  | 5.6924 |  |  |  | 2.1294 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 676b1650-044c-43bf-bea6-3dced2a612c6, abbc8c51-7785-4d04-a735-eb965d943d5a, 167b629e-ae1a-4acd-a435-a9faf6b8f0b1 | A, B, C | OK |  | br_014_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE1 | S_nSSEE1_12.47 | 6122.4 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_014_21.A, br_014_21.B, br_014_21.C | 190 | 1 |  | 6122.4 | 4.9355 | 7.544 | 10.321
| FALSE | FALSE | GSO_64 | GSO_64 | br_064_21 | 36.0801 | -79.7573 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 4285.7 | [6 empty] | 4.2857 |  |  | 4.2857 |  | 4.0714 | 1.2676 | 1.8163 | 2.3845 | 2024-01-21 04:00 |  | 1.6869 |  |  |  | 58.5671 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | aa668afa-9003-4c02-b068-76a760cba7c4, 8ec9092e-c513-4856-b139-17b0f244b287, 96d7ca9d-a8a7-4620-beb4-015993e1495f | A, B, C | OK |  | br_064_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE2 | S_nSSEE2_12.47 | 4285.7 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_064_21.A, br_064_21.B, br_064_21.C | 190 | 1 |  | 4285.7 | 105.6309 | 151.3556 | 198.709
| FALSE | FALSE | GSO_65 | GSO_65 | br_065_21 | 36.0801 | -79.7573 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 4285.7 | [6 empty] | 4.2857 |  |  | 4.2857 |  | 4.0714 | 0.14171 | 0.16918 | 0.21571 | 2024-01-21 04:00 |  | 3.8557 |  |  |  | 5.2982 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | a8421f63-1fb7-4386-80d1-558a9049f658, c0caf65c-2d30-471b-9a8c-36e1484ba877, a2d74127-91f7-4d1b-a98b-b3f287f80eec | A, B, C | OK |  | br_065_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE2 | S_nSSEE2_12.47 | 4285.7 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_065_21.A, br_065_21.B, br_065_21.C | 190 | 1 |  | 4285.7 | 11.8091 | 14.098 | 17.976
| FALSE | FALSE | GSO_66 | GSO_66 | br_066_21 | 36.0801 | -79.7573 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 4285.7 | [6 empty] | 4.2857 |  |  | 4.2857 |  | 4.0714 | 1.3628 | 2.0344 | 2.6972 | 2024-01-21 04:00 |  | 1.3742 |  |  |  | 66.2473 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | aa212fd9-92d5-4c56-9a9e-3014ccc9a7ce, 0cbf5c43-696f-40b4-ab01-fd3dfd670388, 3f826b2c-284b-4880-a9f1-d5554c1e5213 | A, B, C | OK |  | br_066_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE2 | S_nSSEE2_12.47 | 4285.7 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_066_21.A, br_066_21.B, br_066_21.C | 190 | 1 |  | 4285.7 | 113.5657 | 169.5323 | 224.767
| FALSE | FALSE | GSO_67 | GSO_67 | br_067_21 | 36.0801 | -79.7573 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 4285.7 | [6 empty] | 4.2857 |  |  | 4.2857 |  | 4.0714 | 1.4901 | 2.1371 | 2.8646 | 2024-01-21 04:00 |  | 1.2068 |  |  |  | 70.3586 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | fddc71cc-3766-4601-9ca7-c2caab3c7c4d, 5aed073b-49c0-4020-b105-f7e28cfd41ed, 4b3c48a3-9a69-47a9-b110-7d0b18cc7f06 | A, B, C | OK |  | br_067_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE2 | S_nSSEE2_12.47 | 4285.7 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_067_21.A, br_067_21.B, br_067_21.C | 190 | 1 |  | 4285.7 | 124.1763 | 178.0886 | 238.716
| FALSE | FALSE | GSO_68 | GSO_68 | br_068_21 | 36.0801 | -79.7573 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 4285.7 | [6 empty] | 4.2857 |  |  | 4.2857 |  | 4.0714 | 1.2841 | 1.8094 | 2.3491 | 2024-01-21 04:00 |  | 1.7223 |  |  |  | 57.6985 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 6abb0433-d7c1-47cb-b500-310c0966ae29, b14a51cb-21cb-48f4-91a6-564663c5a923, f2986696-35a7-4d1e-a7dd-8b01d8d6756a | A, B, C | OK |  | br_068_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE2 | S_nSSEE2_12.47 | 4285.7 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_068_21.A, br_068_21.B, br_068_21.C | 190 | 1 |  | 4285.7 | 107.0124 | 150.7806 | 195.762
| FALSE | FALSE | GSO_69 | GSO_69 | br_069_21 | 36.0801 | -79.7573 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 4285.7 | [6 empty] | 4.2857 |  |  | 4.2857 |  | 4.0714 | 0.29078 | 0.38227 | 0.49324 | 2024-01-21 04:00 |  | 3.5782 |  |  |  | 12.1146 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 16e446fe-cce5-4d4b-abd0-d9bf98278835, 3f69baec-6464-4c01-91c1-171903c224f7, 9255af13-2569-446c-b326-8de2942e3a26 | A, B, C | OK |  | br_069_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE2 | S_nSSEE2_12.47 | 4285.7 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_069_21.A, br_069_21.B, br_069_21.C | 190 | 1 |  | 4285.7 | 24.2321 | 31.856 | 41.103
| FALSE | FALSE | GSO_7 | GSO_7 | br_07_21 | 36.0852 | -79.8826 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 5714.3 | [6 empty] | 5.7143 |  |  | 5.7143 |  | 5.4286 | 0.029079 | 0.0468 | 0.073416 | 2024-01-21 |  | 5.3552 |  |  |  | 1.3524 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 874fce3a-0ddc-405e-8b4d-496bf1208ffa, 7c4e0a27-0ba8-4589-8efa-9d78e22aeea7, b3997dcd-0479-4422-904f-1e86aedb3b49 | A, B, C | OK |  | br_07_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE0 | S_nSSEE0_12.47 | 5714.3 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_07_21.A, br_07_21.B, br_07_21.C | 190 | 1 |  | 5714.3 | 2.4232 | 3.9 | 6.118
| FALSE | FALSE | GSO_70 | GSO_70 | br_070_21 | 36.0801 | -79.7573 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 4285.7 | [6 empty] | 4.2857 |  |  | 4.2857 |  | 4.0714 | 0.35304 | 0.42007 | 0.51608 | 2024-01-20 22:00 |  | 3.5553 |  |  |  | 12.6758 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | ff4d78df-a97d-465a-9270-6b140f05b7ee, 96d35f0d-746b-4c76-8d6d-a22dac3dcfaa, 7a4e8fb6-f007-4d77-bfcb-6a0b0e18561c | A, B, C | OK |  | br_070_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE2 | S_nSSEE2_12.47 | 4285.7 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_070_21.A, br_070_21.B, br_070_21.C | 190 | 1 |  | 4285.7 | 29.4202 | 35.0057 | 43.007
| FALSE | FALSE | GSO_71 | GSO_71 | br_071_21 | 36.0825 | -79.7708 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 10000 | [6 empty] | 10 |  |  | 10 |  | 9.5 | 2.7774 | 4.1681 | 5.5004 | 2024-01-21 02:00 |  | 3.9996 |  |  |  | 57.8994 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 7dec81b6-3b82-498d-bfaa-f44bf5d9581d, 4ff8b560-0d8d-46ca-aa4f-48e616d84a8c, 828a3353-455f-43cc-a9b0-71980deae8fd | A, B, C | OK |  | br_071_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE3 | S_nSSEE3_12.47 | 10000.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_071_21.A, br_071_21.B, br_071_21.C | 190 | 1 |  | 10000 | 231.4489 | 347.345 | 458.37
| FALSE | FALSE | GSO_72 | GSO_72 | br_072_21 | 36.0825 | -79.7708 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 10000 | [6 empty] | 10 |  |  | 10 |  | 9.5 | 0.95133 | 1.3238 | 1.741 | 2024-01-21 04:00 |  | 7.759 |  |  |  | 18.3268 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 2f6074d9-3367-424b-9912-3b54ba3842dc, 5be2e72a-f9e3-4662-bcdd-f6914b127473, ceb3c16f-b2c1-4384-83e5-47eb8d9787a9 | A, B, C | OK |  | br_072_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE3 | S_nSSEE3_12.47 | 10000.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_072_21.A, br_072_21.B, br_072_21.C | 190 | 1 |  | 10000 | 79.2778 | 110.32 | 145.087
| FALSE | FALSE | GSO_73 | GSO_73 | br_073_21 | 36.0825 | -79.7708 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 10000 | [6 empty] | 10 |  |  | 10 |  | 9.5 | 0.053536 | 0.06612 | 0.097896 | 2024-01-20 20:00 |  | 9.4021 |  |  |  | 1.0305 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | dd7e3ea9-a097-46d9-ba3d-e976877c959f, dc0e22aa-9b17-4812-81b9-805e6e2fcea4, 0a5bd7a0-8dda-4ea9-8140-b43dcad4334a | A, B, C | OK |  | br_073_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE3 | S_nSSEE3_12.47 | 10000.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_073_21.A, br_073_21.B, br_073_21.C | 190 | 1 |  | 10000 | 4.4614 | 5.51 | 8.158
| FALSE | FALSE | GSO_74 | GSO_74 | br_074_21 | 36.0825 | -79.7708 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 10000 | [6 empty] | 10 |  |  | 10 |  | 9.5 | 0.71292 | 0.87569 | 1.0535 | 2024-01-20 23:25 |  | 8.4465 |  |  |  | 11.0898 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 4cb9db9e-b9c3-473e-878d-2df2932f4dcf, 2be1e40d-d971-44eb-9f8e-1f362b00491f, b4794b85-7397-40b2-a7b2-50c82c66983d | A, B, C | OK |  | br_074_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE3 | S_nSSEE3_12.47 | 10000.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_074_21.A, br_074_21.B, br_074_21.C | 190 | 1 |  | 10000 | 59.4096 | 72.9743 | 87.794
| FALSE | FALSE | GSO_75 | GSO_75 | br_075_21 | 36.0825 | -79.7708 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 10000 | [6 empty] | 10 |  |  | 10 |  | 9.5 | 0.43085 | 0.58537 | 0.81054 | 2024-01-18 04:00 |  | 8.6895 |  |  |  | 8.532 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 74ba07cb-a526-4618-b499-1a430d0286b7, dc09ae69-e1ee-4c83-9c04-e09da568c6ab, 8cfdaf81-8e59-4486-ba2f-4e450a23c876 | A, B, C | OK |  | br_075_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE3 | S_nSSEE3_12.47 | 10000.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_075_21.A, br_075_21.B, br_075_21.C | 190 | 1 |  | 10000 | 35.9045 | 48.781 | 67.545
| FALSE | FALSE | GSO_76 | GSO_76 | br_076_21 | 36.0719 | -79.8252 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 6666.7 | [6 empty] | 6.6667 |  |  | 6.6667 |  | 6.3334 | 0.02376 | 0.036908 | 0.052824 | 2024-01-20 23:00 |  | 6.2805 |  |  |  | 0.83406 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 89cbe802-faf3-4709-b370-afa1154a5b70, fd14c6a3-6658-4039-a0b8-c00ab26e307c, a61580ad-490f-42dd-919c-3cfdfb775908 | A, B, C | OK |  | br_076_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_076_21.A, br_076_21.B, br_076_21.C | 190 | 1 |  | 6666.7 | 1.98 | 3.0756 | 4.402
| FALSE | FALSE | GSO_77 | GSO_77 | br_077_21 | 36.0719 | -79.8252 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 6666.7 | [6 empty] | 6.6667 |  |  | 6.6667 |  | 6.3334 | 2.6294 | 3.9175 | 5.1594 | 2024-01-21 04:00 |  | 1.1739 |  |  |  | 81.4642 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 04933340-1f7e-4732-a170-31c687c8d71e, da253492-f9e5-4572-a892-8cf7206f5562, 55611621-48c6-40ab-afb0-d76e41a0d5de | A, B, C | OK |  | br_077_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_077_21.A, br_077_21.B, br_077_21.C | 190 | 1 |  | 6666.7 | 219.1131 | 326.4566 | 429.952
| FALSE | FALSE | GSO_78 | GSO_78 | br_078_21 | 36.0719 | -79.8252 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 6666.7 | [6 empty] | 6.6667 |  |  | 6.6667 |  | 6.3334 | 0.16943 | 0.24664 | 0.32894 | 2024-01-18 04:00 |  | 6.0044 |  |  |  | 5.1938 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | c0ddba19-fbd3-4341-bb7c-f8d96301d889, 648e5aaa-f39d-4756-9d09-ca5503bbc225, 838a2e79-8d23-4760-9eab-eb6ed2d38b4c | A, B, C | OK |  | br_078_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_078_21.A, br_078_21.B, br_078_21.C | 190 | 1 |  | 6666.7 | 14.1194 | 20.5536 | 27.412
| FALSE | FALSE | GSO_79 | GSO_79 | br_079_21 | 36.0719 | -79.8252 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 6666.7 | [6 empty] | 6.6667 |  |  | 6.6667 |  | 6.3334 | 0.85586 | 1.1479 | 1.4952 | 2024-01-21 04:00 |  | 4.8382 |  |  |  | 23.6075 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | dfd547e9-e06c-4fe7-8842-913f0b3f7d52, f68a1c8a-5406-4783-b8ae-a255bce0e795, 02d224d1-8d1b-45bb-98ed-ebc20c74318a | A, B, C | OK |  | br_079_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_079_21.A, br_079_21.B, br_079_21.C | 190 | 1 |  | 6666.7 | 71.3217 | 95.6596 | 124.596
| FALSE | FALSE | GSO_8 | GSO_8 | br_022_21 | 36.1003 | -79.8075 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 5555.6 | [6 empty] | 5.5556 |  |  | 5.5556 |  | 5.2778 | 0.022721 | 0.034476 | 0.058212 | 2024-01-20 17:00 |  | 5.2196 |  |  |  | 1.103 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 9e0bf50d-94bd-4e5d-9a43-95a506f4c534, 14a29c10-6f6b-4045-834c-a8cdccfa7fe8, 674756f5-28ec-40f8-8ece-cd6c8a394c18 | A, B, C | OK |  | br_022_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE10 | S_nSSEE10_12.47 | 5555.6 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_022_21.A, br_022_21.B, br_022_21.C | 190 | 1 |  | 5555.6 | 1.8934 | 2.873 | 4.851
| FALSE | FALSE | GSO_80 | GSO_80 | br_080_21 | 36.0719 | -79.8252 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 6666.7 | [6 empty] | 6.6667 |  |  | 6.6667 |  | 6.3334 | 1.0636 | 1.4855 | 1.9457 | 2024-01-21 02:00 |  | 4.3876 |  |  |  | 30.7217 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 4fb9d568-cec8-4d2c-b185-503c8441a94f, 48527915-ef6b-4d16-9525-f6d17fae71ba, e4842198-5ba7-4542-9415-20f0a87511ac | A, B, C | OK |  | br_080_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_080_21.A, br_080_21.B, br_080_21.C | 190 | 1 |  | 6666.7 | 88.6299 | 123.794 | 162.143
| FALSE | FALSE | GSO_81 | GSO_81 | br_081_21 | 36.0719 | -79.8252 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 6666.7 | [6 empty] | 6.6667 |  |  | 6.6667 |  | 6.3334 | 1.1689 | 1.5889 | 2.07 | 2024-01-21 04:00 |  | 4.2634 |  |  |  | 32.6835 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 9a5c0969-f68d-4cea-a13e-ef351a3d3730, a8a2fc9d-e642-4554-abad-f2610eb29b51, 27bb62b3-e552-4996-874d-31dcad547987 | A, B, C | OK |  | br_081_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_081_21.A, br_081_21.B, br_081_21.C | 190 | 1 |  | 6666.7 | 97.4105 | 132.4067 | 172.497
| FALSE | FALSE | GSO_82 | GSO_82 | br_082_21 | 36.0719 | -79.8252 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 6666.7 | [6 empty] | 6.6667 |  |  | 6.6667 |  | 6.3334 | 1.6447 | 2.5113 | 3.3849 | 2024-01-21 |  | 2.9484 |  |  |  | 53.4463 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | a890d29a-0380-4cd2-8cff-f9826e3ff07b, 918cae00-7f70-4556-9d40-35da1f05977d, 93c33640-e4a0-470f-a164-89c99ae69984 | A, B, C | OK |  | br_082_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_082_21.A, br_082_21.B, br_082_21.C | 190 | 1 |  | 6666.7 | 137.0611 | 209.2763 | 282.079
| FALSE | FALSE | GSO_83 | GSO_83 | br_083_21 | 36.0719 | -79.8252 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 6666.7 | [6 empty] | 6.6667 |  |  | 6.6667 |  | 6.3334 | 2.0902 | 3.158 | 4.2004 | 2024-01-18 04:00 |  | 2.133 |  |  |  | 66.3213 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | af9148e3-1b4f-4f27-b409-3654c3f953f5, 48c0048d-65ab-48a8-8cd9-833258bee864, 8c265c14-8e0f-4c74-9519-46da2dff7cd1 | A, B, C | OK |  | br_083_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_083_21.A, br_083_21.B, br_083_21.C | 190 | 1 |  | 6666.7 | 174.186 | 263.1632 | 350.031
| FALSE | FALSE | GSO_84 | GSO_84 | br_084_21 | 36.0719 | -79.8252 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 6666.7 | [6 empty] | 6.6667 |  |  | 6.6667 |  | 6.3334 | 0.1731 | 0.26237 | 0.36289 | 2024-01-20 06:05 |  | 5.9705 |  |  |  | 5.7298 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | d4454767-7751-4c58-9cbd-79e943f45acf, 4cc5af87-12cf-4fd1-a89c-0318dc07c068, b63c8e73-fffc-4e69-ad08-995c149ebeaa | A, B, C | OK |  | br_084_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_084_21.A, br_084_21.B, br_084_21.C | 190 | 1 |  | 6666.7 | 14.425 | 21.864 | 30.241
| FALSE | FALSE | GSO_85 | GSO_85 | br_085_21 | 36.0719 | -79.8252 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 6666.7 | [6 empty] | 6.6667 |  |  | 6.6667 |  | 6.3334 | 0.46705 | 0.6065 | 0.78437 | 2024-01-21 04:00 |  | 5.549 |  |  |  | 12.3847 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 6fcd01be-d3d1-4df7-bec8-4f8b1042aac0, 4fc59078-b2c4-42d5-b129-faa7a3f54cac, ac192c64-42ef-423f-814b-c8b837b8f5d2 | A, B, C | OK |  | br_085_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_085_21.A, br_085_21.B, br_085_21.C | 190 | 1 |  | 6666.7 | 38.9205 | 50.5416 | 65.364
| FALSE | FALSE | GSO_86 | GSO_86 | br_086_21 | 36.0708 | -79.7962 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 4545.5 | [6 empty] | 4.5455 |  |  | 4.5455 |  | 4.3182 | 1.0764 | 1.5183 | 1.9608 | 2024-01-20 23:00 |  | 2.3574 |  |  |  | 45.4078 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 492c962b-e2b7-4edd-afe9-20606e4114f6, 6182a628-fb52-41b9-8b93-90488a51a0fe, 6927b6e8-4d14-436e-8236-19dc4cdad934 | A, B, C | OK |  | br_086_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_086_21.A, br_086_21.B, br_086_21.C | 190 | 1 |  | 4545.5 | 89.6995 | 126.522 | 163.401
| FALSE | FALSE | GSO_87 | GSO_87 | br_087_21 | 36.0709 | -79.7962 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 4545.5 | [6 empty] | 4.5455 |  |  | 4.5455 |  | 4.3182 | 1.0482 | 1.4151 | 1.8016 | 2024-01-21 04:00 |  | 2.5166 |  |  |  | 41.721 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | e7689375-373b-4d7a-b001-0fa11239a327, 589e4f98-7742-4541-b2c3-6b108b7f9d4d, d9c84a3d-b565-4642-a7d4-3c9df307b1c8 | A, B, C | OK |  | br_087_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_087_21.A, br_087_21.B, br_087_21.C | 190 | 1 |  | 4545.5 | 87.3478 | 117.9236 | 150.134
| FALSE | FALSE | GSO_88 | GSO_88 | br_088_21 | 36.0708 | -79.7962 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 4545.5 | [6 empty] | 4.5455 |  |  | 4.5455 |  | 4.3182 | 0.76138 | 1.0329 | 1.3613 | 2024-01-18 04:00 |  | 2.957 |  |  |  | 31.5235 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 93986b58-113b-4798-b153-eda6e8924352, 73bea406-8df3-48d6-99e8-780c9ba74d8d, b1fd8626-d75b-4f57-95d8-5e0f995f6548 | A, B, C | OK |  | br_088_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_088_21.A, br_088_21.B, br_088_21.C | 190 | 1 |  | 4545.5 | 63.4485 | 86.0716 | 113.438
| FALSE | FALSE | GSO_89 | GSO_89 | br_089_21 | 36.0708 | -79.7962 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 4545.5 | [6 empty] | 4.5455 |  |  | 4.5455 |  | 4.3182 | 0.76922 | 1.013 | 1.3116 | 2024-01-21 04:00 |  | 3.0066 |  |  |  | 30.3739 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | d629f58a-fb37-4300-b174-4dadcd7fdef5, c6e42508-1e1b-4a8d-ad6c-5ed17230666d, a59c7bce-fb93-4255-8dac-4024e2c3a1c9 | A, B, C | OK |  | br_089_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_089_21.A, br_089_21.B, br_089_21.C | 190 | 1 |  | 4545.5 | 64.1018 | 84.414 | 109.301
| FALSE | FALSE | GSO_9 | GSO_9 | br_023_21 | 36.1003 | -79.8075 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 5555.6 | [6 empty] | 5.5556 |  |  | 5.5556 |  | 5.2778 | 0.014247 | 0.022788 | 0.038448 | 2024-01-21 01:00 |  | 5.2394 |  |  |  | 0.72848 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | c7e10126-bd63-4bd3-96ab-07587af29378, f631ee12-3be7-417b-ad19-901e9ad68684, 9b89dc0e-e258-4610-b60b-484b1b02a312 | A, B, C | OK |  | br_023_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE10 | S_nSSEE10_12.47 | 5555.6 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_023_21.A, br_023_21.B, br_023_21.C | 190 | 1 |  | 5555.6 | 1.1873 | 1.899 | 3.204
| FALSE | FALSE | GSO_90 | GSO_90 | br_090_21 | 36.0708 | -79.7962 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 4545.5 | [6 empty] | 4.5455 |  |  | 4.5455 |  | 4.3182 | 0.41465 | 0.50003 | 0.63064 | 2024-01-20 16:00 |  | 3.6876 |  |  |  | 14.6041 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | ab8abf18-0128-43c3-8213-8fcc30f583d2, 59f75e54-a46d-4153-8855-555945d0a888, f35586be-8010-4ad3-b579-d95b9825cae5 | A, B, C | OK |  | br_090_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_090_21.A, br_090_21.B, br_090_21.C | 190 | 1 |  | 4545.5 | 34.5538 | 41.669 | 52.553
| FALSE | FALSE | GSO_91 | GSO_91 | br_091_21 | 36.0708 | -79.7962 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 4545.5 | [6 empty] | 4.5455 |  |  | 4.5455 |  | 4.3182 | 0.96936 | 1.2713 | 1.6821 | 2024-01-21 |  | 2.6361 |  |  |  | 38.9535 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 11eec288-b107-4b0d-8513-8e0e8b097ff9, 66b6c9ff-fe2f-4708-83aa-26715afe7d27, 2494a26c-ddcb-40f8-8643-7c936424dfc0 | A, B, C | OK |  | br_091_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_091_21.A, br_091_21.B, br_091_21.C | 190 | 1 |  | 4545.5 | 80.7802 | 105.9423 | 140.175
| FALSE | FALSE | GSO_92 | GSO_92 | br_092_21 | 36.0708 | -79.7962 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 4545.5 | [6 empty] | 4.5455 |  |  | 4.5455 |  | 4.3182 | 0.50669 | 0.61804 | 0.76915 | 2024-01-21 04:00 |  | 3.5491 |  |  |  | 17.8118 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | a984179e-ff24-4a5b-9bff-44fa02582a26, fbe573a4-e81d-4315-b9c9-510a65c98be6, 9e7256be-44ac-40e3-95c4-e604f1b5b6ea | A, B, C | OK |  | br_092_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_092_21.A, br_092_21.B, br_092_21.C | 190 | 1 |  | 4545.5 | 42.2238 | 51.503 | 64.096
| FALSE | FALSE | GSO_93 | GSO_93 | br_093_21 | 36.0709 | -79.7962 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 4545.5 | [6 empty] | 4.5455 |  |  | 4.5455 |  | 4.3182 | 0.45692 | 0.55536 | 0.70237 | 2024-01-21 04:00 |  | 3.6159 |  |  |  | 16.2653 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | ac7b38f5-50a1-4cc6-bab1-d609ee8f92a4, 75f25960-b76b-4ea6-95b3-22351b5c7fde, 531ef22d-48aa-4ee9-88be-bf0b21101c8d | A, B, C | OK |  | br_093_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_093_21.A, br_093_21.B, br_093_21.C | 190 | 1 |  | 4545.5 | 38.0767 | 46.28 | 58.531
| FALSE | FALSE | GSO_94 | GSO_94 | br_094_21 | 36.0708 | -79.7962 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 4545.5 | [6 empty] | 4.5455 |  |  | 4.5455 |  | 4.3182 | 0.33065 | 0.40645 | 0.50374 | 2024-01-18 04:00 |  | 3.8145 |  |  |  | 11.6653 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | f0bd6ef7-dacb-46d2-ad18-589db990b13a, a82b3639-950c-4ba5-8e39-502e435ad83a, c177967e-e6f6-4644-aa50-326a9ebe3d00 | A, B, C | OK |  | br_094_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_094_21.A, br_094_21.B, br_094_21.C | 190 | 1 |  | 4545.5 | 27.5543 | 33.871 | 41.978
| FALSE | FALSE | GSO_95 | GSO_95 | br_095_21 | 36.0709 | -79.7962 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 4545.5 | [6 empty] | 4.5455 |  |  | 4.5455 |  | 4.3182 | 1.708 | 2.5471 | 3.4292 | 2024-01-18 04:00 |  | 0.88907 |  |  |  | 79.4112 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 859a9ae6-4d75-45f7-af3f-1d1c2c11b96f, ad766f3b-7d19-4707-8a90-38f818011b97, c6b6dfcf-55ed-45e7-9e6a-1ed25774a828 | A, B, C | OK |  | br_095_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_095_21.A, br_095_21.B, br_095_21.C | 190 | 1 |  | 4545.5 | 142.3321 | 212.2589 | 285.763
| FALSE | FALSE | GSO_96 | GSO_96 | br_096_21 | 36.0708 | -79.7962 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 4545.5 | [6 empty] | 4.5455 |  |  | 4.5455 |  | 4.3182 | 0.81239 | 1.0681 | 1.358 | 2024-01-20 06:00 |  | 2.9603 |  |  |  | 31.4471 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 1b5731fb-ced8-4f58-b1ab-d0ee4f8ea875, fcbaf392-5711-44ee-86c0-792317753d2f, fad28770-b3f6-4478-87a1-3b095d264a87 | A, B, C | OK |  | br_096_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_096_21.A, br_096_21.B, br_096_21.C | 190 | 1 |  | 4545.5 | 67.699 | 89.0123 | 113.163
| FALSE | FALSE | GSO_97 | GSO_97 | br_098_21 | 36.061 | -79.7714 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 7500 | [6 empty] | 7.5 |  |  | 7.5 |  | 7.125 | 2.111 | 3.1628 | 4.1702 | 2024-01-21 04:00 |  | 2.9548 |  |  |  | 58.5288 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | 003a8d77-c248-43c2-af2f-1f5f30595e2b, b3f7a58f-66bb-4c73-a447-90250ee96029, 3b017716-3815-48f3-bf37-e278bd03cc9d | A, B, C | OK |  | br_098_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE6 | S_nSSEE6_12.47 | 7500.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_098_21.A, br_098_21.B, br_098_21.C | 190 | 1 |  | 7500 | 175.9206 | 263.5666 | 347.515
| FALSE | FALSE | GSO_98 | GSO_98 | br_099_21 | 36.0611 | -79.7715 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 7500 | [6 empty] | 7.5 |  |  | 7.5 |  | 7.125 | 2.6962 | 4.1417 | 5.674 | 2024-01-21 04:00 |  | 1.451 |  |  |  | 79.6355 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | e19d273e-4ce0-462d-9501-16552f6df1a5, 74d4c75b-fdbd-4356-81ba-130cbea2e530, 43272e40-5062-4f3e-9a6d-0899fa207db5 | A, B, C | OK |  | br_099_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE6 | S_nSSEE6_12.47 | 7500.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_099_21.A, br_099_21.B, br_099_21.C | 190 | 1 |  | 7500 | 224.6811 | 345.1416 | 472.836
| FALSE | FALSE | GSO_99 | GSO_99 | br_0100_21 | 36.061 | -79.7715 | Medium-Low | Stored kVA available; independent calculation unavailable | Cannot independently validate stored breaker rating | 7500 | [6 empty] | 7.5 |  |  | 7.5 |  | 7.125 | 2.3225 | 3.3894 | 4.525 | 2024-01-21 04:00 |  | 2.6 |  |  |  | 63.5094 | 105348 | 5 | 2024-01-01 05:00 | 2024-12-31 23:55 | 3 | a3c897bb-ba13-4a0b-af16-81acabf20ccd, 667e5144-bfb1-4543-a81f-7a88e26190c7, 9d892d7c-e138-4107-8084-bbde890e1cc4 | A, B, C | OK |  | br_0100_21 | CircuitBreaker | switchable_element-Breaker | TRUE | 1 | 0 | TRUE | FALSE | OK | Stored breaker rating_kva only | Resolve breaker rating/unit mismatch before using capacity result | 2023-09-20 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both | S_nSSEE6 | S_nSSEE6_12.47 | 7500.0 |  | MV | 3 | 3 | SENSOR | SMART_scada_data | br_0100_21.A, br_0100_21.B, br_0100_21.C | 190 | 1 |  | 7500 | 193.545 | 282.449 | 377.087

## Topology_Shortlist
CapacityRank | RankEligible | TopologyReadyFlag | FeederID | Description | BreakerElementID | Latitude | Longitude | CapacityConfidence | RatingValidationStatus | AuditFlag | StoredBreakerRatingKVA | BreakerRatingA | BreakerVoltageRaw | VoltageKV | VoltageInterpretation | CalculatedBreakerKVA | RatingDifferencePct | StoredBreakerCapacityMVA | CalculatedBreakerCapacityMVA | AuditedBreakerCapacityMVA | ConservativeBreakerCapacityMVA | AuditedBreakerCapacityMW | ConservativeBreakerCapacityMW | AverageLoadMW | P95LoadMW | PeakLoadMW | PeakLoadTimestamp | ValidatedHeadroomMW | ConservativeHeadroomMW | AverageUtilizationPct_Audited | P95UtilizationPct_Audited | PeakUtilizationPct_Audited | PeakUtilizationPct_Conservative | Observations | MedianIntervalMinutes | FirstTimestamp | LastTimestamp | SelectedSCADASourceCount | SelectedSCADASourceIDs | SelectedSCADAPhases | SCADAStatus | UpstreamElementID | SourceElementID | SourceElementType | SourceElementCustomerType | SourceIsProducer | UpstreamPathElementCount | UpstreamPathDepth | PathTerminatedAtNullUpstream | PathHitMaxDepth | UpstreamPathStatus | CapacityBasis | RecommendedNextStep | GridLastUpdated | ElementType | ElementCustomerType | BreakerPhases | IsProducer | IsConsumer | IsSwitchable | SwitchIsOpen | PowerFlowDirection | Terminal1CN | Terminal2CN | RawRatingKVA | RawRatingA | RawVoltageLevel | KWhSourceCount | UniquePhaseCount | DataSourceTypes | Providers | FriendlyIDs | BreakerSelectionScore | BreakerCandidateRank | AuditedBreakerCapacityKVA | ConservativeBreakerCapacityKVA | AverageIntervalKWh | P95IntervalKWh | PeakIntervalKWh

## Selected_Breakers
grid_id | BreakerElementID | ElementType | ElementCustomerType | BreakerPhases | IsProducer | IsConsumer | IsSwitchable | SwitchIsOpen | PowerFlowDirection | UpstreamElementID | Terminal1CN | Terminal2CN | RawRatingKVA | RawRatingA | RawVoltageLevel | Latitude | Longitude | StoredBreakerRatingKVA | BreakerRatingA | BreakerVoltageRaw | KWhSourceCount | UniquePhaseCount | DataSourceTypes | Providers | FriendlyIDs | BreakerSelectionScore | BreakerCandidateRank | VoltageKV | VoltageInterpretation | CalculatedBreakerKVA | RatingDifferencePct | RatingValidationStatus | CapacityConfidence | CapacityBasis | AuditedBreakerCapacityKVA | ConservativeBreakerCapacityKVA | AuditFlag
GSO_1 | br_01_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 5714.3 |  | MV | 36.0852 | -79.8827 | 5714.3 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_01_21.A, br_01_21.B, br_01_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 5714.3 | Cannot independently validate stored breaker rating
GSO_10 | br_015_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE10 | S_nSSEE10_12.47 | 5555.6 |  | MV | 36.1003 | -79.8075 | 5555.6 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_015_21.A, br_015_21.B, br_015_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 5555.6 | Cannot independently validate stored breaker rating
GSO_100 | br_097_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE6 | S_nSSEE6_12.47 | 7500.0 |  | MV | 36.0611 | -79.7715 | 7500 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_097_21.A, br_097_21.B, br_097_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 7500 | Cannot independently validate stored breaker rating
GSO_101 | br_0101_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE7 | S_nSSEE7_12.47 | 5714.3 |  | MV | 36.0872 | -79.897 | 5714.3 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_0101_21.A, br_0101_21.B, br_0101_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 5714.3 | Cannot independently validate stored breaker rating
GSO_102 | br_0102_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE7 | S_nSSEE7_12.47 | 5714.3 |  | MV | 36.0872 | -79.897 | 5714.3 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_0102_21.A, br_0102_21.B, br_0102_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 5714.3 | Cannot independently validate stored breaker rating
GSO_103 | br_0103_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE7 | S_nSSEE7_12.47 | 5714.3 |  | MV | 36.0872 | -79.897 | 5714.3 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_0103_21.A, br_0103_21.B, br_0103_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 5714.3 | Cannot independently validate stored breaker rating
GSO_104 | br_0104_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE7 | S_nSSEE7_12.47 | 5714.3 |  | MV | 36.0872 | -79.897 | 5714.3 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_0104_21.A, br_0104_21.B, br_0104_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 5714.3 | Cannot independently validate stored breaker rating
GSO_105 | br_0105_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE7 | S_nSSEE7_12.47 | 5714.3 |  | MV | 36.0872 | -79.897 | 5714.3 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_0105_21.A, br_0105_21.B, br_0105_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 5714.3 | Cannot independently validate stored breaker rating
GSO_106 | br_0106_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE7 | S_nSSEE7_12.47 | 5714.3 |  | MV | 36.0872 | -79.897 | 5714.3 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_0106_21.A, br_0106_21.B, br_0106_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 5714.3 | Cannot independently validate stored breaker rating
GSO_107 | br_0107_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE7 | S_nSSEE7_12.47 | 5714.3 |  | MV | 36.0872 | -79.897 | 5714.3 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_0107_21.A, br_0107_21.B, br_0107_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 5714.3 | Cannot independently validate stored breaker rating
GSO_108 | br_0108_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE8 | S_nSSEE8_12.47 | 7142.9 |  | MV | 36.0543 | -79.8942 | 7142.9 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_0108_21.A, br_0108_21.B, br_0108_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 7142.9 | Cannot independently validate stored breaker rating
GSO_109 | br_0109_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE8 | S_nSSEE8_12.47 | 7142.9 |  | MV | 36.0543 | -79.8942 | 7142.9 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_0109_21.A, br_0109_21.B, br_0109_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 7142.9 | Cannot independently validate stored breaker rating
GSO_11 | br_016_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE10 | S_nSSEE10_12.47 | 5555.6 |  | MV | 36.1003 | -79.8075 | 5555.6 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_016_21.A, br_016_21.B, br_016_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 5555.6 | Cannot independently validate stored breaker rating
GSO_110 | br_0110_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE8 | S_nSSEE8_12.47 | 7142.9 |  | MV | 36.0543 | -79.8942 | 7142.9 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_0110_21.A, br_0110_21.B, br_0110_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 7142.9 | Cannot independently validate stored breaker rating
GSO_111 | br_0111_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE8 | S_nSSEE8_12.47 | 7142.9 |  | MV | 36.0543 | -79.8942 | 7142.9 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_0111_21.A, br_0111_21.B, br_0111_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 7142.9 | Cannot independently validate stored breaker rating
GSO_112 | br_0112_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE8 | S_nSSEE8_12.47 | 7142.9 |  | MV | 36.0543 | -79.8942 | 7142.9 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_0112_21.A, br_0112_21.B, br_0112_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 7142.9 | Cannot independently validate stored breaker rating
GSO_113 | br_0113_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE8 | S_nSSEE8_12.47 | 7142.9 |  | MV | 36.0543 | -79.8942 | 7142.9 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_0113_21.A, br_0113_21.B, br_0113_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 7142.9 | Cannot independently validate stored breaker rating
GSO_114 | br_0114_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE8 | S_nSSEE8_12.47 | 7142.9 |  | MV | 36.0543 | -79.8942 | 7142.9 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_0114_21.A, br_0114_21.B, br_0114_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 7142.9 | Cannot independently validate stored breaker rating
GSO_115 | br_0115_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE9 | S_nSSEE9_12.47 | 10000.0 |  | MV | 36.0426 | -79.8533 | 10000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_0115_21.A, br_0115_21.B, br_0115_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 10000 | Cannot independently validate stored breaker rating
GSO_116 | br_0116_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE9 | S_nSSEE9_12.47 | 10000.0 |  | MV | 36.0426 | -79.8533 | 10000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_0116_21.A, br_0116_21.B, br_0116_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 10000 | Cannot independently validate stored breaker rating
GSO_117 | br_0117_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE9 | S_nSSEE9_12.47 | 10000.0 |  | MV | 36.0426 | -79.8533 | 10000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_0117_21.A, br_0117_21.B, br_0117_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 10000 | Cannot independently validate stored breaker rating
GSO_118 | br_0118_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE9 | S_nSSEE9_12.47 | 10000.0 |  | MV | 36.0426 | -79.8533 | 10000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_0118_21.A, br_0118_21.B, br_0118_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 10000 | Cannot independently validate stored breaker rating
GSO_119 | br_0119_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE9 | S_nSSEE9_12.47 | 10000.0 |  | MV | 36.0426 | -79.8533 | 10000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_0119_21.A, br_0119_21.B, br_0119_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 10000 | Cannot independently validate stored breaker rating
GSO_12 | br_017_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE10 | S_nSSEE10_12.47 | 5555.6 |  | MV | 36.1003 | -79.8075 | 5555.6 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_017_21.A, br_017_21.B, br_017_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 5555.6 | Cannot independently validate stored breaker rating
GSO_121 | br_01_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 15000.0 |  | MV | 36.083 | -79.9727 | 15000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_01_22.A, br_01_22.B, br_01_22.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 15000 | Cannot independently validate stored breaker rating
GSO_122 | br_02_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 15000.0 |  | MV | 36.083 | -79.9727 | 15000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_02_22.A, br_02_22.B, br_02_22.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 15000 | Cannot independently validate stored breaker rating
GSO_123 | br_03_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 15000.0 |  | MV | 36.083 | -79.9727 | 15000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_03_22.A, br_03_22.B, br_03_22.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 15000 | Cannot independently validate stored breaker rating
GSO_124 | br_04_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 15000.0 |  | MV | 36.083 | -79.9727 | 15000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_04_22.A, br_04_22.B, br_04_22.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 15000 | Cannot independently validate stored breaker rating
GSO_125 | br_05_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 10000.0 |  | MV | 36.0974 | -79.9235 | 10000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_05_22.A, br_05_22.B, br_05_22.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 10000 | Cannot independently validate stored breaker rating
GSO_126 | br_06_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 10000.0 |  | MV | 36.0974 | -79.9235 | 10000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_06_22.A, br_06_22.B, br_06_22.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 10000 | Cannot independently validate stored breaker rating
GSO_127 | br_07_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 10000.0 |  | MV | 36.0974 | -79.9235 | 10000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_07_22.A, br_07_22.B, br_07_22.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 10000 | Cannot independently validate stored breaker rating
GSO_128 | br_08_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 10000.0 |  | MV | 36.0974 | -79.9234 | 10000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_08_22.A, br_08_22.B, br_08_22.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 10000 | Cannot independently validate stored breaker rating
GSO_129 | br_09_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 8571.4 |  | MV | 36.0811 | -79.94 | 8571.4 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_09_22.A, br_09_22.B, br_09_22.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 8571.4 | Cannot independently validate stored breaker rating
GSO_13 | br_018_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE10 | S_nSSEE10_12.47 | 5555.6 |  | MV | 36.1003 | -79.8075 | 5555.6 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_018_21.A, br_018_21.B, br_018_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 5555.6 | Cannot independently validate stored breaker rating
GSO_130 | br_010_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 8571.4 |  | MV | 36.0811 | -79.94 | 8571.4 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_010_22.A, br_010_22.B, br_010_22.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 8571.4 | Cannot independently validate stored breaker rating
GSO_131 | br_011_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 8571.4 |  | MV | 36.0811 | -79.94 | 8571.4 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_011_22.A, br_011_22.B, br_011_22.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 8571.4 | Cannot independently validate stored breaker rating
GSO_132 | br_012_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 8571.4 |  | MV | 36.0811 | -79.94 | 8571.4 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_012_22.A, br_012_22.B, br_012_22.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 8571.4 | Cannot independently validate stored breaker rating
GSO_133 | br_013_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 8571.4 |  | MV | 36.0811 | -79.94 | 8571.4 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_013_22.A, br_013_22.B, br_013_22.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 8571.4 | Cannot independently validate stored breaker rating
GSO_134 | br_014_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 8571.4 |  | MV | 36.0811 | -79.94 | 8571.4 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_014_22.A, br_014_22.B, br_014_22.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 8571.4 | Cannot independently validate stored breaker rating
GSO_135 | br_015_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 8571.4 |  | MV | 36.0811 | -79.94 | 8571.4 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_015_22.A, br_015_22.B, br_015_22.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 8571.4 | Cannot independently validate stored breaker rating
GSO_136 | br_016_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE3 | S_nSSEE3_12.47 | 6000.0 |  | MV | 36.0705 | -79.9556 | 6000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_016_22.A, br_016_22.B, br_016_22.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 6000 | Cannot independently validate stored breaker rating
GSO_137 | br_017_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE3 | S_nSSEE3_12.47 | 6000.0 |  | MV | 36.0705 | -79.9557 | 6000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_017_22.A, br_017_22.B, br_017_22.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 6000 | Cannot independently validate stored breaker rating
GSO_138 | br_018_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE3 | S_nSSEE3_12.47 | 6000.0 |  | MV | 36.0705 | -79.9556 | 6000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_018_22.A, br_018_22.B, br_018_22.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 6000 | Cannot independently validate stored breaker rating
GSO_139 | br_019_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE3 | S_nSSEE3_12.47 | 6000.0 |  | MV | 36.0705 | -79.9557 | 6000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_019_22.A, br_019_22.B, br_019_22.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 6000 | Cannot independently validate stored breaker rating
GSO_14 | br_019_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE10 | S_nSSEE10_12.47 | 5555.6 |  | MV | 36.1003 | -79.8075 | 5555.6 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_019_21.A, br_019_21.B, br_019_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 5555.6 | Cannot independently validate stored breaker rating
GSO_140 | br_020_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE3 | S_nSSEE3_12.47 | 6000.0 |  | MV | 36.0705 | -79.9556 | 6000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_020_22.A, br_020_22.B, br_020_22.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 6000 | Cannot independently validate stored breaker rating
GSO_141 | br_021_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 12000.0 |  | MV | 36.0459 | -79.947 | 12000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_021_22.A, br_021_22.B, br_021_22.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 12000 | Cannot independently validate stored breaker rating
GSO_142 | br_022_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 12000.0 |  | MV | 36.0459 | -79.947 | 12000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_022_22.A, br_022_22.B, br_022_22.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 12000 | Cannot independently validate stored breaker rating
GSO_143 | br_023_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 12000.0 |  | MV | 36.0459 | -79.947 | 12000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_023_22.A, br_023_22.B, br_023_22.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 12000 | Cannot independently validate stored breaker rating
GSO_144 | br_024_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 12000.0 |  | MV | 36.046 | -79.947 | 12000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_024_22.A, br_024_22.B, br_024_22.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 12000 | Cannot independently validate stored breaker rating
GSO_145 | br_025_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 12000.0 |  | MV | 36.046 | -79.947 | 12000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_025_22.A, br_025_22.B, br_025_22.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 12000 | Cannot independently validate stored breaker rating
GSO_146 | br_026_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 7500.0 |  | MV | 36.114 | -79.9604 | 7500 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_026_22.A, br_026_22.B, br_026_22.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 7500 | Cannot independently validate stored breaker rating
GSO_147 | br_027_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 7500.0 |  | MV | 36.114 | -79.9604 | 7500 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_027_22.A, br_027_22.B, br_027_22.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 7500 | Cannot independently validate stored breaker rating
GSO_148 | br_028_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 7500.0 |  | MV | 36.114 | -79.9604 | 7500 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_028_22.A, br_028_22.B, br_028_22.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 7500 | Cannot independently validate stored breaker rating
GSO_149 | br_029_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 7500.0 |  | MV | 36.114 | -79.9604 | 7500 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_029_22.A, br_029_22.B, br_029_22.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 7500 | Cannot independently validate stored breaker rating
GSO_15 | br_020_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE10 | S_nSSEE10_12.47 | 5555.6 |  | MV | 36.1003 | -79.8075 | 5555.6 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_020_21.A, br_020_21.B, br_020_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 5555.6 | Cannot independently validate stored breaker rating
GSO_150 | br_030_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE6 | S_nSSEE6_12.47 | 6000.0 |  | MV | 36.0823 | -79.9238 | 6000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_030_22.A, br_030_22.B, br_030_22.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 6000 | Cannot independently validate stored breaker rating
GSO_151 | br_031_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE6 | S_nSSEE6_12.47 | 6000.0 |  | MV | 36.0823 | -79.9238 | 6000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_031_22.A, br_031_22.B, br_031_22.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 6000 | Cannot independently validate stored breaker rating
GSO_152 | br_032_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE6 | S_nSSEE6_12.47 | 6000.0 |  | MV | 36.0823 | -79.9238 | 6000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_032_22.A, br_032_22.B, br_032_22.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 6000 | Cannot independently validate stored breaker rating
GSO_153 | br_033_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE6 | S_nSSEE6_12.47 | 6000.0 |  | MV | 36.0823 | -79.9238 | 6000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_033_22.A, br_033_22.B, br_033_22.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 6000 | Cannot independently validate stored breaker rating
GSO_154 | br_034_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE6 | S_nSSEE6_12.47 | 6000.0 |  | MV | 36.0823 | -79.9238 | 6000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_034_22.A, br_034_22.B, br_034_22.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 6000 | Cannot independently validate stored breaker rating
GSO_155 | br_01_23 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 7500.0 |  | MV | 36.1928 | -79.6069 | 7500 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_01_23.A, br_01_23.B, br_01_23.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 7500 | Cannot independently validate stored breaker rating
GSO_156 | br_02_23 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 7500.0 |  | MV | 36.1929 | -79.6068 | 7500 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_02_23.A, br_02_23.B, br_02_23.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 7500 | Cannot independently validate stored breaker rating
GSO_157 | br_03_23 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 7500.0 |  | MV | 36.1929 | -79.6068 | 7500 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_03_23.A, br_03_23.B, br_03_23.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 7500 | Cannot independently validate stored breaker rating
GSO_158 | br_04_23 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 7500.0 |  | MV | 36.1929 | -79.6068 | 7500 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_04_23.A, br_04_23.B, br_04_23.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 7500 | Cannot independently validate stored breaker rating
GSO_159 | br_05_23 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 5714.3 |  | MV | 36.2604 | -79.5886 | 5714.3 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_05_23.A, br_05_23.B, br_05_23.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 5714.3 | Cannot independently validate stored breaker rating
GSO_16 | br_021_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE10 | S_nSSEE10_12.47 | 5555.6 |  | MV | 36.1003 | -79.8075 | 5555.6 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_021_21.A, br_021_21.B, br_021_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 5555.6 | Cannot independently validate stored breaker rating
GSO_160 | br_06_23 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 5714.3 |  | MV | 36.2604 | -79.5886 | 5714.3 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_06_23.A, br_06_23.B, br_06_23.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 5714.3 | Cannot independently validate stored breaker rating
GSO_161 | br_07_23 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 5714.3 |  | MV | 36.2604 | -79.5886 | 5714.3 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_07_23.A, br_07_23.B, br_07_23.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 5714.3 | Cannot independently validate stored breaker rating
GSO_162 | br_08_23 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 8000.0 |  | MV | 36.1644 | -79.7079 | 8000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_08_23.A, br_08_23.B, br_08_23.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 8000 | Cannot independently validate stored breaker rating
GSO_163 | br_09_23 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 8000.0 |  | MV | 36.1644 | -79.708 | 8000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_09_23.A, br_09_23.B, br_09_23.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 8000 | Cannot independently validate stored breaker rating
GSO_17 | br_024_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE11 | S_nSSEE11_12.47 | 13333.3 |  | MV | 36.0264 | -79.8286 | 13333.3 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_024_21.A, br_024_21.B, br_024_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 13333.3 | Cannot independently validate stored breaker rating
GSO_18 | br_025_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE11 | S_nSSEE11_12.47 | 13333.3 |  | MV | 36.0264 | -79.8286 | 13333.3 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_025_21.A, br_025_21.B, br_025_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 13333.3 | Cannot independently validate stored breaker rating
GSO_19 | br_026_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE11 | S_nSSEE11_12.47 | 13333.3 |  | MV | 36.0264 | -79.8286 | 13333.3 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_026_21.A, br_026_21.B, br_026_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 13333.3 | Cannot independently validate stored breaker rating
GSO_2 | br_02_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 5714.3 |  | MV | 36.0852 | -79.8827 | 5714.3 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_02_21.A, br_02_21.B, br_02_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 5714.3 | Cannot independently validate stored breaker rating
GSO_20 | br_027_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE12 | S_nSSEE12_12.47 | 3750.0 |  | MV | 36.0604 | -79.8599 | 3750 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_027_21.A, br_027_21.B, br_027_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 3750 | Cannot independently validate stored breaker rating
GSO_21 | br_028_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE12 | S_nSSEE12_12.47 | 3750.0 |  | MV | 36.0604 | -79.8599 | 3750 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_028_21.A, br_028_21.B, br_028_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 3750 | Cannot independently validate stored breaker rating
GSO_22 | br_029_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE12 | S_nSSEE12_12.47 | 3750.0 |  | MV | 36.0604 | -79.8599 | 3750 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_029_21.A, br_029_21.B, br_029_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 3750 | Cannot independently validate stored breaker rating
GSO_23 | br_030_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE12 | S_nSSEE12_12.47 | 3750.0 |  | MV | 36.0604 | -79.8599 | 3750 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_030_21.A, br_030_21.B, br_030_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 3750 | Cannot independently validate stored breaker rating
GSO_24 | br_031_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE12 | S_nSSEE12_12.47 | 3750.0 |  | MV | 36.0603 | -79.8599 | 3750 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_031_21.A, br_031_21.B, br_031_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 3750 | Cannot independently validate stored breaker rating
GSO_25 | br_032_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE12 | S_nSSEE12_12.47 | 3750.0 |  | MV | 36.0603 | -79.8599 | 3750 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_032_21.A, br_032_21.B, br_032_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 3750 | Cannot independently validate stored breaker rating
GSO_26 | br_033_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE12 | S_nSSEE12_12.47 | 3750.0 |  | MV | 36.0603 | -79.8599 | 3750 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_033_21.A, br_033_21.B, br_033_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 3750 | Cannot independently validate stored breaker rating
GSO_27 | br_034_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE12 | S_nSSEE12_12.47 | 3750.0 |  | MV | 36.0604 | -79.8599 | 3750 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_034_21.A, br_034_21.B, br_034_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 3750 | Cannot independently validate stored breaker rating
GSO_28 | br_035_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE13 | S_nSSEE13_12.47 | 7500.0 |  | MV | 36.1038 | -79.7639 | 7500 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_035_21.A, br_035_21.B, br_035_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 7500 | Cannot independently validate stored breaker rating
GSO_29 | br_036_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE13 | S_nSSEE13_12.47 | 7500.0 |  | MV | 36.1038 | -79.7639 | 7500 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_036_21.A, br_036_21.B, br_036_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 7500 | Cannot independently validate stored breaker rating
GSO_3 | br_03_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 5714.3 |  | MV | 36.0852 | -79.8826 | 5714.3 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_03_21.A, br_03_21.B, br_03_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 5714.3 | Cannot independently validate stored breaker rating
GSO_30 | br_037_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE13 | S_nSSEE13_12.47 | 7500.0 |  | MV | 36.1038 | -79.7639 | 7500 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_037_21.A, br_037_21.B, br_037_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 7500 | Cannot independently validate stored breaker rating
GSO_31 | br_038_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE13 | S_nSSEE13_12.47 | 7500.0 |  | MV | 36.1038 | -79.7639 | 7500 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_038_21.A, br_038_21.B, br_038_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 7500 | Cannot independently validate stored breaker rating
GSO_32 | br_039_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE14 | S_nSSEE14_12.47 | 6666.7 |  | MV | 36.0466 | -79.7995 | 6666.7 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_039_21.A, br_039_21.B, br_039_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 6666.7 | Cannot independently validate stored breaker rating
GSO_33 | br_040_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE14 | S_nSSEE14_12.47 | 6666.7 |  | MV | 36.0466 | -79.7995 | 6666.7 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_040_21.A, br_040_21.B, br_040_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 6666.7 | Cannot independently validate stored breaker rating
GSO_34 | br_041_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE14 | S_nSSEE14_12.47 | 6666.7 |  | MV | 36.0466 | -79.7995 | 6666.7 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_041_21.A, br_041_21.B, br_041_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 6666.7 | Cannot independently validate stored breaker rating
GSO_35 | br_042_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE14 | S_nSSEE14_12.47 | 6666.7 |  | MV | 36.0466 | -79.7995 | 6666.7 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_042_21.A, br_042_21.B, br_042_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 6666.7 | Cannot independently validate stored breaker rating
GSO_36 | br_043_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE14 | S_nSSEE14_12.47 | 6666.7 |  | MV | 36.0466 | -79.7995 | 6666.7 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_043_21.A, br_043_21.B, br_043_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 6666.7 | Cannot independently validate stored breaker rating
GSO_37 | br_044_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE14 | S_nSSEE14_12.47 | 6666.7 |  | MV | 36.0466 | -79.7995 | 6666.7 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_044_21.A, br_044_21.B, br_044_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 6666.7 | Cannot independently validate stored breaker rating
GSO_38 | br_045_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE15 | S_nSSEE15_12.47 | 6000.0 |  | MV | 36.121 | -79.8612 | 6000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_045_21.A, br_045_21.B, br_045_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 6000 | Cannot independently validate stored breaker rating
GSO_39 | br_046_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE15 | S_nSSEE15_12.47 | 6000.0 |  | MV | 36.121 | -79.8612 | 6000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_046_21.A, br_046_21.B, br_046_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 6000 | Cannot independently validate stored breaker rating
GSO_4 | br_04_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 5714.3 |  | MV | 36.0852 | -79.8827 | 5714.3 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_04_21.A, br_04_21.B, br_04_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 5714.3 | Cannot independently validate stored breaker rating
GSO_40 | br_047_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE15 | S_nSSEE15_12.47 | 6000.0 |  | MV | 36.121 | -79.8612 | 6000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_047_21.A, br_047_21.B, br_047_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 6000 | Cannot independently validate stored breaker rating
GSO_41 | br_048_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE15 | S_nSSEE15_12.47 | 6000.0 |  | MV | 36.121 | -79.8612 | 6000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_048_21.A, br_048_21.B, br_048_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 6000 | Cannot independently validate stored breaker rating
GSO_42 | br_049_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE15 | S_nSSEE15_12.47 | 6000.0 |  | MV | 36.121 | -79.8612 | 6000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_049_21.A, br_049_21.B, br_049_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 6000 | Cannot independently validate stored breaker rating
GSO_43 | br_050_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV | 36.0168 | -79.7965 | 5454.5 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_050_21.A, br_050_21.B, br_050_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 5454.5 | Cannot independently validate stored breaker rating
GSO_44 | br_051_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV | 36.0168 | -79.7965 | 5454.5 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_051_21.A, br_051_21.B, br_051_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 5454.5 | Cannot independently validate stored breaker rating
GSO_45 | br_052_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV | 36.0168 | -79.7965 | 5454.5 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_052_21.A, br_052_21.B, br_052_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 5454.5 | Cannot independently validate stored breaker rating
GSO_46 | br_053_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV | 36.0168 | -79.7965 | 5454.5 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_053_21.A, br_053_21.B, br_053_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 5454.5 | Cannot independently validate stored breaker rating
GSO_47 | br_054_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV | 36.0168 | -79.7965 | 5454.5 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_054_21.A, br_054_21.B, br_054_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 5454.5 | Cannot independently validate stored breaker rating
GSO_48 | br_055_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV | 36.0168 | -79.7965 | 5454.5 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_055_21.A, br_055_21.B, br_055_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 5454.5 | Cannot independently validate stored breaker rating
GSO_49 | br_056_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV | 36.0168 | -79.7965 | 5454.5 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_056_21.A, br_056_21.B, br_056_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 5454.5 | Cannot independently validate stored breaker rating
GSO_5 | br_05_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 5714.3 |  | MV | 36.0852 | -79.8827 | 5714.3 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_05_21.A, br_05_21.B, br_05_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 5714.3 | Cannot independently validate stored breaker rating
GSO_50 | br_057_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV | 36.0168 | -79.7965 | 5454.5 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_057_21.A, br_057_21.B, br_057_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 5454.5 | Cannot independently validate stored breaker rating
GSO_51 | br_058_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV | 36.0168 | -79.7965 | 5454.5 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_058_21.A, br_058_21.B, br_058_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 5454.5 | Cannot independently validate stored breaker rating
GSO_52 | br_059_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV | 36.0168 | -79.7965 | 5454.5 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_059_21.A, br_059_21.B, br_059_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 5454.5 | Cannot independently validate stored breaker rating
GSO_53 | br_060_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV | 36.0168 | -79.7965 | 5454.5 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_060_21.A, br_060_21.B, br_060_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 5454.5 | Cannot independently validate stored breaker rating
GSO_54 | br_061_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE17 | S_nSSEE17_12.47 | 10000.0 |  | MV | 36.0131 | -79.8489 | 10000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_061_21.A, br_061_21.B, br_061_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 10000 | Cannot independently validate stored breaker rating
GSO_55 | br_062_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE17 | S_nSSEE17_12.47 | 10000.0 |  | MV | 36.0131 | -79.8489 | 10000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_062_21.A, br_062_21.B, br_062_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 10000 | Cannot independently validate stored breaker rating
GSO_56 | br_063_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE17 | S_nSSEE17_12.47 | 10000.0 |  | MV | 36.0131 | -79.8489 | 10000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_063_21.A, br_063_21.B, br_063_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 10000 | Cannot independently validate stored breaker rating
GSO_57 | br_08_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 6122.4 |  | MV | 36.0872 | -79.8446 | 6122.4 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_08_21.A, br_08_21.B, br_08_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 6122.4 | Cannot independently validate stored breaker rating
GSO_58 | br_09_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 6122.4 |  | MV | 36.0872 | -79.8446 | 6122.4 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_09_21.A, br_09_21.B, br_09_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 6122.4 | Cannot independently validate stored breaker rating
GSO_59 | br_010_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 6122.4 |  | MV | 36.0873 | -79.8446 | 6122.4 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_010_21.A, br_010_21.B, br_010_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 6122.4 | Cannot independently validate stored breaker rating
GSO_6 | br_06_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 5714.3 |  | MV | 36.0852 | -79.8827 | 5714.3 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_06_21.A, br_06_21.B, br_06_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 5714.3 | Cannot independently validate stored breaker rating
GSO_60 | br_011_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 6122.4 |  | MV | 36.0873 | -79.8446 | 6122.4 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_011_21.A, br_011_21.B, br_011_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 6122.4 | Cannot independently validate stored breaker rating
GSO_61 | br_012_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 6122.4 |  | MV | 36.0872 | -79.8446 | 6122.4 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_012_21.A, br_012_21.B, br_012_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 6122.4 | Cannot independently validate stored breaker rating
GSO_62 | br_013_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 6122.4 |  | MV | 36.0873 | -79.8446 | 6122.4 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_013_21.A, br_013_21.B, br_013_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 6122.4 | Cannot independently validate stored breaker rating
GSO_63 | br_014_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 6122.4 |  | MV | 36.0873 | -79.8446 | 6122.4 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_014_21.A, br_014_21.B, br_014_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 6122.4 | Cannot independently validate stored breaker rating
GSO_64 | br_064_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 4285.7 |  | MV | 36.0801 | -79.7573 | 4285.7 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_064_21.A, br_064_21.B, br_064_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 4285.7 | Cannot independently validate stored breaker rating
GSO_65 | br_065_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 4285.7 |  | MV | 36.0801 | -79.7573 | 4285.7 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_065_21.A, br_065_21.B, br_065_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 4285.7 | Cannot independently validate stored breaker rating
GSO_66 | br_066_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 4285.7 |  | MV | 36.0801 | -79.7573 | 4285.7 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_066_21.A, br_066_21.B, br_066_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 4285.7 | Cannot independently validate stored breaker rating
GSO_67 | br_067_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 4285.7 |  | MV | 36.0801 | -79.7573 | 4285.7 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_067_21.A, br_067_21.B, br_067_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 4285.7 | Cannot independently validate stored breaker rating
GSO_68 | br_068_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 4285.7 |  | MV | 36.0801 | -79.7573 | 4285.7 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_068_21.A, br_068_21.B, br_068_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 4285.7 | Cannot independently validate stored breaker rating
GSO_69 | br_069_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 4285.7 |  | MV | 36.0801 | -79.7573 | 4285.7 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_069_21.A, br_069_21.B, br_069_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 4285.7 | Cannot independently validate stored breaker rating
GSO_7 | br_07_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 5714.3 |  | MV | 36.0852 | -79.8826 | 5714.3 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_07_21.A, br_07_21.B, br_07_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 5714.3 | Cannot independently validate stored breaker rating
GSO_70 | br_070_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 4285.7 |  | MV | 36.0801 | -79.7573 | 4285.7 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_070_21.A, br_070_21.B, br_070_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 4285.7 | Cannot independently validate stored breaker rating
GSO_71 | br_071_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE3 | S_nSSEE3_12.47 | 10000.0 |  | MV | 36.0825 | -79.7708 | 10000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_071_21.A, br_071_21.B, br_071_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 10000 | Cannot independently validate stored breaker rating
GSO_72 | br_072_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE3 | S_nSSEE3_12.47 | 10000.0 |  | MV | 36.0825 | -79.7708 | 10000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_072_21.A, br_072_21.B, br_072_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 10000 | Cannot independently validate stored breaker rating
GSO_73 | br_073_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE3 | S_nSSEE3_12.47 | 10000.0 |  | MV | 36.0825 | -79.7708 | 10000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_073_21.A, br_073_21.B, br_073_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 10000 | Cannot independently validate stored breaker rating
GSO_74 | br_074_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE3 | S_nSSEE3_12.47 | 10000.0 |  | MV | 36.0825 | -79.7708 | 10000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_074_21.A, br_074_21.B, br_074_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 10000 | Cannot independently validate stored breaker rating
GSO_75 | br_075_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE3 | S_nSSEE3_12.47 | 10000.0 |  | MV | 36.0825 | -79.7708 | 10000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_075_21.A, br_075_21.B, br_075_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 10000 | Cannot independently validate stored breaker rating
GSO_76 | br_076_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV | 36.0719 | -79.8252 | 6666.7 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_076_21.A, br_076_21.B, br_076_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 6666.7 | Cannot independently validate stored breaker rating
GSO_77 | br_077_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV | 36.0719 | -79.8252 | 6666.7 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_077_21.A, br_077_21.B, br_077_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 6666.7 | Cannot independently validate stored breaker rating
GSO_78 | br_078_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV | 36.0719 | -79.8252 | 6666.7 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_078_21.A, br_078_21.B, br_078_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 6666.7 | Cannot independently validate stored breaker rating
GSO_79 | br_079_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV | 36.0719 | -79.8252 | 6666.7 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_079_21.A, br_079_21.B, br_079_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 6666.7 | Cannot independently validate stored breaker rating
GSO_8 | br_022_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE10 | S_nSSEE10_12.47 | 5555.6 |  | MV | 36.1003 | -79.8075 | 5555.6 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_022_21.A, br_022_21.B, br_022_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 5555.6 | Cannot independently validate stored breaker rating
GSO_80 | br_080_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV | 36.0719 | -79.8252 | 6666.7 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_080_21.A, br_080_21.B, br_080_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 6666.7 | Cannot independently validate stored breaker rating
GSO_81 | br_081_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV | 36.0719 | -79.8252 | 6666.7 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_081_21.A, br_081_21.B, br_081_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 6666.7 | Cannot independently validate stored breaker rating
GSO_82 | br_082_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV | 36.0719 | -79.8252 | 6666.7 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_082_21.A, br_082_21.B, br_082_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 6666.7 | Cannot independently validate stored breaker rating
GSO_83 | br_083_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV | 36.0719 | -79.8252 | 6666.7 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_083_21.A, br_083_21.B, br_083_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 6666.7 | Cannot independently validate stored breaker rating
GSO_84 | br_084_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV | 36.0719 | -79.8252 | 6666.7 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_084_21.A, br_084_21.B, br_084_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 6666.7 | Cannot independently validate stored breaker rating
GSO_85 | br_085_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV | 36.0719 | -79.8252 | 6666.7 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_085_21.A, br_085_21.B, br_085_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 6666.7 | Cannot independently validate stored breaker rating
GSO_86 | br_086_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV | 36.0708 | -79.7962 | 4545.5 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_086_21.A, br_086_21.B, br_086_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 4545.5 | Cannot independently validate stored breaker rating
GSO_87 | br_087_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV | 36.0709 | -79.7962 | 4545.5 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_087_21.A, br_087_21.B, br_087_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 4545.5 | Cannot independently validate stored breaker rating
GSO_88 | br_088_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV | 36.0708 | -79.7962 | 4545.5 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_088_21.A, br_088_21.B, br_088_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 4545.5 | Cannot independently validate stored breaker rating
GSO_89 | br_089_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV | 36.0708 | -79.7962 | 4545.5 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_089_21.A, br_089_21.B, br_089_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 4545.5 | Cannot independently validate stored breaker rating
GSO_9 | br_023_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE10 | S_nSSEE10_12.47 | 5555.6 |  | MV | 36.1003 | -79.8075 | 5555.6 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_023_21.A, br_023_21.B, br_023_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 5555.6 | Cannot independently validate stored breaker rating
GSO_90 | br_090_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV | 36.0708 | -79.7962 | 4545.5 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_090_21.A, br_090_21.B, br_090_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 4545.5 | Cannot independently validate stored breaker rating
GSO_91 | br_091_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV | 36.0708 | -79.7962 | 4545.5 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_091_21.A, br_091_21.B, br_091_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 4545.5 | Cannot independently validate stored breaker rating
GSO_92 | br_092_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV | 36.0708 | -79.7962 | 4545.5 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_092_21.A, br_092_21.B, br_092_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 4545.5 | Cannot independently validate stored breaker rating
GSO_93 | br_093_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV | 36.0709 | -79.7962 | 4545.5 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_093_21.A, br_093_21.B, br_093_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 4545.5 | Cannot independently validate stored breaker rating
GSO_94 | br_094_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV | 36.0708 | -79.7962 | 4545.5 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_094_21.A, br_094_21.B, br_094_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 4545.5 | Cannot independently validate stored breaker rating
GSO_95 | br_095_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV | 36.0709 | -79.7962 | 4545.5 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_095_21.A, br_095_21.B, br_095_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 4545.5 | Cannot independently validate stored breaker rating
GSO_96 | br_096_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV | 36.0708 | -79.7962 | 4545.5 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_096_21.A, br_096_21.B, br_096_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 4545.5 | Cannot independently validate stored breaker rating
GSO_97 | br_098_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE6 | S_nSSEE6_12.47 | 7500.0 |  | MV | 36.061 | -79.7714 | 7500 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_098_21.A, br_098_21.B, br_098_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 7500 | Cannot independently validate stored breaker rating
GSO_98 | br_099_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE6 | S_nSSEE6_12.47 | 7500.0 |  | MV | 36.0611 | -79.7715 | 7500 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_099_21.A, br_099_21.B, br_099_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 7500 | Cannot independently validate stored breaker rating
GSO_99 | br_0100_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE6 | S_nSSEE6_12.47 | 7500.0 |  | MV | 36.061 | -79.7715 | 7500 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_0100_21.A, br_0100_21.B, br_0100_21.C | 190 | 1 |  |  |  |  | Stored kVA available; independent calculation unavailable | Medium-Low | Stored breaker rating_kva only |  | 7500 | Cannot independently validate stored breaker rating

## Breaker_Candidates
grid_id | BreakerElementID | ElementType | ElementCustomerType | BreakerPhases | IsProducer | IsConsumer | IsSwitchable | SwitchIsOpen | PowerFlowDirection | UpstreamElementID | Terminal1CN | Terminal2CN | RawRatingKVA | RawRatingA | RawVoltageLevel | Latitude | Longitude | StoredBreakerRatingKVA | BreakerRatingA | BreakerVoltageRaw | KWhSourceCount | UniquePhaseCount | DataSourceTypes | Providers | FriendlyIDs | BreakerSelectionScore | BreakerCandidateRank
GSO_1 | br_01_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 5714.3 |  | MV | 36.0852 | -79.8827 | 5714.3 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_01_21.A, br_01_21.B, br_01_21.C | 190 | 1
GSO_10 | br_015_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE10 | S_nSSEE10_12.47 | 5555.6 |  | MV | 36.1003 | -79.8075 | 5555.6 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_015_21.A, br_015_21.B, br_015_21.C | 190 | 1
GSO_100 | br_097_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE6 | S_nSSEE6_12.47 | 7500.0 |  | MV | 36.0611 | -79.7715 | 7500 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_097_21.A, br_097_21.B, br_097_21.C | 190 | 1
GSO_101 | br_0101_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE7 | S_nSSEE7_12.47 | 5714.3 |  | MV | 36.0872 | -79.897 | 5714.3 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_0101_21.A, br_0101_21.B, br_0101_21.C | 190 | 1
GSO_102 | br_0102_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE7 | S_nSSEE7_12.47 | 5714.3 |  | MV | 36.0872 | -79.897 | 5714.3 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_0102_21.A, br_0102_21.B, br_0102_21.C | 190 | 1
GSO_103 | br_0103_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE7 | S_nSSEE7_12.47 | 5714.3 |  | MV | 36.0872 | -79.897 | 5714.3 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_0103_21.A, br_0103_21.B, br_0103_21.C | 190 | 1
GSO_104 | br_0104_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE7 | S_nSSEE7_12.47 | 5714.3 |  | MV | 36.0872 | -79.897 | 5714.3 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_0104_21.A, br_0104_21.B, br_0104_21.C | 190 | 1
GSO_105 | br_0105_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE7 | S_nSSEE7_12.47 | 5714.3 |  | MV | 36.0872 | -79.897 | 5714.3 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_0105_21.A, br_0105_21.B, br_0105_21.C | 190 | 1
GSO_106 | br_0106_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE7 | S_nSSEE7_12.47 | 5714.3 |  | MV | 36.0872 | -79.897 | 5714.3 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_0106_21.A, br_0106_21.B, br_0106_21.C | 190 | 1
GSO_107 | br_0107_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE7 | S_nSSEE7_12.47 | 5714.3 |  | MV | 36.0872 | -79.897 | 5714.3 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_0107_21.A, br_0107_21.B, br_0107_21.C | 190 | 1
GSO_108 | br_0108_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE8 | S_nSSEE8_12.47 | 7142.9 |  | MV | 36.0543 | -79.8942 | 7142.9 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_0108_21.A, br_0108_21.B, br_0108_21.C | 190 | 1
GSO_109 | br_0109_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE8 | S_nSSEE8_12.47 | 7142.9 |  | MV | 36.0543 | -79.8942 | 7142.9 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_0109_21.A, br_0109_21.B, br_0109_21.C | 190 | 1
GSO_11 | br_016_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE10 | S_nSSEE10_12.47 | 5555.6 |  | MV | 36.1003 | -79.8075 | 5555.6 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_016_21.A, br_016_21.B, br_016_21.C | 190 | 1
GSO_110 | br_0110_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE8 | S_nSSEE8_12.47 | 7142.9 |  | MV | 36.0543 | -79.8942 | 7142.9 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_0110_21.A, br_0110_21.B, br_0110_21.C | 190 | 1
GSO_111 | br_0111_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE8 | S_nSSEE8_12.47 | 7142.9 |  | MV | 36.0543 | -79.8942 | 7142.9 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_0111_21.A, br_0111_21.B, br_0111_21.C | 190 | 1
GSO_112 | br_0112_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE8 | S_nSSEE8_12.47 | 7142.9 |  | MV | 36.0543 | -79.8942 | 7142.9 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_0112_21.A, br_0112_21.B, br_0112_21.C | 190 | 1
GSO_113 | br_0113_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE8 | S_nSSEE8_12.47 | 7142.9 |  | MV | 36.0543 | -79.8942 | 7142.9 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_0113_21.A, br_0113_21.B, br_0113_21.C | 190 | 1
GSO_114 | br_0114_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE8 | S_nSSEE8_12.47 | 7142.9 |  | MV | 36.0543 | -79.8942 | 7142.9 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_0114_21.A, br_0114_21.B, br_0114_21.C | 190 | 1
GSO_115 | br_0115_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE9 | S_nSSEE9_12.47 | 10000.0 |  | MV | 36.0426 | -79.8533 | 10000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_0115_21.A, br_0115_21.B, br_0115_21.C | 190 | 1
GSO_116 | br_0116_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE9 | S_nSSEE9_12.47 | 10000.0 |  | MV | 36.0426 | -79.8533 | 10000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_0116_21.A, br_0116_21.B, br_0116_21.C | 190 | 1
GSO_117 | br_0117_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE9 | S_nSSEE9_12.47 | 10000.0 |  | MV | 36.0426 | -79.8533 | 10000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_0117_21.A, br_0117_21.B, br_0117_21.C | 190 | 1
GSO_118 | br_0118_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE9 | S_nSSEE9_12.47 | 10000.0 |  | MV | 36.0426 | -79.8533 | 10000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_0118_21.A, br_0118_21.B, br_0118_21.C | 190 | 1
GSO_119 | br_0119_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE9 | S_nSSEE9_12.47 | 10000.0 |  | MV | 36.0426 | -79.8533 | 10000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_0119_21.A, br_0119_21.B, br_0119_21.C | 190 | 1
GSO_12 | br_017_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE10 | S_nSSEE10_12.47 | 5555.6 |  | MV | 36.1003 | -79.8075 | 5555.6 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_017_21.A, br_017_21.B, br_017_21.C | 190 | 1
GSO_121 | br_01_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 15000.0 |  | MV | 36.083 | -79.9727 | 15000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_01_22.A, br_01_22.B, br_01_22.C | 190 | 1
GSO_122 | br_02_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 15000.0 |  | MV | 36.083 | -79.9727 | 15000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_02_22.A, br_02_22.B, br_02_22.C | 190 | 1
GSO_123 | br_03_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 15000.0 |  | MV | 36.083 | -79.9727 | 15000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_03_22.A, br_03_22.B, br_03_22.C | 190 | 1
GSO_124 | br_04_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 15000.0 |  | MV | 36.083 | -79.9727 | 15000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_04_22.A, br_04_22.B, br_04_22.C | 190 | 1
GSO_125 | br_05_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 10000.0 |  | MV | 36.0974 | -79.9235 | 10000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_05_22.A, br_05_22.B, br_05_22.C | 190 | 1
GSO_126 | br_06_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 10000.0 |  | MV | 36.0974 | -79.9235 | 10000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_06_22.A, br_06_22.B, br_06_22.C | 190 | 1
GSO_127 | br_07_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 10000.0 |  | MV | 36.0974 | -79.9235 | 10000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_07_22.A, br_07_22.B, br_07_22.C | 190 | 1
GSO_128 | br_08_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 10000.0 |  | MV | 36.0974 | -79.9234 | 10000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_08_22.A, br_08_22.B, br_08_22.C | 190 | 1
GSO_129 | br_09_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 8571.4 |  | MV | 36.0811 | -79.94 | 8571.4 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_09_22.A, br_09_22.B, br_09_22.C | 190 | 1
GSO_13 | br_018_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE10 | S_nSSEE10_12.47 | 5555.6 |  | MV | 36.1003 | -79.8075 | 5555.6 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_018_21.A, br_018_21.B, br_018_21.C | 190 | 1
GSO_130 | br_010_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 8571.4 |  | MV | 36.0811 | -79.94 | 8571.4 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_010_22.A, br_010_22.B, br_010_22.C | 190 | 1
GSO_131 | br_011_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 8571.4 |  | MV | 36.0811 | -79.94 | 8571.4 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_011_22.A, br_011_22.B, br_011_22.C | 190 | 1
GSO_132 | br_012_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 8571.4 |  | MV | 36.0811 | -79.94 | 8571.4 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_012_22.A, br_012_22.B, br_012_22.C | 190 | 1
GSO_133 | br_013_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 8571.4 |  | MV | 36.0811 | -79.94 | 8571.4 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_013_22.A, br_013_22.B, br_013_22.C | 190 | 1
GSO_134 | br_014_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 8571.4 |  | MV | 36.0811 | -79.94 | 8571.4 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_014_22.A, br_014_22.B, br_014_22.C | 190 | 1
GSO_135 | br_015_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 8571.4 |  | MV | 36.0811 | -79.94 | 8571.4 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_015_22.A, br_015_22.B, br_015_22.C | 190 | 1
GSO_136 | br_016_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE3 | S_nSSEE3_12.47 | 6000.0 |  | MV | 36.0705 | -79.9556 | 6000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_016_22.A, br_016_22.B, br_016_22.C | 190 | 1
GSO_137 | br_017_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE3 | S_nSSEE3_12.47 | 6000.0 |  | MV | 36.0705 | -79.9557 | 6000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_017_22.A, br_017_22.B, br_017_22.C | 190 | 1
GSO_138 | br_018_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE3 | S_nSSEE3_12.47 | 6000.0 |  | MV | 36.0705 | -79.9556 | 6000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_018_22.A, br_018_22.B, br_018_22.C | 190 | 1
GSO_139 | br_019_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE3 | S_nSSEE3_12.47 | 6000.0 |  | MV | 36.0705 | -79.9557 | 6000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_019_22.A, br_019_22.B, br_019_22.C | 190 | 1
GSO_14 | br_019_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE10 | S_nSSEE10_12.47 | 5555.6 |  | MV | 36.1003 | -79.8075 | 5555.6 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_019_21.A, br_019_21.B, br_019_21.C | 190 | 1
GSO_140 | br_020_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE3 | S_nSSEE3_12.47 | 6000.0 |  | MV | 36.0705 | -79.9556 | 6000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_020_22.A, br_020_22.B, br_020_22.C | 190 | 1
GSO_141 | br_021_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 12000.0 |  | MV | 36.0459 | -79.947 | 12000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_021_22.A, br_021_22.B, br_021_22.C | 190 | 1
GSO_142 | br_022_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 12000.0 |  | MV | 36.0459 | -79.947 | 12000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_022_22.A, br_022_22.B, br_022_22.C | 190 | 1
GSO_143 | br_023_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 12000.0 |  | MV | 36.0459 | -79.947 | 12000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_023_22.A, br_023_22.B, br_023_22.C | 190 | 1
GSO_144 | br_024_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 12000.0 |  | MV | 36.046 | -79.947 | 12000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_024_22.A, br_024_22.B, br_024_22.C | 190 | 1
GSO_145 | br_025_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 12000.0 |  | MV | 36.046 | -79.947 | 12000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_025_22.A, br_025_22.B, br_025_22.C | 190 | 1
GSO_146 | br_026_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 7500.0 |  | MV | 36.114 | -79.9604 | 7500 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_026_22.A, br_026_22.B, br_026_22.C | 190 | 1
GSO_147 | br_027_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 7500.0 |  | MV | 36.114 | -79.9604 | 7500 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_027_22.A, br_027_22.B, br_027_22.C | 190 | 1
GSO_148 | br_028_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 7500.0 |  | MV | 36.114 | -79.9604 | 7500 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_028_22.A, br_028_22.B, br_028_22.C | 190 | 1
GSO_149 | br_029_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 7500.0 |  | MV | 36.114 | -79.9604 | 7500 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_029_22.A, br_029_22.B, br_029_22.C | 190 | 1
GSO_15 | br_020_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE10 | S_nSSEE10_12.47 | 5555.6 |  | MV | 36.1003 | -79.8075 | 5555.6 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_020_21.A, br_020_21.B, br_020_21.C | 190 | 1
GSO_150 | br_030_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE6 | S_nSSEE6_12.47 | 6000.0 |  | MV | 36.0823 | -79.9238 | 6000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_030_22.A, br_030_22.B, br_030_22.C | 190 | 1
GSO_151 | br_031_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE6 | S_nSSEE6_12.47 | 6000.0 |  | MV | 36.0823 | -79.9238 | 6000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_031_22.A, br_031_22.B, br_031_22.C | 190 | 1
GSO_152 | br_032_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE6 | S_nSSEE6_12.47 | 6000.0 |  | MV | 36.0823 | -79.9238 | 6000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_032_22.A, br_032_22.B, br_032_22.C | 190 | 1
GSO_153 | br_033_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE6 | S_nSSEE6_12.47 | 6000.0 |  | MV | 36.0823 | -79.9238 | 6000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_033_22.A, br_033_22.B, br_033_22.C | 190 | 1
GSO_154 | br_034_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE6 | S_nSSEE6_12.47 | 6000.0 |  | MV | 36.0823 | -79.9238 | 6000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_034_22.A, br_034_22.B, br_034_22.C | 190 | 1
GSO_155 | br_01_23 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 7500.0 |  | MV | 36.1928 | -79.6069 | 7500 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_01_23.A, br_01_23.B, br_01_23.C | 190 | 1
GSO_156 | br_02_23 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 7500.0 |  | MV | 36.1929 | -79.6068 | 7500 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_02_23.A, br_02_23.B, br_02_23.C | 190 | 1
GSO_157 | br_03_23 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 7500.0 |  | MV | 36.1929 | -79.6068 | 7500 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_03_23.A, br_03_23.B, br_03_23.C | 190 | 1
GSO_158 | br_04_23 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 7500.0 |  | MV | 36.1929 | -79.6068 | 7500 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_04_23.A, br_04_23.B, br_04_23.C | 190 | 1
GSO_159 | br_05_23 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 5714.3 |  | MV | 36.2604 | -79.5886 | 5714.3 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_05_23.A, br_05_23.B, br_05_23.C | 190 | 1
GSO_16 | br_021_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE10 | S_nSSEE10_12.47 | 5555.6 |  | MV | 36.1003 | -79.8075 | 5555.6 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_021_21.A, br_021_21.B, br_021_21.C | 190 | 1
GSO_160 | br_06_23 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 5714.3 |  | MV | 36.2604 | -79.5886 | 5714.3 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_06_23.A, br_06_23.B, br_06_23.C | 190 | 1
GSO_161 | br_07_23 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 5714.3 |  | MV | 36.2604 | -79.5886 | 5714.3 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_07_23.A, br_07_23.B, br_07_23.C | 190 | 1
GSO_162 | br_08_23 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 8000.0 |  | MV | 36.1644 | -79.7079 | 8000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_08_23.A, br_08_23.B, br_08_23.C | 190 | 1
GSO_163 | br_09_23 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 8000.0 |  | MV | 36.1644 | -79.708 | 8000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_09_23.A, br_09_23.B, br_09_23.C | 190 | 1
GSO_17 | br_024_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE11 | S_nSSEE11_12.47 | 13333.3 |  | MV | 36.0264 | -79.8286 | 13333.3 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_024_21.A, br_024_21.B, br_024_21.C | 190 | 1
GSO_18 | br_025_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE11 | S_nSSEE11_12.47 | 13333.3 |  | MV | 36.0264 | -79.8286 | 13333.3 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_025_21.A, br_025_21.B, br_025_21.C | 190 | 1
GSO_19 | br_026_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE11 | S_nSSEE11_12.47 | 13333.3 |  | MV | 36.0264 | -79.8286 | 13333.3 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_026_21.A, br_026_21.B, br_026_21.C | 190 | 1
GSO_2 | br_02_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 5714.3 |  | MV | 36.0852 | -79.8827 | 5714.3 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_02_21.A, br_02_21.B, br_02_21.C | 190 | 1
GSO_20 | br_027_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE12 | S_nSSEE12_12.47 | 3750.0 |  | MV | 36.0604 | -79.8599 | 3750 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_027_21.A, br_027_21.B, br_027_21.C | 190 | 1
GSO_21 | br_028_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE12 | S_nSSEE12_12.47 | 3750.0 |  | MV | 36.0604 | -79.8599 | 3750 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_028_21.A, br_028_21.B, br_028_21.C | 190 | 1
GSO_22 | br_029_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE12 | S_nSSEE12_12.47 | 3750.0 |  | MV | 36.0604 | -79.8599 | 3750 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_029_21.A, br_029_21.B, br_029_21.C | 190 | 1
GSO_23 | br_030_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE12 | S_nSSEE12_12.47 | 3750.0 |  | MV | 36.0604 | -79.8599 | 3750 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_030_21.A, br_030_21.B, br_030_21.C | 190 | 1
GSO_24 | br_031_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE12 | S_nSSEE12_12.47 | 3750.0 |  | MV | 36.0603 | -79.8599 | 3750 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_031_21.A, br_031_21.B, br_031_21.C | 190 | 1
GSO_25 | br_032_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE12 | S_nSSEE12_12.47 | 3750.0 |  | MV | 36.0603 | -79.8599 | 3750 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_032_21.A, br_032_21.B, br_032_21.C | 190 | 1
GSO_26 | br_033_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE12 | S_nSSEE12_12.47 | 3750.0 |  | MV | 36.0603 | -79.8599 | 3750 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_033_21.A, br_033_21.B, br_033_21.C | 190 | 1
GSO_27 | br_034_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE12 | S_nSSEE12_12.47 | 3750.0 |  | MV | 36.0604 | -79.8599 | 3750 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_034_21.A, br_034_21.B, br_034_21.C | 190 | 1
GSO_28 | br_035_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE13 | S_nSSEE13_12.47 | 7500.0 |  | MV | 36.1038 | -79.7639 | 7500 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_035_21.A, br_035_21.B, br_035_21.C | 190 | 1
GSO_29 | br_036_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE13 | S_nSSEE13_12.47 | 7500.0 |  | MV | 36.1038 | -79.7639 | 7500 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_036_21.A, br_036_21.B, br_036_21.C | 190 | 1
GSO_3 | br_03_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 5714.3 |  | MV | 36.0852 | -79.8826 | 5714.3 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_03_21.A, br_03_21.B, br_03_21.C | 190 | 1
GSO_30 | br_037_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE13 | S_nSSEE13_12.47 | 7500.0 |  | MV | 36.1038 | -79.7639 | 7500 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_037_21.A, br_037_21.B, br_037_21.C | 190 | 1
GSO_31 | br_038_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE13 | S_nSSEE13_12.47 | 7500.0 |  | MV | 36.1038 | -79.7639 | 7500 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_038_21.A, br_038_21.B, br_038_21.C | 190 | 1
GSO_32 | br_039_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE14 | S_nSSEE14_12.47 | 6666.7 |  | MV | 36.0466 | -79.7995 | 6666.7 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_039_21.A, br_039_21.B, br_039_21.C | 190 | 1
GSO_33 | br_040_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE14 | S_nSSEE14_12.47 | 6666.7 |  | MV | 36.0466 | -79.7995 | 6666.7 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_040_21.A, br_040_21.B, br_040_21.C | 190 | 1
GSO_34 | br_041_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE14 | S_nSSEE14_12.47 | 6666.7 |  | MV | 36.0466 | -79.7995 | 6666.7 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_041_21.A, br_041_21.B, br_041_21.C | 190 | 1
GSO_35 | br_042_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE14 | S_nSSEE14_12.47 | 6666.7 |  | MV | 36.0466 | -79.7995 | 6666.7 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_042_21.A, br_042_21.B, br_042_21.C | 190 | 1
GSO_36 | br_043_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE14 | S_nSSEE14_12.47 | 6666.7 |  | MV | 36.0466 | -79.7995 | 6666.7 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_043_21.A, br_043_21.B, br_043_21.C | 190 | 1
GSO_37 | br_044_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE14 | S_nSSEE14_12.47 | 6666.7 |  | MV | 36.0466 | -79.7995 | 6666.7 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_044_21.A, br_044_21.B, br_044_21.C | 190 | 1
GSO_38 | br_045_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE15 | S_nSSEE15_12.47 | 6000.0 |  | MV | 36.121 | -79.8612 | 6000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_045_21.A, br_045_21.B, br_045_21.C | 190 | 1
GSO_39 | br_046_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE15 | S_nSSEE15_12.47 | 6000.0 |  | MV | 36.121 | -79.8612 | 6000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_046_21.A, br_046_21.B, br_046_21.C | 190 | 1
GSO_4 | br_04_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 5714.3 |  | MV | 36.0852 | -79.8827 | 5714.3 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_04_21.A, br_04_21.B, br_04_21.C | 190 | 1
GSO_40 | br_047_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE15 | S_nSSEE15_12.47 | 6000.0 |  | MV | 36.121 | -79.8612 | 6000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_047_21.A, br_047_21.B, br_047_21.C | 190 | 1
GSO_41 | br_048_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE15 | S_nSSEE15_12.47 | 6000.0 |  | MV | 36.121 | -79.8612 | 6000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_048_21.A, br_048_21.B, br_048_21.C | 190 | 1
GSO_42 | br_049_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE15 | S_nSSEE15_12.47 | 6000.0 |  | MV | 36.121 | -79.8612 | 6000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_049_21.A, br_049_21.B, br_049_21.C | 190 | 1
GSO_43 | br_050_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV | 36.0168 | -79.7965 | 5454.5 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_050_21.A, br_050_21.B, br_050_21.C | 190 | 1
GSO_44 | br_051_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV | 36.0168 | -79.7965 | 5454.5 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_051_21.A, br_051_21.B, br_051_21.C | 190 | 1
GSO_45 | br_052_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV | 36.0168 | -79.7965 | 5454.5 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_052_21.A, br_052_21.B, br_052_21.C | 190 | 1
GSO_46 | br_053_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV | 36.0168 | -79.7965 | 5454.5 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_053_21.A, br_053_21.B, br_053_21.C | 190 | 1
GSO_47 | br_054_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV | 36.0168 | -79.7965 | 5454.5 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_054_21.A, br_054_21.B, br_054_21.C | 190 | 1
GSO_48 | br_055_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV | 36.0168 | -79.7965 | 5454.5 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_055_21.A, br_055_21.B, br_055_21.C | 190 | 1
GSO_49 | br_056_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV | 36.0168 | -79.7965 | 5454.5 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_056_21.A, br_056_21.B, br_056_21.C | 190 | 1
GSO_5 | br_05_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 5714.3 |  | MV | 36.0852 | -79.8827 | 5714.3 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_05_21.A, br_05_21.B, br_05_21.C | 190 | 1
GSO_50 | br_057_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV | 36.0168 | -79.7965 | 5454.5 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_057_21.A, br_057_21.B, br_057_21.C | 190 | 1
GSO_51 | br_058_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV | 36.0168 | -79.7965 | 5454.5 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_058_21.A, br_058_21.B, br_058_21.C | 190 | 1
GSO_52 | br_059_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV | 36.0168 | -79.7965 | 5454.5 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_059_21.A, br_059_21.B, br_059_21.C | 190 | 1
GSO_53 | br_060_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV | 36.0168 | -79.7965 | 5454.5 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_060_21.A, br_060_21.B, br_060_21.C | 190 | 1
GSO_54 | br_061_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE17 | S_nSSEE17_12.47 | 10000.0 |  | MV | 36.0131 | -79.8489 | 10000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_061_21.A, br_061_21.B, br_061_21.C | 190 | 1
GSO_55 | br_062_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE17 | S_nSSEE17_12.47 | 10000.0 |  | MV | 36.0131 | -79.8489 | 10000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_062_21.A, br_062_21.B, br_062_21.C | 190 | 1
GSO_56 | br_063_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE17 | S_nSSEE17_12.47 | 10000.0 |  | MV | 36.0131 | -79.8489 | 10000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_063_21.A, br_063_21.B, br_063_21.C | 190 | 1
GSO_57 | br_08_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 6122.4 |  | MV | 36.0872 | -79.8446 | 6122.4 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_08_21.A, br_08_21.B, br_08_21.C | 190 | 1
GSO_58 | br_09_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 6122.4 |  | MV | 36.0872 | -79.8446 | 6122.4 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_09_21.A, br_09_21.B, br_09_21.C | 190 | 1
GSO_59 | br_010_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 6122.4 |  | MV | 36.0873 | -79.8446 | 6122.4 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_010_21.A, br_010_21.B, br_010_21.C | 190 | 1
GSO_6 | br_06_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 5714.3 |  | MV | 36.0852 | -79.8827 | 5714.3 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_06_21.A, br_06_21.B, br_06_21.C | 190 | 1
GSO_60 | br_011_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 6122.4 |  | MV | 36.0873 | -79.8446 | 6122.4 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_011_21.A, br_011_21.B, br_011_21.C | 190 | 1
GSO_61 | br_012_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 6122.4 |  | MV | 36.0872 | -79.8446 | 6122.4 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_012_21.A, br_012_21.B, br_012_21.C | 190 | 1
GSO_62 | br_013_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 6122.4 |  | MV | 36.0873 | -79.8446 | 6122.4 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_013_21.A, br_013_21.B, br_013_21.C | 190 | 1
GSO_63 | br_014_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE1 | S_nSSEE1_12.47 | 6122.4 |  | MV | 36.0873 | -79.8446 | 6122.4 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_014_21.A, br_014_21.B, br_014_21.C | 190 | 1
GSO_64 | br_064_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 4285.7 |  | MV | 36.0801 | -79.7573 | 4285.7 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_064_21.A, br_064_21.B, br_064_21.C | 190 | 1
GSO_65 | br_065_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 4285.7 |  | MV | 36.0801 | -79.7573 | 4285.7 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_065_21.A, br_065_21.B, br_065_21.C | 190 | 1
GSO_66 | br_066_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 4285.7 |  | MV | 36.0801 | -79.7573 | 4285.7 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_066_21.A, br_066_21.B, br_066_21.C | 190 | 1
GSO_67 | br_067_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 4285.7 |  | MV | 36.0801 | -79.7573 | 4285.7 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_067_21.A, br_067_21.B, br_067_21.C | 190 | 1
GSO_68 | br_068_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 4285.7 |  | MV | 36.0801 | -79.7573 | 4285.7 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_068_21.A, br_068_21.B, br_068_21.C | 190 | 1
GSO_69 | br_069_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 4285.7 |  | MV | 36.0801 | -79.7573 | 4285.7 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_069_21.A, br_069_21.B, br_069_21.C | 190 | 1
GSO_7 | br_07_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE0 | S_nSSEE0_12.47 | 5714.3 |  | MV | 36.0852 | -79.8826 | 5714.3 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_07_21.A, br_07_21.B, br_07_21.C | 190 | 1
GSO_70 | br_070_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE2 | S_nSSEE2_12.47 | 4285.7 |  | MV | 36.0801 | -79.7573 | 4285.7 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_070_21.A, br_070_21.B, br_070_21.C | 190 | 1
GSO_71 | br_071_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE3 | S_nSSEE3_12.47 | 10000.0 |  | MV | 36.0825 | -79.7708 | 10000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_071_21.A, br_071_21.B, br_071_21.C | 190 | 1
GSO_72 | br_072_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE3 | S_nSSEE3_12.47 | 10000.0 |  | MV | 36.0825 | -79.7708 | 10000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_072_21.A, br_072_21.B, br_072_21.C | 190 | 1
GSO_73 | br_073_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE3 | S_nSSEE3_12.47 | 10000.0 |  | MV | 36.0825 | -79.7708 | 10000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_073_21.A, br_073_21.B, br_073_21.C | 190 | 1
GSO_74 | br_074_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE3 | S_nSSEE3_12.47 | 10000.0 |  | MV | 36.0825 | -79.7708 | 10000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_074_21.A, br_074_21.B, br_074_21.C | 190 | 1
GSO_75 | br_075_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE3 | S_nSSEE3_12.47 | 10000.0 |  | MV | 36.0825 | -79.7708 | 10000 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_075_21.A, br_075_21.B, br_075_21.C | 190 | 1
GSO_76 | br_076_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV | 36.0719 | -79.8252 | 6666.7 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_076_21.A, br_076_21.B, br_076_21.C | 190 | 1
GSO_77 | br_077_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV | 36.0719 | -79.8252 | 6666.7 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_077_21.A, br_077_21.B, br_077_21.C | 190 | 1
GSO_78 | br_078_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV | 36.0719 | -79.8252 | 6666.7 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_078_21.A, br_078_21.B, br_078_21.C | 190 | 1
GSO_79 | br_079_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV | 36.0719 | -79.8252 | 6666.7 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_079_21.A, br_079_21.B, br_079_21.C | 190 | 1
GSO_8 | br_022_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE10 | S_nSSEE10_12.47 | 5555.6 |  | MV | 36.1003 | -79.8075 | 5555.6 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_022_21.A, br_022_21.B, br_022_21.C | 190 | 1
GSO_80 | br_080_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV | 36.0719 | -79.8252 | 6666.7 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_080_21.A, br_080_21.B, br_080_21.C | 190 | 1
GSO_81 | br_081_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV | 36.0719 | -79.8252 | 6666.7 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_081_21.A, br_081_21.B, br_081_21.C | 190 | 1
GSO_82 | br_082_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV | 36.0719 | -79.8252 | 6666.7 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_082_21.A, br_082_21.B, br_082_21.C | 190 | 1
GSO_83 | br_083_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV | 36.0719 | -79.8252 | 6666.7 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_083_21.A, br_083_21.B, br_083_21.C | 190 | 1
GSO_84 | br_084_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV | 36.0719 | -79.8252 | 6666.7 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_084_21.A, br_084_21.B, br_084_21.C | 190 | 1
GSO_85 | br_085_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV | 36.0719 | -79.8252 | 6666.7 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_085_21.A, br_085_21.B, br_085_21.C | 190 | 1
GSO_86 | br_086_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV | 36.0708 | -79.7962 | 4545.5 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_086_21.A, br_086_21.B, br_086_21.C | 190 | 1
GSO_87 | br_087_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV | 36.0709 | -79.7962 | 4545.5 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_087_21.A, br_087_21.B, br_087_21.C | 190 | 1
GSO_88 | br_088_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV | 36.0708 | -79.7962 | 4545.5 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_088_21.A, br_088_21.B, br_088_21.C | 190 | 1
GSO_89 | br_089_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV | 36.0708 | -79.7962 | 4545.5 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_089_21.A, br_089_21.B, br_089_21.C | 190 | 1
GSO_9 | br_023_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE10 | S_nSSEE10_12.47 | 5555.6 |  | MV | 36.1003 | -79.8075 | 5555.6 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_023_21.A, br_023_21.B, br_023_21.C | 190 | 1
GSO_90 | br_090_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV | 36.0708 | -79.7962 | 4545.5 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_090_21.A, br_090_21.B, br_090_21.C | 190 | 1
GSO_91 | br_091_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV | 36.0708 | -79.7962 | 4545.5 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_091_21.A, br_091_21.B, br_091_21.C | 190 | 1
GSO_92 | br_092_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV | 36.0708 | -79.7962 | 4545.5 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_092_21.A, br_092_21.B, br_092_21.C | 190 | 1
GSO_93 | br_093_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV | 36.0709 | -79.7962 | 4545.5 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_093_21.A, br_093_21.B, br_093_21.C | 190 | 1
GSO_94 | br_094_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV | 36.0708 | -79.7962 | 4545.5 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_094_21.A, br_094_21.B, br_094_21.C | 190 | 1
GSO_95 | br_095_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV | 36.0709 | -79.7962 | 4545.5 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_095_21.A, br_095_21.B, br_095_21.C | 190 | 1
GSO_96 | br_096_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV | 36.0708 | -79.7962 | 4545.5 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_096_21.A, br_096_21.B, br_096_21.C | 190 | 1
GSO_97 | br_098_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE6 | S_nSSEE6_12.47 | 7500.0 |  | MV | 36.061 | -79.7714 | 7500 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_098_21.A, br_098_21.B, br_098_21.C | 190 | 1
GSO_98 | br_099_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE6 | S_nSSEE6_12.47 | 7500.0 |  | MV | 36.0611 | -79.7715 | 7500 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_099_21.A, br_099_21.B, br_099_21.C | 190 | 1
GSO_99 | br_0100_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE | both |  | S_nSSEE6 | S_nSSEE6_12.47 | 7500.0 |  | MV | 36.061 | -79.7715 | 7500 |  |  | 3 | 3 | SENSOR | SMART_scada_data | br_0100_21.A, br_0100_21.B, br_0100_21.C | 190 | 1

## SCADA_Summary
Observations | FirstTimestamp | LastTimestamp | MedianIntervalMinutes | AverageIntervalKWh | P95IntervalKWh | PeakIntervalKWh | AverageLoadMW | P95LoadMW | PeakLoadMW | PeakLoadTimestamp | grid_id | BreakerElementID | SelectedSCADASourceCount | SelectedSCADASourceIDs | SelectedSCADAPhases | SCADAStatus
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 47.6222 | 58.155 | 69.703 | 0.57147 | 0.69786 | 0.83644 | 2024-01-20 19:00 | GSO_1 | br_01_21 | 3 | b1e8c057-fded-4c70-8f86-a33db401b6d1, ba6970aa-af7f-428e-9a4f-7826618684b4, ea496fcb-6216-4db1-9885-1da5dbf70fa2 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 82.8253 | 116.5043 | 157.83 | 0.9939 | 1.3981 | 1.894 | 2024-01-21 04:00 | GSO_10 | br_015_21 | 3 | d140ab36-31a8-40c7-820d-c3a2df82604a, b315ece6-7341-4cdf-a1c9-70a8dbfe93ff, 396f73e2-6041-46ac-90d5-a9439aef50d8 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 14.5529 | 22.36 | 30.904 | 0.17463 | 0.26832 | 0.37085 | 2024-01-20 07:05 | GSO_100 | br_097_21 | 3 | 564551fe-ec45-4b6c-a7df-ebfa29a0a242, 3125b67a-cbd0-47b3-94b6-a60b38de7e8b, cc6f9a7e-ea1b-4cdb-9c85-6c672b845068 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 55.7798 | 73.128 | 93.468 | 0.66936 | 0.87754 | 1.1216 | 2024-01-21 04:00 | GSO_101 | br_0101_21 | 3 | f32aafa6-4f97-40b9-85a1-6516b7a34fb0, 8f1038a0-f3d5-4f15-bedf-b8f1215601f3, 6c559f06-b888-4a9d-ba0f-901b0b19b354 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 1.7953 | 2.775 | 4.54 | 0.021543 | 0.0333 | 0.05448 | 2024-07-15 23:00 | GSO_102 | br_0102_21 | 3 | aaef163c-bdc4-464e-9864-b0c0ebdf8662, 3f11f59f-b6f2-44fe-8a16-f4a87144ca07, 58383f3b-39ee-41c1-9a45-f21c6b309b7c | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 168.1721 | 258.5616 | 348.914 | 2.0181 | 3.1027 | 4.187 | 2024-01-21 04:00 | GSO_103 | br_0103_21 | 3 | d5fd099c-84d4-4965-91b3-bbc0c68d61d1, d53e58ae-230d-449a-b78d-6b5cfa60f56b, a3539c00-7186-4684-93db-03123790cf12 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 159.7475 | 240.7818 | 321.785 | 1.917 | 2.8894 | 3.8614 | 2024-01-21 04:00 | GSO_104 | br_0104_21 | 3 | dbaf906f-b53b-4b15-bd48-42442608214a, 0256f17b-1fde-4e5f-aa42-6a293aa27e64, 4922eba1-a72a-4e22-8a37-912d5f9ac46b | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 150.7342 | 231.125 | 305 | 1.8088 | 2.7735 | 3.66 | 2024-01-21 04:00 | GSO_105 | br_0105_21 | 3 | 3943a935-55e7-44b5-a61e-08789763be18, 11bf4c6d-205c-4caf-b572-7246ab210632, 98dc0614-4560-469e-93e2-97b3c41b5000 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 3.439 | 5.378 | 7.74 | 0.041269 | 0.064536 | 0.09288 | 2024-01-20 10:00 | GSO_106 | br_0106_21 | 3 | 1523bf59-c426-49d7-add2-e9b831978748, e37ebffe-ff65-4277-a7e0-2315cac8c267, f0643cc7-b03a-4328-82d5-2924a650f97f | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 5.7446 | 6.98 | 9.627 | 0.068935 | 0.08376 | 0.11552 | 2024-07-16 01:00 | GSO_107 | br_0107_21 | 3 | 4113937f-0ce2-415a-9249-ce7327d121f7, 5d59abb9-0bac-4fa7-a891-4e9d4e794c88, b1339292-267a-4146-8873-ecfc9cb1a82e | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 106.625 | 159.5309 | 207.686 | 1.2795 | 1.9144 | 2.4922 | 2024-01-20 23:30 | GSO_108 | br_0108_21 | 3 | e867a5e4-d5f1-4fdf-98c8-da37424315a6, c0036365-6459-4cc7-b7b1-ed8933515338, 1886a888-6918-466c-929d-0c8f16370dda | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 96.6701 | 141.014 | 185.217 | 1.16 | 1.6922 | 2.2226 | 2024-01-20 13:00 | GSO_109 | br_0109_21 | 3 | 0c75d1f1-8237-436b-a2c8-c9b6fdc7a116, ec8ad3c4-a39d-4acb-8788-e7435be58cb7, e6350d88-56d8-492b-bc1e-dcd90fcca31f | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 101.1181 | 141.697 | 183.017 | 1.2134 | 1.7004 | 2.1962 | 2024-01-21 04:00 | GSO_11 | br_016_21 | 3 | 469868d0-2f60-42bd-aa67-be26d6eae0eb, 9cdbec33-569a-438b-ac44-23b272ad169b, dfea635f-2a86-40f1-9367-d78b6dd6c309 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 182.8709 | 279.822 | 376.282 | 2.1945 | 3.3579 | 4.5154 | 2024-01-21 04:00 | GSO_110 | br_0110_21 | 3 | 1e111a58-963a-4906-b1f6-e2d03049b19a, 8a0dd243-2512-4f92-afd7-db6e79d7496e, ca02189c-f89b-417b-a469-ef0366d6da6e | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 54.7044 | 75.746 | 96.334 | 0.65645 | 0.90895 | 1.156 | 2024-01-18 04:00 | GSO_111 | br_0111_21 | 3 | f8549391-d242-43a9-9a34-33f872443611, 3488e4fc-fa59-4bcf-b967-3b7a890f6c3c, e60c92cc-e283-4345-87b0-ba3a9fd78005 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 39.8632 | 48.388 | 64.278 | 0.47836 | 0.58066 | 0.77134 | 2024-01-21 04:00 | GSO_112 | br_0112_21 | 3 | 407ea9ca-a495-4119-a139-1d1233852fdc, 99fe4744-38fc-4467-902b-d97556b6d295, e1fd2b67-b072-4575-9f5d-c24af5f52b11 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 4.4835 | 5.424 | 7.604 | 0.053802 | 0.065088 | 0.091248 | 2024-01-20 20:00 | GSO_113 | br_0113_21 | 3 | f8ddca03-2f28-483b-97fe-a4538d6c4e2b, a9bc380c-ca71-4a2b-b314-0f03f9f76581, bdf27366-2b21-4e21-8946-86b299b81d14 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 62.7375 | 88.1806 | 117.2 | 0.75285 | 1.0582 | 1.4064 | 2024-01-20 14:00 | GSO_114 | br_0114_21 | 3 | 34c2c476-7801-4ae6-ba1f-ca1a602925b3, 156d4241-1525-4089-8367-effd61eb4969, 3128527e-a25b-4b2c-9d88-b40eb600580e | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 99.7864 | 143.813 | 189.272 | 1.1974 | 1.7258 | 2.2713 | 2024-01-21 04:00 | GSO_115 | br_0115_21 | 3 | d3645b59-a71d-4848-9deb-b044c307c52a, 820fcd78-48b0-467d-8925-554a0333f605, 58786ac1-7ac2-4287-bd8f-add68a4ea208 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 53.4188 | 70.3586 | 90.053 | 0.64103 | 0.8443 | 1.0806 | 2024-01-20 16:00 | GSO_116 | br_0116_21 | 3 | 2a93f307-f837-4de0-9089-b308bde0f0fd, ba9bd088-fa13-4d76-ba16-6dba6a8b45de, e9542020-950f-403c-af95-965f8434a9f8 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 151.7502 | 223.4966 | 294.004 | 1.821 | 2.682 | 3.528 | 2024-01-18 04:00 | GSO_117 | br_0117_21 | 3 | 20ca2ff7-1194-405d-9098-d4544944a36d, 127d58d0-da5d-47a0-a219-b8c1834a136a, 79b91384-9645-42ed-940d-37fdffcc31a0 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 77.2137 | 103.7746 | 131.03 | 0.92656 | 1.2453 | 1.5724 | 2024-01-20 21:00 | GSO_118 | br_0118_21 | 3 | b2273af8-cb6e-4178-93e7-36fab6dbf2c0, cb23fba1-b5a8-477f-b388-dcbc14cf56b2, 7b9e37f6-9e61-405e-8bc5-9d79097397f4 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 12.4758 | 19.259 | 27.93 | 0.14971 | 0.23111 | 0.33516 | 2024-01-20 22:00 | GSO_119 | br_0119_21 | 3 | 1a46aa48-ac4e-4046-aa43-a61c07c816d6, faec1da7-65b2-4b86-be90-e4357dfde1ce, 3aad3364-ed36-4087-b7d0-6d3b3fa6f823 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 102.8633 | 157.9969 | 208.196 | 1.2344 | 1.896 | 2.4984 | 2024-01-18 04:00 | GSO_12 | br_017_21 | 3 | e263a729-e360-4716-9561-679bf6b5d16a, ede6f7c6-f426-4d65-bfe0-7dac24a794c1, 4c1ed359-972e-4bdd-a0cd-1159d7a32c07 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 20.3889 | 25.3796 | 31.802 | 0.24467 | 0.30456 | 0.38162 | 2024-01-17 23:00 | GSO_121 | br_01_22 | 3 | 0eb7ef08-0441-4661-84d4-63da9255ea41, 36cfcc10-f3c4-4989-ae21-5fdd2aa20962, 423b0798-4793-4a14-a787-72bb51fb4cef | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 1.6439 | 2.003 | 2.73 | 0.019727 | 0.024036 | 0.03276 | 2024-01-20 07:00 | GSO_122 | br_02_22 | 3 | e63f1c25-1cac-49ae-9929-f96fa015f74e, 4fa57e43-e6c7-4d4b-a312-3fb0e3337ffc, abf746be-5de9-44ac-9f69-a717abe29437 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 20.6829 | 24.064 | 30.387 | 0.24819 | 0.28877 | 0.36464 | 2024-01-22 04:00 | GSO_123 | br_03_22 | 3 | 22b46d3c-1104-4a6b-baf0-791554532cbe, c84967ed-4e26-4447-aaec-39d0dba00695, 08fe15ea-b154-4270-ad96-7633898d9feb | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 6.4773 | 7.975 | 11.156 | 0.077728 | 0.0957 | 0.13387 | 2024-01-22 04:00 | GSO_124 | br_04_22 | 3 | e9588dba-e5c4-44a0-a87f-6d585846716c, f9dd1e2c-0b53-4323-abbd-c79d2b87bf2e, cbbe0d2b-6245-4a4f-bcc2-e456b3e84669 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 17.2263 | 20.9386 | 27.008 | 0.20672 | 0.25126 | 0.3241 | 2024-01-20 11:00 | GSO_125 | br_05_22 | 3 | cd7fbbb9-9a6f-4dd9-891c-e37a9557fa12, 16682194-aa4b-49e9-acf2-9c6562595352, 99cabfd6-b964-4658-8155-1699ad43459b | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 13.0851 | 15.753 | 20.182 | 0.15702 | 0.18904 | 0.24218 | 2024-01-20 21:00 | GSO_126 | br_06_22 | 3 | 9006b8b1-eda0-485b-a8d0-426580b8950f, bc3fda03-9c4b-412b-a5ef-6db07eeba8fc, 12d09ac1-fdb6-467e-a1aa-f99f6eed49f6 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 1.0502 | 1.388 | 2.101 | 0.012603 | 0.016656 | 0.025212 | 2024-01-20 21:00 | GSO_127 | br_07_22 | 3 | a16d8ea2-fafa-4870-8bff-75e352b48100, 1287cfdf-d61b-4b7d-9c56-4a67e583be03, 9962595a-e18a-4855-ab7a-6bcfb11262e4 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 8.0596 | 9.673 | 12.511 | 0.096715 | 0.11608 | 0.15013 | 2024-07-16 02:00 | GSO_128 | br_08_22 | 3 | 692be577-442c-4ab0-b1e1-5785854345e2, 6cff9753-e438-465f-8082-4b41468b4f8c, 3d10e996-315d-4229-9b7c-a9b8e0697db8 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 14.3968 | 17.421 | 21.922 | 0.17276 | 0.20905 | 0.26306 | 2024-01-22 04:00 | GSO_129 | br_09_22 | 3 | 686b2171-718b-454f-a63f-7a08af910b78, 066b1670-e5b9-40c9-bd97-907fe78b74e9, ca9fa130-fc7c-477e-8464-326c962a06af | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 109.1296 | 159.5763 | 210.912 | 1.3096 | 1.9149 | 2.5309 | 2024-01-21 04:00 | GSO_13 | br_018_21 | 3 | 28993f84-c3b9-4382-b199-7eae1602f7b5, d4524dc1-a63b-454b-a0d9-1683a9db619b, 538bb977-c069-4a72-a1f5-79ade89be85e | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 17.5856 | 20.67 | 26.519 | 0.21103 | 0.24804 | 0.31823 | 2024-01-22 04:00 | GSO_130 | br_010_22 | 3 | ec2f67d6-3e29-40e6-b3db-279de5aeb3e1, 0820aaeb-7057-4894-a6ba-7624e83ee1a7, cab2ab50-4b8d-4ecb-98f8-73c155d0b547 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 3.7691 | 4.4646 | 6.121 | 0.04523 | 0.053576 | 0.073452 | 2024-01-20 18:00 | GSO_131 | br_011_22 | 3 | 434fff6c-2804-492a-a7e9-8c978d0dc8e3, 1a6f96c2-84f7-4c0d-b1a3-ee2364b2f450, 618c145a-b95c-4f8d-9e8d-9389861004d6 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 26.9423 | 31.6646 | 38.23 | 0.32331 | 0.37998 | 0.45876 | 2024-01-20 21:00 | GSO_132 | br_012_22 | 3 | 935c3854-ba34-4cf1-b241-c865be78d3bf, 0716ea38-77d5-4d34-bc24-820dc14d344a, 8eae3b99-7252-4faf-9a4e-4abe914bc30e | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 37.2676 | 44.079 | 56.475 | 0.44721 | 0.52895 | 0.6777 | 2024-01-20 11:00 | GSO_133 | br_013_22 | 3 | dddfb629-b710-4a70-b13f-4f342bc8fe74, 4d344901-644b-4ea0-b7f1-b381d39a7879, c086c5c8-dc85-4746-8b0a-d8e23067358a | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 18.38 | 22.037 | 27.385 | 0.22056 | 0.26444 | 0.32862 | 2024-01-20 09:00 | GSO_134 | br_014_22 | 3 | 4091c3a2-55c3-4b7e-8d9d-a8e4affed314, 57c2fa84-53da-4153-9d01-3c3ac5b2144e, 7325e088-181d-4e0d-b15b-2dd1fbda83f0 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 30.6842 | 35.815 | 43.88 | 0.36821 | 0.42978 | 0.52656 | 2024-01-20 23:05 | GSO_135 | br_015_22 | 3 | c3ac0e33-1470-42fd-9a70-99015f289563, 306b628e-5350-43cc-bd44-5524b56eb0e1, cb036569-e3a3-4f9a-ab6b-ada0cfc7f7a2 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 18.3703 | 21.749 | 28.701 | 0.22044 | 0.26099 | 0.34441 | 2024-01-17 16:00 | GSO_136 | br_016_22 | 3 | 04ce7e89-fb0f-4fb3-9752-836af1c7ab9e, 1985324e-e67a-4d01-bf4e-cbc1776ba800, 66b785ca-af8e-4a6a-8af7-ff9241ec96a5 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 17.8375 | 20.948 | 25.601 | 0.21405 | 0.25138 | 0.30721 | 2024-01-20 18:00 | GSO_137 | br_017_22 | 3 | cf094241-cd71-4a00-ae80-c341e78225f3, d0f42d15-cf63-4976-b310-0a7f21c9a7fc, bb261d99-e16f-41bf-90d2-05acc7b4f39c | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 18.878 | 24.579 | 32.26 | 0.22654 | 0.29495 | 0.38712 | 2024-01-21 04:00 | GSO_138 | br_018_22 | 3 | c812a09e-5775-4fbc-93b7-37aa020f3a4a, b91b7108-02a6-4c8f-9294-9075747bf3d2, 8cf34f38-0fdb-4d44-9870-a7c9c5b5c3b4 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 25.2516 | 30.442 | 41.744 | 0.30302 | 0.3653 | 0.50093 | 2024-01-21 04:00 | GSO_139 | br_019_22 | 3 | 8781de87-205d-4b90-963f-449d72c41e8c, 2a67f2a3-ad9e-4413-af20-999870d5694e, 6ec0fb64-8f9d-48b6-81ae-63048adca78a | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 116.9126 | 169.864 | 224.04 | 1.403 | 2.0384 | 2.6885 | 2024-01-21 04:00 | GSO_14 | br_019_21 | 3 | 9df35035-201c-43e2-9c0f-29f5652d20b6, 4f0a9de3-7d5d-4d74-841a-ad368a655ddc, 37a8aff5-f4d5-48d1-b094-f7ff7add641f | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 17.3466 | 20.6 | 25.77 | 0.20816 | 0.2472 | 0.30924 | 2024-07-15 20:00 | GSO_140 | br_020_22 | 3 | b6e43aeb-290f-443d-917c-933a0af02698, 7ac282db-535a-4cda-bcc4-f62230cc0be1, 52cf19cb-d2f9-48a0-a5d7-3d345a429c59 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 19.5682 | 24.2286 | 31.663 | 0.23482 | 0.29074 | 0.37996 | 2024-01-21 01:00 | GSO_141 | br_021_22 | 3 | 78f844cc-a5b4-4d9d-ba33-ef854d68bc8a, b6f787f7-5117-4b48-81f4-ddbe099f96d7, 0b5869b0-b194-4a18-8593-e04336ade6ea | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 43.7603 | 52.0646 | 66.049 | 0.52512 | 0.62478 | 0.79259 | 2024-07-09 | GSO_142 | br_022_22 | 3 | 5c50320a-6541-43e1-a0eb-b3cc85335f92, d8586197-7e6c-42e3-af81-89d0f76301f9, aeed6de5-7aca-4fa3-a5ca-b1f32ee717c2 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 104.0809 | 157.9957 | 211.73 | 1.249 | 1.8959 | 2.5408 | 2024-01-21 04:00 | GSO_143 | br_023_22 | 3 | b2362459-63fa-42c8-b75d-cdff666f2190, 15ee4200-f93f-4884-ab81-e52eb3d0b73c, ef7cab0d-e432-4fb1-aab4-46e5068286b4 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 4.7843 | 7.507 | 11.072 | 0.057412 | 0.090084 | 0.13286 | 2024-01-20 21:00 | GSO_144 | br_024_22 | 3 | cebe0434-4e95-4fd2-8e1e-22573f21abf5, bd7e1df8-2eb1-4167-bee8-930536ce0573, 82536324-6f01-4e66-a011-7b067544a9ac | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 36.7087 | 46.6936 | 61.202 | 0.4405 | 0.56032 | 0.73442 | 2024-01-21 04:00 | GSO_145 | br_025_22 | 3 | e8f52edb-11b6-4a01-8cb4-dde6abb481d7, 5042bbb0-cc21-499d-9106-09bd8c86b439, 039cb766-152c-4467-9ec0-94180921a657 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 44.8504 | 60.7569 | 81.348 | 0.5382 | 0.72909 | 0.97618 | 2024-01-21 04:00 | GSO_146 | br_026_22 | 3 | 45141e3c-ee87-445b-a8cd-53eaf3cf8ac6, d4d03355-620e-4213-a24e-266e873f3f79, 9c3aa61d-fdd8-4e3a-a859-786b34331466 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 13.544 | 18.0146 | 24.362 | 0.16253 | 0.21618 | 0.29234 | 2024-01-21 04:00 | GSO_147 | br_027_22 | 3 | 783419bf-1c8f-4783-a364-729c4d25328a, b05dca4b-f167-46ba-b479-77fc9d306c98, a6c68db1-932a-455f-9961-2001628d137a | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 24.9351 | 31.138 | 41.328 | 0.29922 | 0.37366 | 0.49594 | 2024-01-21 01:00 | GSO_148 | br_028_22 | 3 | f209db33-c63a-4eeb-9470-44a070b1f980, e51bd3d2-27db-4e8c-85b3-94bb36fdecb2, 9cb02ef5-7d31-4690-b5cc-1c8ff7465b94 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 4.7215 | 5.8096 | 7.637 | 0.056658 | 0.069716 | 0.091644 | 2024-01-17 05:00 | GSO_149 | br_029_22 | 3 | 54f22dd6-dae8-4d6f-8c00-4ee16cc1bce1, a7d55959-39f6-4006-8a75-2ac4375060d6, 22ef08a2-8b87-47bf-912f-a49f8dbe4e0e | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 141.6145 | 210.703 | 279.9 | 1.6994 | 2.5284 | 3.3588 | 2024-01-21 04:00 | GSO_15 | br_020_21 | 3 | 2dfc9022-cd2d-4071-a0ed-f7aa4dbf29b5, 34fb9785-294c-4580-94c1-92b57cb0e642, dd9e89fb-3f9a-4966-a494-c19ab9432a67 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 10.8391 | 13.173 | 18.338 | 0.13007 | 0.15808 | 0.22006 | 2024-01-20 11:00 | GSO_150 | br_030_22 | 3 | 99ca8035-36a9-410b-844c-06c1ddb4c66b, 97ae36fa-2e65-4c6d-8a11-b6c4ba921c0d, e18873a3-19e0-4c86-abaf-03f1ea49ef98 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 35.4508 | 45.74 | 60.865 | 0.42541 | 0.54888 | 0.73038 | 2024-01-21 04:00 | GSO_151 | br_031_22 | 3 | 5b53a681-1338-4fee-9587-71b3e65506cb, 051f7584-2010-41f8-9415-9183657a8ae0, 0542d836-ab02-49aa-a8b7-a4265443a1c4 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 0.99999 | 1.44 | 2.175 | 0.012 | 0.01728 | 0.0261 | 2024-01-20 16:00 | GSO_152 | br_032_22 | 3 | 3f75484a-66ad-416b-bdfc-429bf783f99d, ab723fc3-e0cb-4dbc-8181-5681e5ac3348, 3b38bb39-6b77-49e7-b0c7-d3c699da74dc | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 49.9449 | 58.09 | 70.101 | 0.59934 | 0.69708 | 0.84121 | 2024-07-15 10:00 | GSO_153 | br_033_22 | 3 | 0d3f8e19-033b-4d8c-a34b-ff04747bd082, 5e1ed7ac-1e16-4c51-bb12-e8d8b8c244c4, 07ea0bf7-442d-4e77-b98a-b9e2c8d50114 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 13.4266 | 16.381 | 21.737 | 0.16112 | 0.19657 | 0.26084 | 2024-01-21 04:00 | GSO_154 | br_034_22 | 3 | 6eba73e4-418d-4cd1-96b6-60b826ae450c, 70369b74-10d7-4556-af26-c0ccb8f01935, 0840b23d-66b0-48cf-856c-1f62526c7d6e | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 53.8705 | 78.859 | 106.514 | 0.64645 | 0.94631 | 1.2782 | 2024-01-21 04:00 | GSO_155 | br_01_23 | 3 | 033ba35a-0e88-44c7-ae68-9ef721532ab3, ecb9c3ef-513f-492a-821c-4bff92c1df9c, d1e45bf7-a00b-40dc-a6ec-c751080a13c9 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 132.5721 | 196.1993 | 256.642 | 1.5909 | 2.3544 | 3.0797 | 2024-01-21 04:00 | GSO_156 | br_02_23 | 3 | 2ec12710-cbb3-4ac0-ae81-f21bc775b59d, 17343a92-f390-4c00-96dd-aa4c8e6f2cf5, 12b55d36-db8c-475f-838b-08caf84b6421 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 119.8044 | 177.2403 | 240.749 | 1.4377 | 2.1269 | 2.889 | 2024-01-21 04:00 | GSO_157 | br_03_23 | 3 | d76a1565-b995-4235-9508-12ae427ed548, b96622f9-34da-4d3a-a144-a82c9e2d84a9, 962e5ace-7f13-49d9-a1bd-65973f2adfac | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 114.4589 | 170.9293 | 224.281 | 1.3735 | 2.0512 | 2.6914 | 2024-01-20 21:00 | GSO_158 | br_04_23 | 3 | 8e1d3060-4f17-4027-bb48-9326d72d1f5e, b84e6ee7-bc4b-467a-884d-e5dac0fbac0b, 5320e9a7-8d71-4f75-b9c9-3a6a37f707db | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 143.5038 | 212.7262 | 289.083 | 1.722 | 2.5527 | 3.469 | 2024-01-21 04:00 | GSO_159 | br_05_23 | 3 | 83f2cd36-180e-4d9a-9105-62a32f68ab85, 96fae847-ae01-4905-9884-47b324a88934, 2e882994-3bef-4961-988c-cd677efd6410 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 76.4704 | 107.642 | 142.457 | 0.91765 | 1.2917 | 1.7095 | 2024-01-21 | GSO_16 | br_021_21 | 3 | e4f24c66-81cd-48f4-b9a3-a8aaa9fe8c98, b5d738a6-79bd-43f6-b4e4-0fb4de70abfd, 2b3c0835-4f9e-453c-86b3-35847ab5af94 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 195.0631 | 288.77 | 387.304 | 2.3408 | 3.4652 | 4.6476 | 2024-01-21 04:00 | GSO_160 | br_06_23 | 3 | b9360429-edfb-4e59-a900-8a457dc83cba, c3e81296-2c1a-4ada-80c1-b847107d5cfb, 47f0ee8f-4288-4af4-b69a-10cebf43b645 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 2.4064 | 3.711 | 5.595 | 0.028877 | 0.044532 | 0.06714 | 2024-01-20 21:00 | GSO_161 | br_07_23 | 3 | 89a3b24a-887f-4195-8344-51f18a00dbf7, c4eee589-eb1d-4947-bc9b-3f547ec858d4, e61fb2d3-e704-4d3f-bf86-8b04c3724fd7 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 42.3363 | 62.8216 | 83.807 | 0.50804 | 0.75386 | 1.0057 | 2024-01-20 23:00 | GSO_162 | br_08_23 | 3 | f620b838-2134-4f66-a112-15e5f46318b0, f4ffa257-f9a9-48e6-8ef7-945f8e687e83, 4bfd3a0a-1178-4983-b63c-76c387206a99 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 133.7168 | 197.8567 | 264.237 | 1.6046 | 2.3743 | 3.1708 | 2024-01-18 04:00 | GSO_163 | br_09_23 | 3 | d90170cc-5eec-43f7-a5d9-cb91dca851cb, 9018e821-338d-4aa5-bb0d-3e9aa19f5a3b, 0d2e0f05-d1e8-46f2-953d-daf9b517d3b5 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 151.5207 | 224.6077 | 294.715 | 1.8182 | 2.6953 | 3.5366 | 2024-01-21 04:05 | GSO_17 | br_024_21 | 3 | 3a2af09c-baa8-4dbe-95ab-fb397036b19d, 883c59a4-ab46-45e2-b36d-e1959b7c89b6, f0a67506-31bf-4b47-9614-f559c928646a | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 99.0903 | 142.754 | 190.81 | 1.1891 | 1.713 | 2.2897 | 2024-01-21 | GSO_18 | br_025_21 | 3 | 34cac5e4-313a-4454-a92d-abc9047eadc8, 90d3f27c-2599-462f-8abb-58371a03ece5, 08eb7b30-b593-4a81-854f-d7a00d46db1e | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 209.1713 | 319.6785 | 430.217 | 2.5101 | 3.8361 | 5.1626 | 2024-01-18 04:00 | GSO_19 | br_026_21 | 3 | d5920248-7472-436e-b060-c7c2ff9ef29d, cf54e8e6-a9a5-4011-b2be-1226fbdc86cb, a03bc8be-0c7b-4ca4-b625-79f7823155e9 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 100.2277 | 144.422 | 191.098 | 1.2027 | 1.7331 | 2.2932 | 2024-01-20 08:10 | GSO_2 | br_02_21 | 3 | e16fe26a-3331-4e10-bcda-3d5b4cfc42bc, f5b81547-937f-4c70-92ba-8a0fb6594394, a28c1752-7f45-48c2-b058-b7cdc091e5d6 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 0.27289 | 0.396 | 0.639 | 0.0032747 | 0.004752 | 0.007668 | 2024-07-10 19:00 | GSO_20 | br_027_21 | 3 | 0367f0a8-b7e5-4ca5-94ae-d44fa9d00bfd, a602edca-8fde-46f7-8d51-40a5f85d6a1d, c9015052-da74-4877-bbf1-9a6c4275c44d | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 77.4498 | 106.98 | 140.144 | 0.9294 | 1.2838 | 1.6817 | 2024-01-18 04:00 | GSO_21 | br_028_21 | 3 | 6f7a2c02-ca5d-4d73-a76d-82f0fe3158c9, 39b0a939-9afe-4c84-bfda-5eec318bc35e, a49c303e-bacd-45af-8754-babfb2545a48 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 78.4727 | 112.2883 | 145.782 | 0.94167 | 1.3475 | 1.7494 | 2024-01-18 04:00 | GSO_22 | br_029_21 | 3 | f1fcda72-2c9e-4219-9a68-e344865344e1, c13495f3-7436-4771-9d8e-028fe398e677, 60e175bd-dd8d-424f-b541-e6c27675c2ee | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 53.0838 | 72.912 | 95.702 | 0.63701 | 0.87494 | 1.1484 | 2024-01-18 04:00 | GSO_23 | br_030_21 | 3 | 73114768-3396-46b2-8366-027d7f330c2a, 8896d2cc-f5f3-479a-9806-74f9830d0e65, 306a0179-6b1d-4c84-b7ad-c043978706f4 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 3.5228 | 4.229 | 5.621 | 0.042273 | 0.050748 | 0.067452 | 2024-01-20 16:00 | GSO_24 | br_031_21 | 3 | 8866ae0d-1645-4e1d-85a9-520a2b057093, 0e740376-b7d0-46f1-8238-50979ff53b86, 3abd341d-8629-4be0-888c-4405cbd18a68 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 33.8332 | 41.038 | 52.039 | 0.406 | 0.49246 | 0.62447 | 2024-01-21 04:00 | GSO_25 | br_032_21 | 3 | 8c0cf450-9297-450e-b468-8396988be79f, d4f80b32-222c-49ea-bb38-81080bcb0826, 6a2617f0-409e-448d-8ce4-c1175edcf36a | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 87.2755 | 120.2986 | 157.504 | 1.0473 | 1.4436 | 1.89 | 2024-01-21 04:00 | GSO_26 | br_033_21 | 3 | 2ded452d-d964-456f-bc61-891c5e02102b, 123d2e0f-6c7b-4b17-96d2-32d4328dde67, 06410d93-c578-4f9d-86d8-8eb333ba28c9 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 103.9897 | 149.897 | 200.381 | 1.2479 | 1.7988 | 2.4046 | 2024-01-21 04:00 | GSO_27 | br_034_21 | 3 | 6fdd1896-ad74-48a8-9816-85aa01d652d1, d428eae8-d228-4f79-b9ea-91e3a88bb229, 9dbd0f33-80b1-4155-96b0-ea2e0658e691 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 5.1894 | 6.662 | 9.836 | 0.062273 | 0.079944 | 0.11803 | 2024-01-20 11:00 | GSO_28 | br_035_21 | 3 | c3250712-a026-44dc-83b1-ab0b7bd1cef0, 4cc07d73-767d-4a92-aa56-8d6f6139433c, 4b1de06e-7ccd-42bd-ba7d-141a0d6eed10 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 88.6911 | 127.1367 | 165.623 | 1.0643 | 1.5256 | 1.9875 | 2024-01-20 05:00 | GSO_29 | br_036_21 | 3 | 53ac9d88-ec7e-422c-9547-7b65d0e1b05c, bbdb1c8c-b61b-4af3-a00d-d34e99f936e8, 37be8bbe-3fc1-42ac-aa14-512831f011d9 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 1.1766 | 1.823 | 3.187 | 0.014119 | 0.021876 | 0.038244 | 2024-07-15 08:00 | GSO_3 | br_03_21 | 3 | cabb02b4-86e3-4261-87ef-66f06902bb61, 262d1506-d23e-42d2-a938-f15cb2f35365, 861d3fe8-4f6d-46b5-bb00-6d79ddaf889d | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 78.5223 | 114.0916 | 150.566 | 0.94227 | 1.3691 | 1.8068 | 2024-01-20 09:05 | GSO_30 | br_037_21 | 3 | 80a38063-4b58-4c05-9631-c9f20eaae49f, 07afe75d-2efa-4a63-8500-f5eed954ebc4, 4339844d-f7f4-4af5-a7ce-ff1e206a4bfc | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 1.1878 | 1.851 | 3.019 | 0.014254 | 0.022212 | 0.036228 | 2024-07-15 08:00 | GSO_31 | br_038_21 | 3 | dbd51660-93ed-49dc-b484-ac1a2ff93751, c4bbbd0b-e3cc-4312-b11b-48dca067f34f, f5f51af7-9112-4286-adaa-37e4589d054a | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 58.5184 | 79.0046 | 101.472 | 0.70222 | 0.94806 | 1.2177 | 2024-01-21 | GSO_32 | br_039_21 | 3 | 049d0b94-e086-4825-b104-d454ffd3dc7c, 81e832b4-cd01-4844-b4d8-6ff81d95dbe4, 934aabc4-8b42-44e6-82dc-1b3261dc29d9 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 48.3582 | 58.461 | 73.666 | 0.5803 | 0.70153 | 0.88399 | 2024-01-20 15:00 | GSO_33 | br_040_21 | 3 | ee1a565e-ae8b-4984-9f7a-cab15b5447c3, 2bcc2cc5-82f5-4040-ac32-a00d0d07de51, d858a33a-1b66-4073-aed2-4b1a30ad837b | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 96.588 | 139.3106 | 184.726 | 1.1591 | 1.6717 | 2.2167 | 2024-01-18 04:00 | GSO_34 | br_041_21 | 3 | deb58541-2cca-43d5-86c5-55264c6041d3, 179024ab-8e49-42be-b943-761705fb5abd, 0cbf9200-98b4-43c7-934d-2cc30d8ab63b | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 146.1585 | 221.035 | 295.36 | 1.7539 | 2.6524 | 3.5443 | 2024-01-21 00:05 | GSO_35 | br_042_21 | 3 | efc37dec-e402-4c7d-81af-aa9cb2729757, d7ccdfd6-6a7d-4338-9666-e79b11f003a9, 6d4ede07-2601-4246-903b-56124df12172 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 28.5929 | 33.6716 | 41.267 | 0.34312 | 0.40406 | 0.4952 | 2024-01-20 05:00 | GSO_36 | br_043_21 | 3 | a492b914-7377-4047-b30b-90aa78dc94d3, c95edbeb-bfcc-48be-abeb-7c6ceba7bdae, 1ede274a-9246-4aec-acc0-17642c07af97 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 219.5832 | 331.3441 | 437.846 | 2.635 | 3.9761 | 5.2542 | 2024-01-20 07:05 | GSO_37 | br_044_21 | 3 | e72c363a-7373-4a30-a872-329d650d7569, 547c5604-b333-47b9-83ad-6f6fa1e88927, 53f8a349-7f61-440d-ad82-54a7f6d15d3a | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 1.3018 | 2.017 | 3.528 | 0.015622 | 0.024204 | 0.042336 | 2024-01-20 09:00 | GSO_38 | br_045_21 | 3 | 9c1dc66a-d26b-42ae-9fa5-d4e46c87f492, 31c14863-6ede-40c4-86a5-41eadc729ac2, 15e8162e-962b-481f-923b-b2fe7c7ce432 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 99.4969 | 148.6783 | 197.137 | 1.194 | 1.7841 | 2.3656 | 2024-01-21 04:00 | GSO_39 | br_046_21 | 3 | 93658bef-4bd5-4300-8424-5c388155968b, 1ef359a3-1b23-4781-b7f6-73e5a4c4559f, 77ff5585-562a-45e7-a281-464e98737abb | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 201.0527 | 310.0799 | 418.615 | 2.4126 | 3.721 | 5.0234 | 2024-01-21 04:00 | GSO_4 | br_04_21 | 3 | eda55f14-fedc-4eb6-a389-a51a43231405, 67c44f52-c49c-4993-940f-90408b4b9ae5, 1da22d5c-e6b3-4228-b327-ddf40f1f21b6 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 86.2034 | 128.3382 | 173.644 | 1.0344 | 1.5401 | 2.0837 | 2024-01-20 20:00 | GSO_40 | br_047_21 | 3 | ee7aaead-b8fb-40d3-8a03-8ab58a542fdc, 58cd6faf-3139-48ff-a9ef-b152b7ebf778, 79202d32-8dca-417a-9d59-fc14f3bcaf5f | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 74.5573 | 112.5246 | 154.92 | 0.89469 | 1.3503 | 1.859 | 2024-01-18 04:00 | GSO_41 | br_048_21 | 3 | 4f3f10ee-748f-4c21-b9c3-8ac51c8d41f6, d7d6e014-1cd2-4cb5-84bb-a00b2cad42e3, e1cda877-0a5c-49b1-bd5f-ad8449fb0e0c | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 162.5501 | 250.9263 | 339.604 | 1.9506 | 3.0111 | 4.0752 | 2024-01-21 04:00 | GSO_42 | br_049_21 | 3 | 0b1099db-07b7-4a46-831f-0ab42e837cdd, 119ef0a4-9572-4988-9343-96cacd641d11, 0e80773a-a8cc-45a5-8095-4dc9d8b00215 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 183.9062 | 273.6613 | 364.359 | 2.2069 | 3.2839 | 4.3723 | 2024-01-21 04:00 | GSO_43 | br_050_21 | 3 | 223df89f-b673-46b7-a74d-953aa3cadd02, d8ed1451-4cac-4c54-9238-07312269a3d5, d260c5dc-0f9a-4ff7-a347-cabc3421f531 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 2.2464 | 3.405 | 5.441 | 0.026957 | 0.04086 | 0.065292 | 2024-01-21 | GSO_44 | br_051_21 | 3 | ae9708d6-58e3-48d8-b469-2b865749bda5, 9de5605e-2be3-4478-8321-ec1cfdb77d3e, c206a6a0-74a2-4aa0-b700-0397b158b47c | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 135.2434 | 208.1636 | 281.092 | 1.6229 | 2.498 | 3.3731 | 2024-01-18 04:00 | GSO_45 | br_052_21 | 3 | 0a36e22d-cb96-45c8-8d47-74ede8f433bd, ac9dddc3-7cae-427c-a129-87d3008b8362, 87af0485-ac3b-4ef1-bd8e-39742bb1311b | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 124.6999 | 184.4341 | 244.562 | 1.4964 | 2.2132 | 2.9347 | 2024-01-21 04:00 | GSO_46 | br_053_21 | 3 | 425e9895-3ec9-4ecf-a2de-00e847c9f5d0, e8d1fc00-bcf6-4d05-b6b9-7f38e6915ce5, 0b8f662d-5bc3-42fe-a24e-070da09bdd80 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 18.0821 | 22.5966 | 29.491 | 0.21699 | 0.27116 | 0.35389 | 2024-07-16 03:00 | GSO_47 | br_054_21 | 3 | 44d72b2b-4d39-442e-969c-28bfa609a6ca, df231f2b-7e74-4562-8026-e0248f99acb1, 73020989-8b85-4f2f-ae5e-b46034dccc36 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 29.0078 | 33.8146 | 42.011 | 0.34809 | 0.40578 | 0.50413 | 2024-01-17 21:00 | GSO_48 | br_055_21 | 3 | caead5dd-6652-4002-9205-bf1f5d7841a2, 2756c12d-de33-427b-a20e-a7524bf8ba2a, d501232c-0e9b-4aed-b1c7-0711f51fd12c | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 10.7723 | 12.922 | 16.485 | 0.12927 | 0.15506 | 0.19782 | 2024-06-27 03:00 | GSO_49 | br_056_21 | 3 | 904a534b-b4de-47cc-9111-a909cdd75ff6, cf17223b-5ef6-40ff-aa3f-7eaa71fa5ab1, 4e486c1d-6969-466b-bb85-e868d8c69d96 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 56.6751 | 69.911 | 87.601 | 0.6801 | 0.83893 | 1.0512 | 2024-01-20 15:00 | GSO_5 | br_05_21 | 3 | 1a7b2ce3-8ce4-43f0-822c-bae88f338574, fdea0e08-11f9-40c1-bd4a-4dfdb8ea2803, 921b5057-9802-4094-b921-551288ad3d2e | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 2.2873 | 3.557 | 5.295 | 0.027447 | 0.042684 | 0.06354 | 2024-01-21 | GSO_50 | br_057_21 | 3 | 4d9bb5e2-1e06-49ed-b322-273c65c7ea12, 02cb60eb-e56b-45c0-871a-7d5da5072e9a, ceeee8fb-13b1-43c7-9caf-4433648f6846 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 20.0647 | 23.267 | 29.363 | 0.24078 | 0.2792 | 0.35236 | 2024-01-20 15:00 | GSO_51 | br_058_21 | 3 | 2dabfa67-e633-42fb-88f8-b99c8c81ce3f, 40e658e9-710a-4f81-b823-ce3b23d76208, 100d5254-7678-4ba2-a678-ffa8ba0ac8ce | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 128.7905 | 195.3616 | 264.141 | 1.5455 | 2.3443 | 3.1697 | 2024-01-21 04:00 | GSO_52 | br_059_21 | 3 | 148e241f-8dca-40c2-bc4c-9bba11acb600, 740ff96c-6171-4486-bb6a-904851da7f68, 54cc7298-372e-4f46-9c94-d78d3e7e3368 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 60.036 | 83.116 | 110.049 | 0.72043 | 0.99739 | 1.3206 | 2024-01-21 04:00 | GSO_53 | br_060_21 | 3 | 77c08208-993b-4559-b9e2-42c4c772997c, 4b800952-fa1b-4668-ba63-4244710bab3c, 3b012ead-fe04-4b66-8c50-59d42334a89c | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 209.0296 | 315.702 | 423.322 | 2.5084 | 3.7884 | 5.0799 | 2024-01-21 04:00 | GSO_54 | br_061_21 | 3 | c70624cc-3511-421e-bcd3-4f74ee43c80f, 0c2d5da7-8b73-4e99-a2ec-e1bd371c44f1, b486465e-b5c3-4f46-9979-e961ceb9df52 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 10.2891 | 15.9266 | 22.373 | 0.12347 | 0.19112 | 0.26848 | 2024-01-20 10:00 | GSO_55 | br_062_21 | 3 | 55b291eb-5761-4e7f-8635-63057f856791, 0d627f19-7146-43b0-9f7b-bac68e9966db, efb7b851-1f6e-4084-9dd6-5a62049b7654 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 37.6367 | 51.681 | 67.431 | 0.45164 | 0.62017 | 0.80917 | 2024-01-21 04:00 | GSO_56 | br_063_21 | 3 | d5be6516-e14a-46ab-a02a-0650b74a5159, 748858e9-a0e0-4bc6-a0b7-f4e67d7c9ecd, 620a8a0d-bcbd-4f44-be97-24244e308366 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 44.3296 | 62.5339 | 86.055 | 0.53196 | 0.75041 | 1.0327 | 2024-01-20 10:05 | GSO_57 | br_08_21 | 3 | 27046833-12e1-4f55-aeb1-743d3fddc9b4, e2d61ac2-432e-446d-b560-32b75aebceed, 08dafb35-ef6e-48c6-89ef-1f3412fa5f7e | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 166.8301 | 255.1588 | 347.154 | 2.002 | 3.0619 | 4.1658 | 2024-01-21 04:00 | GSO_58 | br_09_21 | 3 | cd71f269-7897-4746-9a77-c6bc730114fe, ff232009-b42f-4f71-a769-88a952701609, b8c6df33-b602-4d1c-9dda-e52dfeb41665 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 128.7271 | 198.0846 | 266.309 | 1.5447 | 2.377 | 3.1957 | 2024-01-21 04:00 | GSO_59 | br_010_21 | 3 | 4529fb6d-421e-4f02-9b11-c956a4443f8e, 1231155d-ed13-4563-8801-fa08388d11cd, 1b822839-e89f-49f2-b2a9-69df27011548 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 36.9389 | 53.0836 | 68.881 | 0.44327 | 0.637 | 0.82657 | 2024-01-18 04:00 | GSO_6 | br_06_21 | 3 | 145f4423-0120-41c0-a961-6f6b453e91a7, 120599d7-eee0-4966-bd20-36d9e2e8b089, a5d804f2-bcf0-4e70-ad7f-9ffc889ca71a | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 115.5942 | 174.692 | 238.251 | 1.3871 | 2.0963 | 2.859 | 2024-01-21 04:00 | GSO_60 | br_011_21 | 3 | 229fce16-0cb2-401d-957b-9d0d3c2ac1cc, fc187080-4278-4699-8d7f-ded10dc27448, 52980b4f-3c73-4c68-8631-e69ccc722a34 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 211.8673 | 326.8333 | 433.485 | 2.5424 | 3.922 | 5.2018 | 2024-01-20 09:00 | GSO_61 | br_012_21 | 3 | bdb558af-9d90-4dcd-870e-28a86925b8cc, 192ef0e0-59f5-4932-a625-7e967573ec09, 69c0c6b0-aa07-4cdc-9789-b51b223584c4 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 34.1079 | 52.4066 | 71.266 | 0.40929 | 0.62888 | 0.85519 | 2024-01-21 04:00 | GSO_62 | br_013_21 | 3 | 2c8910bb-0c41-4c36-8a5f-d8ffc5e65938, 3f59d58a-b780-49d5-86ae-b0b0f01c076d, decddce1-9f0e-44c6-a3bd-24fdb9cf1a60 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 4.9355 | 7.544 | 10.321 | 0.059226 | 0.090528 | 0.12385 | 2024-07-15 09:00 | GSO_63 | br_014_21 | 3 | 676b1650-044c-43bf-bea6-3dced2a612c6, abbc8c51-7785-4d04-a735-eb965d943d5a, 167b629e-ae1a-4acd-a435-a9faf6b8f0b1 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 105.6309 | 151.3556 | 198.709 | 1.2676 | 1.8163 | 2.3845 | 2024-01-21 04:00 | GSO_64 | br_064_21 | 3 | aa668afa-9003-4c02-b068-76a760cba7c4, 8ec9092e-c513-4856-b139-17b0f244b287, 96d7ca9d-a8a7-4620-beb4-015993e1495f | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 11.8091 | 14.098 | 17.976 | 0.14171 | 0.16918 | 0.21571 | 2024-01-21 04:00 | GSO_65 | br_065_21 | 3 | a8421f63-1fb7-4386-80d1-558a9049f658, c0caf65c-2d30-471b-9a8c-36e1484ba877, a2d74127-91f7-4d1b-a98b-b3f287f80eec | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 113.5657 | 169.5323 | 224.767 | 1.3628 | 2.0344 | 2.6972 | 2024-01-21 04:00 | GSO_66 | br_066_21 | 3 | aa212fd9-92d5-4c56-9a9e-3014ccc9a7ce, 0cbf5c43-696f-40b4-ab01-fd3dfd670388, 3f826b2c-284b-4880-a9f1-d5554c1e5213 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 124.1763 | 178.0886 | 238.716 | 1.4901 | 2.1371 | 2.8646 | 2024-01-21 04:00 | GSO_67 | br_067_21 | 3 | fddc71cc-3766-4601-9ca7-c2caab3c7c4d, 5aed073b-49c0-4020-b105-f7e28cfd41ed, 4b3c48a3-9a69-47a9-b110-7d0b18cc7f06 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 107.0124 | 150.7806 | 195.762 | 1.2841 | 1.8094 | 2.3491 | 2024-01-21 04:00 | GSO_68 | br_068_21 | 3 | 6abb0433-d7c1-47cb-b500-310c0966ae29, b14a51cb-21cb-48f4-91a6-564663c5a923, f2986696-35a7-4d1e-a7dd-8b01d8d6756a | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 24.2321 | 31.856 | 41.103 | 0.29078 | 0.38227 | 0.49324 | 2024-01-21 04:00 | GSO_69 | br_069_21 | 3 | 16e446fe-cce5-4d4b-abd0-d9bf98278835, 3f69baec-6464-4c01-91c1-171903c224f7, 9255af13-2569-446c-b326-8de2942e3a26 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 2.4232 | 3.9 | 6.118 | 0.029079 | 0.0468 | 0.073416 | 2024-01-21 | GSO_7 | br_07_21 | 3 | 874fce3a-0ddc-405e-8b4d-496bf1208ffa, 7c4e0a27-0ba8-4589-8efa-9d78e22aeea7, b3997dcd-0479-4422-904f-1e86aedb3b49 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 29.4202 | 35.0057 | 43.007 | 0.35304 | 0.42007 | 0.51608 | 2024-01-20 22:00 | GSO_70 | br_070_21 | 3 | ff4d78df-a97d-465a-9270-6b140f05b7ee, 96d35f0d-746b-4c76-8d6d-a22dac3dcfaa, 7a4e8fb6-f007-4d77-bfcb-6a0b0e18561c | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 231.4489 | 347.345 | 458.37 | 2.7774 | 4.1681 | 5.5004 | 2024-01-21 02:00 | GSO_71 | br_071_21 | 3 | 7dec81b6-3b82-498d-bfaa-f44bf5d9581d, 4ff8b560-0d8d-46ca-aa4f-48e616d84a8c, 828a3353-455f-43cc-a9b0-71980deae8fd | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 79.2778 | 110.32 | 145.087 | 0.95133 | 1.3238 | 1.741 | 2024-01-21 04:00 | GSO_72 | br_072_21 | 3 | 2f6074d9-3367-424b-9912-3b54ba3842dc, 5be2e72a-f9e3-4662-bcdd-f6914b127473, ceb3c16f-b2c1-4384-83e5-47eb8d9787a9 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 4.4614 | 5.51 | 8.158 | 0.053536 | 0.06612 | 0.097896 | 2024-01-20 20:00 | GSO_73 | br_073_21 | 3 | dd7e3ea9-a097-46d9-ba3d-e976877c959f, dc0e22aa-9b17-4812-81b9-805e6e2fcea4, 0a5bd7a0-8dda-4ea9-8140-b43dcad4334a | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 59.4096 | 72.9743 | 87.794 | 0.71292 | 0.87569 | 1.0535 | 2024-01-20 23:25 | GSO_74 | br_074_21 | 3 | 4cb9db9e-b9c3-473e-878d-2df2932f4dcf, 2be1e40d-d971-44eb-9f8e-1f362b00491f, b4794b85-7397-40b2-a7b2-50c82c66983d | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 35.9045 | 48.781 | 67.545 | 0.43085 | 0.58537 | 0.81054 | 2024-01-18 04:00 | GSO_75 | br_075_21 | 3 | 74ba07cb-a526-4618-b499-1a430d0286b7, dc09ae69-e1ee-4c83-9c04-e09da568c6ab, 8cfdaf81-8e59-4486-ba2f-4e450a23c876 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 1.98 | 3.0756 | 4.402 | 0.02376 | 0.036908 | 0.052824 | 2024-01-20 23:00 | GSO_76 | br_076_21 | 3 | 89cbe802-faf3-4709-b370-afa1154a5b70, fd14c6a3-6658-4039-a0b8-c00ab26e307c, a61580ad-490f-42dd-919c-3cfdfb775908 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 219.1131 | 326.4566 | 429.952 | 2.6294 | 3.9175 | 5.1594 | 2024-01-21 04:00 | GSO_77 | br_077_21 | 3 | 04933340-1f7e-4732-a170-31c687c8d71e, da253492-f9e5-4572-a892-8cf7206f5562, 55611621-48c6-40ab-afb0-d76e41a0d5de | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 14.1194 | 20.5536 | 27.412 | 0.16943 | 0.24664 | 0.32894 | 2024-01-18 04:00 | GSO_78 | br_078_21 | 3 | c0ddba19-fbd3-4341-bb7c-f8d96301d889, 648e5aaa-f39d-4756-9d09-ca5503bbc225, 838a2e79-8d23-4760-9eab-eb6ed2d38b4c | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 71.3217 | 95.6596 | 124.596 | 0.85586 | 1.1479 | 1.4952 | 2024-01-21 04:00 | GSO_79 | br_079_21 | 3 | dfd547e9-e06c-4fe7-8842-913f0b3f7d52, f68a1c8a-5406-4783-b8ae-a255bce0e795, 02d224d1-8d1b-45bb-98ed-ebc20c74318a | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 1.8934 | 2.873 | 4.851 | 0.022721 | 0.034476 | 0.058212 | 2024-01-20 17:00 | GSO_8 | br_022_21 | 3 | 9e0bf50d-94bd-4e5d-9a43-95a506f4c534, 14a29c10-6f6b-4045-834c-a8cdccfa7fe8, 674756f5-28ec-40f8-8ece-cd6c8a394c18 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 88.6299 | 123.794 | 162.143 | 1.0636 | 1.4855 | 1.9457 | 2024-01-21 02:00 | GSO_80 | br_080_21 | 3 | 4fb9d568-cec8-4d2c-b185-503c8441a94f, 48527915-ef6b-4d16-9525-f6d17fae71ba, e4842198-5ba7-4542-9415-20f0a87511ac | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 97.4105 | 132.4067 | 172.497 | 1.1689 | 1.5889 | 2.07 | 2024-01-21 04:00 | GSO_81 | br_081_21 | 3 | 9a5c0969-f68d-4cea-a13e-ef351a3d3730, a8a2fc9d-e642-4554-abad-f2610eb29b51, 27bb62b3-e552-4996-874d-31dcad547987 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 137.0611 | 209.2763 | 282.079 | 1.6447 | 2.5113 | 3.3849 | 2024-01-21 | GSO_82 | br_082_21 | 3 | a890d29a-0380-4cd2-8cff-f9826e3ff07b, 918cae00-7f70-4556-9d40-35da1f05977d, 93c33640-e4a0-470f-a164-89c99ae69984 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 174.186 | 263.1632 | 350.031 | 2.0902 | 3.158 | 4.2004 | 2024-01-18 04:00 | GSO_83 | br_083_21 | 3 | af9148e3-1b4f-4f27-b409-3654c3f953f5, 48c0048d-65ab-48a8-8cd9-833258bee864, 8c265c14-8e0f-4c74-9519-46da2dff7cd1 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 14.425 | 21.864 | 30.241 | 0.1731 | 0.26237 | 0.36289 | 2024-01-20 06:05 | GSO_84 | br_084_21 | 3 | d4454767-7751-4c58-9cbd-79e943f45acf, 4cc5af87-12cf-4fd1-a89c-0318dc07c068, b63c8e73-fffc-4e69-ad08-995c149ebeaa | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 38.9205 | 50.5416 | 65.364 | 0.46705 | 0.6065 | 0.78437 | 2024-01-21 04:00 | GSO_85 | br_085_21 | 3 | 6fcd01be-d3d1-4df7-bec8-4f8b1042aac0, 4fc59078-b2c4-42d5-b129-faa7a3f54cac, ac192c64-42ef-423f-814b-c8b837b8f5d2 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 89.6995 | 126.522 | 163.401 | 1.0764 | 1.5183 | 1.9608 | 2024-01-20 23:00 | GSO_86 | br_086_21 | 3 | 492c962b-e2b7-4edd-afe9-20606e4114f6, 6182a628-fb52-41b9-8b93-90488a51a0fe, 6927b6e8-4d14-436e-8236-19dc4cdad934 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 87.3478 | 117.9236 | 150.134 | 1.0482 | 1.4151 | 1.8016 | 2024-01-21 04:00 | GSO_87 | br_087_21 | 3 | e7689375-373b-4d7a-b001-0fa11239a327, 589e4f98-7742-4541-b2c3-6b108b7f9d4d, d9c84a3d-b565-4642-a7d4-3c9df307b1c8 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 63.4485 | 86.0716 | 113.438 | 0.76138 | 1.0329 | 1.3613 | 2024-01-18 04:00 | GSO_88 | br_088_21 | 3 | 93986b58-113b-4798-b153-eda6e8924352, 73bea406-8df3-48d6-99e8-780c9ba74d8d, b1fd8626-d75b-4f57-95d8-5e0f995f6548 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 64.1018 | 84.414 | 109.301 | 0.76922 | 1.013 | 1.3116 | 2024-01-21 04:00 | GSO_89 | br_089_21 | 3 | d629f58a-fb37-4300-b174-4dadcd7fdef5, c6e42508-1e1b-4a8d-ad6c-5ed17230666d, a59c7bce-fb93-4255-8dac-4024e2c3a1c9 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 1.1873 | 1.899 | 3.204 | 0.014247 | 0.022788 | 0.038448 | 2024-01-21 01:00 | GSO_9 | br_023_21 | 3 | c7e10126-bd63-4bd3-96ab-07587af29378, f631ee12-3be7-417b-ad19-901e9ad68684, 9b89dc0e-e258-4610-b60b-484b1b02a312 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 34.5538 | 41.669 | 52.553 | 0.41465 | 0.50003 | 0.63064 | 2024-01-20 16:00 | GSO_90 | br_090_21 | 3 | ab8abf18-0128-43c3-8213-8fcc30f583d2, 59f75e54-a46d-4153-8855-555945d0a888, f35586be-8010-4ad3-b579-d95b9825cae5 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 80.7802 | 105.9423 | 140.175 | 0.96936 | 1.2713 | 1.6821 | 2024-01-21 | GSO_91 | br_091_21 | 3 | 11eec288-b107-4b0d-8513-8e0e8b097ff9, 66b6c9ff-fe2f-4708-83aa-26715afe7d27, 2494a26c-ddcb-40f8-8643-7c936424dfc0 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 42.2238 | 51.503 | 64.096 | 0.50669 | 0.61804 | 0.76915 | 2024-01-21 04:00 | GSO_92 | br_092_21 | 3 | a984179e-ff24-4a5b-9bff-44fa02582a26, fbe573a4-e81d-4315-b9c9-510a65c98be6, 9e7256be-44ac-40e3-95c4-e604f1b5b6ea | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 38.0767 | 46.28 | 58.531 | 0.45692 | 0.55536 | 0.70237 | 2024-01-21 04:00 | GSO_93 | br_093_21 | 3 | ac7b38f5-50a1-4cc6-bab1-d609ee8f92a4, 75f25960-b76b-4ea6-95b3-22351b5c7fde, 531ef22d-48aa-4ee9-88be-bf0b21101c8d | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 27.5543 | 33.871 | 41.978 | 0.33065 | 0.40645 | 0.50374 | 2024-01-18 04:00 | GSO_94 | br_094_21 | 3 | f0bd6ef7-dacb-46d2-ad18-589db990b13a, a82b3639-950c-4ba5-8e39-502e435ad83a, c177967e-e6f6-4644-aa50-326a9ebe3d00 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 142.3321 | 212.2589 | 285.763 | 1.708 | 2.5471 | 3.4292 | 2024-01-18 04:00 | GSO_95 | br_095_21 | 3 | 859a9ae6-4d75-45f7-af3f-1d1c2c11b96f, ad766f3b-7d19-4707-8a90-38f818011b97, c6b6dfcf-55ed-45e7-9e6a-1ed25774a828 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 67.699 | 89.0123 | 113.163 | 0.81239 | 1.0681 | 1.358 | 2024-01-20 06:00 | GSO_96 | br_096_21 | 3 | 1b5731fb-ced8-4f58-b1ab-d0ee4f8ea875, fcbaf392-5711-44ee-86c0-792317753d2f, fad28770-b3f6-4478-87a1-3b095d264a87 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 175.9206 | 263.5666 | 347.515 | 2.111 | 3.1628 | 4.1702 | 2024-01-21 04:00 | GSO_97 | br_098_21 | 3 | 003a8d77-c248-43c2-af2f-1f5f30595e2b, b3f7a58f-66bb-4c73-a447-90250ee96029, 3b017716-3815-48f3-bf37-e278bd03cc9d | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 224.6811 | 345.1416 | 472.836 | 2.6962 | 4.1417 | 5.674 | 2024-01-21 04:00 | GSO_98 | br_099_21 | 3 | e19d273e-4ce0-462d-9501-16552f6df1a5, 74d4c75b-fdbd-4356-81ba-130cbea2e530, 43272e40-5062-4f3e-9a6d-0899fa207db5 | A, B, C | OK
105348 | 2024-01-01 05:00 | 2024-12-31 23:55 | 5 | 193.545 | 282.449 | 377.087 | 2.3225 | 3.3894 | 4.525 | 2024-01-21 04:00 | GSO_99 | br_0100_21 | 3 | a3c897bb-ba13-4a0b-af16-81acabf20ccd, 667e5144-bfb1-4543-a81f-7a88e26190c7, 9d892d7c-e138-4107-8084-bbde890e1cc4 | A, B, C | OK

## Breaker_Data_Sources
grid_id | DataSourceID | BreakerElementID | ElementType | ElementCustomerType | IsProducer | DataSourceType | Provider | Metrics | FriendlyID | DataSourcePhases | Direction | ValidRange | HasKWh | HasVoltage | NormalizedPhase
GSO_1 | b1e8c057-fded-4c70-8f86-a33db401b6d1 | br_01_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_01_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_1 | ba6970aa-af7f-428e-9a4f-7826618684b4 | br_01_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_01_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_1 | ea496fcb-6216-4db1-9885-1da5dbf70fa2 | br_01_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_01_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_10 | 396f73e2-6041-46ac-90d5-a9439aef50d8 | br_015_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_015_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_10 | b315ece6-7341-4cdf-a1c9-70a8dbfe93ff | br_015_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_015_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_10 | d140ab36-31a8-40c7-820d-c3a2df82604a | br_015_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_015_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_100 | 3125b67a-cbd0-47b3-94b6-a60b38de7e8b | br_097_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_097_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_100 | 564551fe-ec45-4b6c-a7df-ebfa29a0a242 | br_097_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_097_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_100 | cc6f9a7e-ea1b-4cdb-9c85-6c672b845068 | br_097_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_097_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_101 | 6c559f06-b888-4a9d-ba0f-901b0b19b354 | br_0101_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0101_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_101 | 8f1038a0-f3d5-4f15-bedf-b8f1215601f3 | br_0101_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0101_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_101 | f32aafa6-4f97-40b9-85a1-6516b7a34fb0 | br_0101_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0101_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_102 | 3f11f59f-b6f2-44fe-8a16-f4a87144ca07 | br_0102_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0102_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_102 | 58383f3b-39ee-41c1-9a45-f21c6b309b7c | br_0102_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0102_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_102 | aaef163c-bdc4-464e-9864-b0c0ebdf8662 | br_0102_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0102_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_103 | a3539c00-7186-4684-93db-03123790cf12 | br_0103_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0103_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_103 | d53e58ae-230d-449a-b78d-6b5cfa60f56b | br_0103_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0103_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_103 | d5fd099c-84d4-4965-91b3-bbc0c68d61d1 | br_0103_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0103_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_104 | 0256f17b-1fde-4e5f-aa42-6a293aa27e64 | br_0104_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0104_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_104 | 4922eba1-a72a-4e22-8a37-912d5f9ac46b | br_0104_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0104_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_104 | dbaf906f-b53b-4b15-bd48-42442608214a | br_0104_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0104_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_105 | 11bf4c6d-205c-4caf-b572-7246ab210632 | br_0105_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0105_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_105 | 3943a935-55e7-44b5-a61e-08789763be18 | br_0105_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0105_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_105 | 98dc0614-4560-469e-93e2-97b3c41b5000 | br_0105_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0105_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_106 | 1523bf59-c426-49d7-add2-e9b831978748 | br_0106_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0106_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_106 | e37ebffe-ff65-4277-a7e0-2315cac8c267 | br_0106_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0106_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_106 | f0643cc7-b03a-4328-82d5-2924a650f97f | br_0106_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0106_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_107 | 4113937f-0ce2-415a-9249-ce7327d121f7 | br_0107_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0107_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_107 | 5d59abb9-0bac-4fa7-a891-4e9d4e794c88 | br_0107_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0107_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_107 | b1339292-267a-4146-8873-ecfc9cb1a82e | br_0107_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0107_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_108 | 1886a888-6918-466c-929d-0c8f16370dda | br_0108_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0108_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_108 | c0036365-6459-4cc7-b7b1-ed8933515338 | br_0108_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0108_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_108 | e867a5e4-d5f1-4fdf-98c8-da37424315a6 | br_0108_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0108_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_109 | 0c75d1f1-8237-436b-a2c8-c9b6fdc7a116 | br_0109_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0109_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_109 | e6350d88-56d8-492b-bc1e-dcd90fcca31f | br_0109_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0109_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_109 | ec8ad3c4-a39d-4acb-8788-e7435be58cb7 | br_0109_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0109_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_11 | 469868d0-2f60-42bd-aa67-be26d6eae0eb | br_016_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_016_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_11 | 9cdbec33-569a-438b-ac44-23b272ad169b | br_016_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_016_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_11 | dfea635f-2a86-40f1-9367-d78b6dd6c309 | br_016_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_016_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_110 | 1e111a58-963a-4906-b1f6-e2d03049b19a | br_0110_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0110_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_110 | 8a0dd243-2512-4f92-afd7-db6e79d7496e | br_0110_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0110_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_110 | ca02189c-f89b-417b-a469-ef0366d6da6e | br_0110_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0110_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_111 | 3488e4fc-fa59-4bcf-b967-3b7a890f6c3c | br_0111_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0111_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_111 | e60c92cc-e283-4345-87b0-ba3a9fd78005 | br_0111_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0111_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_111 | f8549391-d242-43a9-9a34-33f872443611 | br_0111_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0111_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_112 | 407ea9ca-a495-4119-a139-1d1233852fdc | br_0112_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0112_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_112 | 99fe4744-38fc-4467-902b-d97556b6d295 | br_0112_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0112_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_112 | e1fd2b67-b072-4575-9f5d-c24af5f52b11 | br_0112_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0112_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_113 | a9bc380c-ca71-4a2b-b314-0f03f9f76581 | br_0113_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0113_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_113 | bdf27366-2b21-4e21-8946-86b299b81d14 | br_0113_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0113_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_113 | f8ddca03-2f28-483b-97fe-a4538d6c4e2b | br_0113_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0113_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_114 | 156d4241-1525-4089-8367-effd61eb4969 | br_0114_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0114_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_114 | 3128527e-a25b-4b2c-9d88-b40eb600580e | br_0114_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0114_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_114 | 34c2c476-7801-4ae6-ba1f-ca1a602925b3 | br_0114_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0114_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_115 | 58786ac1-7ac2-4287-bd8f-add68a4ea208 | br_0115_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0115_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_115 | 820fcd78-48b0-467d-8925-554a0333f605 | br_0115_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0115_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_115 | d3645b59-a71d-4848-9deb-b044c307c52a | br_0115_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0115_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_116 | 2a93f307-f837-4de0-9089-b308bde0f0fd | br_0116_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0116_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_116 | ba9bd088-fa13-4d76-ba16-6dba6a8b45de | br_0116_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0116_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_116 | e9542020-950f-403c-af95-965f8434a9f8 | br_0116_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0116_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_117 | 127d58d0-da5d-47a0-a219-b8c1834a136a | br_0117_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0117_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_117 | 20ca2ff7-1194-405d-9098-d4544944a36d | br_0117_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0117_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_117 | 79b91384-9645-42ed-940d-37fdffcc31a0 | br_0117_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0117_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_118 | 7b9e37f6-9e61-405e-8bc5-9d79097397f4 | br_0118_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0118_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_118 | b2273af8-cb6e-4178-93e7-36fab6dbf2c0 | br_0118_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0118_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_118 | cb23fba1-b5a8-477f-b388-dcbc14cf56b2 | br_0118_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0118_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_119 | 1a46aa48-ac4e-4046-aa43-a61c07c816d6 | br_0119_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0119_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_119 | 3aad3364-ed36-4087-b7d0-6d3b3fa6f823 | br_0119_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0119_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_119 | faec1da7-65b2-4b86-be90-e4357dfde1ce | br_0119_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0119_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_12 | 4c1ed359-972e-4bdd-a0cd-1159d7a32c07 | br_017_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_017_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_12 | e263a729-e360-4716-9561-679bf6b5d16a | br_017_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_017_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_12 | ede6f7c6-f426-4d65-bfe0-7dac24a794c1 | br_017_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_017_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_121 | 0eb7ef08-0441-4661-84d4-63da9255ea41 | br_01_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_01_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_121 | 36cfcc10-f3c4-4989-ae21-5fdd2aa20962 | br_01_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_01_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_121 | 423b0798-4793-4a14-a787-72bb51fb4cef | br_01_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_01_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_122 | 4fa57e43-e6c7-4d4b-a312-3fb0e3337ffc | br_02_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_02_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_122 | abf746be-5de9-44ac-9f69-a717abe29437 | br_02_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_02_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_122 | e63f1c25-1cac-49ae-9929-f96fa015f74e | br_02_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_02_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_123 | 08fe15ea-b154-4270-ad96-7633898d9feb | br_03_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_03_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_123 | 22b46d3c-1104-4a6b-baf0-791554532cbe | br_03_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_03_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_123 | c84967ed-4e26-4447-aaec-39d0dba00695 | br_03_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_03_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_124 | cbbe0d2b-6245-4a4f-bcc2-e456b3e84669 | br_04_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_04_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_124 | e9588dba-e5c4-44a0-a87f-6d585846716c | br_04_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_04_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_124 | f9dd1e2c-0b53-4323-abbd-c79d2b87bf2e | br_04_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_04_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_125 | 16682194-aa4b-49e9-acf2-9c6562595352 | br_05_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_05_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_125 | 99cabfd6-b964-4658-8155-1699ad43459b | br_05_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_05_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_125 | cd7fbbb9-9a6f-4dd9-891c-e37a9557fa12 | br_05_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_05_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_126 | 12d09ac1-fdb6-467e-a1aa-f99f6eed49f6 | br_06_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_06_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_126 | 9006b8b1-eda0-485b-a8d0-426580b8950f | br_06_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_06_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_126 | bc3fda03-9c4b-412b-a5ef-6db07eeba8fc | br_06_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_06_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_127 | 1287cfdf-d61b-4b7d-9c56-4a67e583be03 | br_07_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_07_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_127 | 9962595a-e18a-4855-ab7a-6bcfb11262e4 | br_07_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_07_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_127 | a16d8ea2-fafa-4870-8bff-75e352b48100 | br_07_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_07_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_128 | 3d10e996-315d-4229-9b7c-a9b8e0697db8 | br_08_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_08_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_128 | 692be577-442c-4ab0-b1e1-5785854345e2 | br_08_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_08_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_128 | 6cff9753-e438-465f-8082-4b41468b4f8c | br_08_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_08_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_129 | 066b1670-e5b9-40c9-bd97-907fe78b74e9 | br_09_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_09_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_129 | 686b2171-718b-454f-a63f-7a08af910b78 | br_09_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_09_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_129 | ca9fa130-fc7c-477e-8464-326c962a06af | br_09_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_09_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_13 | 28993f84-c3b9-4382-b199-7eae1602f7b5 | br_018_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_018_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_13 | 538bb977-c069-4a72-a1f5-79ade89be85e | br_018_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_018_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_13 | d4524dc1-a63b-454b-a0d9-1683a9db619b | br_018_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_018_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_130 | 0820aaeb-7057-4894-a6ba-7624e83ee1a7 | br_010_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_010_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_130 | cab2ab50-4b8d-4ecb-98f8-73c155d0b547 | br_010_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_010_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_130 | ec2f67d6-3e29-40e6-b3db-279de5aeb3e1 | br_010_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_010_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_131 | 1a6f96c2-84f7-4c0d-b1a3-ee2364b2f450 | br_011_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_011_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_131 | 434fff6c-2804-492a-a7e9-8c978d0dc8e3 | br_011_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_011_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_131 | 618c145a-b95c-4f8d-9e8d-9389861004d6 | br_011_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_011_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_132 | 0716ea38-77d5-4d34-bc24-820dc14d344a | br_012_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_012_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_132 | 8eae3b99-7252-4faf-9a4e-4abe914bc30e | br_012_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_012_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_132 | 935c3854-ba34-4cf1-b241-c865be78d3bf | br_012_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_012_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_133 | 4d344901-644b-4ea0-b7f1-b381d39a7879 | br_013_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_013_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_133 | c086c5c8-dc85-4746-8b0a-d8e23067358a | br_013_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_013_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_133 | dddfb629-b710-4a70-b13f-4f342bc8fe74 | br_013_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_013_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_134 | 4091c3a2-55c3-4b7e-8d9d-a8e4affed314 | br_014_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_014_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_134 | 57c2fa84-53da-4153-9d01-3c3ac5b2144e | br_014_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_014_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_134 | 7325e088-181d-4e0d-b15b-2dd1fbda83f0 | br_014_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_014_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_135 | 306b628e-5350-43cc-bd44-5524b56eb0e1 | br_015_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_015_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_135 | c3ac0e33-1470-42fd-9a70-99015f289563 | br_015_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_015_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_135 | cb036569-e3a3-4f9a-ab6b-ada0cfc7f7a2 | br_015_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_015_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_136 | 04ce7e89-fb0f-4fb3-9752-836af1c7ab9e | br_016_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_016_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_136 | 1985324e-e67a-4d01-bf4e-cbc1776ba800 | br_016_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_016_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_136 | 66b785ca-af8e-4a6a-8af7-ff9241ec96a5 | br_016_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_016_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_137 | bb261d99-e16f-41bf-90d2-05acc7b4f39c | br_017_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_017_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_137 | cf094241-cd71-4a00-ae80-c341e78225f3 | br_017_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_017_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_137 | d0f42d15-cf63-4976-b310-0a7f21c9a7fc | br_017_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_017_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_138 | 8cf34f38-0fdb-4d44-9870-a7c9c5b5c3b4 | br_018_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_018_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_138 | b91b7108-02a6-4c8f-9294-9075747bf3d2 | br_018_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_018_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_138 | c812a09e-5775-4fbc-93b7-37aa020f3a4a | br_018_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_018_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_139 | 2a67f2a3-ad9e-4413-af20-999870d5694e | br_019_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_019_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_139 | 6ec0fb64-8f9d-48b6-81ae-63048adca78a | br_019_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_019_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_139 | 8781de87-205d-4b90-963f-449d72c41e8c | br_019_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_019_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_14 | 37a8aff5-f4d5-48d1-b094-f7ff7add641f | br_019_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_019_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_14 | 4f0a9de3-7d5d-4d74-841a-ad368a655ddc | br_019_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_019_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_14 | 9df35035-201c-43e2-9c0f-29f5652d20b6 | br_019_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_019_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_140 | 52cf19cb-d2f9-48a0-a5d7-3d345a429c59 | br_020_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_020_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_140 | 7ac282db-535a-4cda-bcc4-f62230cc0be1 | br_020_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_020_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_140 | b6e43aeb-290f-443d-917c-933a0af02698 | br_020_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_020_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_141 | 0b5869b0-b194-4a18-8593-e04336ade6ea | br_021_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_021_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_141 | 78f844cc-a5b4-4d9d-ba33-ef854d68bc8a | br_021_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_021_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_141 | b6f787f7-5117-4b48-81f4-ddbe099f96d7 | br_021_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_021_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_142 | 5c50320a-6541-43e1-a0eb-b3cc85335f92 | br_022_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_022_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_142 | aeed6de5-7aca-4fa3-a5ca-b1f32ee717c2 | br_022_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_022_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_142 | d8586197-7e6c-42e3-af81-89d0f76301f9 | br_022_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_022_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_143 | 15ee4200-f93f-4884-ab81-e52eb3d0b73c | br_023_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_023_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_143 | b2362459-63fa-42c8-b75d-cdff666f2190 | br_023_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_023_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_143 | ef7cab0d-e432-4fb1-aab4-46e5068286b4 | br_023_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_023_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_144 | 82536324-6f01-4e66-a011-7b067544a9ac | br_024_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_024_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_144 | bd7e1df8-2eb1-4167-bee8-930536ce0573 | br_024_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_024_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_144 | cebe0434-4e95-4fd2-8e1e-22573f21abf5 | br_024_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_024_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_145 | 039cb766-152c-4467-9ec0-94180921a657 | br_025_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_025_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_145 | 5042bbb0-cc21-499d-9106-09bd8c86b439 | br_025_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_025_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_145 | e8f52edb-11b6-4a01-8cb4-dde6abb481d7 | br_025_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_025_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_146 | 45141e3c-ee87-445b-a8cd-53eaf3cf8ac6 | br_026_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_026_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_146 | 9c3aa61d-fdd8-4e3a-a859-786b34331466 | br_026_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_026_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_146 | d4d03355-620e-4213-a24e-266e873f3f79 | br_026_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_026_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_147 | 783419bf-1c8f-4783-a364-729c4d25328a | br_027_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_027_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_147 | a6c68db1-932a-455f-9961-2001628d137a | br_027_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_027_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_147 | b05dca4b-f167-46ba-b479-77fc9d306c98 | br_027_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_027_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_148 | 9cb02ef5-7d31-4690-b5cc-1c8ff7465b94 | br_028_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_028_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_148 | e51bd3d2-27db-4e8c-85b3-94bb36fdecb2 | br_028_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_028_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_148 | f209db33-c63a-4eeb-9470-44a070b1f980 | br_028_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_028_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_149 | 22ef08a2-8b87-47bf-912f-a49f8dbe4e0e | br_029_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_029_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_149 | 54f22dd6-dae8-4d6f-8c00-4ee16cc1bce1 | br_029_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_029_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_149 | a7d55959-39f6-4006-8a75-2ac4375060d6 | br_029_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_029_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_15 | 2dfc9022-cd2d-4071-a0ed-f7aa4dbf29b5 | br_020_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_020_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_15 | 34fb9785-294c-4580-94c1-92b57cb0e642 | br_020_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_020_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_15 | dd9e89fb-3f9a-4966-a494-c19ab9432a67 | br_020_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_020_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_150 | 97ae36fa-2e65-4c6d-8a11-b6c4ba921c0d | br_030_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_030_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_150 | 99ca8035-36a9-410b-844c-06c1ddb4c66b | br_030_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_030_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_150 | e18873a3-19e0-4c86-abaf-03f1ea49ef98 | br_030_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_030_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_151 | 051f7584-2010-41f8-9415-9183657a8ae0 | br_031_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_031_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_151 | 0542d836-ab02-49aa-a8b7-a4265443a1c4 | br_031_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_031_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_151 | 5b53a681-1338-4fee-9587-71b3e65506cb | br_031_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_031_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_152 | 3b38bb39-6b77-49e7-b0c7-d3c699da74dc | br_032_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_032_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_152 | 3f75484a-66ad-416b-bdfc-429bf783f99d | br_032_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_032_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_152 | ab723fc3-e0cb-4dbc-8181-5681e5ac3348 | br_032_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_032_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_153 | 07ea0bf7-442d-4e77-b98a-b9e2c8d50114 | br_033_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_033_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_153 | 0d3f8e19-033b-4d8c-a34b-ff04747bd082 | br_033_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_033_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_153 | 5e1ed7ac-1e16-4c51-bb12-e8d8b8c244c4 | br_033_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_033_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_154 | 0840b23d-66b0-48cf-856c-1f62526c7d6e | br_034_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_034_22.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_154 | 6eba73e4-418d-4cd1-96b6-60b826ae450c | br_034_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_034_22.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_154 | 70369b74-10d7-4556-af26-c0ccb8f01935 | br_034_22 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_034_22.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_155 | 033ba35a-0e88-44c7-ae68-9ef721532ab3 | br_01_23 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_01_23.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_155 | d1e45bf7-a00b-40dc-a6ec-c751080a13c9 | br_01_23 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_01_23.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_155 | ecb9c3ef-513f-492a-821c-4bff92c1df9c | br_01_23 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_01_23.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_156 | 12b55d36-db8c-475f-838b-08caf84b6421 | br_02_23 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_02_23.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_156 | 17343a92-f390-4c00-96dd-aa4c8e6f2cf5 | br_02_23 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_02_23.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_156 | 2ec12710-cbb3-4ac0-ae81-f21bc775b59d | br_02_23 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_02_23.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_157 | 962e5ace-7f13-49d9-a1bd-65973f2adfac | br_03_23 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_03_23.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_157 | b96622f9-34da-4d3a-a144-a82c9e2d84a9 | br_03_23 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_03_23.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_157 | d76a1565-b995-4235-9508-12ae427ed548 | br_03_23 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_03_23.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_158 | 5320e9a7-8d71-4f75-b9c9-3a6a37f707db | br_04_23 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_04_23.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_158 | 8e1d3060-4f17-4027-bb48-9326d72d1f5e | br_04_23 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_04_23.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_158 | b84e6ee7-bc4b-467a-884d-e5dac0fbac0b | br_04_23 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_04_23.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_159 | 2e882994-3bef-4961-988c-cd677efd6410 | br_05_23 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_05_23.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_159 | 83f2cd36-180e-4d9a-9105-62a32f68ab85 | br_05_23 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_05_23.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_159 | 96fae847-ae01-4905-9884-47b324a88934 | br_05_23 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_05_23.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_16 | 2b3c0835-4f9e-453c-86b3-35847ab5af94 | br_021_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_021_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_16 | b5d738a6-79bd-43f6-b4e4-0fb4de70abfd | br_021_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_021_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_16 | e4f24c66-81cd-48f4-b9a3-a8aaa9fe8c98 | br_021_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_021_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_160 | 47f0ee8f-4288-4af4-b69a-10cebf43b645 | br_06_23 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_06_23.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_160 | b9360429-edfb-4e59-a900-8a457dc83cba | br_06_23 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_06_23.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_160 | c3e81296-2c1a-4ada-80c1-b847107d5cfb | br_06_23 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_06_23.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_161 | 89a3b24a-887f-4195-8344-51f18a00dbf7 | br_07_23 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_07_23.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_161 | c4eee589-eb1d-4947-bc9b-3f547ec858d4 | br_07_23 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_07_23.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_161 | e61fb2d3-e704-4d3f-bf86-8b04c3724fd7 | br_07_23 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_07_23.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_162 | 4bfd3a0a-1178-4983-b63c-76c387206a99 | br_08_23 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_08_23.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_162 | f4ffa257-f9a9-48e6-8ef7-945f8e687e83 | br_08_23 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_08_23.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_162 | f620b838-2134-4f66-a112-15e5f46318b0 | br_08_23 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_08_23.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_163 | 0d2e0f05-d1e8-46f2-953d-daf9b517d3b5 | br_09_23 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_09_23.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_163 | 9018e821-338d-4aa5-bb0d-3e9aa19f5a3b | br_09_23 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_09_23.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_163 | d90170cc-5eec-43f7-a5d9-cb91dca851cb | br_09_23 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_09_23.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_17 | 3a2af09c-baa8-4dbe-95ab-fb397036b19d | br_024_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_024_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_17 | 883c59a4-ab46-45e2-b36d-e1959b7c89b6 | br_024_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_024_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_17 | f0a67506-31bf-4b47-9614-f559c928646a | br_024_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_024_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_18 | 08eb7b30-b593-4a81-854f-d7a00d46db1e | br_025_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_025_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_18 | 34cac5e4-313a-4454-a92d-abc9047eadc8 | br_025_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_025_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_18 | 90d3f27c-2599-462f-8abb-58371a03ece5 | br_025_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_025_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_19 | a03bc8be-0c7b-4ca4-b625-79f7823155e9 | br_026_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_026_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_19 | cf54e8e6-a9a5-4011-b2be-1226fbdc86cb | br_026_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_026_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_19 | d5920248-7472-436e-b060-c7c2ff9ef29d | br_026_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_026_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_2 | a28c1752-7f45-48c2-b058-b7cdc091e5d6 | br_02_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_02_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_2 | e16fe26a-3331-4e10-bcda-3d5b4cfc42bc | br_02_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_02_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_2 | f5b81547-937f-4c70-92ba-8a0fb6594394 | br_02_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_02_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_20 | 0367f0a8-b7e5-4ca5-94ae-d44fa9d00bfd | br_027_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_027_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_20 | a602edca-8fde-46f7-8d51-40a5f85d6a1d | br_027_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_027_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_20 | c9015052-da74-4877-bbf1-9a6c4275c44d | br_027_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_027_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_21 | 39b0a939-9afe-4c84-bfda-5eec318bc35e | br_028_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_028_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_21 | 6f7a2c02-ca5d-4d73-a76d-82f0fe3158c9 | br_028_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_028_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_21 | a49c303e-bacd-45af-8754-babfb2545a48 | br_028_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_028_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_22 | 60e175bd-dd8d-424f-b541-e6c27675c2ee | br_029_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_029_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_22 | c13495f3-7436-4771-9d8e-028fe398e677 | br_029_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_029_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_22 | f1fcda72-2c9e-4219-9a68-e344865344e1 | br_029_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_029_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_23 | 306a0179-6b1d-4c84-b7ad-c043978706f4 | br_030_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_030_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_23 | 73114768-3396-46b2-8366-027d7f330c2a | br_030_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_030_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_23 | 8896d2cc-f5f3-479a-9806-74f9830d0e65 | br_030_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_030_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_24 | 0e740376-b7d0-46f1-8238-50979ff53b86 | br_031_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_031_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_24 | 3abd341d-8629-4be0-888c-4405cbd18a68 | br_031_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_031_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_24 | 8866ae0d-1645-4e1d-85a9-520a2b057093 | br_031_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_031_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_25 | 6a2617f0-409e-448d-8ce4-c1175edcf36a | br_032_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_032_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_25 | 8c0cf450-9297-450e-b468-8396988be79f | br_032_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_032_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_25 | d4f80b32-222c-49ea-bb38-81080bcb0826 | br_032_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_032_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_26 | 06410d93-c578-4f9d-86d8-8eb333ba28c9 | br_033_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_033_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_26 | 123d2e0f-6c7b-4b17-96d2-32d4328dde67 | br_033_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_033_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_26 | 2ded452d-d964-456f-bc61-891c5e02102b | br_033_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_033_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_27 | 6fdd1896-ad74-48a8-9816-85aa01d652d1 | br_034_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_034_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_27 | 9dbd0f33-80b1-4155-96b0-ea2e0658e691 | br_034_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_034_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_27 | d428eae8-d228-4f79-b9ea-91e3a88bb229 | br_034_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_034_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_28 | 4b1de06e-7ccd-42bd-ba7d-141a0d6eed10 | br_035_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_035_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_28 | 4cc07d73-767d-4a92-aa56-8d6f6139433c | br_035_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_035_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_28 | c3250712-a026-44dc-83b1-ab0b7bd1cef0 | br_035_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_035_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_29 | 37be8bbe-3fc1-42ac-aa14-512831f011d9 | br_036_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_036_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_29 | 53ac9d88-ec7e-422c-9547-7b65d0e1b05c | br_036_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_036_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_29 | bbdb1c8c-b61b-4af3-a00d-d34e99f936e8 | br_036_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_036_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_3 | 262d1506-d23e-42d2-a938-f15cb2f35365 | br_03_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_03_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_3 | 861d3fe8-4f6d-46b5-bb00-6d79ddaf889d | br_03_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_03_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_3 | cabb02b4-86e3-4261-87ef-66f06902bb61 | br_03_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_03_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_30 | 07afe75d-2efa-4a63-8500-f5eed954ebc4 | br_037_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_037_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_30 | 4339844d-f7f4-4af5-a7ce-ff1e206a4bfc | br_037_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_037_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_30 | 80a38063-4b58-4c05-9631-c9f20eaae49f | br_037_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_037_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_31 | c4bbbd0b-e3cc-4312-b11b-48dca067f34f | br_038_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_038_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_31 | dbd51660-93ed-49dc-b484-ac1a2ff93751 | br_038_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_038_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_31 | f5f51af7-9112-4286-adaa-37e4589d054a | br_038_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_038_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_32 | 049d0b94-e086-4825-b104-d454ffd3dc7c | br_039_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_039_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_32 | 81e832b4-cd01-4844-b4d8-6ff81d95dbe4 | br_039_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_039_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_32 | 934aabc4-8b42-44e6-82dc-1b3261dc29d9 | br_039_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_039_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_33 | 2bcc2cc5-82f5-4040-ac32-a00d0d07de51 | br_040_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_040_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_33 | d858a33a-1b66-4073-aed2-4b1a30ad837b | br_040_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_040_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_33 | ee1a565e-ae8b-4984-9f7a-cab15b5447c3 | br_040_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_040_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_34 | 0cbf9200-98b4-43c7-934d-2cc30d8ab63b | br_041_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_041_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_34 | 179024ab-8e49-42be-b943-761705fb5abd | br_041_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_041_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_34 | deb58541-2cca-43d5-86c5-55264c6041d3 | br_041_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_041_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_35 | 6d4ede07-2601-4246-903b-56124df12172 | br_042_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_042_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_35 | d7ccdfd6-6a7d-4338-9666-e79b11f003a9 | br_042_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_042_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_35 | efc37dec-e402-4c7d-81af-aa9cb2729757 | br_042_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_042_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_36 | 1ede274a-9246-4aec-acc0-17642c07af97 | br_043_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_043_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_36 | a492b914-7377-4047-b30b-90aa78dc94d3 | br_043_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_043_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_36 | c95edbeb-bfcc-48be-abeb-7c6ceba7bdae | br_043_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_043_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_37 | 53f8a349-7f61-440d-ad82-54a7f6d15d3a | br_044_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_044_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_37 | 547c5604-b333-47b9-83ad-6f6fa1e88927 | br_044_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_044_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_37 | e72c363a-7373-4a30-a872-329d650d7569 | br_044_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_044_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_38 | 15e8162e-962b-481f-923b-b2fe7c7ce432 | br_045_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_045_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_38 | 31c14863-6ede-40c4-86a5-41eadc729ac2 | br_045_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_045_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_38 | 9c1dc66a-d26b-42ae-9fa5-d4e46c87f492 | br_045_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_045_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_39 | 1ef359a3-1b23-4781-b7f6-73e5a4c4559f | br_046_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_046_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_39 | 77ff5585-562a-45e7-a281-464e98737abb | br_046_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_046_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_39 | 93658bef-4bd5-4300-8424-5c388155968b | br_046_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_046_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_4 | 1da22d5c-e6b3-4228-b327-ddf40f1f21b6 | br_04_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_04_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_4 | 67c44f52-c49c-4993-940f-90408b4b9ae5 | br_04_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_04_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_4 | eda55f14-fedc-4eb6-a389-a51a43231405 | br_04_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_04_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_40 | 58cd6faf-3139-48ff-a9ef-b152b7ebf778 | br_047_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_047_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_40 | 79202d32-8dca-417a-9d59-fc14f3bcaf5f | br_047_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_047_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_40 | ee7aaead-b8fb-40d3-8a03-8ab58a542fdc | br_047_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_047_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_41 | 4f3f10ee-748f-4c21-b9c3-8ac51c8d41f6 | br_048_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_048_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_41 | d7d6e014-1cd2-4cb5-84bb-a00b2cad42e3 | br_048_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_048_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_41 | e1cda877-0a5c-49b1-bd5f-ad8449fb0e0c | br_048_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_048_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_42 | 0b1099db-07b7-4a46-831f-0ab42e837cdd | br_049_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_049_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_42 | 0e80773a-a8cc-45a5-8095-4dc9d8b00215 | br_049_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_049_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_42 | 119ef0a4-9572-4988-9343-96cacd641d11 | br_049_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_049_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_43 | 223df89f-b673-46b7-a74d-953aa3cadd02 | br_050_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_050_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_43 | d260c5dc-0f9a-4ff7-a347-cabc3421f531 | br_050_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_050_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_43 | d8ed1451-4cac-4c54-9238-07312269a3d5 | br_050_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_050_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_44 | 9de5605e-2be3-4478-8321-ec1cfdb77d3e | br_051_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_051_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_44 | ae9708d6-58e3-48d8-b469-2b865749bda5 | br_051_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_051_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_44 | c206a6a0-74a2-4aa0-b700-0397b158b47c | br_051_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_051_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_45 | 0a36e22d-cb96-45c8-8d47-74ede8f433bd | br_052_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_052_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_45 | 87af0485-ac3b-4ef1-bd8e-39742bb1311b | br_052_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_052_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_45 | ac9dddc3-7cae-427c-a129-87d3008b8362 | br_052_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_052_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_46 | 0b8f662d-5bc3-42fe-a24e-070da09bdd80 | br_053_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_053_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_46 | 425e9895-3ec9-4ecf-a2de-00e847c9f5d0 | br_053_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_053_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_46 | e8d1fc00-bcf6-4d05-b6b9-7f38e6915ce5 | br_053_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_053_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_47 | 44d72b2b-4d39-442e-969c-28bfa609a6ca | br_054_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_054_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_47 | 73020989-8b85-4f2f-ae5e-b46034dccc36 | br_054_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_054_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_47 | df231f2b-7e74-4562-8026-e0248f99acb1 | br_054_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_054_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_48 | 2756c12d-de33-427b-a20e-a7524bf8ba2a | br_055_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_055_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_48 | caead5dd-6652-4002-9205-bf1f5d7841a2 | br_055_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_055_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_48 | d501232c-0e9b-4aed-b1c7-0711f51fd12c | br_055_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_055_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_49 | 4e486c1d-6969-466b-bb85-e868d8c69d96 | br_056_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_056_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_49 | 904a534b-b4de-47cc-9111-a909cdd75ff6 | br_056_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_056_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_49 | cf17223b-5ef6-40ff-aa3f-7eaa71fa5ab1 | br_056_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_056_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_5 | 1a7b2ce3-8ce4-43f0-822c-bae88f338574 | br_05_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_05_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_5 | 921b5057-9802-4094-b921-551288ad3d2e | br_05_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_05_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_5 | fdea0e08-11f9-40c1-bd4a-4dfdb8ea2803 | br_05_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_05_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_50 | 02cb60eb-e56b-45c0-871a-7d5da5072e9a | br_057_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_057_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_50 | 4d9bb5e2-1e06-49ed-b322-273c65c7ea12 | br_057_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_057_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_50 | ceeee8fb-13b1-43c7-9caf-4433648f6846 | br_057_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_057_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_51 | 100d5254-7678-4ba2-a678-ffa8ba0ac8ce | br_058_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_058_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_51 | 2dabfa67-e633-42fb-88f8-b99c8c81ce3f | br_058_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_058_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_51 | 40e658e9-710a-4f81-b823-ce3b23d76208 | br_058_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_058_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_52 | 148e241f-8dca-40c2-bc4c-9bba11acb600 | br_059_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_059_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_52 | 54cc7298-372e-4f46-9c94-d78d3e7e3368 | br_059_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_059_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_52 | 740ff96c-6171-4486-bb6a-904851da7f68 | br_059_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_059_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_53 | 3b012ead-fe04-4b66-8c50-59d42334a89c | br_060_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_060_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_53 | 4b800952-fa1b-4668-ba63-4244710bab3c | br_060_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_060_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_53 | 77c08208-993b-4559-b9e2-42c4c772997c | br_060_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_060_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_54 | 0c2d5da7-8b73-4e99-a2ec-e1bd371c44f1 | br_061_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_061_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_54 | b486465e-b5c3-4f46-9979-e961ceb9df52 | br_061_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_061_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_54 | c70624cc-3511-421e-bcd3-4f74ee43c80f | br_061_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_061_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_55 | 0d627f19-7146-43b0-9f7b-bac68e9966db | br_062_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_062_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_55 | 55b291eb-5761-4e7f-8635-63057f856791 | br_062_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_062_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_55 | efb7b851-1f6e-4084-9dd6-5a62049b7654 | br_062_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_062_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_56 | 620a8a0d-bcbd-4f44-be97-24244e308366 | br_063_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_063_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_56 | 748858e9-a0e0-4bc6-a0b7-f4e67d7c9ecd | br_063_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_063_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_56 | d5be6516-e14a-46ab-a02a-0650b74a5159 | br_063_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_063_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_57 | 08dafb35-ef6e-48c6-89ef-1f3412fa5f7e | br_08_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_08_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_57 | 27046833-12e1-4f55-aeb1-743d3fddc9b4 | br_08_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_08_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_57 | e2d61ac2-432e-446d-b560-32b75aebceed | br_08_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_08_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_58 | b8c6df33-b602-4d1c-9dda-e52dfeb41665 | br_09_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_09_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_58 | cd71f269-7897-4746-9a77-c6bc730114fe | br_09_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_09_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_58 | ff232009-b42f-4f71-a769-88a952701609 | br_09_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_09_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_59 | 1231155d-ed13-4563-8801-fa08388d11cd | br_010_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_010_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_59 | 1b822839-e89f-49f2-b2a9-69df27011548 | br_010_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_010_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_59 | 4529fb6d-421e-4f02-9b11-c956a4443f8e | br_010_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_010_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_6 | 120599d7-eee0-4966-bd20-36d9e2e8b089 | br_06_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_06_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_6 | 145f4423-0120-41c0-a961-6f6b453e91a7 | br_06_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_06_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_6 | a5d804f2-bcf0-4e70-ad7f-9ffc889ca71a | br_06_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_06_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_60 | 229fce16-0cb2-401d-957b-9d0d3c2ac1cc | br_011_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_011_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_60 | 52980b4f-3c73-4c68-8631-e69ccc722a34 | br_011_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_011_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_60 | fc187080-4278-4699-8d7f-ded10dc27448 | br_011_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_011_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_61 | 192ef0e0-59f5-4932-a625-7e967573ec09 | br_012_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_012_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_61 | 69c0c6b0-aa07-4cdc-9789-b51b223584c4 | br_012_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_012_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_61 | bdb558af-9d90-4dcd-870e-28a86925b8cc | br_012_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_012_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_62 | 2c8910bb-0c41-4c36-8a5f-d8ffc5e65938 | br_013_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_013_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_62 | 3f59d58a-b780-49d5-86ae-b0b0f01c076d | br_013_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_013_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_62 | decddce1-9f0e-44c6-a3bd-24fdb9cf1a60 | br_013_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_013_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_63 | 167b629e-ae1a-4acd-a435-a9faf6b8f0b1 | br_014_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_014_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_63 | 676b1650-044c-43bf-bea6-3dced2a612c6 | br_014_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_014_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_63 | abbc8c51-7785-4d04-a735-eb965d943d5a | br_014_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_014_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_64 | 8ec9092e-c513-4856-b139-17b0f244b287 | br_064_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_064_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_64 | 96d7ca9d-a8a7-4620-beb4-015993e1495f | br_064_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_064_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_64 | aa668afa-9003-4c02-b068-76a760cba7c4 | br_064_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_064_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_65 | a2d74127-91f7-4d1b-a98b-b3f287f80eec | br_065_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_065_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_65 | a8421f63-1fb7-4386-80d1-558a9049f658 | br_065_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_065_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_65 | c0caf65c-2d30-471b-9a8c-36e1484ba877 | br_065_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_065_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_66 | 0cbf5c43-696f-40b4-ab01-fd3dfd670388 | br_066_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_066_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_66 | 3f826b2c-284b-4880-a9f1-d5554c1e5213 | br_066_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_066_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_66 | aa212fd9-92d5-4c56-9a9e-3014ccc9a7ce | br_066_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_066_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_67 | 4b3c48a3-9a69-47a9-b110-7d0b18cc7f06 | br_067_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_067_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_67 | 5aed073b-49c0-4020-b105-f7e28cfd41ed | br_067_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_067_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_67 | fddc71cc-3766-4601-9ca7-c2caab3c7c4d | br_067_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_067_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_68 | 6abb0433-d7c1-47cb-b500-310c0966ae29 | br_068_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_068_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_68 | b14a51cb-21cb-48f4-91a6-564663c5a923 | br_068_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_068_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_68 | f2986696-35a7-4d1e-a7dd-8b01d8d6756a | br_068_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_068_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_69 | 16e446fe-cce5-4d4b-abd0-d9bf98278835 | br_069_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_069_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_69 | 3f69baec-6464-4c01-91c1-171903c224f7 | br_069_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_069_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_69 | 9255af13-2569-446c-b326-8de2942e3a26 | br_069_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_069_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_7 | 7c4e0a27-0ba8-4589-8efa-9d78e22aeea7 | br_07_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_07_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_7 | 874fce3a-0ddc-405e-8b4d-496bf1208ffa | br_07_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_07_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_7 | b3997dcd-0479-4422-904f-1e86aedb3b49 | br_07_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_07_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_70 | 7a4e8fb6-f007-4d77-bfcb-6a0b0e18561c | br_070_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_070_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_70 | 96d35f0d-746b-4c76-8d6d-a22dac3dcfaa | br_070_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_070_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_70 | ff4d78df-a97d-465a-9270-6b140f05b7ee | br_070_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_070_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_71 | 4ff8b560-0d8d-46ca-aa4f-48e616d84a8c | br_071_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_071_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_71 | 7dec81b6-3b82-498d-bfaa-f44bf5d9581d | br_071_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_071_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_71 | 828a3353-455f-43cc-a9b0-71980deae8fd | br_071_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_071_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_72 | 2f6074d9-3367-424b-9912-3b54ba3842dc | br_072_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_072_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_72 | 5be2e72a-f9e3-4662-bcdd-f6914b127473 | br_072_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_072_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_72 | ceb3c16f-b2c1-4384-83e5-47eb8d9787a9 | br_072_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_072_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_73 | 0a5bd7a0-8dda-4ea9-8140-b43dcad4334a | br_073_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_073_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_73 | dc0e22aa-9b17-4812-81b9-805e6e2fcea4 | br_073_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_073_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_73 | dd7e3ea9-a097-46d9-ba3d-e976877c959f | br_073_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_073_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_74 | 2be1e40d-d971-44eb-9f8e-1f362b00491f | br_074_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_074_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_74 | 4cb9db9e-b9c3-473e-878d-2df2932f4dcf | br_074_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_074_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_74 | b4794b85-7397-40b2-a7b2-50c82c66983d | br_074_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_074_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_75 | 74ba07cb-a526-4618-b499-1a430d0286b7 | br_075_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_075_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_75 | 8cfdaf81-8e59-4486-ba2f-4e450a23c876 | br_075_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_075_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_75 | dc09ae69-e1ee-4c83-9c04-e09da568c6ab | br_075_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_075_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_76 | 89cbe802-faf3-4709-b370-afa1154a5b70 | br_076_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_076_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_76 | a61580ad-490f-42dd-919c-3cfdfb775908 | br_076_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_076_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_76 | fd14c6a3-6658-4039-a0b8-c00ab26e307c | br_076_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_076_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_77 | 04933340-1f7e-4732-a170-31c687c8d71e | br_077_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_077_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_77 | 55611621-48c6-40ab-afb0-d76e41a0d5de | br_077_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_077_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_77 | da253492-f9e5-4572-a892-8cf7206f5562 | br_077_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_077_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_78 | 648e5aaa-f39d-4756-9d09-ca5503bbc225 | br_078_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_078_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_78 | 838a2e79-8d23-4760-9eab-eb6ed2d38b4c | br_078_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_078_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_78 | c0ddba19-fbd3-4341-bb7c-f8d96301d889 | br_078_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_078_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_79 | 02d224d1-8d1b-45bb-98ed-ebc20c74318a | br_079_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_079_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_79 | dfd547e9-e06c-4fe7-8842-913f0b3f7d52 | br_079_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_079_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_79 | f68a1c8a-5406-4783-b8ae-a255bce0e795 | br_079_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_079_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_8 | 14a29c10-6f6b-4045-834c-a8cdccfa7fe8 | br_022_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_022_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_8 | 674756f5-28ec-40f8-8ece-cd6c8a394c18 | br_022_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_022_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_8 | 9e0bf50d-94bd-4e5d-9a43-95a506f4c534 | br_022_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_022_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_80 | 48527915-ef6b-4d16-9525-f6d17fae71ba | br_080_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_080_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_80 | 4fb9d568-cec8-4d2c-b185-503c8441a94f | br_080_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_080_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_80 | e4842198-5ba7-4542-9415-20f0a87511ac | br_080_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_080_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_81 | 27bb62b3-e552-4996-874d-31dcad547987 | br_081_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_081_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_81 | 9a5c0969-f68d-4cea-a13e-ef351a3d3730 | br_081_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_081_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_81 | a8a2fc9d-e642-4554-abad-f2610eb29b51 | br_081_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_081_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_82 | 918cae00-7f70-4556-9d40-35da1f05977d | br_082_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_082_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_82 | 93c33640-e4a0-470f-a164-89c99ae69984 | br_082_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_082_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_82 | a890d29a-0380-4cd2-8cff-f9826e3ff07b | br_082_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_082_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_83 | 48c0048d-65ab-48a8-8cd9-833258bee864 | br_083_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_083_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_83 | 8c265c14-8e0f-4c74-9519-46da2dff7cd1 | br_083_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_083_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_83 | af9148e3-1b4f-4f27-b409-3654c3f953f5 | br_083_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_083_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_84 | 4cc5af87-12cf-4fd1-a89c-0318dc07c068 | br_084_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_084_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_84 | b63c8e73-fffc-4e69-ad08-995c149ebeaa | br_084_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_084_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_84 | d4454767-7751-4c58-9cbd-79e943f45acf | br_084_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_084_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_85 | 4fc59078-b2c4-42d5-b129-faa7a3f54cac | br_085_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_085_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_85 | 6fcd01be-d3d1-4df7-bec8-4f8b1042aac0 | br_085_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_085_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_85 | ac192c64-42ef-423f-814b-c8b837b8f5d2 | br_085_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_085_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_86 | 492c962b-e2b7-4edd-afe9-20606e4114f6 | br_086_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_086_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_86 | 6182a628-fb52-41b9-8b93-90488a51a0fe | br_086_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_086_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_86 | 6927b6e8-4d14-436e-8236-19dc4cdad934 | br_086_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_086_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_87 | 589e4f98-7742-4541-b2c3-6b108b7f9d4d | br_087_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_087_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_87 | d9c84a3d-b565-4642-a7d4-3c9df307b1c8 | br_087_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_087_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_87 | e7689375-373b-4d7a-b001-0fa11239a327 | br_087_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_087_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_88 | 73bea406-8df3-48d6-99e8-780c9ba74d8d | br_088_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_088_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_88 | 93986b58-113b-4798-b153-eda6e8924352 | br_088_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_088_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_88 | b1fd8626-d75b-4f57-95d8-5e0f995f6548 | br_088_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_088_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_89 | a59c7bce-fb93-4255-8dac-4024e2c3a1c9 | br_089_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_089_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_89 | c6e42508-1e1b-4a8d-ad6c-5ed17230666d | br_089_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_089_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_89 | d629f58a-fb37-4300-b174-4dadcd7fdef5 | br_089_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_089_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_9 | 9b89dc0e-e258-4610-b60b-484b1b02a312 | br_023_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_023_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_9 | c7e10126-bd63-4bd3-96ab-07587af29378 | br_023_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_023_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_9 | f631ee12-3be7-417b-ad19-901e9ad68684 | br_023_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_023_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_90 | 59f75e54-a46d-4153-8855-555945d0a888 | br_090_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_090_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_90 | ab8abf18-0128-43c3-8213-8fcc30f583d2 | br_090_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_090_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_90 | f35586be-8010-4ad3-b579-d95b9825cae5 | br_090_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_090_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_91 | 11eec288-b107-4b0d-8513-8e0e8b097ff9 | br_091_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_091_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_91 | 2494a26c-ddcb-40f8-8643-7c936424dfc0 | br_091_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_091_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_91 | 66b6c9ff-fe2f-4708-83aa-26715afe7d27 | br_091_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_091_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_92 | 9e7256be-44ac-40e3-95c4-e604f1b5b6ea | br_092_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_092_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_92 | a984179e-ff24-4a5b-9bff-44fa02582a26 | br_092_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_092_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_92 | fbe573a4-e81d-4315-b9c9-510a65c98be6 | br_092_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_092_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_93 | 531ef22d-48aa-4ee9-88be-bf0b21101c8d | br_093_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_093_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_93 | 75f25960-b76b-4ea6-95b3-22351b5c7fde | br_093_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_093_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_93 | ac7b38f5-50a1-4cc6-bab1-d609ee8f92a4 | br_093_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_093_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_94 | a82b3639-950c-4ba5-8e39-502e435ad83a | br_094_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_094_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_94 | c177967e-e6f6-4644-aa50-326a9ebe3d00 | br_094_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_094_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_94 | f0bd6ef7-dacb-46d2-ad18-589db990b13a | br_094_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_094_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_95 | 859a9ae6-4d75-45f7-af3f-1d1c2c11b96f | br_095_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_095_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_95 | ad766f3b-7d19-4707-8a90-38f818011b97 | br_095_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_095_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_95 | c6b6dfcf-55ed-45e7-9e6a-1ed25774a828 | br_095_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_095_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_96 | 1b5731fb-ced8-4f58-b1ab-d0ee4f8ea875 | br_096_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_096_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_96 | fad28770-b3f6-4478-87a1-3b095d264a87 | br_096_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_096_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_96 | fcbaf392-5711-44ee-86c0-792317753d2f | br_096_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_096_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_97 | 003a8d77-c248-43c2-af2f-1f5f30595e2b | br_098_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_098_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_97 | 3b017716-3815-48f3-bf37-e278bd03cc9d | br_098_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_098_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_97 | b3f7a58f-66bb-4c73-a447-90250ee96029 | br_098_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_098_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_98 | 43272e40-5062-4f3e-9a6d-0899fa207db5 | br_099_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_099_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_98 | 74d4c75b-fdbd-4356-81ba-130cbea2e530 | br_099_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_099_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_98 | e19d273e-4ce0-462d-9501-16552f6df1a5 | br_099_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_099_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A
GSO_99 | 667e5144-bfb1-4543-a81f-7a88e26190c7 | br_0100_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0100_21.B | B |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | B
GSO_99 | 9d892d7c-e138-4107-8084-bbde890e1cc4 | br_0100_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0100_21.C | C |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | C
GSO_99 | a3c897bb-ba13-4a0b-af16-81acabf20ccd | br_0100_21 | CircuitBreaker | switchable_element-Breaker | TRUE | SENSOR | SMART_scada_data | ['kWh', 'V'] | br_0100_21.A | A |  | [2024-01-01 05:00:00+00:00, None) | TRUE | TRUE | A

## Upstream_Path_Detail
grid_id | SelectedBreakerElementID | PathElementID | ElementType | ElementCustomerType | Phases | IsProducer | IsConsumer | IsSwitchable | SwitchIsOpen | UpstreamElementID | Terminal1CN | Terminal2CN | RawRatingKVA | RawRatingA | RawVoltageLevel | RawPrimaryVoltage | RawSecondaryVoltage | UpstreamDepth
GSO_1 | br_01_21 | br_01_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE0 | S_nSSEE0_12.47 | 5714.3 |  | MV |  |  | 0
GSO_10 | br_015_21 | br_015_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE10 | S_nSSEE10_12.47 | 5555.6 |  | MV |  |  | 0
GSO_100 | br_097_21 | br_097_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE6 | S_nSSEE6_12.47 | 7500.0 |  | MV |  |  | 0
GSO_101 | br_0101_21 | br_0101_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE7 | S_nSSEE7_12.47 | 5714.3 |  | MV |  |  | 0
GSO_102 | br_0102_21 | br_0102_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE7 | S_nSSEE7_12.47 | 5714.3 |  | MV |  |  | 0
GSO_103 | br_0103_21 | br_0103_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE7 | S_nSSEE7_12.47 | 5714.3 |  | MV |  |  | 0
GSO_104 | br_0104_21 | br_0104_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE7 | S_nSSEE7_12.47 | 5714.3 |  | MV |  |  | 0
GSO_105 | br_0105_21 | br_0105_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE7 | S_nSSEE7_12.47 | 5714.3 |  | MV |  |  | 0
GSO_106 | br_0106_21 | br_0106_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE7 | S_nSSEE7_12.47 | 5714.3 |  | MV |  |  | 0
GSO_107 | br_0107_21 | br_0107_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE7 | S_nSSEE7_12.47 | 5714.3 |  | MV |  |  | 0
GSO_108 | br_0108_21 | br_0108_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE8 | S_nSSEE8_12.47 | 7142.9 |  | MV |  |  | 0
GSO_109 | br_0109_21 | br_0109_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE8 | S_nSSEE8_12.47 | 7142.9 |  | MV |  |  | 0
GSO_11 | br_016_21 | br_016_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE10 | S_nSSEE10_12.47 | 5555.6 |  | MV |  |  | 0
GSO_110 | br_0110_21 | br_0110_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE8 | S_nSSEE8_12.47 | 7142.9 |  | MV |  |  | 0
GSO_111 | br_0111_21 | br_0111_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE8 | S_nSSEE8_12.47 | 7142.9 |  | MV |  |  | 0
GSO_112 | br_0112_21 | br_0112_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE8 | S_nSSEE8_12.47 | 7142.9 |  | MV |  |  | 0
GSO_113 | br_0113_21 | br_0113_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE8 | S_nSSEE8_12.47 | 7142.9 |  | MV |  |  | 0
GSO_114 | br_0114_21 | br_0114_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE8 | S_nSSEE8_12.47 | 7142.9 |  | MV |  |  | 0
GSO_115 | br_0115_21 | br_0115_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE9 | S_nSSEE9_12.47 | 10000.0 |  | MV |  |  | 0
GSO_116 | br_0116_21 | br_0116_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE9 | S_nSSEE9_12.47 | 10000.0 |  | MV |  |  | 0
GSO_117 | br_0117_21 | br_0117_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE9 | S_nSSEE9_12.47 | 10000.0 |  | MV |  |  | 0
GSO_118 | br_0118_21 | br_0118_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE9 | S_nSSEE9_12.47 | 10000.0 |  | MV |  |  | 0
GSO_119 | br_0119_21 | br_0119_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE9 | S_nSSEE9_12.47 | 10000.0 |  | MV |  |  | 0
GSO_12 | br_017_21 | br_017_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE10 | S_nSSEE10_12.47 | 5555.6 |  | MV |  |  | 0
GSO_121 | br_01_22 | br_01_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE0 | S_nSSEE0_12.47 | 15000.0 |  | MV |  |  | 0
GSO_122 | br_02_22 | br_02_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE0 | S_nSSEE0_12.47 | 15000.0 |  | MV |  |  | 0
GSO_123 | br_03_22 | br_03_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE0 | S_nSSEE0_12.47 | 15000.0 |  | MV |  |  | 0
GSO_124 | br_04_22 | br_04_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE0 | S_nSSEE0_12.47 | 15000.0 |  | MV |  |  | 0
GSO_125 | br_05_22 | br_05_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE1 | S_nSSEE1_12.47 | 10000.0 |  | MV |  |  | 0
GSO_126 | br_06_22 | br_06_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE1 | S_nSSEE1_12.47 | 10000.0 |  | MV |  |  | 0
GSO_127 | br_07_22 | br_07_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE1 | S_nSSEE1_12.47 | 10000.0 |  | MV |  |  | 0
GSO_128 | br_08_22 | br_08_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE1 | S_nSSEE1_12.47 | 10000.0 |  | MV |  |  | 0
GSO_129 | br_09_22 | br_09_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE2 | S_nSSEE2_12.47 | 8571.4 |  | MV |  |  | 0
GSO_13 | br_018_21 | br_018_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE10 | S_nSSEE10_12.47 | 5555.6 |  | MV |  |  | 0
GSO_130 | br_010_22 | br_010_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE2 | S_nSSEE2_12.47 | 8571.4 |  | MV |  |  | 0
GSO_131 | br_011_22 | br_011_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE2 | S_nSSEE2_12.47 | 8571.4 |  | MV |  |  | 0
GSO_132 | br_012_22 | br_012_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE2 | S_nSSEE2_12.47 | 8571.4 |  | MV |  |  | 0
GSO_133 | br_013_22 | br_013_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE2 | S_nSSEE2_12.47 | 8571.4 |  | MV |  |  | 0
GSO_134 | br_014_22 | br_014_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE2 | S_nSSEE2_12.47 | 8571.4 |  | MV |  |  | 0
GSO_135 | br_015_22 | br_015_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE2 | S_nSSEE2_12.47 | 8571.4 |  | MV |  |  | 0
GSO_136 | br_016_22 | br_016_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE3 | S_nSSEE3_12.47 | 6000.0 |  | MV |  |  | 0
GSO_137 | br_017_22 | br_017_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE3 | S_nSSEE3_12.47 | 6000.0 |  | MV |  |  | 0
GSO_138 | br_018_22 | br_018_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE3 | S_nSSEE3_12.47 | 6000.0 |  | MV |  |  | 0
GSO_139 | br_019_22 | br_019_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE3 | S_nSSEE3_12.47 | 6000.0 |  | MV |  |  | 0
GSO_14 | br_019_21 | br_019_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE10 | S_nSSEE10_12.47 | 5555.6 |  | MV |  |  | 0
GSO_140 | br_020_22 | br_020_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE3 | S_nSSEE3_12.47 | 6000.0 |  | MV |  |  | 0
GSO_141 | br_021_22 | br_021_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE4 | S_nSSEE4_12.47 | 12000.0 |  | MV |  |  | 0
GSO_142 | br_022_22 | br_022_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE4 | S_nSSEE4_12.47 | 12000.0 |  | MV |  |  | 0
GSO_143 | br_023_22 | br_023_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE4 | S_nSSEE4_12.47 | 12000.0 |  | MV |  |  | 0
GSO_144 | br_024_22 | br_024_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE4 | S_nSSEE4_12.47 | 12000.0 |  | MV |  |  | 0
GSO_145 | br_025_22 | br_025_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE4 | S_nSSEE4_12.47 | 12000.0 |  | MV |  |  | 0
GSO_146 | br_026_22 | br_026_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE5 | S_nSSEE5_12.47 | 7500.0 |  | MV |  |  | 0
GSO_147 | br_027_22 | br_027_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE5 | S_nSSEE5_12.47 | 7500.0 |  | MV |  |  | 0
GSO_148 | br_028_22 | br_028_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE5 | S_nSSEE5_12.47 | 7500.0 |  | MV |  |  | 0
GSO_149 | br_029_22 | br_029_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE5 | S_nSSEE5_12.47 | 7500.0 |  | MV |  |  | 0
GSO_15 | br_020_21 | br_020_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE10 | S_nSSEE10_12.47 | 5555.6 |  | MV |  |  | 0
GSO_150 | br_030_22 | br_030_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE6 | S_nSSEE6_12.47 | 6000.0 |  | MV |  |  | 0
GSO_151 | br_031_22 | br_031_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE6 | S_nSSEE6_12.47 | 6000.0 |  | MV |  |  | 0
GSO_152 | br_032_22 | br_032_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE6 | S_nSSEE6_12.47 | 6000.0 |  | MV |  |  | 0
GSO_153 | br_033_22 | br_033_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE6 | S_nSSEE6_12.47 | 6000.0 |  | MV |  |  | 0
GSO_154 | br_034_22 | br_034_22 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE6 | S_nSSEE6_12.47 | 6000.0 |  | MV |  |  | 0
GSO_155 | br_01_23 | br_01_23 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE0 | S_nSSEE0_12.47 | 7500.0 |  | MV |  |  | 0
GSO_156 | br_02_23 | br_02_23 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE0 | S_nSSEE0_12.47 | 7500.0 |  | MV |  |  | 0
GSO_157 | br_03_23 | br_03_23 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE0 | S_nSSEE0_12.47 | 7500.0 |  | MV |  |  | 0
GSO_158 | br_04_23 | br_04_23 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE0 | S_nSSEE0_12.47 | 7500.0 |  | MV |  |  | 0
GSO_159 | br_05_23 | br_05_23 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE1 | S_nSSEE1_12.47 | 5714.3 |  | MV |  |  | 0
GSO_16 | br_021_21 | br_021_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE10 | S_nSSEE10_12.47 | 5555.6 |  | MV |  |  | 0
GSO_160 | br_06_23 | br_06_23 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE1 | S_nSSEE1_12.47 | 5714.3 |  | MV |  |  | 0
GSO_161 | br_07_23 | br_07_23 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE1 | S_nSSEE1_12.47 | 5714.3 |  | MV |  |  | 0
GSO_162 | br_08_23 | br_08_23 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE2 | S_nSSEE2_12.47 | 8000.0 |  | MV |  |  | 0
GSO_163 | br_09_23 | br_09_23 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE2 | S_nSSEE2_12.47 | 8000.0 |  | MV |  |  | 0
GSO_17 | br_024_21 | br_024_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE11 | S_nSSEE11_12.47 | 13333.3 |  | MV |  |  | 0
GSO_18 | br_025_21 | br_025_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE11 | S_nSSEE11_12.47 | 13333.3 |  | MV |  |  | 0
GSO_19 | br_026_21 | br_026_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE11 | S_nSSEE11_12.47 | 13333.3 |  | MV |  |  | 0
GSO_2 | br_02_21 | br_02_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE0 | S_nSSEE0_12.47 | 5714.3 |  | MV |  |  | 0
GSO_20 | br_027_21 | br_027_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE12 | S_nSSEE12_12.47 | 3750.0 |  | MV |  |  | 0
GSO_21 | br_028_21 | br_028_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE12 | S_nSSEE12_12.47 | 3750.0 |  | MV |  |  | 0
GSO_22 | br_029_21 | br_029_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE12 | S_nSSEE12_12.47 | 3750.0 |  | MV |  |  | 0
GSO_23 | br_030_21 | br_030_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE12 | S_nSSEE12_12.47 | 3750.0 |  | MV |  |  | 0
GSO_24 | br_031_21 | br_031_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE12 | S_nSSEE12_12.47 | 3750.0 |  | MV |  |  | 0
GSO_25 | br_032_21 | br_032_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE12 | S_nSSEE12_12.47 | 3750.0 |  | MV |  |  | 0
GSO_26 | br_033_21 | br_033_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE12 | S_nSSEE12_12.47 | 3750.0 |  | MV |  |  | 0
GSO_27 | br_034_21 | br_034_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE12 | S_nSSEE12_12.47 | 3750.0 |  | MV |  |  | 0
GSO_28 | br_035_21 | br_035_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE13 | S_nSSEE13_12.47 | 7500.0 |  | MV |  |  | 0
GSO_29 | br_036_21 | br_036_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE13 | S_nSSEE13_12.47 | 7500.0 |  | MV |  |  | 0
GSO_3 | br_03_21 | br_03_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE0 | S_nSSEE0_12.47 | 5714.3 |  | MV |  |  | 0
GSO_30 | br_037_21 | br_037_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE13 | S_nSSEE13_12.47 | 7500.0 |  | MV |  |  | 0
GSO_31 | br_038_21 | br_038_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE13 | S_nSSEE13_12.47 | 7500.0 |  | MV |  |  | 0
GSO_32 | br_039_21 | br_039_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE14 | S_nSSEE14_12.47 | 6666.7 |  | MV |  |  | 0
GSO_33 | br_040_21 | br_040_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE14 | S_nSSEE14_12.47 | 6666.7 |  | MV |  |  | 0
GSO_34 | br_041_21 | br_041_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE14 | S_nSSEE14_12.47 | 6666.7 |  | MV |  |  | 0
GSO_35 | br_042_21 | br_042_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE14 | S_nSSEE14_12.47 | 6666.7 |  | MV |  |  | 0
GSO_36 | br_043_21 | br_043_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE14 | S_nSSEE14_12.47 | 6666.7 |  | MV |  |  | 0
GSO_37 | br_044_21 | br_044_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE14 | S_nSSEE14_12.47 | 6666.7 |  | MV |  |  | 0
GSO_38 | br_045_21 | br_045_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE15 | S_nSSEE15_12.47 | 6000.0 |  | MV |  |  | 0
GSO_39 | br_046_21 | br_046_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE15 | S_nSSEE15_12.47 | 6000.0 |  | MV |  |  | 0
GSO_4 | br_04_21 | br_04_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE0 | S_nSSEE0_12.47 | 5714.3 |  | MV |  |  | 0
GSO_40 | br_047_21 | br_047_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE15 | S_nSSEE15_12.47 | 6000.0 |  | MV |  |  | 0
GSO_41 | br_048_21 | br_048_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE15 | S_nSSEE15_12.47 | 6000.0 |  | MV |  |  | 0
GSO_42 | br_049_21 | br_049_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE15 | S_nSSEE15_12.47 | 6000.0 |  | MV |  |  | 0
GSO_43 | br_050_21 | br_050_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV |  |  | 0
GSO_44 | br_051_21 | br_051_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV |  |  | 0
GSO_45 | br_052_21 | br_052_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV |  |  | 0
GSO_46 | br_053_21 | br_053_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV |  |  | 0
GSO_47 | br_054_21 | br_054_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV |  |  | 0
GSO_48 | br_055_21 | br_055_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV |  |  | 0
GSO_49 | br_056_21 | br_056_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV |  |  | 0
GSO_5 | br_05_21 | br_05_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE0 | S_nSSEE0_12.47 | 5714.3 |  | MV |  |  | 0
GSO_50 | br_057_21 | br_057_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV |  |  | 0
GSO_51 | br_058_21 | br_058_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV |  |  | 0
GSO_52 | br_059_21 | br_059_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV |  |  | 0
GSO_53 | br_060_21 | br_060_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE16 | S_nSSEE16_12.47 | 5454.5 |  | MV |  |  | 0
GSO_54 | br_061_21 | br_061_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE17 | S_nSSEE17_12.47 | 10000.0 |  | MV |  |  | 0
GSO_55 | br_062_21 | br_062_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE17 | S_nSSEE17_12.47 | 10000.0 |  | MV |  |  | 0
GSO_56 | br_063_21 | br_063_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE17 | S_nSSEE17_12.47 | 10000.0 |  | MV |  |  | 0
GSO_57 | br_08_21 | br_08_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE1 | S_nSSEE1_12.47 | 6122.4 |  | MV |  |  | 0
GSO_58 | br_09_21 | br_09_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE1 | S_nSSEE1_12.47 | 6122.4 |  | MV |  |  | 0
GSO_59 | br_010_21 | br_010_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE1 | S_nSSEE1_12.47 | 6122.4 |  | MV |  |  | 0
GSO_6 | br_06_21 | br_06_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE0 | S_nSSEE0_12.47 | 5714.3 |  | MV |  |  | 0
GSO_60 | br_011_21 | br_011_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE1 | S_nSSEE1_12.47 | 6122.4 |  | MV |  |  | 0
GSO_61 | br_012_21 | br_012_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE1 | S_nSSEE1_12.47 | 6122.4 |  | MV |  |  | 0
GSO_62 | br_013_21 | br_013_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE1 | S_nSSEE1_12.47 | 6122.4 |  | MV |  |  | 0
GSO_63 | br_014_21 | br_014_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE1 | S_nSSEE1_12.47 | 6122.4 |  | MV |  |  | 0
GSO_64 | br_064_21 | br_064_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE2 | S_nSSEE2_12.47 | 4285.7 |  | MV |  |  | 0
GSO_65 | br_065_21 | br_065_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE2 | S_nSSEE2_12.47 | 4285.7 |  | MV |  |  | 0
GSO_66 | br_066_21 | br_066_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE2 | S_nSSEE2_12.47 | 4285.7 |  | MV |  |  | 0
GSO_67 | br_067_21 | br_067_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE2 | S_nSSEE2_12.47 | 4285.7 |  | MV |  |  | 0
GSO_68 | br_068_21 | br_068_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE2 | S_nSSEE2_12.47 | 4285.7 |  | MV |  |  | 0
GSO_69 | br_069_21 | br_069_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE2 | S_nSSEE2_12.47 | 4285.7 |  | MV |  |  | 0
GSO_7 | br_07_21 | br_07_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE0 | S_nSSEE0_12.47 | 5714.3 |  | MV |  |  | 0
GSO_70 | br_070_21 | br_070_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE2 | S_nSSEE2_12.47 | 4285.7 |  | MV |  |  | 0
GSO_71 | br_071_21 | br_071_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE3 | S_nSSEE3_12.47 | 10000.0 |  | MV |  |  | 0
GSO_72 | br_072_21 | br_072_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE3 | S_nSSEE3_12.47 | 10000.0 |  | MV |  |  | 0
GSO_73 | br_073_21 | br_073_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE3 | S_nSSEE3_12.47 | 10000.0 |  | MV |  |  | 0
GSO_74 | br_074_21 | br_074_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE3 | S_nSSEE3_12.47 | 10000.0 |  | MV |  |  | 0
GSO_75 | br_075_21 | br_075_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE3 | S_nSSEE3_12.47 | 10000.0 |  | MV |  |  | 0
GSO_76 | br_076_21 | br_076_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV |  |  | 0
GSO_77 | br_077_21 | br_077_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV |  |  | 0
GSO_78 | br_078_21 | br_078_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV |  |  | 0
GSO_79 | br_079_21 | br_079_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV |  |  | 0
GSO_8 | br_022_21 | br_022_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE10 | S_nSSEE10_12.47 | 5555.6 |  | MV |  |  | 0
GSO_80 | br_080_21 | br_080_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV |  |  | 0
GSO_81 | br_081_21 | br_081_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV |  |  | 0
GSO_82 | br_082_21 | br_082_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV |  |  | 0
GSO_83 | br_083_21 | br_083_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV |  |  | 0
GSO_84 | br_084_21 | br_084_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV |  |  | 0
GSO_85 | br_085_21 | br_085_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE4 | S_nSSEE4_12.47 | 6666.7 |  | MV |  |  | 0
GSO_86 | br_086_21 | br_086_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV |  |  | 0
GSO_87 | br_087_21 | br_087_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV |  |  | 0
GSO_88 | br_088_21 | br_088_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV |  |  | 0
GSO_89 | br_089_21 | br_089_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV |  |  | 0
GSO_9 | br_023_21 | br_023_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE10 | S_nSSEE10_12.47 | 5555.6 |  | MV |  |  | 0
GSO_90 | br_090_21 | br_090_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV |  |  | 0
GSO_91 | br_091_21 | br_091_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV |  |  | 0
GSO_92 | br_092_21 | br_092_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV |  |  | 0
GSO_93 | br_093_21 | br_093_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV |  |  | 0
GSO_94 | br_094_21 | br_094_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV |  |  | 0
GSO_95 | br_095_21 | br_095_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV |  |  | 0
GSO_96 | br_096_21 | br_096_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE5 | S_nSSEE5_12.47 | 4545.5 |  | MV |  |  | 0
GSO_97 | br_098_21 | br_098_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE6 | S_nSSEE6_12.47 | 7500.0 |  | MV |  |  | 0
GSO_98 | br_099_21 | br_099_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE6 | S_nSSEE6_12.47 | 7500.0 |  | MV |  |  | 0
GSO_99 | br_0100_21 | br_0100_21 | CircuitBreaker | switchable_element-Breaker | ABC | TRUE | FALSE | TRUE | FALSE |  | S_nSSEE6 | S_nSSEE6_12.47 | 7500.0 |  | MV |  |  | 0

## Upstream_Path_Summary
grid_id | BreakerElementID | UpstreamPathElementCount | UpstreamPathDepth | SourceElementID | SourceElementType | SourceElementCustomerType | SourceIsProducer | PathTerminatedAtNullUpstream | PathHitMaxDepth | UpstreamPathStatus
GSO_1 | br_01_21 | 1 | 0 | br_01_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_10 | br_015_21 | 1 | 0 | br_015_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_100 | br_097_21 | 1 | 0 | br_097_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_101 | br_0101_21 | 1 | 0 | br_0101_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_102 | br_0102_21 | 1 | 0 | br_0102_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_103 | br_0103_21 | 1 | 0 | br_0103_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_104 | br_0104_21 | 1 | 0 | br_0104_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_105 | br_0105_21 | 1 | 0 | br_0105_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_106 | br_0106_21 | 1 | 0 | br_0106_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_107 | br_0107_21 | 1 | 0 | br_0107_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_108 | br_0108_21 | 1 | 0 | br_0108_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_109 | br_0109_21 | 1 | 0 | br_0109_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_11 | br_016_21 | 1 | 0 | br_016_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_110 | br_0110_21 | 1 | 0 | br_0110_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_111 | br_0111_21 | 1 | 0 | br_0111_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_112 | br_0112_21 | 1 | 0 | br_0112_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_113 | br_0113_21 | 1 | 0 | br_0113_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_114 | br_0114_21 | 1 | 0 | br_0114_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_115 | br_0115_21 | 1 | 0 | br_0115_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_116 | br_0116_21 | 1 | 0 | br_0116_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_117 | br_0117_21 | 1 | 0 | br_0117_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_118 | br_0118_21 | 1 | 0 | br_0118_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_119 | br_0119_21 | 1 | 0 | br_0119_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_12 | br_017_21 | 1 | 0 | br_017_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_121 | br_01_22 | 1 | 0 | br_01_22 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_122 | br_02_22 | 1 | 0 | br_02_22 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_123 | br_03_22 | 1 | 0 | br_03_22 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_124 | br_04_22 | 1 | 0 | br_04_22 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_125 | br_05_22 | 1 | 0 | br_05_22 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_126 | br_06_22 | 1 | 0 | br_06_22 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_127 | br_07_22 | 1 | 0 | br_07_22 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_128 | br_08_22 | 1 | 0 | br_08_22 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_129 | br_09_22 | 1 | 0 | br_09_22 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_13 | br_018_21 | 1 | 0 | br_018_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_130 | br_010_22 | 1 | 0 | br_010_22 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_131 | br_011_22 | 1 | 0 | br_011_22 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_132 | br_012_22 | 1 | 0 | br_012_22 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_133 | br_013_22 | 1 | 0 | br_013_22 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_134 | br_014_22 | 1 | 0 | br_014_22 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_135 | br_015_22 | 1 | 0 | br_015_22 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_136 | br_016_22 | 1 | 0 | br_016_22 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_137 | br_017_22 | 1 | 0 | br_017_22 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_138 | br_018_22 | 1 | 0 | br_018_22 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_139 | br_019_22 | 1 | 0 | br_019_22 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_14 | br_019_21 | 1 | 0 | br_019_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_140 | br_020_22 | 1 | 0 | br_020_22 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_141 | br_021_22 | 1 | 0 | br_021_22 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_142 | br_022_22 | 1 | 0 | br_022_22 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_143 | br_023_22 | 1 | 0 | br_023_22 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_144 | br_024_22 | 1 | 0 | br_024_22 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_145 | br_025_22 | 1 | 0 | br_025_22 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_146 | br_026_22 | 1 | 0 | br_026_22 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_147 | br_027_22 | 1 | 0 | br_027_22 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_148 | br_028_22 | 1 | 0 | br_028_22 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_149 | br_029_22 | 1 | 0 | br_029_22 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_15 | br_020_21 | 1 | 0 | br_020_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_150 | br_030_22 | 1 | 0 | br_030_22 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_151 | br_031_22 | 1 | 0 | br_031_22 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_152 | br_032_22 | 1 | 0 | br_032_22 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_153 | br_033_22 | 1 | 0 | br_033_22 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_154 | br_034_22 | 1 | 0 | br_034_22 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_155 | br_01_23 | 1 | 0 | br_01_23 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_156 | br_02_23 | 1 | 0 | br_02_23 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_157 | br_03_23 | 1 | 0 | br_03_23 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_158 | br_04_23 | 1 | 0 | br_04_23 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_159 | br_05_23 | 1 | 0 | br_05_23 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_16 | br_021_21 | 1 | 0 | br_021_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_160 | br_06_23 | 1 | 0 | br_06_23 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_161 | br_07_23 | 1 | 0 | br_07_23 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_162 | br_08_23 | 1 | 0 | br_08_23 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_163 | br_09_23 | 1 | 0 | br_09_23 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_17 | br_024_21 | 1 | 0 | br_024_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_18 | br_025_21 | 1 | 0 | br_025_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_19 | br_026_21 | 1 | 0 | br_026_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_2 | br_02_21 | 1 | 0 | br_02_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_20 | br_027_21 | 1 | 0 | br_027_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_21 | br_028_21 | 1 | 0 | br_028_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_22 | br_029_21 | 1 | 0 | br_029_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_23 | br_030_21 | 1 | 0 | br_030_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_24 | br_031_21 | 1 | 0 | br_031_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_25 | br_032_21 | 1 | 0 | br_032_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_26 | br_033_21 | 1 | 0 | br_033_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_27 | br_034_21 | 1 | 0 | br_034_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_28 | br_035_21 | 1 | 0 | br_035_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_29 | br_036_21 | 1 | 0 | br_036_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_3 | br_03_21 | 1 | 0 | br_03_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_30 | br_037_21 | 1 | 0 | br_037_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_31 | br_038_21 | 1 | 0 | br_038_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_32 | br_039_21 | 1 | 0 | br_039_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_33 | br_040_21 | 1 | 0 | br_040_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_34 | br_041_21 | 1 | 0 | br_041_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_35 | br_042_21 | 1 | 0 | br_042_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_36 | br_043_21 | 1 | 0 | br_043_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_37 | br_044_21 | 1 | 0 | br_044_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_38 | br_045_21 | 1 | 0 | br_045_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_39 | br_046_21 | 1 | 0 | br_046_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_4 | br_04_21 | 1 | 0 | br_04_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_40 | br_047_21 | 1 | 0 | br_047_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_41 | br_048_21 | 1 | 0 | br_048_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_42 | br_049_21 | 1 | 0 | br_049_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_43 | br_050_21 | 1 | 0 | br_050_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_44 | br_051_21 | 1 | 0 | br_051_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_45 | br_052_21 | 1 | 0 | br_052_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_46 | br_053_21 | 1 | 0 | br_053_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_47 | br_054_21 | 1 | 0 | br_054_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_48 | br_055_21 | 1 | 0 | br_055_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_49 | br_056_21 | 1 | 0 | br_056_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_5 | br_05_21 | 1 | 0 | br_05_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_50 | br_057_21 | 1 | 0 | br_057_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_51 | br_058_21 | 1 | 0 | br_058_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_52 | br_059_21 | 1 | 0 | br_059_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_53 | br_060_21 | 1 | 0 | br_060_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_54 | br_061_21 | 1 | 0 | br_061_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_55 | br_062_21 | 1 | 0 | br_062_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_56 | br_063_21 | 1 | 0 | br_063_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_57 | br_08_21 | 1 | 0 | br_08_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_58 | br_09_21 | 1 | 0 | br_09_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_59 | br_010_21 | 1 | 0 | br_010_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_6 | br_06_21 | 1 | 0 | br_06_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_60 | br_011_21 | 1 | 0 | br_011_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_61 | br_012_21 | 1 | 0 | br_012_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_62 | br_013_21 | 1 | 0 | br_013_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_63 | br_014_21 | 1 | 0 | br_014_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_64 | br_064_21 | 1 | 0 | br_064_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_65 | br_065_21 | 1 | 0 | br_065_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_66 | br_066_21 | 1 | 0 | br_066_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_67 | br_067_21 | 1 | 0 | br_067_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_68 | br_068_21 | 1 | 0 | br_068_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_69 | br_069_21 | 1 | 0 | br_069_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_7 | br_07_21 | 1 | 0 | br_07_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_70 | br_070_21 | 1 | 0 | br_070_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_71 | br_071_21 | 1 | 0 | br_071_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_72 | br_072_21 | 1 | 0 | br_072_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_73 | br_073_21 | 1 | 0 | br_073_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_74 | br_074_21 | 1 | 0 | br_074_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_75 | br_075_21 | 1 | 0 | br_075_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_76 | br_076_21 | 1 | 0 | br_076_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_77 | br_077_21 | 1 | 0 | br_077_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_78 | br_078_21 | 1 | 0 | br_078_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_79 | br_079_21 | 1 | 0 | br_079_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_8 | br_022_21 | 1 | 0 | br_022_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_80 | br_080_21 | 1 | 0 | br_080_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_81 | br_081_21 | 1 | 0 | br_081_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_82 | br_082_21 | 1 | 0 | br_082_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_83 | br_083_21 | 1 | 0 | br_083_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_84 | br_084_21 | 1 | 0 | br_084_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_85 | br_085_21 | 1 | 0 | br_085_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_86 | br_086_21 | 1 | 0 | br_086_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_87 | br_087_21 | 1 | 0 | br_087_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_88 | br_088_21 | 1 | 0 | br_088_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_89 | br_089_21 | 1 | 0 | br_089_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_9 | br_023_21 | 1 | 0 | br_023_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_90 | br_090_21 | 1 | 0 | br_090_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_91 | br_091_21 | 1 | 0 | br_091_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_92 | br_092_21 | 1 | 0 | br_092_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_93 | br_093_21 | 1 | 0 | br_093_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_94 | br_094_21 | 1 | 0 | br_094_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_95 | br_095_21 | 1 | 0 | br_095_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_96 | br_096_21 | 1 | 0 | br_096_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_97 | br_098_21 | 1 | 0 | br_098_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_98 | br_099_21 | 1 | 0 | br_099_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK
GSO_99 | br_0100_21 | 1 | 0 | br_0100_21 | CircuitBreaker | switchable_element-Breaker | TRUE | TRUE | FALSE | OK

## Methodology
Item | Explanation
Purpose | Validate Greensboro feeder-breaker capacity before detailed topology, bottleneck, hosting-capacity, and optimization modeling.
Primary measurement point | One feeder breaker per GSO grid is selected using breaker-level kWh sources, phase coverage, producer flag, and rating metadata.
Stored capacity metadata | Breaker rating_kva is treated as the stored apparent-power rating candidate.
Independent rating check | Breaker kVA is independently calculated from rating_a and voltage_level using multiple plausible voltage interpretations; the interpretation that best agrees with stored rating_kva is retained.
High confidence | Stored breaker kVA and amp/voltage calculation differ by no more than 10.0%.
Medium confidence | Difference is greater than 10.0% but no more than 20.0%.
Low confidence | Difference exceeds 20.0%; formal audited headroom is withheld.
Real-power conversion | Audited breaker MVA is converted to preliminary MW using assumed power factor 0.95.
SCADA period | Breaker load is summarized from 2024-01-01 00:00:00+00 through 2025-01-01 00:00:00+00.
SCADA conversion | Interval kWh is divided by observed interval duration and 1000 to estimate MW. This assumes kWh values represent interval energy rather than cumulative register values.
Validated headroom | Audited breaker MW minus observed full-year peak MW. Only High/Medium confidence breaker ratings are formally ranked.
Conservative headroom | Uses the smaller of stored breaker kVA and independently calculated breaker kVA; retained for audit but not used as the formal rank when validation fails.
Upstream topology | Recursively follows upstream_grid_element_id from the selected feeder breaker to the highest reachable upstream element.
Important limitation | Breaker headroom is still a feeder-level screen, not final hosting capacity. Path-specific line, transformer, voltage, and power-flow constraints must be evaluated next.
Next phase | Use Topology_Shortlist feeders for detailed electrical-path tracing, downstream load allocation, bottleneck identification, and incremental data-center load testing.