## Candidate_Summary
ThermalRank | CandidateKey | GridID | SubstationID | CandidateLineID | CandidateNode | OriginalScreeningHostingMW | CandidateConfidence | ModeledHours | FirmHostingMW | HostingAvailable99PctHoursMW | HostingAvailable95PctHoursMW | MedianHostingMW | MeanHostingMW | MaximumHostingMW | MinimumRawResidualMW | HoursWithNoAdditionalHosting | PctHoursWithNoAdditionalHosting | MostFrequentLimitingElementID | MostFrequentLimitingElementPct | FirmLimitTimestampUTC | FirmLimitElementID | PathHops | PathLineCount | PathTransformerCount | MeterTopologyMappingPct | SubstationCapacityConstraintApplied | VoltageConstraintApplied | ModelStatus
1 | GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | S_nCCTT45 | 13.5096 | High | 8779 | 13.5111 | 13.5163 | 13.5185 | 13.5228 | 13.5226 | 13.5289 | 13.5111 | 0 | 0 | line_5852_22 | 100 | 2024-01-20 07:00 | line_5852_22 | 2 | 1 | 0 | 100 | FALSE | FALSE | Ready
2 | GSO_124¦line_6716_22 | GSO_124 | hvmv_1_22 | line_6716_22 | S_nCCTT913 | 13.4085 | High | 8779 | 13.4191 | 13.4384 | 13.4472 | 13.4654 | 13.4646 | 13.486 | 13.4191 | 0 | 0 | line_6716_22 | 100 | 2024-07-15 04:00 | line_6716_22 | 2 | 1 | 0 | 100 | FALSE | FALSE | Ready
3 | GSO_123¦line_6019_22 | GSO_123 | hvmv_1_22 | line_6019_22 | S_nCCTT521 | 13.1777 | High | 8779 | 13.1966 | 13.233 | 13.2544 | 13.2976 | 13.2942 | 13.3345 | 13.1966 | 0 | 0 | line_6019_22 | 100 | 2024-01-20 14:00 | line_6019_22 | 2 | 1 | 0 | 100 | FALSE | FALSE | Ready
4 | GSO_121¦line_3530_22 | GSO_121 | hvmv_1_22 | line_3530_22 | S_nCCTT0 | 13.1607 | High | 8779 | 13.1764 | 13.2107 | 13.2381 | 13.3039 | 13.2977 | 13.3494 | 13.1764 | 0 | 0 | line_3530_22 | 100 | 2024-01-20 15:00 | line_3530_22 | 2 | 1 | 0 | 100 | FALSE | FALSE | Ready
5 | GSO_144¦line_5978_22 | GSO_144 | hvmv_5_22 | line_5978_22 | S_nCCTT504 | 11.2671 | High | 8779 | 11.2719 | 11.2951 | 11.31 | 11.3463 | 11.3426 | 11.3638 | 11.2719 | 0 | 0 | br_024_22 | 100 | 2024-01-20 06:00 | br_024_22 | 2 | 1 | 0 | 100 | FALSE | FALSE | Ready
6 | GSO_141¦line_4565_22 | GSO_141 | hvmv_5_22 | line_4565_22 | S_nCCTT1344 | 11.02 | High | 8779 | 11.0413 | 11.0828 | 11.1097 | 11.1706 | 11.1652 | 11.2206 | 11.0413 | 0 | 0 | br_021_22 | 100 | 2024-01-21 01:00 | br_021_22 | 2 | 1 | 0 | 100 | FALSE | FALSE | Ready
7 | GSO_145¦line_6170_22 | GSO_145 | hvmv_5_22 | line_6170_22 | S_nCCTT59 | 10.6656 | Medium | 8779 | 10.6976 | 10.7799 | 10.8409 | 10.9717 | 10.9595 | 11.0855 | 10.6976 | 0 | 0 | br_025_22 | 100 | 2024-01-21 04:00 | br_025_22 | 2 | 1 | 0 | 90.9677 | FALSE | FALSE | Ready
8 | GSO_142¦line_5429_22 | GSO_142 | hvmv_5_22 | line_5429_22 | S_nCCTT245 | 10.6074 | High | 8779 | 10.6509 | 10.724 | 10.777 | 10.8838 | 10.8749 | 10.9694 | 10.6509 | 0 | 0 | br_022_22 | 100 | 2024-01-21 02:00 | br_022_22 | 2 | 1 | 0 | 100 | FALSE | FALSE | Ready
9 | GSO_18¦line_108323_21 | GSO_18 | hvmv_4_21 | line_108323_21 | S_nCCTT10746 | 10.3769 | High | 8779 | 10.4099 | 10.7307 | 10.9528 | 11.531 | 11.4776 | 11.8336 | 10.4099 | 0 | 0 | br_025_21 | 100 | 2024-01-21 | br_025_21 | 2 | 1 | 0 | 100 | FALSE | FALSE | Ready
10 | GSO_127¦line_6871_22 | GSO_127 | hvmv_2_22 | line_6871_22 | UCMV43 | 9.4748 | High | 8779 | 9.479 | 9.4819 | 9.4836 | 9.4875 | 9.4874 | 9.4938 | 9.479 | 0 | 0 | br_07_22 | 100 | 2024-01-22 04:00 | br_07_22 | 2 | 1 | 0 | 100 | FALSE | FALSE | Ready

## Test_DC_Levels
CandidateKey | GridID | SubstationID | CandidateLineID | TestDCLoadMW | FeasibleHours | ConstrainedHours | FeasibleHoursPct | ConstraintHoursPct
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 5 | 8779 | 0 | 100 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 7.5 | 8779 | 0 | 100 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 10 | 8779 | 0 | 100 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 12.5 | 8779 | 0 | 100 | 0
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | 15 | 0 | 8779 | 0 | 100
GSO_124¦line_6716_22 | GSO_124 | hvmv_1_22 | line_6716_22 | 5 | 8779 | 0 | 100 | 0
GSO_124¦line_6716_22 | GSO_124 | hvmv_1_22 | line_6716_22 | 7.5 | 8779 | 0 | 100 | 0
GSO_124¦line_6716_22 | GSO_124 | hvmv_1_22 | line_6716_22 | 10 | 8779 | 0 | 100 | 0
GSO_124¦line_6716_22 | GSO_124 | hvmv_1_22 | line_6716_22 | 12.5 | 8779 | 0 | 100 | 0
GSO_124¦line_6716_22 | GSO_124 | hvmv_1_22 | line_6716_22 | 15 | 0 | 8779 | 0 | 100
GSO_123¦line_6019_22 | GSO_123 | hvmv_1_22 | line_6019_22 | 5 | 8779 | 0 | 100 | 0
GSO_123¦line_6019_22 | GSO_123 | hvmv_1_22 | line_6019_22 | 7.5 | 8779 | 0 | 100 | 0
GSO_123¦line_6019_22 | GSO_123 | hvmv_1_22 | line_6019_22 | 10 | 8779 | 0 | 100 | 0
GSO_123¦line_6019_22 | GSO_123 | hvmv_1_22 | line_6019_22 | 12.5 | 8779 | 0 | 100 | 0
GSO_123¦line_6019_22 | GSO_123 | hvmv_1_22 | line_6019_22 | 15 | 0 | 8779 | 0 | 100
GSO_121¦line_3530_22 | GSO_121 | hvmv_1_22 | line_3530_22 | 5 | 8779 | 0 | 100 | 0
GSO_121¦line_3530_22 | GSO_121 | hvmv_1_22 | line_3530_22 | 7.5 | 8779 | 0 | 100 | 0
GSO_121¦line_3530_22 | GSO_121 | hvmv_1_22 | line_3530_22 | 10 | 8779 | 0 | 100 | 0
GSO_121¦line_3530_22 | GSO_121 | hvmv_1_22 | line_3530_22 | 12.5 | 8779 | 0 | 100 | 0
GSO_121¦line_3530_22 | GSO_121 | hvmv_1_22 | line_3530_22 | 15 | 0 | 8779 | 0 | 100
GSO_144¦line_5978_22 | GSO_144 | hvmv_5_22 | line_5978_22 | 5 | 8779 | 0 | 100 | 0
GSO_144¦line_5978_22 | GSO_144 | hvmv_5_22 | line_5978_22 | 7.5 | 8779 | 0 | 100 | 0
GSO_144¦line_5978_22 | GSO_144 | hvmv_5_22 | line_5978_22 | 10 | 8779 | 0 | 100 | 0
GSO_144¦line_5978_22 | GSO_144 | hvmv_5_22 | line_5978_22 | 12.5 | 0 | 8779 | 0 | 100
GSO_144¦line_5978_22 | GSO_144 | hvmv_5_22 | line_5978_22 | 15 | 0 | 8779 | 0 | 100
GSO_141¦line_4565_22 | GSO_141 | hvmv_5_22 | line_4565_22 | 5 | 8779 | 0 | 100 | 0
GSO_141¦line_4565_22 | GSO_141 | hvmv_5_22 | line_4565_22 | 7.5 | 8779 | 0 | 100 | 0
GSO_141¦line_4565_22 | GSO_141 | hvmv_5_22 | line_4565_22 | 10 | 8779 | 0 | 100 | 0
GSO_141¦line_4565_22 | GSO_141 | hvmv_5_22 | line_4565_22 | 12.5 | 0 | 8779 | 0 | 100
GSO_141¦line_4565_22 | GSO_141 | hvmv_5_22 | line_4565_22 | 15 | 0 | 8779 | 0 | 100
GSO_145¦line_6170_22 | GSO_145 | hvmv_5_22 | line_6170_22 | 5 | 8779 | 0 | 100 | 0
GSO_145¦line_6170_22 | GSO_145 | hvmv_5_22 | line_6170_22 | 7.5 | 8779 | 0 | 100 | 0
GSO_145¦line_6170_22 | GSO_145 | hvmv_5_22 | line_6170_22 | 10 | 8779 | 0 | 100 | 0
GSO_145¦line_6170_22 | GSO_145 | hvmv_5_22 | line_6170_22 | 12.5 | 0 | 8779 | 0 | 100
GSO_145¦line_6170_22 | GSO_145 | hvmv_5_22 | line_6170_22 | 15 | 0 | 8779 | 0 | 100
GSO_142¦line_5429_22 | GSO_142 | hvmv_5_22 | line_5429_22 | 5 | 8779 | 0 | 100 | 0
GSO_142¦line_5429_22 | GSO_142 | hvmv_5_22 | line_5429_22 | 7.5 | 8779 | 0 | 100 | 0
GSO_142¦line_5429_22 | GSO_142 | hvmv_5_22 | line_5429_22 | 10 | 8779 | 0 | 100 | 0
GSO_142¦line_5429_22 | GSO_142 | hvmv_5_22 | line_5429_22 | 12.5 | 0 | 8779 | 0 | 100
GSO_142¦line_5429_22 | GSO_142 | hvmv_5_22 | line_5429_22 | 15 | 0 | 8779 | 0 | 100
GSO_18¦line_108323_21 | GSO_18 | hvmv_4_21 | line_108323_21 | 5 | 8779 | 0 | 100 | 0
GSO_18¦line_108323_21 | GSO_18 | hvmv_4_21 | line_108323_21 | 7.5 | 8779 | 0 | 100 | 0
GSO_18¦line_108323_21 | GSO_18 | hvmv_4_21 | line_108323_21 | 10 | 8779 | 0 | 100 | 0
GSO_18¦line_108323_21 | GSO_18 | hvmv_4_21 | line_108323_21 | 12.5 | 0 | 8779 | 0 | 100
GSO_18¦line_108323_21 | GSO_18 | hvmv_4_21 | line_108323_21 | 15 | 0 | 8779 | 0 | 100
GSO_127¦line_6871_22 | GSO_127 | hvmv_2_22 | line_6871_22 | 5 | 8779 | 0 | 100 | 0
GSO_127¦line_6871_22 | GSO_127 | hvmv_2_22 | line_6871_22 | 7.5 | 8779 | 0 | 100 | 0
GSO_127¦line_6871_22 | GSO_127 | hvmv_2_22 | line_6871_22 | 10 | 0 | 8779 | 0 | 100
GSO_127¦line_6871_22 | GSO_127 | hvmv_2_22 | line_6871_22 | 12.5 | 0 | 8779 | 0 | 100
GSO_127¦line_6871_22 | GSO_127 | hvmv_2_22 | line_6871_22 | 15 | 0 | 8779 | 0 | 100

## Path_Constraints
CandidateKey | GridID | SubstationID | CandidateLineID | ElementID | ElementType | ElementClass | CapacityMW | PeakExistingLoadMW | P95ExistingLoadMW | MinimumResidualMW | RatingKVA | RatingA | VoltageKV | PhaseCount | CapacityMethod
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | br_02_22 | CircuitBreaker | Breaker | 14.25 | 0.031234 | 0.023827 | 14.2188 | 15000
GSO_122¦line_5852_22 | GSO_122 | hvmv_1_22 | line_5852_22 | line_5852_22 | ACLineSegment | Line | 13.5424 | 0.031234 | 0.023827 | 13.5111 |  | 660 | 12.47 | 3 | 3Phase_sqrt3_VLL_I
GSO_124¦line_6716_22 | GSO_124 | hvmv_1_22 | line_6716_22 | br_04_22 | CircuitBreaker | Breaker | 14.25 | 0.1233 | 0.095119 | 14.1267 | 15000
GSO_124¦line_6716_22 | GSO_124 | hvmv_1_22 | line_6716_22 | line_6716_22 | ACLineSegment | Line | 13.5424 | 0.1233 | 0.095119 | 13.4191 |  | 660 | 12.47 | 3 | 3Phase_sqrt3_VLL_I
GSO_123¦line_6019_22 | GSO_123 | hvmv_1_22 | line_6019_22 | br_03_22 | CircuitBreaker | Breaker | 14.25 | 0.34579 | 0.28797 | 13.9042 | 15000
GSO_123¦line_6019_22 | GSO_123 | hvmv_1_22 | line_6019_22 | line_6019_22 | ACLineSegment | Line | 13.5424 | 0.34579 | 0.28797 | 13.1966 |  | 660 | 12.47 | 3 | 3Phase_sqrt3_VLL_I
GSO_121¦line_3530_22 | GSO_121 | hvmv_1_22 | line_3530_22 | br_01_22 | CircuitBreaker | Breaker | 14.25 | 0.36598 | 0.30425 | 13.884 | 15000
GSO_121¦line_3530_22 | GSO_121 | hvmv_1_22 | line_3530_22 | line_3530_22 | ACLineSegment | Line | 13.5424 | 0.36598 | 0.30425 | 13.1764 |  | 660 | 12.47 | 3 | 3Phase_sqrt3_VLL_I
GSO_144¦line_5978_22 | GSO_144 | hvmv_5_22 | line_5978_22 | br_024_22 | CircuitBreaker | Breaker | 11.4 | 0.12812 | 0.090001 | 11.2719 | 12000
GSO_144¦line_5978_22 | GSO_144 | hvmv_5_22 | line_5978_22 | line_5978_22 | ACLineSegment | Line | 12.3112 | 0.12812 | 0.090001 | 12.1831 |  | 600 | 12.47 | 3 | 3Phase_sqrt3_VLL_I
GSO_141¦line_4565_22 | GSO_141 | hvmv_5_22 | line_4565_22 | br_021_22 | CircuitBreaker | Breaker | 11.4 | 0.35867 | 0.2903 | 11.0413 | 12000
GSO_141¦line_4565_22 | GSO_141 | hvmv_5_22 | line_4565_22 | line_4565_22 | ACLineSegment | Line | 13.5424 | 0.35867 | 0.2903 | 13.1837 |  | 660 | 12.47 | 3 | 3Phase_sqrt3_VLL_I
GSO_145¦line_6170_22 | GSO_145 | hvmv_5_22 | line_6170_22 | br_025_22 | CircuitBreaker | Breaker | 11.4 | 0.70243 | 0.5591 | 10.6976 | 12000
GSO_145¦line_6170_22 | GSO_145 | hvmv_5_22 | line_6170_22 | line_6170_22 | ACLineSegment | Line | 13.5424 | 0.66153 | 0.52834 | 12.8808 |  | 660 | 12.47 | 3 | 3Phase_sqrt3_VLL_I
GSO_142¦line_5429_22 | GSO_142 | hvmv_5_22 | line_5429_22 | br_022_22 | CircuitBreaker | Breaker | 11.4 | 0.74905 | 0.62297 | 10.6509 | 12000
GSO_142¦line_5429_22 | GSO_142 | hvmv_5_22 | line_5429_22 | line_5429_22 | ACLineSegment | Line | 13.5424 | 0.74905 | 0.62297 | 12.7933 |  | 660 | 12.47 | 3 | 3Phase_sqrt3_VLL_I
GSO_18¦line_108323_21 | GSO_18 | hvmv_4_21 | line_108323_21 | br_025_21 | CircuitBreaker | Breaker | 12.6666 | 2.2568 | 1.7138 | 10.4099 | 13333.3
GSO_18¦line_108323_21 | GSO_18 | hvmv_4_21 | line_108323_21 | line_108323_21 | ACLineSegment | Line | 13.5424 | 2.2568 | 1.7138 | 11.2856 |  | 660 | 12.47 | 3 | 3Phase_sqrt3_VLL_I
GSO_127¦line_6871_22 | GSO_127 | hvmv_2_22 | line_6871_22 | br_07_22 | CircuitBreaker | Breaker | 9.5 | 0.02104 | 0.016376 | 9.479 | 10000
GSO_127¦line_6871_22 | GSO_127 | hvmv_2_22 | line_6871_22 | line_6871_22 | ACLineSegment | Line | 13.5424 | 0.02104 | 0.016376 | 13.5213 |  | 660 | 12.47 | 3 | 3Phase_sqrt3_VLL_I

## Feeder_Diagnostics
GridID | BreakerID | ModeledHours | BreakerPeakMW | MeterCount | MeterTopologyMappingPct | GraphNodes | GraphEdges | DuplicateParallelNodePairs | SkippedOpenSwitches | SkippedMissingTerminalElements | RootAggregationMaxErrorMW | BaselineThermalOverloadCount | MeterSourceCount | MetersWithoutKWhSource | MetersWithMultipleKWhSources | TotalMeterHourCells | MissingMeterHourCellsBeforeFill | FilledMeterHourCells | MissingMeterHourCellsAfterFill | MeterHourFillPct | RawMeterEnergyMWh | BreakerEnergyMWh | RawMeterToBreakerEnergyRatio | CalibrationFactorMedian | CalibrationFactorP05 | CalibrationFactorP95 | CalibrationFallbackHours | PostCalibrationMaxAbsoluteErrorMW
GSO_122 | br_02_22 | 8779 | 0.031234 | 3 | 100 | 11 | 10 | 0 | 0 | 0 | 6.9389e-18 | 0 | 3 | 0 | 0 | 26337 | 0 | 0 | 0 | 0 | 166.5245 | 173.1856 | 0.96154 | 1.04 | 1.0383 | 1.0417 | 0 | 6.9389e-18
GSO_124 | br_04_22 | 8779 | 0.1233 | 16 | 100 | 58 | 57 | 0 | 0 | 0 | 4.1633e-17 | 0 | 16 | 0 | 0 | 140464 | 0 | 0 | 0 | 0 | 656.1289 | 682.3711 | 0.96154 | 1.04 | 1.0383 | 1.0417 | 0 | 5.5511e-17
GSO_123 | br_03_22 | 8779 | 0.34579 | 47 | 100 | 183 | 182 | 0 | 0 | 0 | 2.7756e-16 | 1 | 47 | 0 | 0 | 412613 | 0 | 0 | 0 | 0 | 2095.094 | 2178.9009 | 0.96154 | 1.04 | 1.0383 | 1.0417 | 0 | 2.7756e-16
GSO_121 | br_01_22 | 8779 | 0.36598 | 72 | 100 | 280 | 280 | 0 | 0 | 0 | 2.7756e-16 | 2 | 74 | 0 | 2 | 632088 | 0 | 0 | 0 | 0 | 2086.7152 | 2147.9335 | 0.9715 | 1.0391 | 0.98957 | 1.0415 | 0 | 2.7756e-16
GSO_144 | br_024_22 | 8779 | 0.12812 | 32 | 100 | 80 | 79 | 0 | 0 | 0 | 6.9389e-17 | 2 | 32 | 0 | 0 | 280928 | 0 | 0 | 0 | 0 | 484.6365 | 504.0176 | 0.96155 | 1.04 | 1.0374 | 1.0426 | 0 | 6.9389e-17
GSO_141 | br_021_22 | 8779 | 0.35867 | 68 | 100 | 240 | 239 | 0 | 0 | 0 | 2.498e-16 | 3 | 68 | 0 | 0 | 596972 | 0 | 0 | 0 | 0 | 1982.2248 | 2061.47 | 0.96156 | 1.04 | 1.0383 | 1.0417 | 0 | 3.0531e-16
GSO_145 | br_025_22 | 8779 | 0.70243 | 155 | 90.9677 | 497 | 495 | 0 | 0 | 0 | 6.6613e-16 | 4 | 157 | 0 | 2 | 1360745 | 0 | 0 | 0 | 0 | 4055.0377 | 3867.187 | 1.0486 | 0.98592 | 0.83086 | 0.99948 | 0 | 9.992e-16
GSO_142 | br_022_22 | 8779 | 0.74905 | 140 | 100 | 563 | 564 | 0 | 0 | 0 | 8.8818e-16 | 6 | 141 | 0 | 1 | 1229060 | 0 | 0 | 0 | 0 | 4468.2634 | 4610.0614 | 0.96924 | 1.0391 | 1.0033 | 1.0415 | 0 | 9.992e-16
GSO_18 | br_025_21 | 8779 | 2.2568 | 584 | 100 | 1416 | 1417 | 0 | 0 | 0 | 4.2188e-15 | 54 | 589 | 0 | 5 | 5126936 | 0 | 0 | 0 | 0 | 10211.2903 | 10438.9644 | 0.97819 | 1.0391 | 0.95905 | 1.0415 | 0 | 1.2434e-14
GSO_127 | br_07_22 | 8779 | 0.02104 | 1 | 100 | 3 | 2 | 0 | 0 | 0 | 3.4694e-18 | 0 | 1 | 0 | 0 | 8779 | 0 | 0 | 0 | 0 | 106.3849 | 110.6401 | 0.96154 | 1.04 | 1.0383 | 1.0417 | 0 | 3.4694e-18

## Element_Load_Summary
GridID | GridElementID | ElementType | ElementClass | CapacityMW | PeakExistingLoadMW | P95ExistingLoadMW | PeakUtilizationPct | BaselineOverload | PeakTimestampUTC | RatingA | VoltageKV | RatingKVA | PhaseCount | CapacityMethod
GSO_122 | line_2430_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_122 | line_5871_22 | ACLineSegment | Line | 0.51338 | 0.0052919 | 0.0037346 | 1.0308 | FALSE | 2024-01-20 18:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_122 | tr_993_22 | Transformer | Transformer | 0.285 | 0.0052919 | 0.0037346 | 1.8568 | FALSE | 2024-01-20 18:00 |  |  | 300 | 3 | Transformer_kVA_x_PF
GSO_122 | line_2978_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_122 | line_5379_22 | ACLineSegment | Line | 0.034884 | 0.0047892 | 0.0033583 | 13.729 | FALSE | 2024-01-20 18:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_122 | tr_741_22 | Transformer | Transformer | 0.02375 | 0.0047892 | 0.0033583 | 20.1649 | FALSE | 2024-01-20 18:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_122 | line_5376_22 | ACLineSegment | Line | 13.5424 | 0.027785 | 0.020687 | 0.20517 | FALSE | 2024-01-20 07:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_122 | line_5852_22 | ACLineSegment | Line | 13.5424 | 0.031234 | 0.023827 | 0.23064 | FALSE | 2024-01-20 07:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_122 | line_5377_22 | ACLineSegment | Line | 13.5424 | 0.025276 | 0.017884 | 0.18664 | FALSE | 2024-01-20 07:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_124 | line_3767_22 | ACLineSegment | Line | 13.5424 | 0.04539 | 0.035545 | 0.33517 | FALSE | 2024-07-16 01:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_124 | line_3830_22 | ACLineSegment | Line | 13.5424 | 0.052382 | 0.040876 | 0.3868 | FALSE | 2024-01-18 02:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_124 | tr_1387_22 | Transformer | Transformer | 0.095 | 0.0052792 | 0.0041145 | 5.557 | FALSE | 2024-01-17 10:00 |  |  | 100 | 3 | Transformer_kVA_x_PF
GSO_124 | tr_183_22 | Transformer | Transformer | 0.02375 | 0.0051716 | 0.002851 | 21.775 | FALSE | 2024-01-20 07:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_124 | line_1276_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_124 | line_3768_22 | ACLineSegment | Line | 0.034884 | 0.0080641 | 0.0045087 | 23.1171 | FALSE | 2024-07-15 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_124 | tr_87_22 | Transformer | Transformer | 0.02375 | 0.0080641 | 0.0045087 | 33.9539 | FALSE | 2024-07-15 10:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_124 | line_1278_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_124 | line_3774_22 | ACLineSegment | Line | 0.51338 | 0.0074772 | 0.0050741 | 1.4565 | FALSE | 2024-01-20 09:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_124 | tr_89_22 | Transformer | Transformer | 0.95 | 0.0074772 | 0.0050741 | 0.78708 | FALSE | 2024-01-20 09:00 |  |  | 1000 | 3 | Transformer_kVA_x_PF
GSO_124 | line_1299_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_124 | line_3832_22 | ACLineSegment | Line | 0.51338 | 0.0065566 | 0.0049091 | 1.2771 | FALSE | 2024-01-20 20:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_124 | tr_107_22 | Transformer | Transformer | 0.95 | 0.0065566 | 0.0049091 | 0.69016 | FALSE | 2024-01-20 20:00 |  |  | 1000 | 3 | Transformer_kVA_x_PF
GSO_124 | line_1332_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_124 | line_6708_22 | ACLineSegment | Line | 0.51338 | 0.0073141 | 0.0056523 | 1.4247 | FALSE | 2024-07-05 13:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_124 | tr_1498_22 | Transformer | Transformer | 0.95 | 0.0073141 | 0.0056523 | 0.7699 | FALSE | 2024-07-05 13:00 |  |  | 1000 | 3 | Transformer_kVA_x_PF
GSO_124 | line_1442_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_124 | line_4021_22 | ACLineSegment | Line | 0.034884 | 0.0051716 | 0.002851 | 14.8252 | FALSE | 2024-01-20 07:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_124 | line_1545_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_124 | line_4131_22 | ACLineSegment | Line | 0.51338 | 0.0082184 | 0.0060734 | 1.6008 | FALSE | 2024-01-20 13:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_124 | tr_231_22 | Transformer | Transformer | 0.475 | 0.0082184 | 0.0060734 | 1.7302 | FALSE | 2024-01-20 13:00 |  |  | 500 | 3 | Transformer_kVA_x_PF
GSO_124 | line_2873_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_124 | line_2874_22 | ACLineSegment | Line | 0.038174 | 0.022702 | 0.019028 | 59.4683 | FALSE | 2024-08-29 13:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_124 | line_2875_22 | ACLineSegment | Line | 0.025406 | 0.01874 | 0.016488 | 73.7615 | FALSE | 2024-07-14 06:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_124 | line_2876_22 | ACLineSegment | Line | 0.025406 | 0.0066157 | 0.0036605 | 26.0401 | FALSE | 2024-07-15 13:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_124 | tr_831_22 | Transformer | Transformer | 0.0475 | 0.022702 | 0.019028 | 47.793 | FALSE | 2024-08-29 13:00 |  |  | 50 | 1 | Transformer_kVA_x_PF
GSO_124 | line_3009_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_124 | line_5396_22 | ACLineSegment | Line | 0.51338 | 0.007864 | 0.0055975 | 1.5318 | FALSE | 2024-07-06 02:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_124 | tr_748_22 | Transformer | Transformer | 0.07125 | 0.007864 | 0.0055975 | 11.0371 | FALSE | 2024-07-06 02:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_124 | line_3246_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_124 | line_5689_22 | ACLineSegment | Line | 0.22905 | 0.0060797 | 0.0046649 | 2.6543 | FALSE | 2024-01-20 06:00 | 290 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_124 | tr_904_22 | Transformer | Transformer | 0.07125 | 0.0060797 | 0.0046649 | 8.5329 | FALSE | 2024-01-20 06:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_124 | line_3766_22 | ACLineSegment | Line | 13.5424 | 0.039436 | 0.032309 | 0.2912 | FALSE | 2024-01-18 02:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_124 | line_5515_22 | ACLineSegment | Line | 13.5424 | 0.033696 | 0.027254 | 0.24882 | FALSE | 2024-01-18 02:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_124 | tr_1156_22 | Transformer | Transformer | 0.02375 | 0.0084863 | 0.006581 | 35.732 | FALSE | 2024-07-15 16:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_124 | line_3772_22 | ACLineSegment | Line | 13.5424 | 0.0073141 | 0.0056523 | 0.054009 | FALSE | 2024-07-05 13:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_124 | line_3773_22 | ACLineSegment | Line | 13.5424 | 0.01284 | 0.0098445 | 0.094813 | FALSE | 2024-01-20 16:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_124 | line_4130_22 | ACLineSegment | Line | 13.5424 | 0.066723 | 0.047578 | 0.4927 | FALSE | 2024-01-21 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_124 | line_5663_22 | ACLineSegment | Line | 13.5424 | 0.026548 | 0.020907 | 0.19603 | FALSE | 2024-01-21 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_124 | line_3829_22 | ACLineSegment | Line | 13.5424 | 0.07142 | 0.051856 | 0.52738 | FALSE | 2024-01-21 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_124 | line_3831_22 | ACLineSegment | Line | 13.5424 | 0.11885 | 0.092229 | 0.87764 | FALSE | 2024-07-15 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_124 | line_6716_22 | ACLineSegment | Line | 13.5424 | 0.1233 | 0.095119 | 0.91051 | FALSE | 2024-07-15 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_124 | tr_1508_22 | Transformer | Transformer | 0.02375 | 0.0051393 | 0.003357 | 21.6393 | FALSE | 2024-01-20 05:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_124 | line_454_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_124 | line_6185_22 | ACLineSegment | Line | 0.034884 | 0.0084863 | 0.006581 | 24.3277 | FALSE | 2024-07-15 16:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_124 | line_476_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_124 | line_6130_22 | ACLineSegment | Line | 0.51338 | 0.0067131 | 0.0048815 | 1.3076 | FALSE | 2024-01-20 19:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_124 | tr_1129_22 | Transformer | Transformer | 0.475 | 0.0067131 | 0.0048815 | 1.4133 | FALSE | 2024-01-20 19:00 |  |  | 500 | 3 | Transformer_kVA_x_PF
GSO_124 | line_5514_22 | ACLineSegment | Line | 12.3112 | 0.0067131 | 0.0048815 | 0.054528 | FALSE | 2024-01-20 19:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_124 | line_5664_22 | ACLineSegment | Line | 13.5424 | 0.022833 | 0.017094 | 0.1686 | FALSE | 2024-01-21 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_124 | line_6560_22 | ACLineSegment | Line | 0.51338 | 0.0052792 | 0.0041145 | 1.0283 | FALSE | 2024-01-17 10:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_124 | line_809_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_124 | line_6717_22 | ACLineSegment | Line | 0.034884 | 0.0051393 | 0.003357 | 14.7329 | FALSE | 2024-01-20 05:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_123 | line_1133_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_123 | line_3593_22 | ACLineSegment | Line | 0.51338 | 0.0057147 | 0.0043717 | 1.1132 | FALSE | 2024-01-21 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | tr_25_22 | Transformer | Transformer | 0.095 | 0.0057147 | 0.0043717 | 6.0155 | FALSE | 2024-01-21 |  |  | 100 | 3 | Transformer_kVA_x_PF
GSO_123 | line_1134_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_123 | line_3607_22 | ACLineSegment | Line | 0.51338 | 0.0067118 | 0.005065 | 1.3074 | FALSE | 2024-01-21 10:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | tr_30_22 | Transformer | Transformer | 0.285 | 0.0067118 | 0.005065 | 2.355 | FALSE | 2024-01-21 10:00 |  |  | 300 | 3 | Transformer_kVA_x_PF
GSO_123 | line_1272_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_123 | line_3732_22 | ACLineSegment | Line | 0.51338 | 0.0065182 | 0.0050045 | 1.2697 | FALSE | 2024-01-20 08:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | tr_74_22 | Transformer | Transformer | 0.095 | 0.0065182 | 0.0050045 | 6.8613 | FALSE | 2024-01-20 08:00 |  |  | 100 | 3 | Transformer_kVA_x_PF
GSO_123 | line_1281_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_123 | line_3744_22 | ACLineSegment | Line | 0.51338 | 0.0072771 | 0.0055665 | 1.4175 | FALSE | 2024-01-21 03:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | tr_78_22 | Transformer | Transformer | 0.1425 | 0.0072771 | 0.0055665 | 5.1067 | FALSE | 2024-01-21 03:00 |  |  | 150 | 3 | Transformer_kVA_x_PF
GSO_123 | line_1288_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_123 | line_3746_22 | ACLineSegment | Line | 0.51338 | 0.0040493 | 0.0029802 | 0.78875 | FALSE | 2024-07-15 11:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | tr_79_22 | Transformer | Transformer | 0.285 | 0.0040493 | 0.0029802 | 1.4208 | FALSE | 2024-07-15 11:00 |  |  | 300 | 3 | Transformer_kVA_x_PF
GSO_123 | line_1333_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_123 | line_6711_22 | ACLineSegment | Line | 0.51338 | 0.0043781 | 0.0031864 | 0.85279 | FALSE | 2024-01-20 17:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | tr_1502_22 | Transformer | Transformer | 0.285 | 0.0043781 | 0.0031864 | 1.5362 | FALSE | 2024-01-20 17:00 |  |  | 300 | 3 | Transformer_kVA_x_PF
GSO_123 | line_1337_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_123 | line_6709_22 | ACLineSegment | Line | 0.51338 | 0.0059907 | 0.0044791 | 1.1669 | FALSE | 2024-01-20 08:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | tr_1499_22 | Transformer | Transformer | 0.07125 | 0.0059907 | 0.0044791 | 8.4079 | FALSE | 2024-01-20 08:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_123 | line_1357_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_123 | line_6729_22 | ACLineSegment | Line | 0.034884 | 0.0087761 | 0.0059415 | 25.1584 | FALSE | 2024-01-20 07:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_123 | tr_1520_22 | Transformer | Transformer | 0.0475 | 0.0087761 | 0.0059415 | 18.476 | FALSE | 2024-01-20 07:00 |  |  | 50 | 1 | Transformer_kVA_x_PF
GSO_123 | line_1376_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_123 | line_3879_22 | ACLineSegment | Line | 0.51338 | 0.0092375 | 0.0064115 | 1.7994 | FALSE | 2024-01-20 13:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | tr_123_22 | Transformer | Transformer | 0.285 | 0.0092375 | 0.0064115 | 3.2412 | FALSE | 2024-01-20 13:00 |  |  | 300 | 3 | Transformer_kVA_x_PF
GSO_123 | line_1418_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_123 | line_3955_22 | ACLineSegment | Line | 0.51338 | 0.006155 | 0.0042751 | 1.1989 | FALSE | 2024-01-21 01:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | tr_154_22 | Transformer | Transformer | 0.07125 | 0.006155 | 0.0042751 | 8.6386 | FALSE | 2024-01-21 01:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_123 | line_1439_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_123 | line_4023_22 | ACLineSegment | Line | 0.51338 | 0.027668 | 0.018066 | 5.3895 | FALSE | 2024-01-21 02:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | tr_184_22 | Transformer | Transformer | 0.95 | 0.027668 | 0.018066 | 2.9125 | FALSE | 2024-01-21 02:00 |  |  | 1000 | 3 | Transformer_kVA_x_PF
GSO_123 | line_1444_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_123 | line_4034_22 | ACLineSegment | Line | 0.51338 | 0.0087834 | 0.0056029 | 1.7109 | FALSE | 2024-07-15 17:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | tr_188_22 | Transformer | Transformer | 0.07125 | 0.0087834 | 0.0056029 | 12.3276 | FALSE | 2024-07-15 17:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_123 | line_1477_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_123 | line_4048_22 | ACLineSegment | Line | 0.51338 | 0.0066985 | 0.0051597 | 1.3048 | FALSE | 2024-07-15 19:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | tr_195_22 | Transformer | Transformer | 0.285 | 0.0066985 | 0.0051597 | 2.3504 | FALSE | 2024-07-15 19:00 |  |  | 300 | 3 | Transformer_kVA_x_PF
GSO_123 | line_1546_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_123 | line_4143_22 | ACLineSegment | Line | 0.025406 | 0.003267 | 0.0018545 | 12.8594 | FALSE | 2024-01-20 09:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_123 | tr_236_22 | Transformer | Transformer | 0.02375 | 0.003267 | 0.0018545 | 13.7559 | FALSE | 2024-01-20 09:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_123 | line_1639_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_123 | line_4181_22 | ACLineSegment | Line | 0.51338 | 0.028199 | 0.016836 | 5.4929 | FALSE | 2024-01-21 03:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | tr_250_22 | Transformer | Transformer | 0.285 | 0.028199 | 0.016836 | 9.8945 | FALSE | 2024-01-21 03:00 |  |  | 300 | 3 | Transformer_kVA_x_PF
GSO_123 | line_1642_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_123 | line_4186_22 | ACLineSegment | Line | 0.51338 | 0.0075065 | 0.0051272 | 1.4622 | FALSE | 2024-01-20 13:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | tr_252_22 | Transformer | Transformer | 0.1425 | 0.0075065 | 0.0051272 | 5.2677 | FALSE | 2024-01-20 13:00 |  |  | 150 | 3 | Transformer_kVA_x_PF
GSO_123 | line_1769_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_123 | line_4390_22 | ACLineSegment | Line | 0.51338 | 0.0056495 | 0.004358 | 1.1005 | FALSE | 2024-01-21 05:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | tr_320_22 | Transformer | Transformer | 0.095 | 0.0056495 | 0.004358 | 5.9469 | FALSE | 2024-01-21 05:00 |  |  | 100 | 3 | Transformer_kVA_x_PF
GSO_123 | line_1926_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_123 | line_4426_22 | ACLineSegment | Line | 0.51338 | 0.0085177 | 0.0066054 | 1.6591 | FALSE | 2024-01-20 21:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | tr_334_22 | Transformer | Transformer | 0.07125 | 0.0085177 | 0.0066054 | 11.9546 | FALSE | 2024-01-20 21:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_123 | line_1948_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_123 | line_4508_22 | ACLineSegment | Line | 0.51338 | 0.023696 | 0.017516 | 4.6157 | FALSE | 2024-01-18 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | tr_365_22 | Transformer | Transformer | 0.07125 | 0.023696 | 0.017516 | 33.2577 | FALSE | 2024-01-18 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_123 | line_1992_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_123 | line_4629_22 | ACLineSegment | Line | 0.51338 | 0.006137 | 0.004393 | 1.1954 | FALSE | 2024-01-20 12:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | tr_411_22 | Transformer | Transformer | 0.285 | 0.006137 | 0.004393 | 2.1533 | FALSE | 2024-01-20 12:00 |  |  | 300 | 3 | Transformer_kVA_x_PF
GSO_123 | line_2094_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_123 | line_4781_22 | ACLineSegment | Line | 0.51338 | 0.02749 | 0.019957 | 5.3546 | FALSE | 2024-07-16 02:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | tr_475_22 | Transformer | Transformer | 0.285 | 0.02749 | 0.019957 | 9.6455 | FALSE | 2024-07-16 02:00 |  |  | 300 | 3 | Transformer_kVA_x_PF
GSO_123 | line_2180_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_123 | line_5159_22 | ACLineSegment | Line | 0.51338 | 0.0081259 | 0.006171 | 1.5828 | FALSE | 2024-01-20 08:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | tr_648_22 | Transformer | Transformer | 0.475 | 0.0081259 | 0.006171 | 1.7107 | FALSE | 2024-01-20 08:00 |  |  | 500 | 3 | Transformer_kVA_x_PF
GSO_123 | line_2708_22 | ACLineSegment | Line | 0.51338 | 0.0077095 | 0.0055739 | 1.5017 | FALSE | 2024-07-15 22:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | tr_768_22 | Transformer | Transformer | 0.475 | 0.0077095 | 0.0055739 | 1.623 | FALSE | 2024-07-15 22:00 |  |  | 500 | 3 | Transformer_kVA_x_PF
GSO_123 | line_2709_22 | ACLineSegment | Line | 0.51338 | 0.0077095 | 0.0055739 | 1.5017 | FALSE | 2024-07-15 22:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | line_2812_22 | ACLineSegment | Line | 0.22905 | 0.0065363 | 0.0045663 | 2.8537 | FALSE | 2024-01-20 15:00 | 290 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | tr_812_22 | Transformer | Transformer | 0.07125 | 0.0065363 | 0.0045663 | 9.1738 | FALSE | 2024-01-20 15:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_123 | line_2813_22 | ACLineSegment | Line | 0.22905 | 0.0065363 | 0.0045663 | 2.8537 | FALSE | 2024-01-20 15:00 | 290 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | line_3104_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_123 | line_5693_22 | ACLineSegment | Line | 0.034884 | 0.0045752 | 0.0031999 | 13.1156 | FALSE | 2024-01-20 12:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_123 | tr_917_22 | Transformer | Transformer | 0.02375 | 0.0045752 | 0.0031999 | 19.2639 | FALSE | 2024-01-20 12:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_123 | line_3120_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_123 | line_5722_22 | ACLineSegment | Line | 0.034884 | 0.0051788 | 0.0030112 | 14.846 | FALSE | 2024-07-16 01:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_123 | tr_930_22 | Transformer | Transformer | 0.02375 | 0.0051788 | 0.0030112 | 21.8054 | FALSE | 2024-07-16 01:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_123 | line_3224_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_123 | line_5589_22 | ACLineSegment | Line | 0.51338 | 0.0067438 | 0.0050174 | 1.3136 | FALSE | 2024-06-27 03:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | tr_869_22 | Transformer | Transformer | 0.1425 | 0.0067438 | 0.0050174 | 4.7325 | FALSE | 2024-06-27 03:00 |  |  | 150 | 3 | Transformer_kVA_x_PF
GSO_123 | line_3366_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_123 | line_5914_22 | ACLineSegment | Line | 0.034884 | 0.0070294 | 0.005373 | 20.1511 | FALSE | 2024-01-21 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_123 | tr_1023_22 | Transformer | Transformer | 0.02375 | 0.0070294 | 0.005373 | 29.5975 | FALSE | 2024-01-21 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_123 | line_344_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_123 | line_6009_22 | ACLineSegment | Line | 0.51338 | 0.0055771 | 0.0041244 | 1.0863 | FALSE | 2024-07-16 03:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | tr_1067_22 | Transformer | Transformer | 0.095 | 0.0055771 | 0.0041244 | 5.8706 | FALSE | 2024-07-16 03:00 |  |  | 100 | 3 | Transformer_kVA_x_PF
GSO_123 | line_3471_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_123 | line_5853_22 | ACLineSegment | Line | 0.51338 | 0.021885 | 0.016791 | 4.263 | FALSE | 2024-07-11 01:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | tr_994_22 | Transformer | Transformer | 0.07125 | 0.021885 | 0.016791 | 30.7162 | FALSE | 2024-07-11 01:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_123 | line_3493_22 | ACLineSegment | Line | 0.034884 | 0.0073166 | 0.003517 | 20.9743 | FALSE | 2024-01-20 16:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_123 | line_3495_22 | ACLineSegment | Line | 0.034884 | 0.0076973 | 0.0048789 | 22.0659 | FALSE | 2024-01-21 03:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_123 | tr_990_22 | Transformer | Transformer | 0.0475 | 0.012314 | 0.0077236 | 25.9245 | FALSE | 2024-01-20 16:00 |  |  | 50 | 1 | Transformer_kVA_x_PF
GSO_123 | line_3494_22 | ACLineSegment | Line | 0.034884 | 0.0073166 | 0.003517 | 20.9743 | FALSE | 2024-01-20 16:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_123 | line_3496_22 | ACLineSegment | Line | 0.034884 | 0.0076973 | 0.0048789 | 22.0659 | FALSE | 2024-01-21 03:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_123 | line_357_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_123 | line_6020_22 | ACLineSegment | Line | 0.51338 | 0.010005 | 0.0071505 | 1.9488 | FALSE | 2024-01-17 17:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | tr_1073_22 | Transformer | Transformer | 0.475 | 0.010005 | 0.0071505 | 2.1062 | FALSE | 2024-01-17 17:00 |  |  | 500 | 3 | Transformer_kVA_x_PF
GSO_123 | line_3591_22 | ACLineSegment | Line | 13.5424 | 0.1722 | 0.13925 | 1.2716 | FALSE | 2024-01-21 03:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | line_4185_22 | ACLineSegment | Line | 13.5424 | 0.17456 | 0.14348 | 1.289 | FALSE | 2024-01-21 03:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | line_3592_22 | ACLineSegment | Line | 13.5424 | 0.169 | 0.13539 | 1.248 | FALSE | 2024-01-21 03:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | line_6181_22 | ACLineSegment | Line | 13.5424 | 0.039246 | 0.025802 | 0.2898 | FALSE | 2024-01-21 03:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | line_3605_22 | ACLineSegment | Line | 13.5424 | 0.31817 | 0.26216 | 2.3494 | FALSE | 2024-01-20 14:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | line_3606_22 | ACLineSegment | Line | 13.5424 | 0.32218 | 0.26652 | 2.3791 | FALSE | 2024-01-20 14:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | line_5721_22 | ACLineSegment | Line | 13.5424 | 0.30261 | 0.24896 | 2.2346 | FALSE | 2024-01-20 14:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | line_4780_22 | ACLineSegment | Line | 13.5424 | 0.02749 | 0.019957 | 0.20299 | FALSE | 2024-07-16 02:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | line_6019_22 | ACLineSegment | Line | 13.5424 | 0.34579 | 0.28797 | 2.5534 | FALSE | 2024-01-20 14:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | line_368_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_123 | line_6076_22 | ACLineSegment | Line | 0.51338 | 0.0075588 | 0.0058104 | 1.4724 | FALSE | 2024-07-15 17:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | tr_1103_22 | Transformer | Transformer | 0.07125 | 0.0075588 | 0.0058104 | 10.6089 | FALSE | 2024-07-15 17:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_123 | line_3731_22 | ACLineSegment | Line | 13.5424 | 0.0065182 | 0.0050045 | 0.048132 | FALSE | 2024-01-20 08:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | line_5692_22 | ACLineSegment | Line | 13.5424 | 0.010199 | 0.0076863 | 0.07531 | FALSE | 2024-01-20 08:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | line_3742_22 | ACLineSegment | Line | 13.5424 | 0.1073 | 0.089702 | 0.79231 | FALSE | 2024-01-21 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | line_6691_22 | ACLineSegment | Line | 13.5424 | 0.11205 | 0.092987 | 0.82739 | FALSE | 2024-01-21 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | tr_1486_22 | Transformer | Transformer | 0.095 | 0.0052536 | 0.0040179 | 5.5301 | FALSE | 2024-01-20 18:00 |  |  | 100 | 3 | Transformer_kVA_x_PF
GSO_123 | line_3743_22 | ACLineSegment | Line | 13.5424 | 0.10273 | 0.08544 | 0.75859 | FALSE | 2024-01-21 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | line_6670_22 | ACLineSegment | Line | 13.5424 | 0.099594 | 0.081654 | 0.73542 | FALSE | 2024-01-21 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | line_3745_22 | ACLineSegment | Line | 13.5424 | 0.0040493 | 0.0029802 | 0.029901 | FALSE | 2024-07-15 11:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | line_6357_22 | ACLineSegment | Line | 13.5424 | 0.09332 | 0.075786 | 0.6891 | FALSE | 2024-01-21 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | tr_1474_22 | Transformer | Transformer | 0.475 | 0.0059955 | 0.0044335 | 1.2622 | FALSE | 2024-07-15 13:00 |  |  | 500 | 3 | Transformer_kVA_x_PF
GSO_123 | line_3878_22 | ACLineSegment | Line | 13.5424 | 0.0092375 | 0.0064115 | 0.068212 | FALSE | 2024-01-20 13:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | line_3953_22 | ACLineSegment | Line | 13.5424 | 0.26268 | 0.21811 | 1.9397 | FALSE | 2024-01-20 14:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | line_3954_22 | ACLineSegment | Line | 13.5424 | 0.26635 | 0.22154 | 1.9668 | FALSE | 2024-01-20 14:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | line_4022_22 | ACLineSegment | Line | 13.5424 | 0.24667 | 0.2034 | 1.8215 | FALSE | 2024-01-20 14:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | line_5430_22 | ACLineSegment | Line | 13.5424 | 0.2718 | 0.22581 | 2.0071 | FALSE | 2024-01-20 14:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | line_4389_22 | ACLineSegment | Line | 13.5424 | 0.24292 | 0.20005 | 1.7938 | FALSE | 2024-01-20 14:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | line_4032_22 | ACLineSegment | Line | 13.5424 | 0.11523 | 0.095603 | 0.85085 | FALSE | 2024-01-21 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | line_4033_22 | ACLineSegment | Line | 13.5424 | 0.11983 | 0.099969 | 0.88488 | FALSE | 2024-01-21 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | line_4047_22 | ACLineSegment | Line | 13.5424 | 0.0066985 | 0.0051597 | 0.049464 | FALSE | 2024-07-15 19:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | line_6584_22 | ACLineSegment | Line | 13.5424 | 0.051402 | 0.037742 | 0.37957 | FALSE | 2024-01-21 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | line_6585_22 | ACLineSegment | Line | 13.5424 | 0.021229 | 0.015803 | 0.15676 | FALSE | 2024-01-21 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | tr_1402_22 | Transformer | Transformer | 0.02375 | 0.026536 | 0.021032 | 111.7291 | TRUE | 2024-01-17 22:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_123 | line_4141_22 | ACLineSegment | Line | 12.3112 | 0.033236 | 0.021926 | 0.26996 | FALSE | 2024-01-21 03:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | line_4142_22 | ACLineSegment | Line | 13.5424 | 0.036052 | 0.023383 | 0.26621 | FALSE | 2024-01-21 03:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | tr_1153_22 | Transformer | Transformer | 0.02375 | 0.0054657 | 0.0030102 | 23.0133 | FALSE | 2024-01-18 03:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_123 | line_4507_22 | ACLineSegment | Line | 13.5424 | 0.19084 | 0.15763 | 1.4092 | FALSE | 2024-01-20 14:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | line_5492_22 | ACLineSegment | Line | 13.5424 | 0.059589 | 0.046882 | 0.44002 | FALSE | 2024-01-08 23:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | tr_1336_22 | Transformer | Transformer | 0.1425 | 0.0091813 | 0.0069425 | 6.443 | FALSE | 2024-07-15 11:00 |  |  | 150 | 3 | Transformer_kVA_x_PF
GSO_123 | line_4425_22 | ACLineSegment | Line | 13.5424 | 0.0085177 | 0.0066054 | 0.062896 | FALSE | 2024-01-20 21:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | line_4627_22 | ACLineSegment | Line | 13.5424 | 0.29022 | 0.24081 | 2.143 | FALSE | 2024-01-20 14:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | line_4628_22 | ACLineSegment | Line | 13.5424 | 0.28624 | 0.23717 | 2.1136 | FALSE | 2024-01-20 14:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | line_5588_22 | ACLineSegment | Line | 13.5424 | 0.28119 | 0.23412 | 2.0764 | FALSE | 2024-01-20 14:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | line_5158_22 | ACLineSegment | Line | 13.5424 | 0.0081259 | 0.006171 | 0.060004 | FALSE | 2024-01-20 08:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | line_6075_22 | ACLineSegment | Line | 13.5424 | 0.067875 | 0.054273 | 0.50121 | FALSE | 2024-01-21 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | line_6628_22 | ACLineSegment | Line | 13.5424 | 0.057798 | 0.045169 | 0.42679 | FALSE | 2024-01-21 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | line_5587_22 | ACLineSegment | Line | 13.5424 | 0.27589 | 0.23046 | 2.0372 | FALSE | 2024-01-20 14:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | line_5491_22 | ACLineSegment | Line | 13.5424 | 0.0563 | 0.043439 | 0.41573 | FALSE | 2024-01-08 23:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | line_6329_22 | ACLineSegment | Line | 13.5424 | 0.033932 | 0.025939 | 0.25056 | FALSE | 2024-08-28 22:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | tr_1230_22 | Transformer | Transformer | 0.095 | 0.029307 | 0.022766 | 30.8494 | FALSE | 2024-01-22 04:00 |  |  | 100 | 3 | Transformer_kVA_x_PF
GSO_123 | line_5844_22 | ACLineSegment | Line | 13.5424 | 0.081571 | 0.065517 | 0.60234 | FALSE | 2024-01-21 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | tr_1247_22 | Transformer | Transformer | 0.285 | 0.0052979 | 0.0040108 | 1.8589 | FALSE | 2024-01-20 14:00 |  |  | 300 | 3 | Transformer_kVA_x_PF
GSO_123 | line_5843_22 | ACLineSegment | Line | 13.5424 | 0.072642 | 0.058674 | 0.5364 | FALSE | 2024-01-21 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | line_587_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_123 | line_6330_22 | ACLineSegment | Line | 0.51338 | 0.029307 | 0.022766 | 5.7086 | FALSE | 2024-01-22 04:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | line_588_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_123 | line_6358_22 | ACLineSegment | Line | 0.51338 | 0.0052979 | 0.0040108 | 1.032 | FALSE | 2024-01-20 14:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | line_6182_22 | ACLineSegment | Line | 0.034884 | 0.0054657 | 0.0030102 | 15.6683 | FALSE | 2024-01-18 03:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_123 | line_6642_22 | ACLineSegment | Line | 13.5424 | 0.0059209 | 0.004437 | 0.043721 | FALSE | 2024-01-20 23:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | tr_1451_22 | Transformer | Transformer | 0.07125 | 0.029962 | 0.022472 | 42.0525 | FALSE | 2024-10-06 09:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_123 | line_6463_22 | ACLineSegment | Line | 13.5424 | 0.0091646 | 0.0068099 | 0.067674 | FALSE | 2024-01-17 20:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | tr_1439_22 | Transformer | Transformer | 0.285 | 0.0048475 | 0.0031983 | 1.7009 | FALSE | 2024-01-20 19:00 |  |  | 300 | 3 | Transformer_kVA_x_PF
GSO_123 | tr_1314_22 | Transformer | Transformer | 0.285 | 0.0091646 | 0.0068099 | 3.2157 | FALSE | 2024-01-17 20:00 |  |  | 300 | 3 | Transformer_kVA_x_PF
GSO_123 | line_6464_22 | ACLineSegment | Line | 0.51338 | 0.0091646 | 0.0068099 | 1.7852 | FALSE | 2024-01-17 20:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | line_699_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_123 | line_6502_22 | ACLineSegment | Line | 0.51338 | 0.0091813 | 0.0069425 | 1.7884 | FALSE | 2024-07-15 11:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | line_737_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_123 | line_6586_22 | ACLineSegment | Line | 0.034884 | 0.026536 | 0.021032 | 76.0694 | FALSE | 2024-01-17 22:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_123 | line_807_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_123 | line_6629_22 | ACLineSegment | Line | 0.51338 | 0.0048475 | 0.0031983 | 0.94423 | FALSE | 2024-01-20 19:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | line_864_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_123 | tr_1593_22 | Transformer | Transformer | 0.475 | 0.0059209 | 0.004437 | 1.2465 | FALSE | 2024-01-20 23:00 |  |  | 500 | 3 | Transformer_kVA_x_PF
GSO_123 | line_6643_22 | ACLineSegment | Line | 0.51338 | 0.029962 | 0.022472 | 5.8363 | FALSE | 2024-10-06 09:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | line_913_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_123 | line_6671_22 | ACLineSegment | Line | 0.51338 | 0.0059955 | 0.0044335 | 1.1679 | FALSE | 2024-07-15 13:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | line_897_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_123 | line_6692_22 | ACLineSegment | Line | 0.51338 | 0.0052536 | 0.0040179 | 1.0233 | FALSE | 2024-01-20 18:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | line_957_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_123 | line_6858_22 | ACLineSegment | Line | 0.51338 | 0.0059209 | 0.004437 | 1.1533 | FALSE | 2024-01-20 23:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_123 | line_998_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_5619_22 | ACLineSegment | Line | 13.5424 | 0.11922 | 0.087338 | 0.88033 | FALSE | 2024-01-20 13:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | line_6085_22 | ACLineSegment | Line | 13.5424 | 0.09284 | 0.070569 | 0.68555 | FALSE | 2024-01-20 13:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | tr_1107_22 | Transformer | Transformer | 0.02375 | 0.019752 | 0.011299 | 83.1675 | FALSE | 2024-01-20 13:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_121 | line_6086_22 | ACLineSegment | Line | 0.94778 | 0.012692 | 0.0075631 | 1.3391 | FALSE | 2024-07-05 22:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_4865_22 | ACLineSegment | Line | 12.3112 | 0.060418 | 0.045534 | 0.49075 | FALSE | 2024-01-20 21:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | tr_512_22 | Transformer | Transformer | 0.095 | 0.0052144 | 0.0040309 | 5.4888 | FALSE | 2024-06-26 21:00 |  |  | 100 | 3 | Transformer_kVA_x_PF
GSO_121 | line_4867_22 | ACLineSegment | Line | 2.3694 | 0.0092033 | 0.0053787 | 0.38842 | FALSE | 2024-01-21 01:00 | 600 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_11_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_5902_22 | ACLineSegment | Line | 0.51338 | 0.0057544 | 0.0044642 | 1.1209 | FALSE | 2024-01-20 06:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | tr_1016_22 | Transformer | Transformer | 0.07125 | 0.0057544 | 0.0044642 | 8.0763 | FALSE | 2024-01-20 06:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_121 | line_1940_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_4475_22 | ACLineSegment | Line | 0.51338 | 0.0058188 | 0.004284 | 1.1334 | FALSE | 2024-06-23 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | tr_353_22 | Transformer | Transformer | 0.095 | 0.0058188 | 0.004284 | 6.1251 | FALSE | 2024-06-23 |  |  | 100 | 3 | Transformer_kVA_x_PF
GSO_121 | line_1950_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_4574_22 | ACLineSegment | Line | 0.51338 | 0.022144 | 0.01643 | 4.3133 | FALSE | 2024-01-20 21:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | tr_389_22 | Transformer | Transformer | 0.285 | 0.022144 | 0.01643 | 7.7697 | FALSE | 2024-01-20 21:00 |  |  | 300 | 3 | Transformer_kVA_x_PF
GSO_121 | line_1951_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_4515_22 | ACLineSegment | Line | 0.51338 | 0.0084549 | 0.0059784 | 1.6469 | FALSE | 2024-01-20 12:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | tr_367_22 | Transformer | Transformer | 0.07125 | 0.0084549 | 0.0059784 | 11.8666 | FALSE | 2024-01-20 12:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_121 | line_1996_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_4640_22 | ACLineSegment | Line | 0.51338 | 0.0049352 | 0.0038595 | 0.96132 | FALSE | 2024-01-21 01:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | tr_415_22 | Transformer | Transformer | 0.07125 | 0.0049352 | 0.0038595 | 6.9266 | FALSE | 2024-01-21 01:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_121 | line_2002_22 | ACLineSegment | Line | 0.025406 | 0.0080159 | 0.0039955 | 31.5517 | FALSE | 2024-01-21 02:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_2004_22 | ACLineSegment | Line | 0.025406 | 0.0055735 | 0.0032006 | 21.938 | FALSE | 2024-07-15 19:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | tr_407_22 | Transformer | Transformer | 0.02375 | 0.013039 | 0.0069763 | 54.9029 | FALSE | 2024-01-21 02:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_121 | line_2003_22 | ACLineSegment | Line | 0.025406 | 0.0080159 | 0.0039955 | 31.5517 | FALSE | 2024-01-21 02:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_2005_22 | ACLineSegment | Line | 0.025406 | 0.0055735 | 0.0032006 | 21.938 | FALSE | 2024-07-15 19:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_2044_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_4702_22 | ACLineSegment | Line | 0.025406 | 0.0073004 | 0.0048665 | 28.7354 | FALSE | 2024-01-20 10:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | tr_441_22 | Transformer | Transformer | 0.02375 | 0.0073004 | 0.0048665 | 30.7387 | FALSE | 2024-01-20 10:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_121 | line_2054_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_4708_22 | ACLineSegment | Line | 0.51338 | 0.0059594 | 0.003756 | 1.1608 | FALSE | 2024-01-20 05:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | tr_444_22 | Transformer | Transformer | 0.07125 | 0.0059594 | 0.003756 | 8.3641 | FALSE | 2024-01-20 05:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_121 | line_2073_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_4839_22 | ACLineSegment | Line | 0.025406 | 0.0054055 | 0.003199 | 21.2766 | FALSE | 2024-05-08 17:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | tr_499_22 | Transformer | Transformer | 0.02375 | 0.0054055 | 0.003199 | 22.7598 | FALSE | 2024-05-08 17:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_121 | line_2107_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_4868_22 | ACLineSegment | Line | 0.51338 | 0.0052144 | 0.0040309 | 1.0157 | FALSE | 2024-06-26 21:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | line_2381_22 | ACLineSegment | Line | 0.025406 | 0.0044366 | 0.0024488 | 17.4632 | FALSE | 2024-01-17 20:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_2397_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_5662_22 | ACLineSegment | Line | 0.025406 | 0.0069 | 0.005012 | 27.1593 | FALSE | 2024-01-20 13:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | tr_893_22 | Transformer | Transformer | 0.02375 | 0.010678 | 0.0069443 | 44.958 | FALSE | 2024-01-20 13:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_121 | line_2382_22 | ACLineSegment | Line | 0.025406 | 0.0044366 | 0.0024488 | 17.4632 | FALSE | 2024-01-17 20:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_2411_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_5824_22 | ACLineSegment | Line | 0.034884 | 0.0052432 | 0.0027544 | 15.0306 | FALSE | 2024-07-05 22:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | tr_971_22 | Transformer | Transformer | 0.02375 | 0.0052432 | 0.0027544 | 22.0767 | FALSE | 2024-07-05 22:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_121 | line_2445_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_5716_22 | ACLineSegment | Line | 0.025406 | 0.0026215 | 0.0013209 | 10.3185 | FALSE | 2024-01-17 21:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | tr_915_22 | Transformer | Transformer | 0.02375 | 0.0026215 | 0.0013209 | 11.0379 | FALSE | 2024-01-17 21:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_121 | line_2494_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_5569_22 | ACLineSegment | Line | 0.025406 | 0.0081989 | 0.0041554 | 32.2718 | FALSE | 2024-01-21 03:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | tr_849_22 | Transformer | Transformer | 0.02375 | 0.0081989 | 0.0041554 | 34.5217 | FALSE | 2024-01-21 03:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_121 | line_2523_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_3531_22 | ACLineSegment | Line | 0.51338 | 0.014633 | 0.011501 | 2.8504 | FALSE | 2024-01-20 10:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | tr_1_22 | Transformer | Transformer | 0.95 | 0.014633 | 0.011501 | 1.5403 | FALSE | 2024-01-20 10:00 |  |  | 1000 | 3 | Transformer_kVA_x_PF
GSO_121 | line_2772_22 | ACLineSegment | Line | 0.51338 | 0.0075275 | 0.0049278 | 1.4663 | FALSE | 2024-01-20 08:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | tr_803_22 | Transformer | Transformer | 0.475 | 0.0075275 | 0.0049278 | 1.5847 | FALSE | 2024-01-20 08:00 |  |  | 500 | 3 | Transformer_kVA_x_PF
GSO_121 | line_2773_22 | ACLineSegment | Line | 0.51338 | 0.0075275 | 0.0049278 | 1.4663 | FALSE | 2024-01-20 08:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | line_2810_22 | ACLineSegment | Line | 0.51338 | 0.0097744 | 0.0073555 | 1.9039 | FALSE | 2024-07-15 15:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | tr_806_22 | Transformer | Transformer | 0.475 | 0.0097744 | 0.0073555 | 2.0578 | FALSE | 2024-07-15 15:00 |  |  | 500 | 3 | Transformer_kVA_x_PF
GSO_121 | line_2811_22 | ACLineSegment | Line | 0.51338 | 0.0097744 | 0.0073555 | 1.9039 | FALSE | 2024-07-15 15:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | line_295_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_6018_22 | ACLineSegment | Line | 0.025406 | 0.0024582 | 0.0015071 | 9.6756 | FALSE | 2024-01-20 09:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | tr_1072_22 | Transformer | Transformer | 0.02375 | 0.0024582 | 0.0015071 | 10.3501 | FALSE | 2024-01-20 09:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_121 | line_2964_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_5373_22 | ACLineSegment | Line | 0.51338 | 0.0068538 | 0.0050815 | 1.335 | FALSE | 2024-01-18 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | tr_739_22 | Transformer | Transformer | 0.07125 | 0.0068538 | 0.0050815 | 9.6194 | FALSE | 2024-01-18 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_121 | line_3149_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_5742_22 | ACLineSegment | Line | 0.51338 | 0.0074586 | 0.0053779 | 1.4529 | FALSE | 2024-01-21 14:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | tr_941_22 | Transformer | Transformer | 0.095 | 0.0074586 | 0.0053779 | 7.8512 | FALSE | 2024-01-21 14:00 |  |  | 100 | 3 | Transformer_kVA_x_PF
GSO_121 | line_3161_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_5526_22 | ACLineSegment | Line | 0.51338 | 0.0073504 | 0.0054892 | 1.4318 | FALSE | 2024-01-20 15:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | tr_837_22 | Transformer | Transformer | 0.1425 | 0.0073504 | 0.0054892 | 5.1582 | FALSE | 2024-01-20 15:00 |  |  | 150 | 3 | Transformer_kVA_x_PF
GSO_121 | line_3_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_5899_22 | ACLineSegment | Line | 0.025406 | 0.0062547 | 0.0045246 | 24.6193 | FALSE | 2024-01-20 06:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | tr_1004_22 | Transformer | Transformer | 0.02375 | 0.0062547 | 0.0045246 | 26.3356 | FALSE | 2024-01-20 06:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_121 | line_3230_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_5851_22 | ACLineSegment | Line | 0.51338 | 0.0047179 | 0.0037178 | 0.919 | FALSE | 2024-07-15 22:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | tr_982_22 | Transformer | Transformer | 0.285 | 0.0047179 | 0.0037178 | 1.6554 | FALSE | 2024-07-15 22:00 |  |  | 300 | 3 | Transformer_kVA_x_PF
GSO_121 | line_3233_22 | ACLineSegment | Line | 0.034884 | 0.0034417 | 0.0020145 | 9.8664 | FALSE | 2024-01-21 01:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_3235_22 | ACLineSegment | Line | 0.034884 | 0.0057806 | 0.0027521 | 16.5713 | FALSE | 2024-01-20 14:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | tr_881_22 | Transformer | Transformer | 0.02375 | 0.0084269 | 0.0045333 | 35.4817 | FALSE | 2024-01-21 01:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_121 | line_3234_22 | ACLineSegment | Line | 0.034884 | 0.0034417 | 0.0020145 | 9.8664 | FALSE | 2024-01-21 01:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_3236_22 | ACLineSegment | Line | 0.034884 | 0.0057806 | 0.0027521 | 16.5713 | FALSE | 2024-01-20 14:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_3243_22 | ACLineSegment | Line | 0.025406 | 0.0034353 | 0.001925 | 13.5217 | FALSE | 2024-01-17 14:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_3244_22 | ACLineSegment | Line | 0.025406 | 0.0034353 | 0.001925 | 13.5217 | FALSE | 2024-01-17 14:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_3245_22 | ACLineSegment | Line | 0.025406 | 0.0034353 | 0.001925 | 13.5217 | FALSE | 2024-01-17 14:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_5636_22 | ACLineSegment | Line | 0.025406 | 0.004278 | 0.0020652 | 16.8386 | FALSE | 2024-01-20 12:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | tr_889_22 | Transformer | Transformer | 0.02375 | 0.0065627 | 0.0037964 | 27.6322 | FALSE | 2024-01-20 12:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_121 | line_3259_22 | ACLineSegment | Line | 0.025406 | 0.0030884 | 0.0017245 | 12.1565 | FALSE | 2024-01-20 05:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_3277_22 | ACLineSegment | Line | 0.025406 | 0.007298 | 0.0035776 | 28.7256 | FALSE | 2024-01-20 21:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | tr_926_22 | Transformer | Transformer | 0.02375 | 0.010169 | 0.0051174 | 42.8154 | FALSE | 2024-01-20 21:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_121 | line_3260_22 | ACLineSegment | Line | 0.025406 | 0.0030884 | 0.0017245 | 12.1565 | FALSE | 2024-01-20 05:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_3276_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_3279_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_5639_22 | ACLineSegment | Line | 0.025406 | 0.0039799 | 0.0020639 | 15.6652 | FALSE | 2024-01-20 08:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_5640_22 | ACLineSegment | Line | 0.025406 | 0.003579 | 0.0019503 | 14.0874 | FALSE | 2024-01-17 18:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | tr_891_22 | Transformer | Transformer | 0.02375 | 0.0071452 | 0.0038487 | 30.0851 | FALSE | 2024-01-20 08:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_121 | line_3278_22 | ACLineSegment | Line | 0.025406 | 0.007298 | 0.0035776 | 28.7256 | FALSE | 2024-01-20 21:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_3296_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_5666_22 | ACLineSegment | Line | 0.51338 | 0.0084201 | 0.0062275 | 1.6401 | FALSE | 2024-01-20 08:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | tr_905_22 | Transformer | Transformer | 0.285 | 0.0084201 | 0.0062275 | 2.9544 | FALSE | 2024-01-20 08:00 |  |  | 300 | 3 | Transformer_kVA_x_PF
GSO_121 | line_3339_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_5921_22 | ACLineSegment | Line | 0.025406 | 0.0068539 | 0.0047419 | 26.9776 | FALSE | 2024-01-20 06:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | tr_1015_22 | Transformer | Transformer | 0.02375 | 0.0068539 | 0.0047419 | 28.8584 | FALSE | 2024-01-20 06:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_121 | line_3355_22 | ACLineSegment | Line | 0.025406 | 0.0039293 | 0.0023281 | 15.466 | FALSE | 2024-01-17 22:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_3385_22 | ACLineSegment | Line | 0.025406 | 0.01638 | 0.0096702 | 64.4722 | FALSE | 2024-01-20 13:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | tr_1060_22 | Transformer | Transformer | 0.02375 | 0.019377 | 0.011814 | 81.5853 | FALSE | 2024-01-20 13:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_121 | line_3356_22 | ACLineSegment | Line | 0.025406 | 0.0039293 | 0.0023281 | 15.466 | FALSE | 2024-01-17 22:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_3370_22 | ACLineSegment | Line | 0.025406 | 0.0044997 | 0.0027496 | 17.7112 | FALSE | 2024-01-20 12:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_3384_22 | ACLineSegment | Line | 0.025406 | 0.0092492 | 0.0057788 | 36.4059 | FALSE | 2024-01-20 08:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_3400_22 | ACLineSegment | Line | 0.025406 | 0.0059361 | 0.0033039 | 23.365 | FALSE | 2024-01-20 15:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_3371_22 | ACLineSegment | Line | 0.025406 | 0.0044997 | 0.0027496 | 17.7112 | FALSE | 2024-01-20 12:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_3386_22 | ACLineSegment | Line | 0.025406 | 0.0076726 | 0.0041341 | 30.2002 | FALSE | 2024-01-20 22:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_3413_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_5788_22 | ACLineSegment | Line | 0.025406 | 0.005483 | 0.0027955 | 21.5817 | FALSE | 2024-01-20 20:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | tr_966_22 | Transformer | Transformer | 0.02375 | 0.005483 | 0.0027955 | 23.0863 | FALSE | 2024-01-20 20:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_121 | line_346_22 | ACLineSegment | Line | 0.025406 | 0.0038955 | 0.0022246 | 15.3331 | FALSE | 2024-01-20 08:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_352_22 | ACLineSegment | Line | 0.025406 | 0.0067812 | 0.0038047 | 26.6914 | FALSE | 2024-01-21 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_353_22 | ACLineSegment | Line | 0.025406 | 0.0031605 | 0.0017015 | 12.4402 | FALSE | 2024-01-21 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_347_22 | ACLineSegment | Line | 0.025406 | 0.0038955 | 0.0022246 | 15.3331 | FALSE | 2024-01-20 08:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_348_22 | ACLineSegment | Line | 0.025406 | 0.0046907 | 0.0027047 | 18.4632 | FALSE | 2024-01-20 23:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_350_22 | ACLineSegment | Line | 0.025406 | 0.0066037 | 0.0043366 | 25.9931 | FALSE | 2024-01-18 02:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_351_22 | ACLineSegment | Line | 0.025406 | 0.0030624 | 0.0017947 | 12.054 | FALSE | 2024-01-18 04:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_349_22 | ACLineSegment | Line | 0.025406 | 0.0046907 | 0.0027047 | 18.4632 | FALSE | 2024-01-20 23:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | tr_1080_22 | Transformer | Transformer | 0.02375 | 0.012698 | 0.0079715 | 53.466 | FALSE | 2024-01-21 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_121 | line_3529_22 | ACLineSegment | Line | 13.5424 | 0.35579 | 0.29433 | 2.6273 | FALSE | 2024-01-20 15:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | line_3530_22 | ACLineSegment | Line | 13.5424 | 0.36598 | 0.30425 | 2.7025 | FALSE | 2024-01-20 15:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | line_5665_22 | ACLineSegment | Line | 13.5424 | 0.35056 | 0.28958 | 2.5886 | FALSE | 2024-01-20 15:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | line_382_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_6089_22 | ACLineSegment | Line | 0.51338 | 0.017403 | 0.013713 | 3.39 | FALSE | 2024-07-15 10:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | tr_1108_22 | Transformer | Transformer | 0.1425 | 0.017403 | 0.013713 | 12.2129 | FALSE | 2024-07-15 10:00 |  |  | 150 | 3 | Transformer_kVA_x_PF
GSO_121 | line_385_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_6053_22 | ACLineSegment | Line | 0.025406 | 0.035244 | 0.022503 | 138.7255 | TRUE | 2024-07-05 23:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | tr_1094_22 | Transformer | Transformer | 0.02375 | 0.035244 | 0.022503 | 148.3967 | TRUE | 2024-07-05 23:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_121 | line_399_22 | ACLineSegment | Line | 0.034884 | 0.0084727 | 0.0040516 | 24.2885 | FALSE | 2024-01-20 22:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_401_22 | ACLineSegment | Line | 0.034884 | 0.0075602 | 0.0040586 | 21.6727 | FALSE | 2024-07-15 11:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_403_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_6087_22 | ACLineSegment | Line | 0.034884 | 0.0068577 | 0.0039564 | 19.6587 | FALSE | 2024-01-20 23:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_400_22 | ACLineSegment | Line | 0.034884 | 0.0084727 | 0.0040516 | 24.2885 | FALSE | 2024-01-20 22:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_402_22 | ACLineSegment | Line | 0.034884 | 0.0075602 | 0.0040586 | 21.6727 | FALSE | 2024-07-15 11:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_4473_22 | ACLineSegment | Line | 12.3112 | 0.044038 | 0.033045 | 0.35771 | FALSE | 2024-07-15 22:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | line_4474_22 | ACLineSegment | Line | 12.3112 | 0.038843 | 0.029033 | 0.31551 | FALSE | 2024-07-15 22:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | tr_1462_22 | Transformer | Transformer | 0.475 | 0.0060531 | 0.0043795 | 1.2743 | FALSE | 2024-01-20 15:00 |  |  | 500 | 3 | Transformer_kVA_x_PF
GSO_121 | line_4512_22 | ACLineSegment | Line | 13.5424 | 0.11361 | 0.085063 | 0.83894 | FALSE | 2024-01-20 21:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | line_4513_22 | ACLineSegment | Line | 13.5424 | 0.11734 | 0.089901 | 0.86644 | FALSE | 2024-01-20 21:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | line_4707_22 | ACLineSegment | Line | 12.3112 | 0.11889 | 0.092928 | 0.9657 | FALSE | 2024-01-20 21:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | line_4572_22 | ACLineSegment | Line | 12.3112 | 0.018857 | 0.01069 | 0.15317 | FALSE | 2024-01-20 08:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | line_4573_22 | ACLineSegment | Line | 12.3112 | 0.036123 | 0.025358 | 0.29341 | FALSE | 2024-07-15 22:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | line_4618_22 | ACLineSegment | Line | 2.3694 | 0.023498 | 0.014644 | 0.99173 | FALSE | 2024-01-21 02:00 | 600 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_4619_22 | ACLineSegment | Line | 2.3694 | 0.012698 | 0.0079715 | 0.53591 | FALSE | 2024-01-21 | 600 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_4639_22 | ACLineSegment | Line | 12.3112 | 0.10996 | 0.081848 | 0.8932 | FALSE | 2024-01-20 21:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | line_4700_22 | ACLineSegment | Line | 2.3694 | 0.010678 | 0.0069443 | 0.45063 | FALSE | 2024-01-20 13:00 | 600 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_4701_22 | ACLineSegment | Line | 2.3694 | 0.017183 | 0.011026 | 0.72517 | FALSE | 2024-01-20 10:00 | 600 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_482_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_6145_22 | ACLineSegment | Line | 0.51338 | 0.005212 | 0.0038229 | 1.0152 | FALSE | 2024-01-17 20:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | tr_1138_22 | Transformer | Transformer | 0.285 | 0.005212 | 0.0038229 | 1.8288 | FALSE | 2024-01-17 20:00 |  |  | 300 | 3 | Transformer_kVA_x_PF
GSO_121 | line_4836_22 | ACLineSegment | Line | 2.3694 | 0.043556 | 0.030084 | 1.8382 | FALSE | 2024-01-20 22:00 | 600 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_5553_22 | ACLineSegment | Line | 2.3694 | 0.038428 | 0.026296 | 1.6218 | FALSE | 2024-01-20 08:00 | 600 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_4837_22 | ACLineSegment | Line | 2.3694 | 0.011089 | 0.0062825 | 0.46802 | FALSE | 2024-01-20 21:00 | 600 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_4838_22 | ACLineSegment | Line | 2.3694 | 0.054731 | 0.037691 | 2.3098 | FALSE | 2024-01-20 22:00 | 600 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_4866_22 | ACLineSegment | Line | 12.3112 | 0.049139 | 0.03755 | 0.39914 | FALSE | 2024-01-21 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | tr_1022_22 | Transformer | Transformer | 0.02375 | 0.0092033 | 0.0053787 | 38.7508 | FALSE | 2024-01-21 01:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_121 | line_499_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_6236_22 | ACLineSegment | Line | 0.51338 | 0.0060059 | 0.0042342 | 1.1699 | FALSE | 2024-01-20 22:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | tr_1178_22 | Transformer | Transformer | 0.1425 | 0.0060059 | 0.0042342 | 4.2147 | FALSE | 2024-01-20 22:00 |  |  | 150 | 3 | Transformer_kVA_x_PF
GSO_121 | line_5372_22 | ACLineSegment | Line | 12.3112 | 0.065778 | 0.049455 | 0.5343 | FALSE | 2024-01-20 21:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | line_539_22 | ACLineSegment | Line | 0.025406 | 0.0066923 | 0.0037013 | 26.3416 | FALSE | 2024-01-20 11:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_541_22 | ACLineSegment | Line | 0.034884 | 0.010808 | 0.0071983 | 30.9839 | FALSE | 2024-01-20 14:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | tr_1185_22 | Transformer | Transformer | 0.02375 | 0.016657 | 0.0099044 | 70.1348 | FALSE | 2024-01-20 15:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_121 | line_540_22 | ACLineSegment | Line | 0.025406 | 0.0066923 | 0.0037013 | 26.3416 | FALSE | 2024-01-20 11:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_542_22 | ACLineSegment | Line | 0.034884 | 0.010808 | 0.0071983 | 30.9839 | FALSE | 2024-01-20 14:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_5478_22 | ACLineSegment | Line | 2.3694 | 0.0071452 | 0.0038487 | 0.30156 | FALSE | 2024-01-20 08:00 | 600 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_5479_22 | ACLineSegment | Line | 12.3112 | 0.014673 | 0.0082177 | 0.11918 | FALSE | 2024-01-20 08:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | line_5483_22 | ACLineSegment | Line | 12.3112 | 0.10283 | 0.076084 | 0.83524 | FALSE | 2024-01-20 21:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | line_6051_22 | ACLineSegment | Line | 12.3112 | 0.039658 | 0.027167 | 0.32213 | FALSE | 2024-07-05 23:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | tr_1312_22 | Transformer | Transformer | 0.285 | 0.0061794 | 0.0049361 | 2.1682 | FALSE | 2024-01-20 22:00 |  |  | 300 | 3 | Transformer_kVA_x_PF
GSO_121 | line_5524_22 | ACLineSegment | Line | 13.5424 | 0.023979 | 0.018897 | 0.17706 | FALSE | 2024-01-20 17:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | line_6088_22 | ACLineSegment | Line | 13.5424 | 0.01905 | 0.014773 | 0.14067 | FALSE | 2024-07-15 10:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | tr_1365_22 | Transformer | Transformer | 0.285 | 0.0071185 | 0.0048771 | 2.4977 | FALSE | 2024-01-20 12:00 |  |  | 300 | 3 | Transformer_kVA_x_PF
GSO_121 | line_5525_22 | ACLineSegment | Line | 13.5424 | 0.030283 | 0.023643 | 0.22362 | FALSE | 2024-01-17 15:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | line_5826_22 | ACLineSegment | Line | 13.5424 | 0.033776 | 0.026983 | 0.24941 | FALSE | 2024-01-17 15:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | tr_1413_22 | Transformer | Transformer | 0.475 | 0.0059492 | 0.0042839 | 1.2525 | FALSE | 2024-01-20 16:00 |  |  | 500 | 3 | Transformer_kVA_x_PF
GSO_121 | line_553_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_6266_22 | ACLineSegment | Line | 0.51338 | 0.005097 | 0.0039854 | 0.99283 | FALSE | 2024-01-17 08:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | tr_1197_22 | Transformer | Transformer | 0.475 | 0.005097 | 0.0039854 | 1.073 | FALSE | 2024-01-17 08:00 |  |  | 500 | 3 | Transformer_kVA_x_PF
GSO_121 | line_5618_22 | ACLineSegment | Line | 13.5424 | 0.1232 | 0.091793 | 0.90974 | FALSE | 2024-01-20 13:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | line_5800_22 | ACLineSegment | Line | 13.5424 | 0.14243 | 0.11031 | 1.0517 | FALSE | 2024-01-20 08:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | line_5801_22 | ACLineSegment | Line | 13.5424 | 0.024767 | 0.019356 | 0.18288 | FALSE | 2024-08-02 23:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | line_5634_22 | ACLineSegment | Line | 2.3694 | 0.078969 | 0.05604 | 3.3328 | FALSE | 2024-01-20 12:00 | 600 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_5872_22 | ACLineSegment | Line | 13.5424 | 0.089478 | 0.06743 | 0.66073 | FALSE | 2024-01-21 02:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | line_5635_22 | ACLineSegment | Line | 2.3694 | 0.072407 | 0.05243 | 3.0559 | FALSE | 2024-01-20 12:00 | 600 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | tr_1401_22 | Transformer | Transformer | 0.02375 | 0.0080413 | 0.0059137 | 33.8582 | FALSE | 2024-01-21 05:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_121 | line_6422_22 | ACLineSegment | Line | 13.5424 | 0.1555 | 0.12289 | 1.1483 | FALSE | 2024-01-20 21:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | tr_1286_22 | Transformer | Transformer | 0.1425 | 0.030218 | 0.021432 | 21.2059 | FALSE | 2024-07-10 10:00 |  |  | 150 | 3 | Transformer_kVA_x_PF
GSO_121 | line_5690_22 | ACLineSegment | Line | 2.3694 | 0.010169 | 0.0051174 | 0.42916 | FALSE | 2024-01-20 21:00 | 600 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_6235_22 | ACLineSegment | Line | 13.5424 | 0.15211 | 0.11621 | 1.1232 | FALSE | 2024-01-20 08:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | tr_1458_22 | Transformer | Transformer | 0.02375 | 0.011055 | 0.0066839 | 46.5455 | FALSE | 2024-01-17 22:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_121 | line_5825_22 | ACLineSegment | Line | 13.5424 | 0.037898 | 0.030094 | 0.27984 | FALSE | 2024-07-15 15:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | line_6144_22 | ACLineSegment | Line | 13.5424 | 0.041713 | 0.033144 | 0.30802 | FALSE | 2024-01-17 15:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | line_5873_22 | ACLineSegment | Line | 12.3112 | 0.011414 | 0.0085706 | 0.092714 | FALSE | 2024-01-20 17:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | line_6017_22 | ACLineSegment | Line | 12.3112 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | tr_1302_22 | Transformer | Transformer | 0.1425 | 0.0072394 | 0.0053687 | 5.0803 | FALSE | 2024-07-15 21:00 |  |  | 150 | 3 | Transformer_kVA_x_PF
GSO_121 | line_5900_22 | ACLineSegment | Line | 2.3694 | 0.0068539 | 0.0047419 | 0.28926 | FALSE | 2024-01-20 06:00 | 600 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_5901_22 | ACLineSegment | Line | 12.3112 | 0.12234 | 0.096544 | 0.99376 | FALSE | 2024-01-20 21:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | line_5912_22 | ACLineSegment | Line | 0.025406 | 0.0049556 | 0.0025644 | 19.5058 | FALSE | 2024-07-15 21:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_5913_22 | ACLineSegment | Line | 0.025406 | 0.0061607 | 0.0030325 | 24.2493 | FALSE | 2024-01-20 21:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_6016_22 | ACLineSegment | Line | 12.3112 | 0.0024582 | 0.0015071 | 0.019967 | FALSE | 2024-01-20 09:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | tr_1447_22 | Transformer | Transformer | 0.02375 | 0.012692 | 0.0075631 | 53.4405 | FALSE | 2024-07-05 22:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_121 | line_6234_22 | ACLineSegment | Line | 13.5424 | 0.1916 | 0.15143 | 1.4148 | FALSE | 2024-01-20 22:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | line_6249_22 | ACLineSegment | Line | 13.5424 | 0.13842 | 0.10848 | 1.0222 | FALSE | 2024-01-20 21:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | line_6474_22 | ACLineSegment | Line | 13.5424 | 0.14419 | 0.1136 | 1.0647 | FALSE | 2024-01-20 21:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | tr_1317_22 | Transformer | Transformer | 0.285 | 0.0082718 | 0.006274 | 2.9024 | FALSE | 2024-07-16 03:00 |  |  | 300 | 3 | Transformer_kVA_x_PF
GSO_121 | line_6250_22 | ACLineSegment | Line | 12.3112 | 0.1278 | 0.10105 | 1.0381 | FALSE | 2024-01-20 21:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | tr_1384_22 | Transformer | Transformer | 0.02375 | 0.0071118 | 0.0057457 | 29.9446 | FALSE | 2024-01-20 06:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_121 | line_6423_22 | ACLineSegment | Line | 0.51338 | 0.030218 | 0.021432 | 5.8862 | FALSE | 2024-07-10 10:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | line_671_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_6448_22 | ACLineSegment | Line | 0.51338 | 0.0072394 | 0.0053687 | 1.4101 | FALSE | 2024-07-15 21:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | line_664_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_6460_22 | ACLineSegment | Line | 0.51338 | 0.0061794 | 0.0049361 | 1.2037 | FALSE | 2024-01-20 22:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | line_724_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_6475_22 | ACLineSegment | Line | 0.51338 | 0.0082718 | 0.006274 | 1.6112 | FALSE | 2024-07-16 03:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | line_715_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_6536_22 | ACLineSegment | Line | 0.51338 | 0.0071185 | 0.0048771 | 1.3866 | FALSE | 2024-01-20 12:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | line_759_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_6558_22 | ACLineSegment | Line | 0.025406 | 0.0071118 | 0.0057457 | 27.993 | FALSE | 2024-01-20 06:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_799_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_6583_22 | ACLineSegment | Line | 0.025406 | 0.0080413 | 0.0059137 | 31.6516 | FALSE | 2024-01-21 05:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_792_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_6587_22 | ACLineSegment | Line | 0.51338 | 0.0068739 | 0.0052868 | 1.3389 | FALSE | 2024-01-20 12:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | line_821_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | tr_1403_22 | Transformer | Transformer | 0.07125 | 0.0068739 | 0.0052868 | 9.6475 | FALSE | 2024-01-20 12:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_121 | line_6599_22 | ACLineSegment | Line | 0.51338 | 0.0059492 | 0.0042839 | 1.1588 | FALSE | 2024-01-20 16:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | line_796_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_6655_22 | ACLineSegment | Line | 0.51338 | 0.0060531 | 0.0043795 | 1.1791 | FALSE | 2024-01-20 15:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_121 | line_911_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_870_22 | ACLineSegment | Line | 0.034884 | 0.0080766 | 0.0040137 | 23.1529 | FALSE | 2024-01-21 04:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_872_22 | ACLineSegment | Line | 0.034884 | 0.0066381 | 0.0050211 | 19.0295 | FALSE | 2024-01-17 16:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_871_22 | ACLineSegment | Line | 0.034884 | 0.0080766 | 0.0040137 | 23.1529 | FALSE | 2024-01-21 04:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_873_22 | ACLineSegment | Line | 0.034884 | 0.0066381 | 0.0050211 | 19.0295 | FALSE | 2024-01-17 16:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_898_22 | ACLineSegment | Line | 0.034884 | 0.0052632 | 0.0029931 | 15.0881 | FALSE | 2024-05-20 17:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_901_22 | ACLineSegment | Line | 0.034884 | 0.0089509 | 0.0048679 | 25.6595 | FALSE | 2024-01-20 19:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_899_22 | ACLineSegment | Line | 0.034884 | 0.0052632 | 0.0029931 | 15.0881 | FALSE | 2024-05-20 17:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_121 | line_902_22 | ACLineSegment | Line | 0.034884 | 0.0089509 | 0.0048679 | 25.6595 | FALSE | 2024-01-20 19:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | line_5978_22 | ACLineSegment | Line | 12.3112 | 0.12812 | 0.090001 | 1.0407 | FALSE | 2024-01-20 06:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_144 | tr_1054_22 | Transformer | Transformer | 0.02375 | 0.018663 | 0.011911 | 78.5794 | FALSE | 2024-01-20 21:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_144 | line_5977_22 | ACLineSegment | Line | 2.3694 | 0.111 | 0.078488 | 4.6848 | FALSE | 2024-01-20 06:00 | 600 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | line_270_22 | ACLineSegment | Line | 0.025406 | 0.0070213 | 0.0041447 | 27.6368 | FALSE | 2024-01-20 06:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | line_271_22 | ACLineSegment | Line | 0.025406 | 0.013053 | 0.0079585 | 51.377 | FALSE | 2024-07-15 12:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | line_272_22 | ACLineSegment | Line | 0.025406 | 0.0070198 | 0.0040676 | 27.6308 | FALSE | 2024-01-20 23:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | line_276_22 | ACLineSegment | Line | 0.025406 | 0.0070213 | 0.0041447 | 27.6368 | FALSE | 2024-01-20 06:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | line_280_22 | ACLineSegment | Line | 0.025406 | 0.016127 | 0.01024 | 63.4779 | FALSE | 2024-01-20 06:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | line_287_22 | ACLineSegment | Line | 0.025406 | 0.0040851 | 0.0024277 | 16.0794 | FALSE | 2024-01-20 16:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | line_273_22 | ACLineSegment | Line | 0.025406 | 0.0042971 | 0.0026389 | 16.9138 | FALSE | 2024-07-15 16:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | line_277_22 | ACLineSegment | Line | 0.025406 | 0.0092858 | 0.0058217 | 36.55 | FALSE | 2024-01-20 07:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | line_286_22 | ACLineSegment | Line | 0.025406 | 0.0061512 | 0.0034643 | 24.2118 | FALSE | 2024-01-21 01:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | line_274_22 | ACLineSegment | Line | 0.025406 | 0.0042971 | 0.0026389 | 16.9138 | FALSE | 2024-07-15 16:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | line_278_22 | ACLineSegment | Line | 0.025406 | 0.012177 | 0.0079196 | 47.9293 | FALSE | 2024-07-16 01:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | line_279_22 | ACLineSegment | Line | 0.025406 | 0.0045303 | 0.002272 | 17.8316 | FALSE | 2024-07-15 04:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | line_283_22 | ACLineSegment | Line | 0.025406 | 0.030281 | 0.019158 | 119.1894 | TRUE | 2024-01-20 06:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | line_289_22 | ACLineSegment | Line | 0.038174 | 0.039999 | 0.026892 | 104.7795 | TRUE | 2024-01-20 06:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | line_281_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | line_282_22 | ACLineSegment | Line | 0.025406 | 0.0052688 | 0.0028276 | 20.7386 | FALSE | 2024-01-17 10:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | line_284_22 | ACLineSegment | Line | 0.025406 | 0.0045137 | 0.0028217 | 17.7664 | FALSE | 2024-01-20 05:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | line_285_22 | ACLineSegment | Line | 0.025406 | 0.0071692 | 0.0040952 | 28.2188 | FALSE | 2024-01-20 17:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | line_288_22 | ACLineSegment | Line | 0.025406 | 0.0052688 | 0.0028276 | 20.7386 | FALSE | 2024-01-17 10:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | line_5983_22 | ACLineSegment | Line | 0.025406 | 0.0058097 | 0.0033199 | 22.8676 | FALSE | 2024-01-18 02:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | tr_1055_22 | Transformer | Transformer | 0.0475 | 0.043235 | 0.030034 | 91.0214 | FALSE | 2024-01-20 06:00 |  |  | 50 | 1 | Transformer_kVA_x_PF
GSO_144 | line_297_22 | ACLineSegment | Line | 0.025406 | 0.0080612 | 0.0042982 | 31.7297 | FALSE | 2024-01-21 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | line_298_22 | ACLineSegment | Line | 0.025406 | 0.0080612 | 0.0042982 | 31.7297 | FALSE | 2024-01-21 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | line_300_22 | ACLineSegment | Line | 0.025406 | 0.0080612 | 0.0042982 | 31.7297 | FALSE | 2024-01-21 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | line_299_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | line_301_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | line_5979_22 | ACLineSegment | Line | 0.025406 | 0.0041069 | 0.0025071 | 16.1651 | FALSE | 2024-07-15 17:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | line_5980_22 | ACLineSegment | Line | 0.025406 | 0.0047615 | 0.0023839 | 18.7419 | FALSE | 2024-01-21 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | line_5981_22 | ACLineSegment | Line | 0.025406 | 0.0059786 | 0.0033485 | 23.5326 | FALSE | 2024-07-15 13:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | line_304_22 | ACLineSegment | Line | 0.025406 | 0.016086 | 0.010832 | 63.3156 | FALSE | 2024-01-20 21:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | line_305_22 | ACLineSegment | Line | 0.025406 | 0.016086 | 0.010832 | 63.3156 | FALSE | 2024-01-20 21:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | line_307_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | line_315_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | line_316_22 | ACLineSegment | Line | 0.025406 | 0.0062125 | 0.0031598 | 24.4532 | FALSE | 2024-01-21 02:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | line_317_22 | ACLineSegment | Line | 0.025406 | 0.0044978 | 0.0025249 | 17.7037 | FALSE | 2024-01-21 03:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | line_318_22 | ACLineSegment | Line | 0.025406 | 0.0047717 | 0.0027887 | 18.7822 | FALSE | 2024-07-16 03:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | line_319_22 | ACLineSegment | Line | 0.025406 | 0.0062375 | 0.0030039 | 24.5515 | FALSE | 2024-01-20 06:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | line_306_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | line_309_22 | ACLineSegment | Line | 0.025406 | 0.013115 | 0.0080928 | 51.6239 | FALSE | 2024-01-20 17:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | line_320_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | line_321_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | line_5987_22 | ACLineSegment | Line | 0.025406 | 0.0022022 | 0.0011588 | 8.6681 | FALSE | 2024-01-20 11:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | line_5988_22 | ACLineSegment | Line | 0.025406 | 0.0060892 | 0.0034213 | 23.9677 | FALSE | 2024-07-15 20:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | line_5989_22 | ACLineSegment | Line | 0.025406 | 0.0065333 | 0.0035828 | 25.7159 | FALSE | 2024-01-20 13:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | line_5990_22 | ACLineSegment | Line | 0.025406 | 0.0063705 | 0.0037746 | 25.0752 | FALSE | 2024-01-20 17:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | tr_1057_22 | Transformer | Transformer | 0.0475 | 0.044271 | 0.029916 | 93.2027 | FALSE | 2024-01-20 17:00 |  |  | 50 | 1 | Transformer_kVA_x_PF
GSO_144 | line_308_22 | ACLineSegment | Line | 0.025406 | 0.013115 | 0.0080928 | 51.6239 | FALSE | 2024-01-20 17:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | line_310_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | line_311_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | line_312_22 | ACLineSegment | Line | 0.025406 | 0.0035911 | 0.0020165 | 14.1351 | FALSE | 2024-01-20 12:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | line_313_22 | ACLineSegment | Line | 0.025406 | 0.0076361 | 0.0039952 | 30.0566 | FALSE | 2024-01-20 17:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | line_314_22 | ACLineSegment | Line | 0.025406 | 0.0040504 | 0.0024933 | 15.9428 | FALSE | 2024-07-15 07:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | line_331_22 | ACLineSegment | Line | 0.025406 | 0.0067879 | 0.00409 | 26.7181 | FALSE | 2024-07-15 08:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | line_332_22 | ACLineSegment | Line | 0.025406 | 0.0067879 | 0.00409 | 26.7181 | FALSE | 2024-07-15 08:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | line_333_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | line_334_22 | ACLineSegment | Line | 0.025406 | 0.0035889 | 0.0020296 | 14.1264 | FALSE | 2024-01-17 08:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | line_335_22 | ACLineSegment | Line | 0.025406 | 0.0040994 | 0.0022057 | 16.1357 | FALSE | 2024-01-21 01:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | line_336_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | line_342_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | line_5984_22 | ACLineSegment | Line | 0.025406 | 0.0066528 | 0.0037169 | 26.1861 | FALSE | 2024-01-20 21:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | line_5985_22 | ACLineSegment | Line | 0.025406 | 0.0059506 | 0.0036267 | 23.4221 | FALSE | 2024-07-15 07:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | line_5986_22 | ACLineSegment | Line | 0.025406 | 0.0040258 | 0.0022893 | 15.8462 | FALSE | 2024-01-21 03:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | tr_1056_22 | Transformer | Transformer | 0.02375 | 0.021451 | 0.013064 | 90.3209 | FALSE | 2024-01-20 21:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_144 | line_3345_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | line_3347_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | line_5975_22 | ACLineSegment | Line | 0.025406 | 0.0060318 | 0.0031463 | 23.7417 | FALSE | 2024-01-20 07:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | line_5976_22 | ACLineSegment | Line | 0.025406 | 0.0057724 | 0.0030496 | 22.7209 | FALSE | 2024-01-20 12:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | tr_1053_22 | Transformer | Transformer | 0.02375 | 0.010256 | 0.0059538 | 43.182 | FALSE | 2024-01-20 09:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_144 | line_5973_22 | ACLineSegment | Line | 2.3694 | 0.053945 | 0.035588 | 2.2767 | FALSE | 2024-01-20 17:00 | 600 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | line_5974_22 | ACLineSegment | Line | 2.3694 | 0.044271 | 0.029916 | 1.8684 | FALSE | 2024-01-20 17:00 | 600 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_144 | line_5982_22 | ACLineSegment | Line | 2.3694 | 0.072693 | 0.048274 | 3.0679 | FALSE | 2024-01-20 21:00 | 600 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_4758_22 | ACLineSegment | Line | 12.3112 | 0.022233 | 0.01514 | 0.18059 | FALSE | 2024-01-21 01:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | tr_464_22 | Transformer | Transformer | 0.285 | 0.0052793 | 0.003803 | 1.8524 | FALSE | 2024-01-21 04:00 |  |  | 300 | 3 | Transformer_kVA_x_PF
GSO_141 | line_4258_22 | ACLineSegment | Line | 0.94778 | 0.018107 | 0.011891 | 1.9105 | FALSE | 2024-01-21 01:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_1653_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_4269_22 | ACLineSegment | Line | 0.034884 | 0.0036736 | 0.0020954 | 10.531 | FALSE | 2024-01-21 02:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | tr_275_22 | Transformer | Transformer | 0.02375 | 0.0036736 | 0.0020954 | 15.4677 | FALSE | 2024-01-21 02:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_141 | line_1662_22 | ACLineSegment | Line | 0.034884 | 0.0030244 | 0.0018374 | 8.6699 | FALSE | 2024-07-15 14:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_1663_22 | ACLineSegment | Line | 0.034884 | 0.0030244 | 0.0018374 | 8.6699 | FALSE | 2024-07-15 14:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_1664_22 | ACLineSegment | Line | 0.034884 | 0.0030244 | 0.0018374 | 8.6699 | FALSE | 2024-07-15 14:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_4252_22 | ACLineSegment | Line | 0.034884 | 0.0041218 | 0.0025836 | 11.8159 | FALSE | 2024-01-20 06:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | tr_269_22 | Transformer | Transformer | 0.02375 | 0.0066951 | 0.0042416 | 28.1898 | FALSE | 2024-01-20 23:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_141 | line_1731_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_4301_22 | ACLineSegment | Line | 0.51338 | 0.005038 | 0.0036322 | 0.98133 | FALSE | 2024-07-15 20:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | tr_287_22 | Transformer | Transformer | 0.1425 | 0.005038 | 0.0036322 | 3.5354 | FALSE | 2024-07-15 20:00 |  |  | 150 | 3 | Transformer_kVA_x_PF
GSO_141 | line_1732_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_4371_22 | ACLineSegment | Line | 0.51338 | 0.0097384 | 0.005382 | 1.8969 | FALSE | 2024-01-20 14:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | tr_312_22 | Transformer | Transformer | 0.285 | 0.0097384 | 0.005382 | 3.417 | FALSE | 2024-01-20 14:00 |  |  | 300 | 3 | Transformer_kVA_x_PF
GSO_141 | line_1844_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_4362_22 | ACLineSegment | Line | 0.51338 | 0.0070843 | 0.005119 | 1.3799 | FALSE | 2024-01-21 06:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | tr_309_22 | Transformer | Transformer | 0.095 | 0.0070843 | 0.005119 | 7.4571 | FALSE | 2024-01-21 06:00 |  |  | 100 | 3 | Transformer_kVA_x_PF
GSO_141 | line_1881_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_4915_22 | ACLineSegment | Line | 0.51338 | 0.0079834 | 0.0056253 | 1.5551 | FALSE | 2024-01-20 18:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | tr_534_22 | Transformer | Transformer | 0.07125 | 0.0079834 | 0.0056253 | 11.2048 | FALSE | 2024-01-20 18:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_141 | line_1888_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_4888_22 | ACLineSegment | Line | 0.51338 | 0.0060146 | 0.0041833 | 1.1716 | FALSE | 2024-07-15 17:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | tr_521_22 | Transformer | Transformer | 0.07125 | 0.0060146 | 0.0041833 | 8.4415 | FALSE | 2024-07-15 17:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_141 | line_1906_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_4503_22 | ACLineSegment | Line | 0.51338 | 0.0061108 | 0.0042226 | 1.1903 | FALSE | 2024-01-20 05:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | tr_363_22 | Transformer | Transformer | 0.1425 | 0.0061108 | 0.0042226 | 4.2883 | FALSE | 2024-01-20 05:00 |  |  | 150 | 3 | Transformer_kVA_x_PF
GSO_141 | line_19_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_4552_22 | ACLineSegment | Line | 0.51338 | 0.0054614 | 0.0041761 | 1.0638 | FALSE | 2024-01-20 11:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | tr_370_22 | Transformer | Transformer | 0.07125 | 0.0054614 | 0.0041761 | 7.6651 | FALSE | 2024-01-20 11:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_141 | line_1991_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_4603_22 | ACLineSegment | Line | 0.034884 | 0.009104 | 0.0067273 | 26.0984 | FALSE | 2024-01-20 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | tr_401_22 | Transformer | Transformer | 0.0475 | 0.009104 | 0.0067273 | 19.1664 | FALSE | 2024-01-20 10:00 |  |  | 50 | 1 | Transformer_kVA_x_PF
GSO_141 | line_2040_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_4759_22 | ACLineSegment | Line | 0.51338 | 0.0052793 | 0.003803 | 1.0283 | FALSE | 2024-01-21 04:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | line_2063_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_4711_22 | ACLineSegment | Line | 0.51338 | 0.0070893 | 0.005379 | 1.3809 | FALSE | 2024-01-20 11:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | tr_445_22 | Transformer | Transformer | 0.07125 | 0.0070893 | 0.005379 | 9.9499 | FALSE | 2024-01-20 11:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_141 | line_2074_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_4816_22 | ACLineSegment | Line | 0.51338 | 0.0080884 | 0.0061934 | 1.5755 | FALSE | 2024-01-21 19:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | tr_489_22 | Transformer | Transformer | 0.07125 | 0.0080884 | 0.0061934 | 11.3521 | FALSE | 2024-01-21 19:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_141 | line_2077_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_4850_22 | ACLineSegment | Line | 0.51338 | 0.0049529 | 0.0036329 | 0.96477 | FALSE | 2024-01-17 21:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | tr_504_22 | Transformer | Transformer | 0.285 | 0.0049529 | 0.0036329 | 1.7379 | FALSE | 2024-01-17 21:00 |  |  | 300 | 3 | Transformer_kVA_x_PF
GSO_141 | line_2082_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_4804_22 | ACLineSegment | Line | 0.51338 | 0.007402 | 0.0054337 | 1.4418 | FALSE | 2024-07-15 08:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | tr_484_22 | Transformer | Transformer | 0.285 | 0.007402 | 0.0054337 | 2.5972 | FALSE | 2024-07-15 08:00 |  |  | 300 | 3 | Transformer_kVA_x_PF
GSO_141 | line_232_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_4897_22 | ACLineSegment | Line | 0.51338 | 0.0029775 | 0.0021908 | 0.57998 | FALSE | 2024-07-15 09:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | tr_514_22 | Transformer | Transformer | 0.285 | 0.0029775 | 0.0021908 | 1.0447 | FALSE | 2024-07-15 09:00 |  |  | 300 | 3 | Transformer_kVA_x_PF
GSO_141 | line_2339_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_6650_22 | ACLineSegment | Line | 0.034884 | 0.0067725 | 0.005107 | 19.4146 | FALSE | 2024-07-15 23:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | tr_1448_22 | Transformer | Transformer | 0.02375 | 0.0067725 | 0.005107 | 28.5158 | FALSE | 2024-07-15 23:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_141 | line_2428_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_6782_22 | ACLineSegment | Line | 0.51338 | 0.0063514 | 0.0046466 | 1.2372 | FALSE | 2024-01-20 09:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | tr_1537_22 | Transformer | Transformer | 0.1425 | 0.0063514 | 0.0046466 | 4.4571 | FALSE | 2024-01-20 09:00 |  |  | 150 | 3 | Transformer_kVA_x_PF
GSO_141 | line_2495_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_4118_22 | ACLineSegment | Line | 0.025406 | 0.0087909 | 0.0066443 | 34.6022 | FALSE | 2024-01-17 07:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | tr_214_22 | Transformer | Transformer | 0.02375 | 0.0087909 | 0.0066443 | 37.0144 | FALSE | 2024-01-17 07:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_141 | line_2546_22 | ACLineSegment | Line | 0.034884 | 0.007512 | 0.0043251 | 21.5346 | FALSE | 2024-07-15 14:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_2547_22 | ACLineSegment | Line | 0.034884 | 0.021357 | 0.012811 | 61.225 | FALSE | 2024-01-20 06:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_2548_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_2549_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_2550_22 | ACLineSegment | Line | 0.034884 | 0.0056815 | 0.0028023 | 16.287 | FALSE | 2024-01-20 22:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_2551_22 | ACLineSegment | Line | 0.034884 | 0.0040782 | 0.0020594 | 11.6908 | FALSE | 2024-01-20 14:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_2552_22 | ACLineSegment | Line | 0.034884 | 0.0039924 | 0.0020337 | 11.4451 | FALSE | 2024-01-21 04:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_2553_22 | ACLineSegment | Line | 0.034884 | 0.0049597 | 0.0025289 | 14.2179 | FALSE | 2024-01-20 06:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_2583_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_2584_22 | ACLineSegment | Line | 0.034884 | 0.0045105 | 0.0025783 | 12.9303 | FALSE | 2024-07-15 14:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_2585_22 | ACLineSegment | Line | 0.034884 | 0.0033114 | 0.0019237 | 9.4927 | FALSE | 2024-01-20 05:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_2561_22 | ACLineSegment | Line | 0.034884 | 0.021357 | 0.012811 | 61.225 | FALSE | 2024-01-20 06:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_2560_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_2562_22 | ACLineSegment | Line | 0.034884 | 0.029781 | 0.019303 | 85.3731 | FALSE | 2024-01-20 06:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_2563_22 | ACLineSegment | Line | 0.034884 | 0.0092446 | 0.005387 | 26.5014 | FALSE | 2024-01-21 01:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_2564_22 | ACLineSegment | Line | 0.034884 | 0.0024158 | 0.0014297 | 6.9254 | FALSE | 2024-01-20 06:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_2643_22 | ACLineSegment | Line | 0.034884 | 0.029781 | 0.019303 | 85.3731 | FALSE | 2024-01-20 06:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_2598_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_2599_22 | ACLineSegment | Line | 0.034884 | 0.031698 | 0.021019 | 90.8671 | FALSE | 2024-01-20 21:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_2600_22 | ACLineSegment | Line | 0.034884 | 0.023888 | 0.015185 | 68.4788 | FALSE | 2024-07-15 08:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_2601_22 | ACLineSegment | Line | 0.034884 | 0.0053376 | 0.0030564 | 15.3011 | FALSE | 2024-01-20 16:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_2602_22 | ACLineSegment | Line | 0.034884 | 0.0063453 | 0.003445 | 18.1899 | FALSE | 2024-01-18 02:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_2644_22 | ACLineSegment | Line | 0.034884 | 0.038333 | 0.025548 | 109.8882 | TRUE | 2024-01-20 06:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_2822_22 | ACLineSegment | Line | 0.034884 | 0.067331 | 0.046448 | 193.0174 | TRUE | 2024-01-20 14:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_2727_22 | ACLineSegment | Line | 0.034884 | 0.019912 | 0.012077 | 57.0811 | FALSE | 2024-07-15 08:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_2904_22 | ACLineSegment | Line | 0.034884 | 0.0056607 | 0.0032786 | 16.2274 | FALSE | 2024-01-20 13:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_2621_22 | ACLineSegment | Line | 0.034884 | 0.0056119 | 0.0033908 | 16.0875 | FALSE | 2024-01-21 04:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_2622_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_2623_22 | ACLineSegment | Line | 0.034884 | 0.019912 | 0.012077 | 57.0811 | FALSE | 2024-07-15 08:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_2624_22 | ACLineSegment | Line | 0.034884 | 0.004716 | 0.002957 | 13.5193 | FALSE | 2024-07-15 22:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_2625_22 | ACLineSegment | Line | 0.034884 | 0.0072541 | 0.0038293 | 20.7953 | FALSE | 2024-07-15 08:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_2626_22 | ACLineSegment | Line | 0.034884 | 0.0049045 | 0.0026623 | 14.0598 | FALSE | 2024-01-20 06:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_2686_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_2687_22 | ACLineSegment | Line | 0.034884 | 0.0037979 | 0.0020903 | 10.8873 | FALSE | 2024-01-21 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_2688_22 | ACLineSegment | Line | 0.034884 | 0.0024946 | 0.001408 | 7.1513 | FALSE | 2024-01-21 04:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_2645_22 | ACLineSegment | Line | 0.034884 | 0.0049667 | 0.0029466 | 14.2378 | FALSE | 2024-01-20 08:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_2646_22 | ACLineSegment | Line | 0.034884 | 0.0068096 | 0.0039086 | 19.5209 | FALSE | 2024-01-20 19:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_2663_22 | ACLineSegment | Line | 0.51338 | 0.0047604 | 0.0035326 | 0.92726 | FALSE | 2024-01-21 17:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | tr_763_22 | Transformer | Transformer | 0.1425 | 0.0047604 | 0.0035326 | 3.3406 | FALSE | 2024-01-21 17:00 |  |  | 150 | 3 | Transformer_kVA_x_PF
GSO_141 | line_2664_22 | ACLineSegment | Line | 0.51338 | 0.0047604 | 0.0035326 | 0.92726 | FALSE | 2024-01-21 17:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | line_2696_22 | ACLineSegment | Line | 0.51338 | 0.0042854 | 0.0032239 | 0.83475 | FALSE | 2024-06-26 04:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | tr_781_22 | Transformer | Transformer | 0.95 | 0.0042854 | 0.0032239 | 0.4511 | FALSE | 2024-06-26 04:00 |  |  | 1000 | 3 | Transformer_kVA_x_PF
GSO_141 | line_2697_22 | ACLineSegment | Line | 0.51338 | 0.0042854 | 0.0032239 | 0.83475 | FALSE | 2024-06-26 04:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | line_5505_22 | ACLineSegment | Line | 0.034884 | 0.0044737 | 0.0027193 | 12.8247 | FALSE | 2024-01-21 04:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | tr_815_22 | Transformer | Transformer | 0.0475 | 0.070088 | 0.048984 | 147.5527 | TRUE | 2024-01-20 19:00 |  |  | 50 | 1 | Transformer_kVA_x_PF
GSO_141 | line_3111_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_5678_22 | ACLineSegment | Line | 0.51338 | 0.019766 | 0.01504 | 3.8501 | FALSE | 2024-01-17 21:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | tr_910_22 | Transformer | Transformer | 0.1425 | 0.019766 | 0.01504 | 13.8708 | FALSE | 2024-01-17 21:00 |  |  | 150 | 3 | Transformer_kVA_x_PF
GSO_141 | line_3151_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_5744_22 | ACLineSegment | Line | 0.51338 | 0.0049573 | 0.0038501 | 0.96561 | FALSE | 2024-01-20 22:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | tr_942_22 | Transformer | Transformer | 0.285 | 0.0049573 | 0.0038501 | 1.7394 | FALSE | 2024-01-20 22:00 |  |  | 300 | 3 | Transformer_kVA_x_PF
GSO_141 | line_3360_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_5933_22 | ACLineSegment | Line | 0.51338 | 0.00603 | 0.0045444 | 1.1746 | FALSE | 2024-01-21 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | tr_1033_22 | Transformer | Transformer | 0.285 | 0.00603 | 0.0045444 | 2.1158 | FALSE | 2024-01-21 |  |  | 300 | 3 | Transformer_kVA_x_PF
GSO_141 | line_343_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_6008_22 | ACLineSegment | Line | 0.51338 | 0.0048581 | 0.0038553 | 0.94629 | FALSE | 2024-07-11 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | tr_1066_22 | Transformer | Transformer | 0.285 | 0.0048581 | 0.0038553 | 1.7046 | FALSE | 2024-07-11 |  |  | 300 | 3 | Transformer_kVA_x_PF
GSO_141 | line_377_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_6061_22 | ACLineSegment | Line | 0.51338 | 0.0066204 | 0.0044128 | 1.2896 | FALSE | 2024-01-21 02:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | tr_1097_22 | Transformer | Transformer | 0.285 | 0.0066204 | 0.0044128 | 2.3229 | FALSE | 2024-01-21 02:00 |  |  | 300 | 3 | Transformer_kVA_x_PF
GSO_141 | line_4094_22 | ACLineSegment | Line | 12.3112 | 0.091622 | 0.075644 | 0.74421 | FALSE | 2024-01-21 01:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | line_4095_22 | ACLineSegment | Line | 12.3112 | 0.11416 | 0.092614 | 0.92728 | FALSE | 2024-01-20 14:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | line_4096_22 | ACLineSegment | Line | 12.3112 | 0.017356 | 0.013185 | 0.14098 | FALSE | 2024-01-20 22:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | line_4250_22 | ACLineSegment | Line | 13.5424 | 0.21798 | 0.17314 | 1.6096 | FALSE | 2024-01-20 14:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | line_4401_22 | ACLineSegment | Line | 13.5424 | 0.2244 | 0.17999 | 1.657 | FALSE | 2024-01-20 14:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | line_4803_22 | ACLineSegment | Line | 13.5424 | 0.0047604 | 0.0035326 | 0.035152 | FALSE | 2024-01-21 17:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | line_4251_22 | ACLineSegment | Line | 13.5424 | 0.21387 | 0.16907 | 1.5793 | FALSE | 2024-01-20 14:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | line_4361_22 | ACLineSegment | Line | 13.5424 | 0.14498 | 0.12071 | 1.0706 | FALSE | 2024-01-20 16:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | line_4257_22 | ACLineSegment | Line | 0.94778 | 0.015811 | 0.0098904 | 1.6682 | FALSE | 2024-01-20 23:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | tr_271_22 | Transformer | Transformer | 0.02375 | 0.0035402 | 0.0021073 | 14.906 | FALSE | 2024-01-20 08:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_141 | line_4268_22 | ACLineSegment | Line | 0.94778 | 0.0036736 | 0.0020954 | 0.3876 | FALSE | 2024-01-21 02:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_4437_22 | ACLineSegment | Line | 0.94778 | 0.011368 | 0.00631 | 1.1995 | FALSE | 2024-01-20 14:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | tr_338_22 | Transformer | Transformer | 0.02375 | 0.0029199 | 0.0018065 | 12.2941 | FALSE | 2024-01-21 03:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_141 | line_4259_22 | ACLineSegment | Line | 0.034884 | 0.0035402 | 0.0021073 | 10.1486 | FALSE | 2024-01-20 08:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_4300_22 | ACLineSegment | Line | 12.3112 | 0.088077 | 0.072633 | 0.71542 | FALSE | 2024-01-21 01:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | line_4360_22 | ACLineSegment | Line | 13.5424 | 0.14046 | 0.11677 | 1.0372 | FALSE | 2024-01-20 14:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | line_4370_22 | ACLineSegment | Line | 12.3112 | 0.0097384 | 0.005382 | 0.079102 | FALSE | 2024-01-20 14:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | line_4403_22 | ACLineSegment | Line | 13.5424 | 0.22768 | 0.18418 | 1.6813 | FALSE | 2024-01-20 14:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | tr_325_22 | Transformer | Transformer | 0.02375 | 0.006944 | 0.0049712 | 29.2381 | FALSE | 2024-01-20 13:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_141 | line_4710_22 | ACLineSegment | Line | 13.5424 | 0.23237 | 0.18836 | 1.7159 | FALSE | 2024-01-20 14:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | line_4431_22 | ACLineSegment | Line | 0.034884 | 0.006944 | 0.0049712 | 19.9064 | FALSE | 2024-01-20 13:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_75_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | tr_755_22 | Transformer | Transformer | 0.02375 | 0.011368 | 0.00631 | 47.8672 | FALSE | 2024-01-20 14:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_141 | line_4438_22 | ACLineSegment | Line | 0.034884 | 0.0029199 | 0.0018065 | 8.3703 | FALSE | 2024-01-21 03:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_4502_22 | ACLineSegment | Line | 12.3112 | 0.0061108 | 0.0042226 | 0.049636 | FALSE | 2024-01-20 05:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | tr_1157_22 | Transformer | Transformer | 0.285 | 0.0063553 | 0.004248 | 2.2299 | FALSE | 2024-01-20 10:00 |  |  | 300 | 3 | Transformer_kVA_x_PF
GSO_141 | line_4522_22 | ACLineSegment | Line | 13.5424 | 0.010754 | 0.0084863 | 0.079414 | FALSE | 2024-01-20 10:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | line_4523_22 | ACLineSegment | Line | 13.5424 | 0.015296 | 0.01217 | 0.11295 | FALSE | 2024-07-15 19:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | line_4602_22 | ACLineSegment | Line | 13.5424 | 0.0029775 | 0.0021908 | 0.021987 | FALSE | 2024-07-15 09:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | line_4815_22 | ACLineSegment | Line | 12.3112 | 0.025144 | 0.019967 | 0.20424 | FALSE | 2024-01-20 09:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | line_4887_22 | ACLineSegment | Line | 12.3112 | 0.0079834 | 0.0056253 | 0.064846 | FALSE | 2024-01-20 18:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | line_455_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_6186_22 | ACLineSegment | Line | 0.51338 | 0.0063553 | 0.004248 | 1.2379 | FALSE | 2024-01-20 10:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | line_4565_22 | ACLineSegment | Line | 13.5424 | 0.35867 | 0.2903 | 2.6485 | FALSE | 2024-01-21 01:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | line_4566_22 | ACLineSegment | Line | 13.5424 | 0.35254 | 0.28694 | 2.6032 | FALSE | 2024-01-21 01:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | tr_386_22 | Transformer | Transformer | 0.02375 | 0.0071664 | 0.0037108 | 30.1742 | FALSE | 2024-01-21 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_141 | line_5449_22 | ACLineSegment | Line | 13.5424 | 0.029712 | 0.020613 | 0.2194 | FALSE | 2024-07-15 07:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | line_6472_22 | ACLineSegment | Line | 13.5424 | 0.30262 | 0.25012 | 2.2346 | FALSE | 2024-01-21 01:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | line_4567_22 | ACLineSegment | Line | 0.034884 | 0.0071664 | 0.0037108 | 20.5437 | FALSE | 2024-01-21 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_4709_22 | ACLineSegment | Line | 13.5424 | 0.23528 | 0.19281 | 1.7373 | FALSE | 2024-01-20 16:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | line_5743_22 | ACLineSegment | Line | 13.5424 | 0.23876 | 0.19611 | 1.7631 | FALSE | 2024-01-20 16:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | line_474_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_6119_22 | ACLineSegment | Line | 0.025406 | 0.0042656 | 0.0024251 | 16.7898 | FALSE | 2024-01-17 18:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | tr_1124_22 | Transformer | Transformer | 0.02375 | 0.0042656 | 0.0024251 | 17.9603 | FALSE | 2024-01-17 18:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_141 | line_4849_22 | ACLineSegment | Line | 12.3112 | 0.0049529 | 0.0036329 | 0.040231 | FALSE | 2024-01-17 21:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | line_6059_22 | ACLineSegment | Line | 12.3112 | 0.030612 | 0.021935 | 0.24865 | FALSE | 2024-01-20 05:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | line_6060_22 | ACLineSegment | Line | 12.3112 | 0.037951 | 0.028436 | 0.30827 | FALSE | 2024-01-21 02:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | line_4878_22 | ACLineSegment | Line | 12.3112 | 0.25463 | 0.20957 | 2.0683 | FALSE | 2024-01-20 09:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | line_4879_22 | ACLineSegment | Line | 13.5424 | 0.25058 | 0.20661 | 1.8504 | FALSE | 2024-01-20 09:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | tr_518_22 | Transformer | Transformer | 0.02375 | 0.0057939 | 0.0035828 | 24.3954 | FALSE | 2024-01-20 07:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_141 | line_4880_22 | ACLineSegment | Line | 0.025406 | 0.0057939 | 0.0035828 | 22.8055 | FALSE | 2024-01-20 07:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_493_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_6176_22 | ACLineSegment | Line | 0.51338 | 0.0083734 | 0.0060834 | 1.631 | FALSE | 2024-07-15 05:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | tr_1150_22 | Transformer | Transformer | 0.285 | 0.0083734 | 0.0060834 | 2.938 | FALSE | 2024-07-15 05:00 |  |  | 300 | 3 | Transformer_kVA_x_PF
GSO_141 | line_524_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_6242_22 | ACLineSegment | Line | 0.51338 | 0.0077182 | 0.0054988 | 1.5034 | FALSE | 2024-01-20 20:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | tr_1181_22 | Transformer | Transformer | 0.285 | 0.0077182 | 0.0054988 | 2.7081 | FALSE | 2024-01-20 20:00 |  |  | 300 | 3 | Transformer_kVA_x_PF
GSO_141 | line_5409_22 | ACLineSegment | Line | 0.034884 | 0.0080252 | 0.0041444 | 23.0056 | FALSE | 2024-01-20 14:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_5410_22 | ACLineSegment | Line | 0.034884 | 0.0040221 | 0.0024336 | 11.5302 | FALSE | 2024-01-20 22:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_5448_22 | ACLineSegment | Line | 13.5424 | 0.026423 | 0.018147 | 0.19512 | FALSE | 2024-07-15 07:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | line_565_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_6295_22 | ACLineSegment | Line | 0.025406 | 0.0048706 | 0.0037948 | 19.1713 | FALSE | 2024-07-10 10:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | tr_1211_22 | Transformer | Transformer | 0.02375 | 0.0048706 | 0.0037948 | 20.5078 | FALSE | 2024-07-10 10:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_141 | line_5658_22 | ACLineSegment | Line | 12.3112 | 0.25863 | 0.21316 | 2.1007 | FALSE | 2024-01-20 09:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | line_6471_22 | ACLineSegment | Line | 12.3112 | 0.29773 | 0.24597 | 2.4184 | FALSE | 2024-01-20 09:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | line_6887_22 | ACLineSegment | Line | 12.3112 | 0.017784 | 0.0126 | 0.14446 | FALSE | 2024-07-15 07:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | line_5659_22 | ACLineSegment | Line | 0.51338 | 0.0054829 | 0.0042782 | 1.068 | FALSE | 2024-01-20 13:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | tr_900_22 | Transformer | Transformer | 0.095 | 0.0054829 | 0.0042782 | 5.7714 | FALSE | 2024-01-20 13:00 |  |  | 100 | 3 | Transformer_kVA_x_PF
GSO_141 | line_5676_22 | ACLineSegment | Line | 12.3112 | 0.069782 | 0.056131 | 0.56682 | FALSE | 2024-01-21 01:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | line_5677_22 | ACLineSegment | Line | 12.3112 | 0.085349 | 0.069025 | 0.69326 | FALSE | 2024-01-21 01:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | line_5932_22 | ACLineSegment | Line | 12.3112 | 0.00603 | 0.0045444 | 0.04898 | FALSE | 2024-01-21 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | line_6241_22 | ACLineSegment | Line | 12.3112 | 0.011943 | 0.0093127 | 0.097011 | FALSE | 2024-07-05 09:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | line_6007_22 | ACLineSegment | Line | 12.3112 | 0.066324 | 0.052907 | 0.53873 | FALSE | 2024-01-21 01:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | line_6175_22 | ACLineSegment | Line | 12.3112 | 0.049124 | 0.038982 | 0.39902 | FALSE | 2024-01-20 09:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | tr_1378_22 | Transformer | Transformer | 0.02375 | 0.0085806 | 0.0063579 | 36.1288 | FALSE | 2024-06-23 19:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_141 | line_6118_22 | ACLineSegment | Line | 12.3112 | 0.012677 | 0.0073006 | 0.10297 | FALSE | 2024-01-20 14:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | line_6174_22 | ACLineSegment | Line | 12.3112 | 0.044842 | 0.034318 | 0.36424 | FALSE | 2024-01-21 02:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | tr_1306_22 | Transformer | Transformer | 0.1425 | 0.0047584 | 0.0033767 | 3.3392 | FALSE | 2024-01-18 02:00 |  |  | 150 | 3 | Transformer_kVA_x_PF
GSO_141 | line_6294_22 | ACLineSegment | Line | 12.3112 | 0.041561 | 0.03166 | 0.33758 | FALSE | 2024-01-21 02:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | line_631_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_6363_22 | ACLineSegment | Line | 0.51338 | 0.010107 | 0.0068053 | 1.9687 | FALSE | 2024-01-18 01:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | tr_1250_22 | Transformer | Transformer | 0.285 | 0.010107 | 0.0068053 | 3.5462 | FALSE | 2024-01-18 01:00 |  |  | 300 | 3 | Transformer_kVA_x_PF
GSO_141 | line_6454_22 | ACLineSegment | Line | 0.51338 | 0.0047584 | 0.0033767 | 0.92688 | FALSE | 2024-01-18 02:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | line_689_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | tr_1316_22 | Transformer | Transformer | 0.95 | 0.0066095 | 0.0052297 | 0.69573 | FALSE | 2024-07-15 11:00 |  |  | 1000 | 3 | Transformer_kVA_x_PF
GSO_141 | line_6473_22 | ACLineSegment | Line | 0.51338 | 0.0066095 | 0.0052297 | 1.2874 | FALSE | 2024-07-15 11:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_141 | line_708_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_6551_22 | ACLineSegment | Line | 0.025406 | 0.0085806 | 0.0063579 | 33.7742 | FALSE | 2024-06-23 19:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_141 | line_786_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_4226_22 | ACLineSegment | Line | 13.5424 | 0.46949 | 0.37429 | 3.4668 | FALSE | 2024-01-21 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | tr_1353_22 | Transformer | Transformer | 0.1425 | 0.0038701 | 0.0028317 | 2.7158 | FALSE | 2024-07-14 08:00 |  |  | 150 | 3 | Transformer_kVA_x_PF
GSO_145 | line_5362_22 | ACLineSegment | Line | 0.94778 | 0.0090058 | 0.006152 | 0.9502 | FALSE | 2024-01-20 11:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_5834_22 | ACLineSegment | Line | 13.5424 | 0.0065819 | 0.005007 | 0.048603 | FALSE | 2024-01-21 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | tr_987_22 | Transformer | Transformer | 0.07125 | 0.0058832 | 0.0044453 | 8.2571 | FALSE | 2024-01-20 09:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_145 | line_5835_22 | ACLineSegment | Line | 0.94778 | 0.0013471 | 0.0008159 | 0.14213 | FALSE | 2024-01-20 11:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_4225_22 | ACLineSegment | Line | 13.5424 | 0.47644 | 0.37989 | 3.5182 | FALSE | 2024-01-21 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | tr_262_22 | Transformer | Transformer | 0.02375 | 0.0077334 | 0.0051572 | 32.5615 | FALSE | 2024-01-20 13:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_145 | line_4219_22 | ACLineSegment | Line | 0.94778 | 0.0028558 | 0.0018845 | 0.30131 | FALSE | 2024-01-20 23:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | tr_676_22 | Transformer | Transformer | 0.02375 | 0.0057832 | 0.0034791 | 24.3504 | FALSE | 2024-01-17 14:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_145 | line_4287_22 | ACLineSegment | Line | 0.94778 | 0.013701 | 0.00845 | 1.4456 | FALSE | 2024-07-15 05:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_5816_22 | ACLineSegment | Line | 13.5424 | 0.0419 | 0.027867 | 0.3094 | FALSE | 2024-07-15 08:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_6370_22 | ACLineSegment | Line | 13.5424 | 0.029056 | 0.01993 | 0.21455 | FALSE | 2024-01-17 08:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | tr_1416_22 | Transformer | Transformer | 0.095 | 0.0084582 | 0.005139 | 8.9034 | FALSE | 2024-07-15 08:00 |  |  | 100 | 3 | Transformer_kVA_x_PF
GSO_145 | tr_285_22 | Transformer | Transformer | 0.02375 | 0.010987 | 0.0049027 | 46.2627 | FALSE | 2024-01-20 18:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_145 | line_5474_22 | ACLineSegment | Line | 13.5424 | 0.0063911 | 0.0038897 | 0.047194 | FALSE | 2024-07-05 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_6492_22 | ACLineSegment | Line | 13.5424 | 0.012166 | 0.0081803 | 0.089836 | FALSE | 2024-01-21 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | tr_1329_22 | Transformer | Transformer | 0.1425 | 0.0040936 | 0.0028881 | 2.8727 | FALSE | 2024-01-21 02:00 |  |  | 150 | 3 | Transformer_kVA_x_PF
GSO_145 | tr_394_22 | Transformer | Transformer | 0.02375 | 0.0043565 | 0.0022743 | 18.3432 | FALSE | 2024-01-21 01:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_145 | line_4785_22 | ACLineSegment | Line | 13.5424 | 0.051815 | 0.036223 | 0.38261 | FALSE | 2024-07-15 08:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_4787_22 | ACLineSegment | Line | 13.5424 | 0.044576 | 0.030585 | 0.32916 | FALSE | 2024-07-15 08:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_4788_22 | ACLineSegment | Line | 13.5424 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | tr_477_22 | Transformer | Transformer | 0.07125 | 0.0051045 | 0.0037759 | 7.1643 | FALSE | 2024-01-20 11:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_145 | line_4786_22 | ACLineSegment | Line | 0.94778 | 0.0055711 | 0.002771 | 0.58781 | FALSE | 2024-01-20 10:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_5164_22 | ACLineSegment | Line | 13.5424 | 0.59469 | 0.47596 | 4.3914 | FALSE | 2024-01-21 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_5166_22 | ACLineSegment | Line | 13.5424 | 0.62174 | 0.49846 | 4.5911 | FALSE | 2024-01-21 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | tr_651_22 | Transformer | Transformer | 0.02375 | 0.0062144 | 0.0035082 | 26.166 | FALSE | 2024-07-15 20:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_145 | line_5165_22 | ACLineSegment | Line | 0.94778 | 0.030247 | 0.020512 | 3.1914 | FALSE | 2024-01-21 02:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_1021_22 | ACLineSegment | Line | 0.034884 | 0.030541 | 0.019658 | 87.5506 | FALSE | 2024-01-20 19:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_950_22 | ACLineSegment | Line | 0.034884 | 0.012549 | 0.008173 | 35.9737 | FALSE | 2024-07-15 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_963_22 | ACLineSegment | Line | 0.034884 | 0.004719 | 0.0027146 | 13.5278 | FALSE | 2024-07-16 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | tr_1148_22 | Transformer | Transformer | 0.0475 | 0.042207 | 0.0302 | 88.8561 | FALSE | 2024-01-20 19:00 |  |  | 50 | 1 | Transformer_kVA_x_PF
GSO_145 | line_1022_22 | ACLineSegment | Line | 0.034884 | 0.0046229 | 0.0025232 | 13.2524 | FALSE | 2024-07-15 13:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_925_22 | ACLineSegment | Line | 0.034884 | 0.015228 | 0.0093528 | 43.6534 | FALSE | 2024-01-20 18:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_938_22 | ACLineSegment | Line | 0.034884 | 0.012498 | 0.0083251 | 35.8277 | FALSE | 2024-01-17 14:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_1045_22 | ACLineSegment | Line | 0.034884 | 0.005156 | 0.0026516 | 14.7807 | FALSE | 2024-01-20 06:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_983_22 | ACLineSegment | Line | 0.034884 | 0.005156 | 0.0026516 | 14.7807 | FALSE | 2024-01-20 06:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_1650_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_1651_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_4282_22 | ACLineSegment | Line | 0.034884 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_4283_22 | ACLineSegment | Line | 0.034884 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | tr_280_22 | Transformer | Transformer | 0.02375 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_145 | line_1719_22 | ACLineSegment | Line | 0.034884 | 0.0037904 | 0.0019946 | 10.866 | FALSE | 2024-01-21 04:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_1721_22 | ACLineSegment | Line | 0.034884 | 0.006583 | 0.0037322 | 18.8714 | FALSE | 2024-01-20 15:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | tr_282_22 | Transformer | Transformer | 0.02375 | 0.0090812 | 0.0055208 | 38.2367 | FALSE | 2024-07-15 05:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_145 | line_1720_22 | ACLineSegment | Line | 0.025406 | 0.0037904 | 0.0019946 | 14.9196 | FALSE | 2024-01-21 04:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_1722_22 | ACLineSegment | Line | 0.034884 | 0.006583 | 0.0037322 | 18.8714 | FALSE | 2024-01-20 15:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_1729_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_4295_22 | ACLineSegment | Line | 0.034884 | 0.010987 | 0.0049027 | 31.4974 | FALSE | 2024-01-20 18:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_1774_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_4398_22 | ACLineSegment | Line | 0.22905 | 0.0076554 | 0.0056382 | 3.3423 | FALSE | 2024-01-20 21:00 | 290 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | tr_323_22 | Transformer | Transformer | 0.07125 | 0.0076554 | 0.0056382 | 10.7445 | FALSE | 2024-01-20 21:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_145 | line_1835_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_4374_22 | ACLineSegment | Line | 0.51338 | 0.0051071 | 0.0037548 | 0.9948 | FALSE | 2024-01-20 10:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | tr_313_22 | Transformer | Transformer | 0.1425 | 0.0051071 | 0.0037548 | 3.5839 | FALSE | 2024-01-20 10:00 |  |  | 150 | 3 | Transformer_kVA_x_PF
GSO_145 | line_1845_22 | ACLineSegment | Line | 0.034884 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_1848_22 | ACLineSegment | Line | 0.034884 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_1846_22 | ACLineSegment | Line | 0.034884 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_1847_22 | ACLineSegment | Line | 0.034884 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_1849_22 | ACLineSegment | Line | 0.034884 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | tr_317_22 | Transformer | Transformer | 0.02375 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_145 | line_1850_22 | ACLineSegment | Line | 0.034884 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_1925_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_4472_22 | ACLineSegment | Line | 0.22905 | 0.02039 | 0.016809 | 8.9021 | FALSE | 2024-07-16 | 290 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | tr_352_22 | Transformer | Transformer | 0.07125 | 0.02039 | 0.016809 | 28.6175 | FALSE | 2024-07-16 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_145 | line_1960_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_4517_22 | ACLineSegment | Line | 0.51338 | 0.0085615 | 0.005836 | 1.6677 | FALSE | 2024-01-21 06:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | tr_368_22 | Transformer | Transformer | 0.285 | 0.0085615 | 0.005836 | 3.004 | FALSE | 2024-01-21 06:00 |  |  | 300 | 3 | Transformer_kVA_x_PF
GSO_145 | line_1985_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_4586_22 | ACLineSegment | Line | 0.034884 | 0.0043565 | 0.0022743 | 12.4887 | FALSE | 2024-01-21 01:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2000_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_4636_22 | ACLineSegment | Line | 0.51338 | 0.0057488 | 0.0042441 | 1.1198 | FALSE | 2024-01-17 20:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | tr_413_22 | Transformer | Transformer | 0.475 | 0.0057488 | 0.0042441 | 1.2103 | FALSE | 2024-01-17 20:00 |  |  | 500 | 3 | Transformer_kVA_x_PF
GSO_145 | line_2012_22 | ACLineSegment | Line | 0.034884 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2013_22 | ACLineSegment | Line | 0.034884 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2014_22 | ACLineSegment | Line | 0.034884 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_4617_22 | ACLineSegment | Line | 0.034884 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | tr_406_22 | Transformer | Transformer | 0.02375 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_145 | line_2035_22 | ACLineSegment | Line | 0.51338 | 0.0052655 | 0.0037273 | 1.0257 | FALSE | 2024-07-16 03:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_2037_22 | ACLineSegment | Line | 0.51338 | 0.02778 | 0.020898 | 5.4111 | FALSE | 2024-01-21 02:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_2038_22 | ACLineSegment | Line | 0.51338 | 0.024143 | 0.017742 | 4.7028 | FALSE | 2024-01-21 04:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_2036_22 | ACLineSegment | Line | 0.51338 | 0.0052655 | 0.0037273 | 1.0257 | FALSE | 2024-07-16 03:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | tr_453_22 | Transformer | Transformer | 0.095 | 0.02778 | 0.020898 | 29.2418 | FALSE | 2024-01-21 02:00 |  |  | 100 | 3 | Transformer_kVA_x_PF
GSO_145 | line_2057_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_4720_22 | ACLineSegment | Line | 0.51338 | 0.006772 | 0.0043339 | 1.3191 | FALSE | 2024-07-16 03:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | tr_449_22 | Transformer | Transformer | 0.285 | 0.006772 | 0.0043339 | 2.3762 | FALSE | 2024-07-16 03:00 |  |  | 300 | 3 | Transformer_kVA_x_PF
GSO_145 | line_2064_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_4734_22 | ACLineSegment | Line | 0.51338 | 0.0054199 | 0.0038741 | 1.0557 | FALSE | 2024-01-21 01:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | tr_455_22 | Transformer | Transformer | 0.07125 | 0.0054199 | 0.0038741 | 7.6068 | FALSE | 2024-01-21 01:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_145 | line_2095_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_4789_22 | ACLineSegment | Line | 0.51338 | 0.0051045 | 0.0037759 | 0.9943 | FALSE | 2024-01-20 11:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_2170_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_5167_22 | ACLineSegment | Line | 0.034884 | 0.0062144 | 0.0035082 | 17.8148 | FALSE | 2024-07-15 20:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_222_22 | ACLineSegment | Line | 0.034884 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_224_22 | ACLineSegment | Line | 0.034884 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | tr_503_22 | Transformer | Transformer | 0.02375 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_145 | line_223_22 | ACLineSegment | Line | 0.034884 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_225_22 | ACLineSegment | Line | 0.034884 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_239_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_5248_22 | ACLineSegment | Line | 0.51338 | 0.0065632 | 0.0046409 | 1.2784 | FALSE | 2024-07-14 22:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | tr_685_22 | Transformer | Transformer | 0.07125 | 0.0065632 | 0.0046409 | 9.2115 | FALSE | 2024-07-14 22:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_145 | line_256_22 | ACLineSegment | Line | 0.034884 | 0.0091552 | 0.0058159 | 26.2449 | FALSE | 2024-01-21 13:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_258_22 | ACLineSegment | Line | 0.034884 | 0.0091552 | 0.0058159 | 26.2449 | FALSE | 2024-01-21 13:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_257_22 | ACLineSegment | Line | 0.034884 | 0.0091552 | 0.0058159 | 26.2449 | FALSE | 2024-01-21 13:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_260_22 | ACLineSegment | Line | 0.034884 | 0.0050878 | 0.0026957 | 14.585 | FALSE | 2024-01-20 20:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_5274_22 | ACLineSegment | Line | 0.034884 | 0.034899 | 0.022104 | 100.0432 | TRUE | 2024-01-17 23:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | tr_695_22 | Transformer | Transformer | 0.0475 | 0.043788 | 0.028645 | 92.1845 | FALSE | 2024-01-17 23:00 |  |  | 50 | 1 | Transformer_kVA_x_PF
GSO_145 | line_261_22 | ACLineSegment | Line | 0.025406 | 0.0050878 | 0.0026957 | 20.026 | FALSE | 2024-01-20 20:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2605_22 | ACLineSegment | Line | 0.51338 | 0.023639 | 0.015768 | 4.6046 | FALSE | 2024-01-21 04:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | tr_681_22 | Transformer | Transformer | 0.285 | 0.023639 | 0.015768 | 8.2943 | FALSE | 2024-01-21 04:00 |  |  | 300 | 3 | Transformer_kVA_x_PF
GSO_145 | line_2606_22 | ACLineSegment | Line | 0.51338 | 0.023639 | 0.015768 | 4.6046 | FALSE | 2024-01-21 04:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_263_22 | ACLineSegment | Line | 0.034884 | 0.0037736 | 0.0023505 | 10.8178 | FALSE | 2024-01-17 20:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_267_22 | ACLineSegment | Line | 0.034884 | 0.0037736 | 0.0023505 | 10.8178 | FALSE | 2024-01-17 20:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_264_22 | ACLineSegment | Line | 0.034884 | 0.0037736 | 0.0023505 | 10.8178 | FALSE | 2024-01-17 20:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2633_22 | ACLineSegment | Line | 0.034884 | 0.0027899 | 0.001556 | 7.9978 | FALSE | 2024-07-15 05:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2635_22 | ACLineSegment | Line | 0.034884 | 0.0032111 | 0.0017462 | 9.2053 | FALSE | 2024-01-20 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | tr_679_22 | Transformer | Transformer | 0.02375 | 0.0055429 | 0.0031183 | 23.3385 | FALSE | 2024-01-20 10:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_145 | line_2634_22 | ACLineSegment | Line | 0.034884 | 0.0027899 | 0.001556 | 7.9978 | FALSE | 2024-07-15 05:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2636_22 | ACLineSegment | Line | 0.034884 | 0.0032111 | 0.0017462 | 9.2053 | FALSE | 2024-01-20 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2649_22 | ACLineSegment | Line | 0.025406 | 0.0024947 | 0.0014176 | 9.8196 | FALSE | 2024-01-20 20:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2650_22 | ACLineSegment | Line | 0.025406 | 0.0057832 | 0.0034791 | 22.7634 | FALSE | 2024-01-17 14:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2651_22 | ACLineSegment | Line | 0.025406 | 0.0037174 | 0.0021904 | 14.6321 | FALSE | 2024-07-15 06:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2652_22 | ACLineSegment | Line | 0.025406 | 0.0024947 | 0.0014176 | 9.8196 | FALSE | 2024-01-20 20:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_265_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_266_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_5270_22 | ACLineSegment | Line | 0.034884 | 0.0059491 | 0.0034686 | 17.0542 | FALSE | 2024-01-20 14:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_5271_22 | ACLineSegment | Line | 0.034884 | 0.0035497 | 0.0018073 | 10.1758 | FALSE | 2024-01-20 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_5272_22 | ACLineSegment | Line | 0.034884 | 0.0044252 | 0.0023401 | 12.6856 | FALSE | 2024-01-20 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | tr_694_22 | Transformer | Transformer | 0.02375 | 0.015729 | 0.0093805 | 66.2268 | FALSE | 2024-01-20 10:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_145 | line_2657_22 | ACLineSegment | Line | 0.51338 | 0.027571 | 0.017864 | 5.3704 | FALSE | 2024-01-20 10:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | tr_786_22 | Transformer | Transformer | 0.285 | 0.027571 | 0.017864 | 9.6739 | FALSE | 2024-01-20 10:00 |  |  | 300 | 3 | Transformer_kVA_x_PF
GSO_145 | line_2658_22 | ACLineSegment | Line | 0.51338 | 0.027571 | 0.017864 | 5.3704 | FALSE | 2024-01-20 10:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_2766_22 | ACLineSegment | Line | 0.51338 | 0.0063911 | 0.0038897 | 1.2449 | FALSE | 2024-07-05 04:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | tr_800_22 | Transformer | Transformer | 0.07125 | 0.0063911 | 0.0038897 | 8.97 | FALSE | 2024-07-05 04:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_145 | line_2767_22 | ACLineSegment | Line | 0.51338 | 0.0063911 | 0.0038897 | 1.2449 | FALSE | 2024-07-05 04:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_2778_22 | ACLineSegment | Line | 0.034884 | 0.0050148 | 0.0025406 | 14.376 | FALSE | 2024-01-20 16:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2779_22 | ACLineSegment | Line | 0.034884 | 0.0074025 | 0.0045625 | 21.2206 | FALSE | 2024-01-20 14:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2780_22 | ACLineSegment | Line | 0.034884 | 0.0038483 | 0.002344 | 11.0318 | FALSE | 2024-07-15 06:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2787_22 | ACLineSegment | Line | 0.034884 | 0.0050148 | 0.0025406 | 14.376 | FALSE | 2024-01-20 16:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2784_22 | ACLineSegment | Line | 0.034884 | 0.010713 | 0.0068826 | 30.7114 | FALSE | 2024-01-20 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | tr_805_22 | Transformer | Transformer | 0.02375 | 0.017521 | 0.011229 | 73.7715 | FALSE | 2024-01-20 10:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_145 | line_2781_22 | ACLineSegment | Line | 0.034884 | 0.0063492 | 0.0038029 | 18.2012 | FALSE | 2024-01-17 17:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2785_22 | ACLineSegment | Line | 0.034884 | 0.0056723 | 0.0032572 | 16.2606 | FALSE | 2024-01-20 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2782_22 | ACLineSegment | Line | 0.034884 | 0.0036121 | 0.0021213 | 10.3547 | FALSE | 2024-01-17 17:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2783_22 | ACLineSegment | Line | 0.034884 | 0.0032895 | 0.0018073 | 9.43 | FALSE | 2024-01-20 13:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2786_22 | ACLineSegment | Line | 0.034884 | 0.0036121 | 0.0021213 | 10.3547 | FALSE | 2024-01-17 17:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2820_22 | ACLineSegment | Line | 0.51338 | 0.0073266 | 0.0051705 | 1.4271 | FALSE | 2024-01-17 10:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | tr_802_22 | Transformer | Transformer | 0.1425 | 0.0073266 | 0.0051705 | 5.1415 | FALSE | 2024-01-17 10:00 |  |  | 150 | 3 | Transformer_kVA_x_PF
GSO_145 | line_2821_22 | ACLineSegment | Line | 0.51338 | 0.0073266 | 0.0051705 | 1.4271 | FALSE | 2024-01-17 10:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_2851_22 | ACLineSegment | Line | 0.51338 | 0.0054088 | 0.004126 | 1.0536 | FALSE | 2024-07-06 02:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | tr_819_22 | Transformer | Transformer | 0.07125 | 0.0054088 | 0.004126 | 7.5914 | FALSE | 2024-07-06 02:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_145 | line_2852_22 | ACLineSegment | Line | 0.51338 | 0.0054088 | 0.004126 | 1.0536 | FALSE | 2024-07-06 02:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_2877_22 | ACLineSegment | Line | 0.034884 | 0.0047232 | 0.0030928 | 13.5399 | FALSE | 2024-05-13 16:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2878_22 | ACLineSegment | Line | 0.034884 | 0.027562 | 0.017806 | 79.0127 | FALSE | 2024-01-20 11:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2879_22 | ACLineSegment | Line | 0.034884 | 0.018993 | 0.012738 | 54.4468 | FALSE | 2024-01-20 23:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2880_22 | ACLineSegment | Line | 0.034884 | 0.0070351 | 0.003825 | 20.1673 | FALSE | 2024-07-15 04:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2881_22 | ACLineSegment | Line | 0.034884 | 0.0047232 | 0.0030928 | 13.5399 | FALSE | 2024-05-13 16:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2885_22 | ACLineSegment | Line | 0.034884 | 0.022039 | 0.014678 | 63.1793 | FALSE | 2024-01-20 11:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2886_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2887_22 | ACLineSegment | Line | 0.046073 | 0.055783 | 0.037065 | 121.0767 | TRUE | 2024-01-20 11:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2888_22 | ACLineSegment | Line | 0.034884 | 0.0050333 | 0.0026033 | 14.429 | FALSE | 2024-01-20 23:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2889_22 | ACLineSegment | Line | 0.034884 | 0.0051134 | 0.0027965 | 14.6584 | FALSE | 2024-01-20 08:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2894_22 | ACLineSegment | Line | 0.034884 | 0.014183 | 0.0086638 | 40.6595 | FALSE | 2024-01-20 22:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2895_22 | ACLineSegment | Line | 0.034884 | 0.0073295 | 0.0043785 | 21.0112 | FALSE | 2024-01-20 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2882_22 | ACLineSegment | Line | 0.034884 | 0.0082857 | 0.0048756 | 23.7524 | FALSE | 2024-07-15 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2899_22 | ACLineSegment | Line | 0.034884 | 0.0082857 | 0.0048756 | 23.7524 | FALSE | 2024-07-15 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2883_22 | ACLineSegment | Line | 0.034884 | 0.0035565 | 0.0020719 | 10.1955 | FALSE | 2024-01-21 01:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2884_22 | ACLineSegment | Line | 0.034884 | 0.0056307 | 0.0029958 | 16.1414 | FALSE | 2024-01-17 14:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2890_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2891_22 | ACLineSegment | Line | 0.034884 | 0.012508 | 0.0078057 | 35.8559 | FALSE | 2024-07-15 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2892_22 | ACLineSegment | Line | 0.034884 | 0.0071137 | 0.0041704 | 20.3926 | FALSE | 2024-01-21 04:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2893_22 | ACLineSegment | Line | 0.034884 | 0.0058632 | 0.0031994 | 16.808 | FALSE | 2024-07-15 22:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | tr_724_22 | Transformer | Transformer | 0.0475 | 0.055783 | 0.037065 | 117.4382 | TRUE | 2024-01-20 11:00 |  |  | 50 | 1 | Transformer_kVA_x_PF
GSO_145 | line_2900_22 | ACLineSegment | Line | 0.034884 | 0.010534 | 0.0062352 | 30.1984 | FALSE | 2024-07-15 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2901_22 | ACLineSegment | Line | 0.034884 | 0.0031978 | 0.0017144 | 9.1671 | FALSE | 2024-01-21 02:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2897_22 | ACLineSegment | Line | 0.034884 | 0.010802 | 0.0069246 | 30.9659 | FALSE | 2024-01-20 06:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2905_22 | ACLineSegment | Line | 0.034884 | 0.0036908 | 0.001907 | 10.5804 | FALSE | 2024-01-20 22:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2896_22 | ACLineSegment | Line | 0.034884 | 0.0062383 | 0.0035726 | 17.8832 | FALSE | 2024-01-21 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2898_22 | ACLineSegment | Line | 0.034884 | 0.0062292 | 0.0036659 | 17.8571 | FALSE | 2024-01-20 12:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2903_22 | ACLineSegment | Line | 0.034884 | 0.0062383 | 0.0035726 | 17.8832 | FALSE | 2024-01-21 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2902_22 | ACLineSegment | Line | 0.034884 | 0.0026208 | 0.0015492 | 7.513 | FALSE | 2024-07-15 21:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2907_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_5349_22 | ACLineSegment | Line | 0.51338 | 0.0085295 | 0.0057278 | 1.6614 | FALSE | 2024-01-20 17:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | tr_726_22 | Transformer | Transformer | 0.285 | 0.0085295 | 0.0057278 | 2.9928 | FALSE | 2024-01-20 17:00 |  |  | 300 | 3 | Transformer_kVA_x_PF
GSO_145 | line_2923_22 | ACLineSegment | Line | 0.034884 | 0.01292 | 0.0076636 | 37.0389 | FALSE | 2024-01-20 19:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2924_22 | ACLineSegment | Line | 0.034884 | 0.018697 | 0.011254 | 53.5989 | FALSE | 2024-01-20 07:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2925_22 | ACLineSegment | Line | 0.034884 | 0.0032107 | 0.0018791 | 9.2042 | FALSE | 2024-01-20 07:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2926_22 | ACLineSegment | Line | 0.034884 | 0.0041067 | 0.0020797 | 11.7727 | FALSE | 2024-01-20 11:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2936_22 | ACLineSegment | Line | 0.034884 | 0.01292 | 0.0076636 | 37.0389 | FALSE | 2024-01-20 19:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2951_22 | ACLineSegment | Line | 0.034884 | 0.021819 | 0.013503 | 62.5489 | FALSE | 2024-01-20 07:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2952_22 | ACLineSegment | Line | 0.034884 | 0.0055737 | 0.0025408 | 15.9781 | FALSE | 2024-01-21 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2927_22 | ACLineSegment | Line | 0.034884 | 0.030563 | 0.019566 | 87.6158 | FALSE | 2024-01-20 14:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2928_22 | ACLineSegment | Line | 0.034884 | 0.030563 | 0.019566 | 87.6158 | FALSE | 2024-01-20 14:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2947_22 | ACLineSegment | Line | 0.034884 | 0.028424 | 0.017449 | 81.4831 | FALSE | 2024-01-20 18:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2950_22 | ACLineSegment | Line | 0.034884 | 0.0046332 | 0.0022973 | 13.2819 | FALSE | 2024-01-20 16:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_5402_22 | ACLineSegment | Line | 0.034884 | 0.0041844 | 0.002393 | 11.9953 | FALSE | 2024-01-20 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | tr_751_22 | Transformer | Transformer | 0.0475 | 0.052815 | 0.035173 | 111.1893 | TRUE | 2024-01-21 03:00 |  |  | 50 | 1 | Transformer_kVA_x_PF
GSO_145 | line_2929_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2930_22 | ACLineSegment | Line | 0.034884 | 0.017622 | 0.0091477 | 50.5156 | FALSE | 2024-01-20 18:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2931_22 | ACLineSegment | Line | 0.034884 | 0.02552 | 0.015398 | 73.1583 | FALSE | 2024-01-20 18:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2932_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2933_22 | ACLineSegment | Line | 0.034884 | 0.0047093 | 0.0021688 | 13.5001 | FALSE | 2024-01-20 23:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2934_22 | ACLineSegment | Line | 0.034884 | 0.0039298 | 0.0019647 | 11.2655 | FALSE | 2024-01-21 01:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2935_22 | ACLineSegment | Line | 0.034884 | 0.0051588 | 0.0028354 | 14.7886 | FALSE | 2024-01-20 20:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2937_22 | ACLineSegment | Line | 0.034884 | 0.01181 | 0.0054651 | 33.8555 | FALSE | 2024-01-20 18:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2942_22 | ACLineSegment | Line | 0.034884 | 0.0073007 | 0.0040636 | 20.9289 | FALSE | 2024-01-20 11:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2948_22 | ACLineSegment | Line | 0.034884 | 0.0035735 | 0.002227 | 10.2441 | FALSE | 2024-01-18 04:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2940_22 | ACLineSegment | Line | 0.034884 | 0.0066855 | 0.0039668 | 19.1652 | FALSE | 2024-01-20 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2941_22 | ACLineSegment | Line | 0.034884 | 0.007911 | 0.0039761 | 22.6782 | FALSE | 2024-01-20 19:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2938_22 | ACLineSegment | Line | 0.034884 | 0.009028 | 0.0036258 | 25.8804 | FALSE | 2024-01-20 18:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2939_22 | ACLineSegment | Line | 0.034884 | 0.0037726 | 0.0020098 | 10.8149 | FALSE | 2024-01-20 12:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2949_22 | ACLineSegment | Line | 0.034884 | 0.009028 | 0.0036258 | 25.8804 | FALSE | 2024-01-20 18:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2943_22 | ACLineSegment | Line | 0.034884 | 0.0024815 | 0.0013958 | 7.1138 | FALSE | 2024-01-20 15:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2946_22 | ACLineSegment | Line | 0.034884 | 0.0045758 | 0.0027355 | 13.1174 | FALSE | 2024-01-20 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2944_22 | ACLineSegment | Line | 0.034884 | 0.0024815 | 0.0013958 | 7.1138 | FALSE | 2024-01-20 15:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_2981_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_5365_22 | ACLineSegment | Line | 0.51338 | 0.0051181 | 0.0039239 | 0.99695 | FALSE | 2024-06-26 22:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | tr_734_22 | Transformer | Transformer | 0.285 | 0.0051181 | 0.0039239 | 1.7958 | FALSE | 2024-06-26 22:00 |  |  | 300 | 3 | Transformer_kVA_x_PF
GSO_145 | line_3004_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_5368_22 | ACLineSegment | Line | 0.51338 | 0.0060248 | 0.0041726 | 1.1736 | FALSE | 2024-07-06 01:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | tr_735_22 | Transformer | Transformer | 0.1425 | 0.0060248 | 0.0041726 | 4.2279 | FALSE | 2024-07-06 01:00 |  |  | 150 | 3 | Transformer_kVA_x_PF
GSO_145 | line_3008_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_5392_22 | ACLineSegment | Line | 0.51338 | 0.0050443 | 0.0036326 | 0.98257 | FALSE | 2024-01-20 06:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | tr_746_22 | Transformer | Transformer | 0.285 | 0.0050443 | 0.0036326 | 1.7699 | FALSE | 2024-01-20 06:00 |  |  | 300 | 3 | Transformer_kVA_x_PF
GSO_145 | line_3250_22 | ACLineSegment | Line | 0.034884 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_3254_22 | ACLineSegment | Line | 0.034884 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_3251_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_3252_22 | ACLineSegment | Line | 0.034884 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_3253_22 | ACLineSegment | Line | 0.034884 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_3255_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_5632_22 | ACLineSegment | Line | 0.034884 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_5633_22 | ACLineSegment | Line | 0.034884 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | tr_888_22 | Transformer | Transformer | 0.02375 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_145 | line_3299_22 | ACLineSegment | Line | 0.034884 | 0.010373 | 0.005724 | 29.7355 | FALSE | 2024-07-15 06:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_3309_22 | ACLineSegment | Line | 0.034884 | 0.01514 | 0.0093193 | 43.4002 | FALSE | 2024-07-14 23:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_3310_22 | ACLineSegment | Line | 0.034884 | 0.0079958 | 0.0051553 | 22.9213 | FALSE | 2024-07-10 22:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_3300_22 | ACLineSegment | Line | 0.034884 | 0.010373 | 0.005724 | 29.7355 | FALSE | 2024-07-15 06:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_3313_22 | ACLineSegment | Line | 0.034884 | 0.0040589 | 0.0020608 | 11.6356 | FALSE | 2024-01-20 19:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_3314_22 | ACLineSegment | Line | 0.034884 | 0.0077549 | 0.0038375 | 22.2308 | FALSE | 2024-01-21 02:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_3301_22 | ACLineSegment | Line | 0.034884 | 0.010486 | 0.0066515 | 30.0608 | FALSE | 2024-07-16 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_3302_22 | ACLineSegment | Line | 0.034884 | 0.003677 | 0.0019278 | 10.5408 | FALSE | 2024-01-17 16:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_3303_22 | ACLineSegment | Line | 0.034884 | 0.017498 | 0.011879 | 50.1609 | FALSE | 2024-01-21 02:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_3304_22 | ACLineSegment | Line | 0.034884 | 0.0061506 | 0.0037608 | 17.6319 | FALSE | 2024-07-15 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_3305_22 | ACLineSegment | Line | 0.034884 | 0.0046607 | 0.0026991 | 13.3607 | FALSE | 2024-07-15 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_3306_22 | ACLineSegment | Line | 0.034884 | 0.0068294 | 0.0041539 | 19.5776 | FALSE | 2024-07-16 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_3308_22 | ACLineSegment | Line | 0.034884 | 0.003677 | 0.0019278 | 10.5408 | FALSE | 2024-01-17 16:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | tr_903_22 | Transformer | Transformer | 0.0475 | 0.030247 | 0.020512 | 63.6778 | FALSE | 2024-01-21 02:00 |  |  | 50 | 1 | Transformer_kVA_x_PF
GSO_145 | line_3307_22 | ACLineSegment | Line | 0.034884 | 0.0046607 | 0.0026991 | 13.3607 | FALSE | 2024-07-15 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_3317_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_5956_22 | ACLineSegment | Line | 0.51338 | 0.002696 | 0.0020993 | 0.52515 | FALSE | 2024-01-20 18:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | tr_1044_22 | Transformer | Transformer | 0.285 | 0.002696 | 0.0020993 | 0.94597 | FALSE | 2024-01-20 18:00 |  |  | 300 | 3 | Transformer_kVA_x_PF
GSO_145 | line_3367_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_5931_22 | ACLineSegment | Line | 0.51338 | 0.0067696 | 0.0046783 | 1.3186 | FALSE | 2024-01-21 03:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | tr_1032_22 | Transformer | Transformer | 0.07125 | 0.0067696 | 0.0046783 | 9.5012 | FALSE | 2024-01-21 03:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_145 | line_3412_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_5783_22 | ACLineSegment | Line | 0.025406 | 0.0057576 | 0.0042559 | 22.6626 | FALSE | 2024-01-20 21:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | tr_963_22 | Transformer | Transformer | 0.02375 | 0.0057576 | 0.0042559 | 24.2425 | FALSE | 2024-01-20 21:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_145 | line_345_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_6029_22 | ACLineSegment | Line | 0.22905 | 0.019509 | 0.013527 | 8.5177 | FALSE | 2024-01-17 18:00 | 290 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | tr_1079_22 | Transformer | Transformer | 0.07125 | 0.019509 | 0.013527 | 27.3817 | FALSE | 2024-01-17 18:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_145 | line_3472_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_5817_22 | ACLineSegment | Line | 0.51338 | 0.0045564 | 0.0034766 | 0.88753 | FALSE | 2024-01-21 13:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | tr_979_22 | Transformer | Transformer | 0.07125 | 0.0045564 | 0.0034766 | 6.3949 | FALSE | 2024-01-21 13:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_145 | line_3478_22 | ACLineSegment | Line | 0.51338 | 0.0049642 | 0.0037997 | 0.96695 | FALSE | 2024-07-15 10:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_3480_22 | ACLineSegment | Line | 0.51338 | 0.0037645 | 0.0028276 | 0.73327 | FALSE | 2024-01-17 16:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | tr_997_22 | Transformer | Transformer | 0.095 | 0.0074789 | 0.0058981 | 7.8725 | FALSE | 2024-01-20 12:00 |  |  | 100 | 3 | Transformer_kVA_x_PF
GSO_145 | line_3479_22 | ACLineSegment | Line | 0.51338 | 0.0049642 | 0.0037997 | 0.96695 | FALSE | 2024-07-15 10:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_3481_22 | ACLineSegment | Line | 0.51338 | 0.0037645 | 0.0028276 | 0.73327 | FALSE | 2024-01-17 16:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_3483_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_5865_22 | ACLineSegment | Line | 0.025406 | 0.016022 | 0.011561 | 63.0635 | FALSE | 2024-07-15 09:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | tr_1000_22 | Transformer | Transformer | 0.02375 | 0.016022 | 0.011561 | 67.46 | FALSE | 2024-07-15 09:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_145 | line_3520_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_5883_22 | ACLineSegment | Line | 0.51338 | 0.0054714 | 0.0039977 | 1.0658 | FALSE | 2024-01-20 14:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | tr_1007_22 | Transformer | Transformer | 0.1425 | 0.0054714 | 0.0039977 | 3.8395 | FALSE | 2024-01-20 14:00 |  |  | 150 | 3 | Transformer_kVA_x_PF
GSO_145 | line_359_22 | ACLineSegment | Line | 0.025406 | 0.011039 | 0.0099044 | 43.4523 | FALSE | 2024-01-21 07:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_361_22 | ACLineSegment | Line | 0.025406 | 0.0050527 | 0.0030701 | 19.8882 | FALSE | 2024-07-15 05:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | tr_1086_22 | Transformer | Transformer | 0.0475 | 0.015305 | 0.012216 | 32.2218 | FALSE | 2024-01-17 20:00 |  |  | 50 | 1 | Transformer_kVA_x_PF
GSO_145 | line_360_22 | ACLineSegment | Line | 0.025406 | 0.011039 | 0.0099044 | 43.4523 | FALSE | 2024-01-21 07:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_362_22 | ACLineSegment | Line | 0.025406 | 0.0050527 | 0.0030701 | 19.8882 | FALSE | 2024-07-15 05:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_378_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_6071_22 | ACLineSegment | Line | 0.51338 | 0.017559 | 0.012414 | 3.4203 | FALSE | 2024-01-20 21:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | tr_1101_22 | Transformer | Transformer | 0.285 | 0.017559 | 0.012414 | 6.1612 | FALSE | 2024-01-20 21:00 |  |  | 300 | 3 | Transformer_kVA_x_PF
GSO_145 | tr_260_22 | Transformer | Transformer | 0.02375 | 0.0028558 | 0.0018845 | 12.0242 | FALSE | 2024-01-20 23:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_145 | line_4220_22 | ACLineSegment | Line | 0.034884 | 0.0028558 | 0.0018845 | 8.1865 | FALSE | 2024-01-20 23:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_4279_22 | ACLineSegment | Line | 12.3112 | 0.48045 | 0.3834 | 3.9025 | FALSE | 2024-01-21 04:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | tr_279_22 | Transformer | Transformer | 0.1425 | 0.0056447 | 0.0042624 | 3.9612 | FALSE | 2024-07-05 07:00 |  |  | 150 | 3 | Transformer_kVA_x_PF
GSO_145 | line_4227_22 | ACLineSegment | Line | 0.034884 | 0.0077334 | 0.0051572 | 22.1691 | FALSE | 2024-01-20 13:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_4242_22 | ACLineSegment | Line | 13.5424 | 0.27394 | 0.21641 | 2.0228 | FALSE | 2024-01-21 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_4243_22 | ACLineSegment | Line | 13.5424 | 0.2916 | 0.23151 | 2.1533 | FALSE | 2024-01-21 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | tr_266_22 | Transformer | Transformer | 0.07125 | 0.0088106 | 0.0067394 | 12.3658 | FALSE | 2024-01-17 12:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_145 | line_4396_22 | ACLineSegment | Line | 13.5424 | 0.15858 | 0.12042 | 1.171 | FALSE | 2024-01-17 23:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_4397_22 | ACLineSegment | Line | 13.5424 | 0.12143 | 0.094277 | 0.89666 | FALSE | 2024-01-20 09:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_5609_22 | ACLineSegment | Line | 13.5424 | 0.29394 | 0.23405 | 2.1705 | FALSE | 2024-01-21 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | tr_878_22 | Transformer | Transformer | 0.07125 | 0.0045922 | 0.0034855 | 6.4452 | FALSE | 2024-01-20 17:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_145 | line_4244_22 | ACLineSegment | Line | 13.5424 | 0.018251 | 0.011358 | 0.13477 | FALSE | 2024-07-17 22:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_5671_22 | ACLineSegment | Line | 13.5424 | 0.012125 | 0.0061286 | 0.089535 | FALSE | 2024-07-05 21:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_4245_22 | ACLineSegment | Line | 0.51338 | 0.0088106 | 0.0067394 | 1.7162 | FALSE | 2024-01-17 12:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_4280_22 | ACLineSegment | Line | 0.51338 | 0.0056447 | 0.0042624 | 1.0995 | FALSE | 2024-07-05 07:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_4281_22 | ACLineSegment | Line | 0.94778 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_4288_22 | ACLineSegment | Line | 0.94778 | 0.0055429 | 0.0031183 | 0.58483 | FALSE | 2024-01-20 10:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_4319_22 | ACLineSegment | Line | 0.94778 | 0.0035275 | 0.0022168 | 0.37219 | FALSE | 2024-01-20 06:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | tr_733_22 | Transformer | Transformer | 0.02375 | 0.006216 | 0.004079 | 26.1725 | FALSE | 2024-07-14 11:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_145 | tr_295_22 | Transformer | Transformer | 0.02375 | 0.0035275 | 0.0022168 | 14.8526 | FALSE | 2024-01-20 06:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_145 | line_4320_22 | ACLineSegment | Line | 0.025406 | 0.0035275 | 0.0022168 | 13.8847 | FALSE | 2024-01-20 06:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_433_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_6099_22 | ACLineSegment | Line | 0.51338 | 0.0063626 | 0.0040797 | 1.2394 | FALSE | 2024-01-22 03:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | tr_1114_22 | Transformer | Transformer | 0.1425 | 0.0063626 | 0.0040797 | 4.465 | FALSE | 2024-01-22 03:00 |  |  | 150 | 3 | Transformer_kVA_x_PF
GSO_145 | line_4372_22 | ACLineSegment | Line | 12.3112 | 0.43333 | 0.34143 | 3.5198 | FALSE | 2024-01-21 04:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_4373_22 | ACLineSegment | Line | 12.3112 | 0.43807 | 0.34505 | 3.5583 | FALSE | 2024-01-21 04:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_4377_22 | ACLineSegment | Line | 0.94778 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_4848_22 | ACLineSegment | Line | 0.94778 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | tr_314_22 | Transformer | Transformer | 0.02375 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_145 | line_4382_22 | ACLineSegment | Line | 0.94778 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_4615_22 | ACLineSegment | Line | 0.94778 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_4616_22 | ACLineSegment | Line | 0.94778 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_6028_22 | ACLineSegment | Line | 13.5424 | 0.14225 | 0.10946 | 1.0504 | FALSE | 2024-01-17 23:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_6138_22 | ACLineSegment | Line | 13.5424 | 0.11751 | 0.090882 | 0.86773 | FALSE | 2024-01-20 18:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | tr_1134_22 | Transformer | Transformer | 0.07125 | 0.0060051 | 0.0045347 | 8.4282 | FALSE | 2024-01-21 07:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_145 | line_4400_22 | ACLineSegment | Line | 0.034884 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_48_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_4471_22 | ACLineSegment | Line | 13.5424 | 0.02039 | 0.016809 | 0.15056 | FALSE | 2024-07-16 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_5366_22 | ACLineSegment | Line | 13.5424 | 0.036561 | 0.029285 | 0.26997 | FALSE | 2024-07-15 16:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | tr_1371_22 | Transformer | Transformer | 0.285 | 0.0080882 | 0.0060959 | 2.838 | FALSE | 2024-07-15 06:00 |  |  | 300 | 3 | Transformer_kVA_x_PF
GSO_145 | line_4633_22 | ACLineSegment | Line | 13.5424 | 0.50643 | 0.40865 | 3.7396 | FALSE | 2024-01-21 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_6069_22 | ACLineSegment | Line | 13.5424 | 0.0057461 | 0.0044877 | 0.042431 | FALSE | 2024-07-06 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_6070_22 | ACLineSegment | Line | 13.5424 | 0.5231 | 0.42225 | 3.8627 | FALSE | 2024-01-21 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_4634_22 | ACLineSegment | Line | 13.5424 | 0.49894 | 0.40271 | 3.6843 | FALSE | 2024-01-21 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_4635_22 | ACLineSegment | Line | 13.5424 | 0.0044248 | 0.0034033 | 0.032674 | FALSE | 2024-01-21 10:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | tr_1205_22 | Transformer | Transformer | 0.1425 | 0.0060872 | 0.0046425 | 4.2717 | FALSE | 2024-01-20 07:00 |  |  | 150 | 3 | Transformer_kVA_x_PF
GSO_145 | tr_1449_22 | Transformer | Transformer | 0.475 | 0.0044248 | 0.0034033 | 0.93153 | FALSE | 2024-01-21 10:00 |  |  | 500 | 3 | Transformer_kVA_x_PF
GSO_145 | line_4718_22 | ACLineSegment | Line | 12.3112 | 0.020255 | 0.01604 | 0.16452 | FALSE | 2024-01-20 21:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_4719_22 | ACLineSegment | Line | 12.3112 | 0.016022 | 0.0124 | 0.13014 | FALSE | 2024-01-20 21:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_4729_22 | ACLineSegment | Line | 12.3112 | 0.02778 | 0.020898 | 0.22564 | FALSE | 2024-01-21 02:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_4733_22 | ACLineSegment | Line | 13.5424 | 0.0054199 | 0.0038741 | 0.040022 | FALSE | 2024-01-21 01:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_5247_22 | ACLineSegment | Line | 13.5424 | 0.0065632 | 0.0046409 | 0.048464 | FALSE | 2024-07-14 22:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_5497_22 | ACLineSegment | Line | 13.5424 | 0.014077 | 0.011293 | 0.10395 | FALSE | 2024-07-16 02:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_5401_22 | ACLineSegment | Line | 13.5424 | 0.097899 | 0.069392 | 0.72291 | FALSE | 2024-01-20 18:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | tr_935_22 | Transformer | Transformer | 0.02375 | 0.0055711 | 0.002771 | 23.4573 | FALSE | 2024-01-20 10:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_145 | line_5672_22 | ACLineSegment | Line | 13.5424 | 0.0044185 | 0.002374 | 0.032627 | FALSE | 2024-01-20 12:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | tr_1264_22 | Transformer | Transformer | 0.02375 | 0.0044185 | 0.002374 | 18.6041 | FALSE | 2024-01-20 12:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_145 | line_481_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_6139_22 | ACLineSegment | Line | 0.51338 | 0.0060051 | 0.0045347 | 1.1697 | FALSE | 2024-01-21 07:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_4812_22 | ACLineSegment | Line | 13.5424 | 0.10666 | 0.082595 | 0.7876 | FALSE | 2024-07-16 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_6309_22 | ACLineSegment | Line | 13.5424 | 0.12077 | 0.095517 | 0.89181 | FALSE | 2024-07-11 01:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | tr_1323_22 | Transformer | Transformer | 0.02375 | 0.0045854 | 0.0026499 | 19.3071 | FALSE | 2024-01-17 15:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_145 | line_4813_22 | ACLineSegment | Line | 13.5424 | 0.1026 | 0.079914 | 0.75763 | FALSE | 2024-01-17 23:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | tr_488_22 | Transformer | Transformer | 0.07125 | 0.0044247 | 0.0034262 | 6.2101 | FALSE | 2024-01-18 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_145 | line_5367_22 | ACLineSegment | Line | 13.5424 | 0.098661 | 0.076503 | 0.72853 | FALSE | 2024-01-17 23:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | tr_1414_22 | Transformer | Transformer | 0.02375 | 0.0062291 | 0.0039518 | 26.228 | FALSE | 2024-01-17 15:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_145 | line_4814_22 | ACLineSegment | Line | 0.51338 | 0.0044247 | 0.0034262 | 0.86188 | FALSE | 2024-01-18 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_494_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_6195_22 | ACLineSegment | Line | 0.51338 | 0.0040004 | 0.0030204 | 0.77923 | FALSE | 2024-07-15 13:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | tr_1163_22 | Transformer | Transformer | 0.07125 | 0.0040004 | 0.0030204 | 5.6146 | FALSE | 2024-07-15 13:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_145 | line_507_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_6264_22 | ACLineSegment | Line | 0.51338 | 0.0042466 | 0.0030704 | 0.82718 | FALSE | 2024-01-17 16:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | tr_1195_22 | Transformer | Transformer | 0.07125 | 0.0042466 | 0.0030704 | 5.9601 | FALSE | 2024-01-17 16:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_145 | line_5344_22 | ACLineSegment | Line | 13.5424 | 0.54824 | 0.43937 | 4.0484 | FALSE | 2024-01-21 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_6170_22 | ACLineSegment | Line | 13.5424 | 0.66153 | 0.52834 | 4.8849 | FALSE | 2024-01-21 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_521_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_6237_22 | ACLineSegment | Line | 0.51338 | 0.0057461 | 0.0044877 | 1.1193 | FALSE | 2024-07-06 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | tr_1179_22 | Transformer | Transformer | 0.475 | 0.0057461 | 0.0044877 | 1.2097 | FALSE | 2024-07-06 |  |  | 500 | 3 | Transformer_kVA_x_PF
GSO_145 | line_5232_22 | ACLineSegment | Line | 12.3112 | 0.021584 | 0.01483 | 0.17532 | FALSE | 2024-01-21 04:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_5239_22 | ACLineSegment | Line | 12.3112 | 0.030873 | 0.022853 | 0.25077 | FALSE | 2024-01-20 21:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_5240_22 | ACLineSegment | Line | 12.3112 | 0.051497 | 0.036757 | 0.41829 | FALSE | 2024-01-21 04:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_5457_22 | ACLineSegment | Line | 12.3112 | 0.06719 | 0.05189 | 0.54576 | FALSE | 2024-01-20 10:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_5267_22 | ACLineSegment | Line | 13.5424 | 0.053007 | 0.035807 | 0.39142 | FALSE | 2024-01-17 23:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_5268_22 | ACLineSegment | Line | 13.5424 | 0.067553 | 0.046044 | 0.49882 | FALSE | 2024-01-17 23:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_5269_22 | ACLineSegment | Line | 13.5424 | 0.0042466 | 0.0030704 | 0.031358 | FALSE | 2024-01-17 16:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_5273_22 | ACLineSegment | Line | 13.5424 | 0.013008 | 0.0088657 | 0.096052 | FALSE | 2024-01-17 10:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_6194_22 | ACLineSegment | Line | 13.5424 | 0.0040004 | 0.0030204 | 0.02954 | FALSE | 2024-07-15 13:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | tr_1322_22 | Transformer | Transformer | 0.02375 | 0.010059 | 0.0062484 | 42.3521 | FALSE | 2024-01-17 10:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_145 | line_5482_22 | ACLineSegment | Line | 13.5424 | 0.5316 | 0.42839 | 3.9254 | FALSE | 2024-01-21 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_5347_22 | ACLineSegment | Line | 2.3694 | 0.0057576 | 0.0042559 | 0.24299 | FALSE | 2024-01-20 21:00 | 600 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_5348_22 | ACLineSegment | Line | 12.3112 | 0.01266 | 0.0091544 | 0.10284 | FALSE | 2024-01-20 21:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | tr_1344_22 | Transformer | Transformer | 0.02375 | 0.0050294 | 0.0039187 | 21.1764 | FALSE | 2024-01-20 13:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_145 | line_5363_22 | ACLineSegment | Line | 0.034884 | 0.0036675 | 0.0021518 | 10.5134 | FALSE | 2024-07-16 03:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_5364_22 | ACLineSegment | Line | 0.034884 | 0.0039081 | 0.0021399 | 11.2034 | FALSE | 2024-01-20 11:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_6314_22 | ACLineSegment | Line | 13.5424 | 0.029174 | 0.02246 | 0.21543 | FALSE | 2024-01-21 09:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | tr_1443_22 | Transformer | Transformer | 0.475 | 0.0041636 | 0.0031556 | 0.87656 | FALSE | 2024-01-20 15:00 |  |  | 500 | 3 | Transformer_kVA_x_PF
GSO_145 | line_5477_22 | ACLineSegment | Line | 12.3112 | 0.0073266 | 0.0051705 | 0.059512 | FALSE | 2024-01-17 10:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_5955_22 | ACLineSegment | Line | 13.5424 | 0.52968 | 0.42655 | 3.9113 | FALSE | 2024-01-21 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_5536_22 | ACLineSegment | Line | 13.5424 | 0.024572 | 0.018487 | 0.18145 | FALSE | 2024-01-21 15:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | tr_1222_22 | Transformer | Transformer | 0.07125 | 0.0065579 | 0.0050545 | 9.2041 | FALSE | 2024-01-22 04:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_145 | tr_841_22 | Transformer | Transformer | 0.07125 | 0.024572 | 0.018487 | 34.4874 | FALSE | 2024-01-21 15:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_145 | line_5537_22 | ACLineSegment | Line | 0.22905 | 0.024572 | 0.018487 | 10.7281 | FALSE | 2024-01-21 15:00 | 290 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_5610_22 | ACLineSegment | Line | 0.51338 | 0.0045922 | 0.0034855 | 0.89451 | FALSE | 2024-01-20 17:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_561_22 | ACLineSegment | Line | 0.51338 | 0.004416 | 0.0030832 | 0.86018 | FALSE | 2024-01-21 10:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | tr_1202_22 | Transformer | Transformer | 0.285 | 0.004416 | 0.0030832 | 1.5495 | FALSE | 2024-01-21 10:00 |  |  | 300 | 3 | Transformer_kVA_x_PF
GSO_145 | line_562_22 | ACLineSegment | Line | 0.51338 | 0.004416 | 0.0030832 | 0.86018 | FALSE | 2024-01-21 10:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | tr_908_22 | Transformer | Transformer | 0.02375 | 0.0094626 | 0.004809 | 39.8424 | FALSE | 2024-07-05 21:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_145 | line_5673_22 | ACLineSegment | Line | 0.034884 | 0.0094626 | 0.004809 | 27.1262 | FALSE | 2024-07-05 21:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_5730_22 | ACLineSegment | Line | 0.034884 | 0.0055711 | 0.002771 | 15.9706 | FALSE | 2024-01-20 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_576_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_6271_22 | ACLineSegment | Line | 0.51338 | 0.0059106 | 0.0034881 | 1.1513 | FALSE | 2024-01-20 10:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | tr_1199_22 | Transformer | Transformer | 0.095 | 0.0059106 | 0.0034881 | 6.2217 | FALSE | 2024-01-20 10:00 |  |  | 100 | 3 | Transformer_kVA_x_PF
GSO_145 | line_578_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_6281_22 | ACLineSegment | Line | 0.51338 | 0.0060872 | 0.0046425 | 1.1857 | FALSE | 2024-01-20 07:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_580_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_6310_22 | ACLineSegment | Line | 0.51338 | 0.022366 | 0.016336 | 4.3566 | FALSE | 2024-06-24 23:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | tr_1220_22 | Transformer | Transformer | 0.07125 | 0.022366 | 0.016336 | 31.3904 | FALSE | 2024-06-24 23:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_145 | tr_1255_22 | Transformer | Transformer | 0.1425 | 0.02413 | 0.015337 | 16.9336 | FALSE | 2024-07-15 08:00 |  |  | 150 | 3 | Transformer_kVA_x_PF
GSO_145 | tr_1373_22 | Transformer | Transformer | 0.02375 | 0.0013471 | 0.0008159 | 5.6718 | FALSE | 2024-01-20 11:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_145 | line_5836_22 | ACLineSegment | Line | 0.22905 | 0.0058832 | 0.0044453 | 2.5686 | FALSE | 2024-01-20 09:00 | 290 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_5863_22 | ACLineSegment | Line | 12.3112 | 0.45811 | 0.36322 | 3.721 | FALSE | 2024-01-21 04:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_5864_22 | ACLineSegment | Line | 12.3112 | 0.44715 | 0.35392 | 3.6321 | FALSE | 2024-01-21 04:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | tr_1281_22 | Transformer | Transformer | 0.1425 | 0.0083266 | 0.0060503 | 5.8432 | FALSE | 2024-07-11 03:00 |  |  | 150 | 3 | Transformer_kVA_x_PF
GSO_145 | line_5881_22 | ACLineSegment | Line | 12.3112 | 0.42826 | 0.33744 | 3.4786 | FALSE | 2024-01-21 04:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_5882_22 | ACLineSegment | Line | 12.3112 | 0.35823 | 0.28451 | 2.9098 | FALSE | 2024-01-21 04:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_6098_22 | ACLineSegment | Line | 12.3112 | 0.35507 | 0.28091 | 2.8841 | FALSE | 2024-01-21 04:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | tr_1334_22 | Transformer | Transformer | 0.285 | 0.0077998 | 0.005328 | 2.7368 | FALSE | 2024-01-17 14:00 |  |  | 300 | 3 | Transformer_kVA_x_PF
GSO_145 | line_6040_22 | ACLineSegment | Line | 12.3112 | 0.32741 | 0.26058 | 2.6594 | FALSE | 2024-01-21 04:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | tr_1331_22 | Transformer | Transformer | 0.07125 | 0.0066172 | 0.0051153 | 9.2874 | FALSE | 2024-07-10 02:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_145 | line_6270_22 | ACLineSegment | Line | 12.3112 | 0.46075 | 0.36608 | 3.7425 | FALSE | 2024-01-21 04:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_6277_22 | ACLineSegment | Line | 12.3112 | 0.35304 | 0.27877 | 2.8676 | FALSE | 2024-01-21 04:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_6315_22 | ACLineSegment | Line | 0.51338 | 0.0065579 | 0.0050545 | 1.2774 | FALSE | 2024-01-22 04:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_6371_22 | ACLineSegment | Line | 0.51338 | 0.02413 | 0.015337 | 4.7003 | FALSE | 2024-07-15 08:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_6392_22 | ACLineSegment | Line | 0.034884 | 0.0044185 | 0.002374 | 12.6664 | FALSE | 2024-01-20 12:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_6416_22 | ACLineSegment | Line | 0.51338 | 0.0083266 | 0.0060503 | 1.6219 | FALSE | 2024-07-11 03:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_673_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_6480_22 | ACLineSegment | Line | 0.034884 | 0.0064087 | 0.0037952 | 18.3718 | FALSE | 2024-01-17 07:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_6481_22 | ACLineSegment | Line | 0.034884 | 0.0047454 | 0.0026773 | 13.6036 | FALSE | 2024-01-20 19:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_709_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_710_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_6482_22 | ACLineSegment | Line | 0.034884 | 0.0045854 | 0.0026499 | 13.145 | FALSE | 2024-01-17 15:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_726_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_6493_22 | ACLineSegment | Line | 0.51338 | 0.0040936 | 0.0028881 | 0.79737 | FALSE | 2024-01-21 02:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_733_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_6495_22 | ACLineSegment | Line | 12.3112 | 0.33159 | 0.26529 | 2.6934 | FALSE | 2024-01-21 04:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_6496_22 | ACLineSegment | Line | 0.51338 | 0.0066172 | 0.0051153 | 1.289 | FALSE | 2024-07-10 02:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_697_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_6500_22 | ACLineSegment | Line | 0.51338 | 0.0077998 | 0.005328 | 1.5193 | FALSE | 2024-01-17 14:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_711_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_6513_22 | ACLineSegment | Line | 0.025406 | 0.0050294 | 0.0039187 | 19.7963 | FALSE | 2024-01-20 13:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_747_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_6521_22 | ACLineSegment | Line | 0.51338 | 0.0038701 | 0.0028317 | 0.75384 | FALSE | 2024-07-14 08:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_760_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_6542_22 | ACLineSegment | Line | 0.51338 | 0.0080882 | 0.0060959 | 1.5755 | FALSE | 2024-07-15 06:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_781_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_6545_22 | ACLineSegment | Line | 0.034884 | 0.0013471 | 0.0008159 | 3.8616 | FALSE | 2024-01-20 11:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_6600_22 | ACLineSegment | Line | 0.034884 | 0.0062291 | 0.0039518 | 17.857 | FALSE | 2024-01-17 15:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_6602_22 | ACLineSegment | Line | 0.51338 | 0.0084582 | 0.005139 | 1.6476 | FALSE | 2024-07-15 08:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_867_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_6635_22 | ACLineSegment | Line | 0.51338 | 0.0041636 | 0.0031556 | 0.81102 | FALSE | 2024-01-20 15:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_894_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_6640_22 | ACLineSegment | Line | 0.51338 | 0.0044248 | 0.0034033 | 0.86189 | FALSE | 2024-01-21 10:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_145 | line_868_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_924_22 | ACLineSegment | Line | 0.034884 | 0.010452 | 0.0064835 | 29.9633 | FALSE | 2024-01-20 18:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_926_22 | ACLineSegment | Line | 0.034884 | 0.0056039 | 0.0030745 | 16.0647 | FALSE | 2024-01-20 08:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_984_22 | ACLineSegment | Line | 0.034884 | 0.00693 | 0.0040666 | 19.866 | FALSE | 2024-01-20 18:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_937_22 | ACLineSegment | Line | 0.034884 | 0.0097767 | 0.0061923 | 28.0268 | FALSE | 2024-01-17 14:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_939_22 | ACLineSegment | Line | 0.034884 | 0.004397 | 0.0022984 | 12.6048 | FALSE | 2024-01-20 23:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_993_22 | ACLineSegment | Line | 0.034884 | 0.0097767 | 0.0061923 | 28.0268 | FALSE | 2024-01-17 14:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_949_22 | ACLineSegment | Line | 0.034884 | 0.007888 | 0.004801 | 22.6125 | FALSE | 2024-07-15 23:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_951_22 | ACLineSegment | Line | 0.034884 | 0.0069044 | 0.0037677 | 19.7927 | FALSE | 2024-07-15 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_970_22 | ACLineSegment | Line | 0.034884 | 0.0024559 | 0.0015105 | 7.0404 | FALSE | 2024-07-15 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_971_22 | ACLineSegment | Line | 0.034884 | 0.0063776 | 0.003446 | 18.2825 | FALSE | 2024-07-15 23:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_964_22 | ACLineSegment | Line | 0.034884 | 0.004719 | 0.0027146 | 13.5278 | FALSE | 2024-07-16 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_977_22 | ACLineSegment | Line | 0.034884 | 0.0024559 | 0.0015105 | 7.0404 | FALSE | 2024-07-15 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_994_22 | ACLineSegment | Line | 0.034884 | 0.0032323 | 0.0018527 | 9.2659 | FALSE | 2024-07-16 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_145 | line_995_22 | ACLineSegment | Line | 0.034884 | 0.007376 | 0.0044745 | 21.1446 | FALSE | 2024-01-17 14:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_3723_22 | ACLineSegment | Line | 13.5424 | 0.074594 | 0.057059 | 0.55082 | FALSE | 2024-01-17 08:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_3724_22 | ACLineSegment | Line | 13.5424 | 0.059912 | 0.046057 | 0.44241 | FALSE | 2024-01-17 08:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_70_22 | Transformer | Transformer | 0.07125 | 0.0086811 | 0.0063882 | 12.184 | FALSE | 2024-07-10 07:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_142 | line_3690_22 | ACLineSegment | Line | 0.94778 | 0.012294 | 0.0082957 | 1.2972 | FALSE | 2024-01-20 09:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_4796_22 | ACLineSegment | Line | 13.5424 | 0.011306 | 0.0089197 | 0.083486 | FALSE | 2024-06-26 08:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_1271_22 | Transformer | Transformer | 0.07125 | 0.0067855 | 0.0048356 | 9.5235 | FALSE | 2024-01-21 16:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_142 | line_6343_22 | ACLineSegment | Line | 0.94778 | 0.0072565 | 0.0048002 | 0.76564 | FALSE | 2024-01-18 04:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_3872_22 | ACLineSegment | Line | 13.5424 | 0.0099522 | 0.0075072 | 0.073489 | FALSE | 2024-01-20 07:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_3873_22 | ACLineSegment | Line | 13.5424 | 0.019743 | 0.015692 | 0.14578 | FALSE | 2024-01-20 20:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_121_22 | Transformer | Transformer | 0.07125 | 0.0053198 | 0.0040524 | 7.4664 | FALSE | 2024-01-20 23:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_142 | tr_495_22 | Transformer | Transformer | 0.0475 | 0.0078985 | 0.00598 | 16.6283 | FALSE | 2024-01-17 08:00 |  |  | 50 | 1 | Transformer_kVA_x_PF
GSO_142 | line_4386_22 | ACLineSegment | Line | 13.5424 | 0.077595 | 0.062914 | 0.57298 | FALSE | 2024-01-20 20:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_4769_22 | ACLineSegment | Line | 13.5424 | 0.13017 | 0.10713 | 0.9612 | FALSE | 2024-01-20 07:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_4808_22 | ACLineSegment | Line | 13.5424 | 0.028326 | 0.021839 | 0.20917 | FALSE | 2024-01-20 19:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_486_22 | Transformer | Transformer | 0.095 | 0.028621 | 0.022319 | 30.127 | FALSE | 2024-07-14 07:00 |  |  | 100 | 3 | Transformer_kVA_x_PF
GSO_142 | line_3946_22 | ACLineSegment | Line | 0.94778 | 0.006694 | 0.005074 | 0.70628 | FALSE | 2024-07-15 05:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_3596_22 | ACLineSegment | Line | 13.5424 | 0.008109 | 0.006291 | 0.059879 | FALSE | 2024-07-15 22:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_26_22 | Transformer | Transformer | 0.07125 | 0.0038284 | 0.0026226 | 5.3732 | FALSE | 2024-07-15 08:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_142 | line_3595_22 | ACLineSegment | Line | 0.94778 | 0.005883 | 0.0044498 | 0.62071 | FALSE | 2024-01-17 09:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_4350_22 | ACLineSegment | Line | 13.5424 | 0.026195 | 0.019765 | 0.19343 | FALSE | 2024-01-20 11:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_306_22 | Transformer | Transformer | 0.07125 | 0.02133 | 0.016403 | 29.9368 | FALSE | 2024-07-11 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_142 | line_4351_22 | ACLineSegment | Line | 0.94778 | 0.0060145 | 0.0044572 | 0.63459 | FALSE | 2024-01-20 12:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_4527_22 | ACLineSegment | Line | 13.5424 | 0.15266 | 0.098178 | 1.1273 | FALSE | 2024-10-02 08:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_4528_22 | ACLineSegment | Line | 13.5424 | 0.15898 | 0.10443 | 1.1739 | FALSE | 2024-10-02 08:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_372_22 | Transformer | Transformer | 0.07125 | 0.0059557 | 0.0038686 | 8.3588 | FALSE | 2024-01-21 01:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_142 | tr_377_22 | Transformer | Transformer | 0.0475 | 0.0072735 | 0.0050006 | 15.3126 | FALSE | 2024-01-21 01:00 |  |  | 50 | 1 | Transformer_kVA_x_PF
GSO_142 | line_4716_22 | ACLineSegment | Line | 13.5424 | 0.020209 | 0.015101 | 0.14923 | FALSE | 2024-07-15 08:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_532_22 | Transformer | Transformer | 0.07125 | 0.017686 | 0.012805 | 24.8231 | FALSE | 2024-07-15 08:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_142 | line_4899_22 | ACLineSegment | Line | 0.94778 | 0.0039907 | 0.0030933 | 0.42106 | FALSE | 2024-07-11 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | tr_1437_22 | Transformer | Transformer | 0.285 | 0.0068903 | 0.0050917 | 2.4177 | FALSE | 2024-01-21 04:00 |  |  | 300 | 3 | Transformer_kVA_x_PF
GSO_142 | line_5115_22 | ACLineSegment | Line | 0.94778 | 0.022988 | 0.017666 | 2.4255 | FALSE | 2024-01-20 19:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_4942_22 | ACLineSegment | Line | 13.5424 | 0.0051723 | 0.0038982 | 0.038193 | FALSE | 2024-01-20 18:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_1504_22 | Transformer | Transformer | 0.0475 | 0.024377 | 0.0186 | 51.3195 | FALSE | 2024-01-20 17:00 |  |  | 50 | 1 | Transformer_kVA_x_PF
GSO_142 | line_5135_22 | ACLineSegment | Line | 0.94778 | 0.034098 | 0.025686 | 3.5977 | FALSE | 2024-01-22 02:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_1053_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_6402_22 | ACLineSegment | Line | 0.51338 | 0.0087372 | 0.0061663 | 1.7019 | FALSE | 2024-01-20 22:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_1259_22 | Transformer | Transformer | 0.07125 | 0.0087372 | 0.0061663 | 12.2628 | FALSE | 2024-01-20 22:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_142 | line_1070_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_6417_22 | ACLineSegment | Line | 0.51338 | 0.0067855 | 0.0048356 | 1.3217 | FALSE | 2024-01-21 16:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_1375_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_3874_22 | ACLineSegment | Line | 0.51338 | 0.0053198 | 0.0040524 | 1.0362 | FALSE | 2024-01-20 23:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_1402_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_3947_22 | ACLineSegment | Line | 0.034884 | 0.006694 | 0.005074 | 19.1895 | FALSE | 2024-07-15 05:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | tr_151_22 | Transformer | Transformer | 0.0475 | 0.006694 | 0.005074 | 14.0926 | FALSE | 2024-07-15 05:00 |  |  | 50 | 1 | Transformer_kVA_x_PF
GSO_142 | line_1426_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_3985_22 | ACLineSegment | Line | 0.51338 | 0.0032988 | 0.0025107 | 0.64257 | FALSE | 2024-01-21 11:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_167_22 | Transformer | Transformer | 0.285 | 0.0032988 | 0.0025107 | 1.1575 | FALSE | 2024-01-21 11:00 |  |  | 300 | 3 | Transformer_kVA_x_PF
GSO_142 | line_1699_22 | ACLineSegment | Line | 0.025406 | 0.027794 | 0.018529 | 109.4019 | TRUE | 2024-01-21 04:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_1701_22 | ACLineSegment | Line | 0.025406 | 0.027794 | 0.018529 | 109.4019 | TRUE | 2024-01-21 04:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_1700_22 | ACLineSegment | Line | 0.025406 | 0.027794 | 0.018529 | 109.4019 | TRUE | 2024-01-21 04:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_4263_22 | ACLineSegment | Line | 0.025406 | 0.0031695 | 0.0018242 | 12.4756 | FALSE | 2024-01-20 07:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | tr_273_22 | Transformer | Transformer | 0.02375 | 0.029951 | 0.019835 | 126.1109 | TRUE | 2024-01-21 04:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_142 | line_17_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_4491_22 | ACLineSegment | Line | 0.034884 | 0.0058303 | 0.0043355 | 16.7136 | FALSE | 2024-07-15 12:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | tr_348_22 | Transformer | Transformer | 0.0475 | 0.0058303 | 0.0043355 | 12.2743 | FALSE | 2024-07-15 12:00 |  |  | 50 | 1 | Transformer_kVA_x_PF
GSO_142 | line_1828_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_4352_22 | ACLineSegment | Line | 0.51338 | 0.02133 | 0.016403 | 4.1548 | FALSE | 2024-07-11 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_1856_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_4388_22 | ACLineSegment | Line | 0.51338 | 0.0063459 | 0.0047425 | 1.2361 | FALSE | 2024-07-15 01:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_319_22 | Transformer | Transformer | 0.07125 | 0.0063459 | 0.0047425 | 8.9066 | FALSE | 2024-07-15 01:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_142 | line_1857_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_4394_22 | ACLineSegment | Line | 0.51338 | 0.0068478 | 0.0048043 | 1.3339 | FALSE | 2024-01-20 13:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_321_22 | Transformer | Transformer | 0.07125 | 0.0068478 | 0.0048043 | 9.611 | FALSE | 2024-01-20 13:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_142 | line_1864_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_4914_22 | ACLineSegment | Line | 0.51338 | 0.0037074 | 0.0026516 | 0.72216 | FALSE | 2024-01-20 20:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_533_22 | Transformer | Transformer | 0.07125 | 0.0037074 | 0.0026516 | 5.2034 | FALSE | 2024-01-20 20:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_142 | line_1865_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_4912_22 | ACLineSegment | Line | 0.51338 | 0.017686 | 0.012805 | 3.4451 | FALSE | 2024-07-15 08:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_1866_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_4922_22 | ACLineSegment | Line | 0.51338 | 0.0060097 | 0.0045004 | 1.1706 | FALSE | 2024-01-20 07:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_538_22 | Transformer | Transformer | 0.07125 | 0.0060097 | 0.0045004 | 8.4347 | FALSE | 2024-01-20 07:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_142 | line_1868_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_4930_22 | ACLineSegment | Line | 0.51338 | 0.0060367 | 0.0040238 | 1.1759 | FALSE | 2024-01-21 08:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_543_22 | Transformer | Transformer | 0.07125 | 0.0060367 | 0.0040238 | 8.4725 | FALSE | 2024-01-21 08:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_142 | line_1869_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_4892_22 | ACLineSegment | Line | 0.51338 | 0.0058906 | 0.0043 | 1.1474 | FALSE | 2024-07-14 06:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_523_22 | Transformer | Transformer | 0.07125 | 0.0058906 | 0.0043 | 8.2675 | FALSE | 2024-07-14 06:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_142 | line_1870_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_4900_22 | ACLineSegment | Line | 0.034884 | 0.0039907 | 0.0030933 | 11.4401 | FALSE | 2024-07-11 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | tr_526_22 | Transformer | Transformer | 0.02375 | 0.0039907 | 0.0030933 | 16.803 | FALSE | 2024-07-11 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_142 | line_1871_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_4906_22 | ACLineSegment | Line | 0.034884 | 0.0080449 | 0.0060123 | 23.0623 | FALSE | 2024-01-20 06:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | tr_529_22 | Transformer | Transformer | 0.0475 | 0.0080449 | 0.0060123 | 16.9367 | FALSE | 2024-01-20 06:00 |  |  | 50 | 1 | Transformer_kVA_x_PF
GSO_142 | line_1872_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_4923_22 | ACLineSegment | Line | 0.034884 | 0.005883 | 0.0044498 | 16.8646 | FALSE | 2024-01-17 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | tr_539_22 | Transformer | Transformer | 0.02375 | 0.005883 | 0.0044498 | 24.7704 | FALSE | 2024-01-17 09:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_142 | line_1876_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_4920_22 | ACLineSegment | Line | 0.51338 | 0.0045953 | 0.0033093 | 0.89511 | FALSE | 2024-06-26 11:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_537_22 | Transformer | Transformer | 0.07125 | 0.0045953 | 0.0033093 | 6.4496 | FALSE | 2024-06-26 11:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_142 | line_1877_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_4890_22 | ACLineSegment | Line | 0.51338 | 0.0070601 | 0.0048984 | 1.3752 | FALSE | 2024-01-20 10:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_522_22 | Transformer | Transformer | 0.07125 | 0.0070601 | 0.0048984 | 9.9089 | FALSE | 2024-01-20 10:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_142 | line_1882_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_4911_22 | ACLineSegment | Line | 0.51338 | 0.0063554 | 0.0047708 | 1.238 | FALSE | 2024-07-15 11:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_531_22 | Transformer | Transformer | 0.07125 | 0.0063554 | 0.0047708 | 8.9199 | FALSE | 2024-07-15 11:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_142 | line_1883_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_4925_22 | ACLineSegment | Line | 0.51338 | 0.0073459 | 0.0050028 | 1.4309 | FALSE | 2024-07-15 05:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_540_22 | Transformer | Transformer | 0.07125 | 0.0073459 | 0.0050028 | 10.3101 | FALSE | 2024-07-15 05:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_142 | line_1894_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_4877_22 | ACLineSegment | Line | 0.034884 | 0.0072011 | 0.0037764 | 20.6433 | FALSE | 2024-01-21 02:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | tr_517_22 | Transformer | Transformer | 0.02375 | 0.0072011 | 0.0037764 | 30.3205 | FALSE | 2024-01-21 02:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_142 | line_1895_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_4909_22 | ACLineSegment | Line | 0.029092 | 0.0069778 | 0.0055738 | 23.9857 | FALSE | 2024-07-15 07:00 | 221 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | tr_530_22 | Transformer | Transformer | 0.0475 | 0.0069778 | 0.0055738 | 14.6901 | FALSE | 2024-07-15 07:00 |  |  | 50 | 1 | Transformer_kVA_x_PF
GSO_142 | line_1899_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_4936_22 | ACLineSegment | Line | 0.51338 | 0.0053577 | 0.0037786 | 1.0436 | FALSE | 2024-07-16 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_546_22 | Transformer | Transformer | 0.285 | 0.0053577 | 0.0037786 | 1.8799 | FALSE | 2024-07-16 |  |  | 300 | 3 | Transformer_kVA_x_PF
GSO_142 | line_1901_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_4943_22 | ACLineSegment | Line | 0.51338 | 0.0051723 | 0.0038982 | 1.0075 | FALSE | 2024-01-20 18:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_549_22 | Transformer | Transformer | 0.475 | 0.0051723 | 0.0038982 | 1.0889 | FALSE | 2024-01-20 18:00 |  |  | 500 | 3 | Transformer_kVA_x_PF
GSO_142 | line_1904_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_4441_22 | ACLineSegment | Line | 0.51338 | 0.0068668 | 0.0045268 | 1.3376 | FALSE | 2024-01-20 20:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_339_22 | Transformer | Transformer | 0.095 | 0.0068668 | 0.0045268 | 7.2283 | FALSE | 2024-01-20 20:00 |  |  | 100 | 3 | Transformer_kVA_x_PF
GSO_142 | line_1924_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_4420_22 | ACLineSegment | Line | 0.22905 | 0.0054587 | 0.0038787 | 2.3832 | FALSE | 2024-01-20 20:00 | 290 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_331_22 | Transformer | Transformer | 0.07125 | 0.0054587 | 0.0038787 | 7.6614 | FALSE | 2024-01-20 20:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_142 | line_1932_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_1933_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_4478_22 | ACLineSegment | Line | 0.51338 | 0.0067433 | 0.0043325 | 1.3135 | FALSE | 2024-01-20 23:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_4479_22 | ACLineSegment | Line | 0.51338 | 0.0060499 | 0.0045208 | 1.1784 | FALSE | 2024-01-18 04:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_354_22 | Transformer | Transformer | 0.095 | 0.010992 | 0.008203 | 11.5704 | FALSE | 2024-01-17 08:00 |  |  | 100 | 3 | Transformer_kVA_x_PF
GSO_142 | line_1935_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_4459_22 | ACLineSegment | Line | 0.034884 | 0.0069332 | 0.0051774 | 19.8752 | FALSE | 2024-01-20 16:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | tr_346_22 | Transformer | Transformer | 0.02375 | 0.0069332 | 0.0051774 | 29.1923 | FALSE | 2024-01-20 16:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_142 | line_1953_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_1954_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_4550_22 | ACLineSegment | Line | 0.51338 | 0.0066265 | 0.0041767 | 1.2908 | FALSE | 2024-01-21 01:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_4551_22 | ACLineSegment | Line | 0.51338 | 0.0058515 | 0.0045135 | 1.1398 | FALSE | 2024-07-15 17:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_380_22 | Transformer | Transformer | 0.095 | 0.012361 | 0.0082954 | 13.0112 | FALSE | 2024-01-21 01:00 |  |  | 100 | 3 | Transformer_kVA_x_PF
GSO_142 | line_1963_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_4529_22 | ACLineSegment | Line | 0.51338 | 0.0059557 | 0.0038686 | 1.1601 | FALSE | 2024-01-21 01:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_1967_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_4542_22 | ACLineSegment | Line | 0.034884 | 0.0072735 | 0.0050006 | 20.8508 | FALSE | 2024-01-21 01:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_1968_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_4547_22 | ACLineSegment | Line | 0.025406 | 0.0033863 | 0.0018861 | 13.3289 | FALSE | 2024-07-15 07:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | tr_379_22 | Transformer | Transformer | 0.02375 | 0.0033863 | 0.0018861 | 14.2581 | FALSE | 2024-07-15 07:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_142 | line_1975_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_4563_22 | ACLineSegment | Line | 0.51338 | 0.006096 | 0.0045885 | 1.1874 | FALSE | 2024-01-20 15:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_385_22 | Transformer | Transformer | 0.1425 | 0.006096 | 0.0045885 | 4.2779 | FALSE | 2024-01-20 15:00 |  |  | 150 | 3 | Transformer_kVA_x_PF
GSO_142 | line_1976_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_4571_22 | ACLineSegment | Line | 0.51338 | 0.0059015 | 0.0041549 | 1.1495 | FALSE | 2024-01-20 19:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_388_22 | Transformer | Transformer | 0.1425 | 0.0059015 | 0.0041549 | 4.1414 | FALSE | 2024-01-20 19:00 |  |  | 150 | 3 | Transformer_kVA_x_PF
GSO_142 | line_1981_22 | ACLineSegment | Line | 0.029092 | 0.007142 | 0.0055572 | 24.55 | FALSE | 2024-06-26 05:00 | 221 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_1983_22 | ACLineSegment | Line | 0.029092 | 0.0036936 | 0.0027248 | 12.6964 | FALSE | 2024-07-05 09:00 | 221 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | tr_393_22 | Transformer | Transformer | 0.07125 | 0.0097383 | 0.0078455 | 13.6677 | FALSE | 2024-07-15 20:00 |  |  | 75 | 1 | Transformer_kVA_x_PF
GSO_142 | line_1982_22 | ACLineSegment | Line | 0.029092 | 0.007142 | 0.0055572 | 24.55 | FALSE | 2024-06-26 05:00 | 221 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_1984_22 | ACLineSegment | Line | 0.029092 | 0.0036936 | 0.0027248 | 12.6964 | FALSE | 2024-07-05 09:00 | 221 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_1986_22 | ACLineSegment | Line | 0.51338 | 0.0051764 | 0.0037791 | 1.0083 | FALSE | 2024-01-20 12:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_1988_22 | ACLineSegment | Line | 0.51338 | 0.0051764 | 0.0037791 | 1.0083 | FALSE | 2024-01-20 12:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_1987_22 | ACLineSegment | Line | 0.51338 | 0.0051764 | 0.0037791 | 1.0083 | FALSE | 2024-01-20 12:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_4587_22 | ACLineSegment | Line | 0.51338 | 0.0054681 | 0.0040294 | 1.0651 | FALSE | 2024-01-21 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_395_22 | Transformer | Transformer | 0.095 | 0.0098187 | 0.0071861 | 10.3355 | FALSE | 2024-01-21 |  |  | 100 | 3 | Transformer_kVA_x_PF
GSO_142 | line_1994_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_6517_22 | ACLineSegment | Line | 0.51338 | 0.0060038 | 0.0041667 | 1.1695 | FALSE | 2024-01-20 21:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_1337_22 | Transformer | Transformer | 0.07125 | 0.0060038 | 0.0041667 | 8.4264 | FALSE | 2024-01-20 21:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_142 | line_1995_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_4679_22 | ACLineSegment | Line | 0.51338 | 0.022964 | 0.016781 | 4.4731 | FALSE | 2024-01-17 16:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_431_22 | Transformer | Transformer | 0.07125 | 0.022964 | 0.016781 | 32.2304 | FALSE | 2024-01-17 16:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_142 | line_2006_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_6529_22 | ACLineSegment | Line | 0.51338 | 0.007491 | 0.0055889 | 1.4592 | FALSE | 2024-01-20 22:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_1348_22 | Transformer | Transformer | 0.07125 | 0.007491 | 0.0055889 | 10.5137 | FALSE | 2024-01-20 22:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_142 | line_2009_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_4659_22 | ACLineSegment | Line | 0.51338 | 0.0052931 | 0.0038964 | 1.031 | FALSE | 2024-07-10 05:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_422_22 | Transformer | Transformer | 0.285 | 0.0052931 | 0.0038964 | 1.8572 | FALSE | 2024-07-10 05:00 |  |  | 300 | 3 | Transformer_kVA_x_PF
GSO_142 | line_20_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_4637_22 | ACLineSegment | Line | 0.22905 | 0.012762 | 0.007896 | 5.5718 | FALSE | 2024-01-18 | 290 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_403_22 | Transformer | Transformer | 0.07125 | 0.012762 | 0.007896 | 17.9115 | FALSE | 2024-01-18 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_142 | line_2028_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_4683_22 | ACLineSegment | Line | 0.025406 | 0.0079195 | 0.0057925 | 31.172 | FALSE | 2024-07-15 20:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | tr_433_22 | Transformer | Transformer | 0.02375 | 0.0079195 | 0.0057925 | 33.3452 | FALSE | 2024-07-15 20:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_142 | line_2029_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_4686_22 | ACLineSegment | Line | 0.51338 | 0.0056827 | 0.0039279 | 1.1069 | FALSE | 2024-01-21 03:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_434_22 | Transformer | Transformer | 0.07125 | 0.0056827 | 0.0039279 | 7.9757 | FALSE | 2024-01-21 03:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_142 | line_2076_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_4831_22 | ACLineSegment | Line | 0.51338 | 0.0046932 | 0.0037609 | 0.91417 | FALSE | 2024-01-17 19:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_496_22 | Transformer | Transformer | 0.285 | 0.0046932 | 0.0037609 | 1.6467 | FALSE | 2024-01-17 19:00 |  |  | 300 | 3 | Transformer_kVA_x_PF
GSO_142 | line_2084_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_4809_22 | ACLineSegment | Line | 0.51338 | 0.028621 | 0.022319 | 5.575 | FALSE | 2024-07-14 07:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_2085_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_4793_22 | ACLineSegment | Line | 0.51338 | 0.0070134 | 0.0053829 | 1.3661 | FALSE | 2024-07-10 18:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_479_22 | Transformer | Transformer | 0.095 | 0.0070134 | 0.0053829 | 7.3825 | FALSE | 2024-07-10 18:00 |  |  | 100 | 3 | Transformer_kVA_x_PF
GSO_142 | line_2086_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_4829_22 | ACLineSegment | Line | 0.034884 | 0.0078985 | 0.00598 | 22.6424 | FALSE | 2024-01-17 08:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_2088_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_4794_22 | ACLineSegment | Line | 0.51338 | 0.0090112 | 0.0059973 | 1.7553 | FALSE | 2024-01-20 20:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_480_22 | Transformer | Transformer | 0.095 | 0.0090112 | 0.0059973 | 9.4855 | FALSE | 2024-01-20 20:00 |  |  | 100 | 3 | Transformer_kVA_x_PF
GSO_142 | line_2106_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_4856_22 | ACLineSegment | Line | 0.51338 | 0.0058725 | 0.0043942 | 1.1439 | FALSE | 2024-07-05 09:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_507_22 | Transformer | Transformer | 0.095 | 0.0058725 | 0.0043942 | 6.1816 | FALSE | 2024-07-05 09:00 |  |  | 100 | 3 | Transformer_kVA_x_PF
GSO_142 | line_2109_22 | ACLineSegment | Line | 0.025406 | 0.0092181 | 0.005602 | 36.2837 | FALSE | 2024-01-21 02:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_2111_22 | ACLineSegment | Line | 0.025406 | 0.0044411 | 0.0023544 | 17.4806 | FALSE | 2024-01-20 07:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | tr_511_22 | Transformer | Transformer | 0.02375 | 0.012844 | 0.0070146 | 54.0808 | FALSE | 2024-01-21 02:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_142 | line_2110_22 | ACLineSegment | Line | 0.025406 | 0.0092181 | 0.005602 | 36.2837 | FALSE | 2024-01-21 02:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_2112_22 | ACLineSegment | Line | 0.025406 | 0.0044411 | 0.0023544 | 17.4806 | FALSE | 2024-01-20 07:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_213_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_4937_22 | ACLineSegment | Line | 0.22905 | 0.026881 | 0.020293 | 11.736 | FALSE | 2024-01-22 04:00 | 290 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_536_22 | Transformer | Transformer | 0.07125 | 0.026881 | 0.020293 | 37.7275 | FALSE | 2024-01-22 04:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_142 | line_2136_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_5100_22 | ACLineSegment | Line | 0.029092 | 0.0067666 | 0.005292 | 23.2597 | FALSE | 2024-01-18 04:00 | 221 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | tr_619_22 | Transformer | Transformer | 0.0475 | 0.0067666 | 0.005292 | 14.2455 | FALSE | 2024-01-18 04:00 |  |  | 50 | 1 | Transformer_kVA_x_PF
GSO_142 | line_2142_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_5110_22 | ACLineSegment | Line | 0.51338 | 0.0044235 | 0.0028883 | 0.86165 | FALSE | 2024-01-20 15:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_623_22 | Transformer | Transformer | 0.07125 | 0.0044235 | 0.0028883 | 6.2085 | FALSE | 2024-01-20 15:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_142 | line_2147_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_5112_22 | ACLineSegment | Line | 0.51338 | 0.0074082 | 0.0054797 | 1.443 | FALSE | 2024-07-15 15:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_624_22 | Transformer | Transformer | 0.07125 | 0.0074082 | 0.0054797 | 10.3975 | FALSE | 2024-07-15 15:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_142 | line_2151_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_5139_22 | ACLineSegment | Line | 0.51338 | 0.0075116 | 0.0054275 | 1.4632 | FALSE | 2024-01-20 17:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_639_22 | Transformer | Transformer | 0.285 | 0.0075116 | 0.0054275 | 2.6356 | FALSE | 2024-01-20 17:00 |  |  | 300 | 3 | Transformer_kVA_x_PF
GSO_142 | line_2161_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_5116_22 | ACLineSegment | Line | 0.025406 | 0.022988 | 0.017666 | 90.4838 | FALSE | 2024-01-20 19:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | tr_627_22 | Transformer | Transformer | 0.02375 | 0.022988 | 0.017666 | 96.7919 | FALSE | 2024-01-20 19:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_142 | line_2169_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_5169_22 | ACLineSegment | Line | 0.025406 | 0.0078929 | 0.0053708 | 31.0674 | FALSE | 2024-07-16 03:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | tr_652_22 | Transformer | Transformer | 0.02375 | 0.0078929 | 0.0053708 | 33.2333 | FALSE | 2024-07-16 03:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_142 | line_2171_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_5130_22 | ACLineSegment | Line | 0.034884 | 0.0068834 | 0.0037228 | 19.7324 | FALSE | 2024-07-10 04:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | tr_633_22 | Transformer | Transformer | 0.02375 | 0.0068834 | 0.0037228 | 28.9826 | FALSE | 2024-07-10 04:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_142 | line_2172_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_5118_22 | ACLineSegment | Line | 0.034884 | 0.0076835 | 0.0047031 | 22.0261 | FALSE | 2024-01-20 17:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | tr_628_22 | Transformer | Transformer | 0.02375 | 0.0076835 | 0.0047031 | 32.3515 | FALSE | 2024-01-20 17:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_142 | line_218_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_4998_22 | ACLineSegment | Line | 0.51338 | 0.0066763 | 0.0052663 | 1.3005 | FALSE | 2024-07-10 04:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_559_22 | Transformer | Transformer | 0.07125 | 0.0066763 | 0.0052663 | 9.3703 | FALSE | 2024-07-10 04:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_142 | line_219_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_4795_22 | ACLineSegment | Line | 0.034884 | 0.0063894 | 0.0047897 | 18.3164 | FALSE | 2024-07-15 04:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | tr_470_22 | Transformer | Transformer | 0.0475 | 0.0063894 | 0.0047897 | 13.4514 | FALSE | 2024-07-15 04:00 |  |  | 50 | 1 | Transformer_kVA_x_PF
GSO_142 | line_220_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_4822_22 | ACLineSegment | Line | 0.034884 | 0.0012055 | 0.00079692 | 3.4558 | FALSE | 2024-01-21 01:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | tr_481_22 | Transformer | Transformer | 0.02375 | 0.0012055 | 0.00079692 | 5.0757 | FALSE | 2024-01-21 01:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_142 | line_221_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_4847_22 | ACLineSegment | Line | 0.22905 | 0.0044919 | 0.0034965 | 1.9611 | FALSE | 2024-01-21 04:00 | 290 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_492_22 | Transformer | Transformer | 0.07125 | 0.0044919 | 0.0034965 | 6.3045 | FALSE | 2024-01-21 04:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_142 | line_2332_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_6342_22 | ACLineSegment | Line | 0.034884 | 0.005237 | 0.0038929 | 15.0128 | FALSE | 2024-01-20 18:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | tr_1226_22 | Transformer | Transformer | 0.0475 | 0.005237 | 0.0038929 | 11.0253 | FALSE | 2024-01-20 18:00 |  |  | 50 | 1 | Transformer_kVA_x_PF
GSO_142 | line_2336_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_6681_22 | ACLineSegment | Line | 0.51338 | 0.0040236 | 0.002906 | 0.78374 | FALSE | 2024-01-20 05:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_1470_22 | Transformer | Transformer | 0.07125 | 0.0040236 | 0.002906 | 5.6471 | FALSE | 2024-01-20 05:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_142 | line_2386_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_3911_22 | ACLineSegment | Line | 0.51338 | 0.0035457 | 0.0027046 | 0.69067 | FALSE | 2024-07-05 20:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_126_22 | Transformer | Transformer | 0.07125 | 0.0035457 | 0.0027046 | 4.9765 | FALSE | 2024-07-05 20:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_142 | line_2387_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_6802_22 | ACLineSegment | Line | 0.034884 | 0.0078713 | 0.0055803 | 22.5646 | FALSE | 2024-01-17 20:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | tr_1548_22 | Transformer | Transformer | 0.0475 | 0.0078713 | 0.0055803 | 16.5712 | FALSE | 2024-01-17 20:00 |  |  | 50 | 1 | Transformer_kVA_x_PF
GSO_142 | line_2388_22 | ACLineSegment | Line | 0.034884 | 0.0060043 | 0.0043248 | 17.2124 | FALSE | 2024-07-11 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_2390_22 | ACLineSegment | Line | 0.034884 | 0.02032 | 0.015157 | 58.2514 | FALSE | 2024-01-20 17:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_2389_22 | ACLineSegment | Line | 0.034884 | 0.0060043 | 0.0043248 | 17.2124 | FALSE | 2024-07-11 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_2391_22 | ACLineSegment | Line | 0.034884 | 0.02032 | 0.015157 | 58.2514 | FALSE | 2024-01-20 17:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_2429_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_3750_22 | ACLineSegment | Line | 0.22905 | 0.0086811 | 0.0063882 | 3.7901 | FALSE | 2024-07-10 07:00 | 290 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_2431_22 | ACLineSegment | Line | 0.025406 | 0.0054188 | 0.0031946 | 21.329 | FALSE | 2024-01-20 21:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_2433_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_3689_22 | ACLineSegment | Line | 0.029092 | 0.0071711 | 0.0051495 | 24.6502 | FALSE | 2024-06-26 05:00 | 221 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | tr_48_22 | Transformer | Transformer | 0.0475 | 0.010299 | 0.007516 | 21.6821 | FALSE | 2024-01-17 13:00 |  |  | 50 | 1 | Transformer_kVA_x_PF
GSO_142 | line_2432_22 | ACLineSegment | Line | 0.025406 | 0.0054188 | 0.0031946 | 21.329 | FALSE | 2024-01-20 21:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_2434_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_3633_22 | ACLineSegment | Line | 0.51338 | 0.0038284 | 0.0026226 | 0.74573 | FALSE | 2024-07-15 08:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_2437_22 | ACLineSegment | Line | 0.51338 | 0.0071441 | 0.0052293 | 1.3916 | FALSE | 2024-01-20 23:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_2439_22 | ACLineSegment | Line | 0.51338 | 0.0054887 | 0.0040366 | 1.0691 | FALSE | 2024-07-15 05:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_159_22 | Transformer | Transformer | 0.095 | 0.011155 | 0.0085053 | 11.7422 | FALSE | 2024-01-20 23:00 |  |  | 100 | 3 | Transformer_kVA_x_PF
GSO_142 | line_2438_22 | ACLineSegment | Line | 0.51338 | 0.0071441 | 0.0052293 | 1.3916 | FALSE | 2024-01-20 23:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_2440_22 | ACLineSegment | Line | 0.51338 | 0.0054887 | 0.0040366 | 1.0691 | FALSE | 2024-07-15 05:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_2441_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_2442_22 | ACLineSegment | Line | 0.029092 | 0.0053472 | 0.00397 | 18.3808 | FALSE | 2024-07-05 20:00 | 221 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_6761_22 | ACLineSegment | Line | 0.025406 | 0.0040416 | 0.0023214 | 15.9084 | FALSE | 2024-01-21 03:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | tr_1526_22 | Transformer | Transformer | 0.0475 | 0.0081258 | 0.0057047 | 17.1069 | FALSE | 2024-07-15 20:00 |  |  | 50 | 1 | Transformer_kVA_x_PF
GSO_142 | line_2443_22 | ACLineSegment | Line | 0.029092 | 0.0053472 | 0.00397 | 18.3808 | FALSE | 2024-07-05 20:00 | 221 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_2444_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_6857_22 | ACLineSegment | Line | 0.51338 | 0.0054157 | 0.0039926 | 1.0549 | FALSE | 2024-01-20 18:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_1581_22 | Transformer | Transformer | 0.285 | 0.0054157 | 0.0039926 | 1.9003 | FALSE | 2024-01-20 18:00 |  |  | 300 | 3 | Transformer_kVA_x_PF
GSO_142 | line_2446_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_3817_22 | ACLineSegment | Line | 0.51338 | 0.0096797 | 0.0073138 | 1.8855 | FALSE | 2024-07-15 05:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_92_22 | Transformer | Transformer | 0.285 | 0.0096797 | 0.0073138 | 3.3964 | FALSE | 2024-07-15 05:00 |  |  | 300 | 3 | Transformer_kVA_x_PF
GSO_142 | line_2464_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_2465_22 | ACLineSegment | Line | 0.034884 | 0.0086423 | 0.0052885 | 24.7748 | FALSE | 2024-01-17 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_2466_22 | ACLineSegment | Line | 0.034884 | 0.0050669 | 0.0029174 | 14.5253 | FALSE | 2024-01-17 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_2467_22 | ACLineSegment | Line | 0.034884 | 0.004598 | 0.0026898 | 13.1811 | FALSE | 2024-01-21 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_2469_22 | ACLineSegment | Line | 0.034884 | 0.019225 | 0.012427 | 55.1131 | FALSE | 2024-01-20 19:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_2474_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_2475_22 | ACLineSegment | Line | 0.034884 | 0.0067078 | 0.0037161 | 19.2291 | FALSE | 2024-01-20 19:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_2476_22 | ACLineSegment | Line | 0.034884 | 0.0074109 | 0.0040438 | 21.2447 | FALSE | 2024-01-20 22:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_2468_22 | ACLineSegment | Line | 0.034884 | 0.0099772 | 0.006005 | 28.6015 | FALSE | 2024-01-20 19:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_2470_22 | ACLineSegment | Line | 0.034884 | 0.029203 | 0.017935 | 83.7146 | FALSE | 2024-01-20 19:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_2471_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_2472_22 | ACLineSegment | Line | 0.034884 | 0.0040446 | 0.002429 | 11.5946 | FALSE | 2024-07-15 12:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_2473_22 | ACLineSegment | Line | 0.034884 | 0.006479 | 0.0037946 | 18.5733 | FALSE | 2024-07-06 03:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_3594_22 | ACLineSegment | Line | 0.034884 | 0.0031809 | 0.0016187 | 9.1186 | FALSE | 2024-01-20 19:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | tr_15_22 | Transformer | Transformer | 0.02375 | 0.032383 | 0.019411 | 136.3515 | TRUE | 2024-01-20 19:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_142 | line_2477_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_6819_22 | ACLineSegment | Line | 0.51338 | 0.0061532 | 0.0045566 | 1.1986 | FALSE | 2024-06-25 01:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_1559_22 | Transformer | Transformer | 0.07125 | 0.0061532 | 0.0045566 | 8.6361 | FALSE | 2024-06-25 01:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_142 | line_2478_22 | ACLineSegment | Line | 0.034884 | 0.0038645 | 0.0022306 | 11.0783 | FALSE | 2024-01-20 07:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_2482_22 | ACLineSegment | Line | 0.034884 | 0.0038645 | 0.0022306 | 11.0783 | FALSE | 2024-01-20 07:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_2479_22 | ACLineSegment | Line | 0.025406 | 0.0038645 | 0.0022306 | 15.2112 | FALSE | 2024-01-20 07:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_2480_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_3721_22 | ACLineSegment | Line | 0.034884 | 0.0037138 | 0.0021743 | 10.6463 | FALSE | 2024-01-20 05:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_3722_22 | ACLineSegment | Line | 0.034884 | 0.0076246 | 0.0043937 | 21.8574 | FALSE | 2024-07-15 08:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | tr_59_22 | Transformer | Transformer | 0.02375 | 0.012294 | 0.0082957 | 51.7658 | FALSE | 2024-01-20 09:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_142 | line_2483_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_3884_22 | ACLineSegment | Line | 0.034884 | 0.0064529 | 0.0047752 | 18.4984 | FALSE | 2024-01-17 12:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | tr_115_22 | Transformer | Transformer | 0.02375 | 0.0064529 | 0.0047752 | 27.1701 | FALSE | 2024-01-17 12:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_142 | line_2484_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_6737_22 | ACLineSegment | Line | 0.51338 | 0.0057022 | 0.0037529 | 1.1107 | FALSE | 2024-01-20 05:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_1515_22 | Transformer | Transformer | 0.07125 | 0.0057022 | 0.0037529 | 8.0031 | FALSE | 2024-01-20 05:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_142 | line_2485_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_3939_22 | ACLineSegment | Line | 0.034884 | 0.0058086 | 0.0027796 | 16.6513 | FALSE | 2024-01-21 02:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | tr_137_22 | Transformer | Transformer | 0.02375 | 0.0058086 | 0.0027796 | 24.4571 | FALSE | 2024-01-21 02:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_142 | line_2486_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_4013_22 | ACLineSegment | Line | 0.51338 | 0.10533 | 0.057813 | 20.5167 | FALSE | 2024-03-19 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_170_22 | Transformer | Transformer | 0.285 | 0.10533 | 0.057813 | 36.9575 | FALSE | 2024-03-19 |  |  | 300 | 3 | Transformer_kVA_x_PF
GSO_142 | line_2496_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_4144_22 | ACLineSegment | Line | 0.025406 | 0.004537 | 0.0025116 | 17.8583 | FALSE | 2024-01-20 05:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | tr_226_22 | Transformer | Transformer | 0.02375 | 0.004537 | 0.0025116 | 19.1033 | FALSE | 2024-01-20 05:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_142 | line_26_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_4607_22 | ACLineSegment | Line | 0.51338 | 0.0084155 | 0.0062552 | 1.6392 | FALSE | 2024-01-20 23:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_392_22 | Transformer | Transformer | 0.07125 | 0.0084155 | 0.0062552 | 11.8113 | FALSE | 2024-01-20 23:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_142 | line_2659_22 | ACLineSegment | Line | 0.034884 | 0.025793 | 0.01764 | 73.9391 | FALSE | 2024-01-20 18:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | tr_767_22 | Transformer | Transformer | 0.02375 | 0.025793 | 0.01764 | 108.6003 | TRUE | 2024-01-20 18:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_142 | line_2660_22 | ACLineSegment | Line | 0.034884 | 0.025793 | 0.01764 | 73.9391 | FALSE | 2024-01-20 18:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_2675_22 | ACLineSegment | Line | 0.51338 | 0.0050266 | 0.0035758 | 0.97912 | FALSE | 2024-01-20 14:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_766_22 | Transformer | Transformer | 0.285 | 0.0050266 | 0.0035758 | 1.7637 | FALSE | 2024-01-20 14:00 |  |  | 300 | 3 | Transformer_kVA_x_PF
GSO_142 | line_2676_22 | ACLineSegment | Line | 0.51338 | 0.0050266 | 0.0035758 | 0.97912 | FALSE | 2024-01-20 14:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_2692_22 | ACLineSegment | Line | 0.51338 | 0.006096 | 0.0046628 | 1.1874 | FALSE | 2024-01-21 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_778_22 | Transformer | Transformer | 0.07125 | 0.006096 | 0.0046628 | 8.5558 | FALSE | 2024-01-21 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_142 | line_2693_22 | ACLineSegment | Line | 0.51338 | 0.006096 | 0.0046628 | 1.1874 | FALSE | 2024-01-21 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_2700_22 | ACLineSegment | Line | 0.51338 | 0.026234 | 0.018405 | 5.1101 | FALSE | 2024-01-20 10:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_765_22 | Transformer | Transformer | 0.07125 | 0.026234 | 0.018405 | 36.8199 | FALSE | 2024-01-20 10:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_142 | line_2701_22 | ACLineSegment | Line | 0.51338 | 0.026234 | 0.018405 | 5.1101 | FALSE | 2024-01-20 10:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_2710_22 | ACLineSegment | Line | 0.51338 | 0.0048303 | 0.0036158 | 0.94088 | FALSE | 2024-01-21 01:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_772_22 | Transformer | Transformer | 0.07125 | 0.0048303 | 0.0036158 | 6.7793 | FALSE | 2024-01-21 01:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_142 | line_2711_22 | ACLineSegment | Line | 0.51338 | 0.0048303 | 0.0036158 | 0.94088 | FALSE | 2024-01-21 01:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_2740_22 | ACLineSegment | Line | 0.025406 | 0.01326 | 0.010709 | 52.1912 | FALSE | 2024-07-06 01:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | tr_789_22 | Transformer | Transformer | 0.02375 | 0.01326 | 0.010709 | 55.8297 | FALSE | 2024-07-06 01:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_142 | line_2741_22 | ACLineSegment | Line | 0.025406 | 0.01326 | 0.010709 | 52.1912 | FALSE | 2024-07-06 01:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_2746_22 | ACLineSegment | Line | 0.51338 | 0.0052404 | 0.0040903 | 1.0208 | FALSE | 2024-01-21 03:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_792_22 | Transformer | Transformer | 0.07125 | 0.0052404 | 0.0040903 | 7.3549 | FALSE | 2024-01-21 03:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_142 | line_2747_22 | ACLineSegment | Line | 0.51338 | 0.0052404 | 0.0040903 | 1.0208 | FALSE | 2024-01-21 03:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_2865_22 | ACLineSegment | Line | 0.51338 | 0.014034 | 0.0090836 | 2.7337 | FALSE | 2024-05-05 17:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_825_22 | Transformer | Transformer | 0.07125 | 0.014034 | 0.0090836 | 19.697 | FALSE | 2024-05-05 17:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_142 | line_2866_22 | ACLineSegment | Line | 0.51338 | 0.014034 | 0.0090836 | 2.7337 | FALSE | 2024-05-05 17:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_2906_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_5346_22 | ACLineSegment | Line | 0.51338 | 0.0054712 | 0.0036975 | 1.0657 | FALSE | 2024-01-20 20:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_725_22 | Transformer | Transformer | 0.07125 | 0.0054712 | 0.0036975 | 7.6789 | FALSE | 2024-01-20 20:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_142 | line_3013_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_5411_22 | ACLineSegment | Line | 0.51338 | 0.0081844 | 0.0057209 | 1.5942 | FALSE | 2024-01-20 14:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_756_22 | Transformer | Transformer | 0.07125 | 0.0081844 | 0.0057209 | 11.4869 | FALSE | 2024-01-20 14:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_142 | line_3024_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_5184_22 | ACLineSegment | Line | 0.51338 | 0.0062439 | 0.0045606 | 1.2162 | FALSE | 2024-01-20 20:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_647_22 | Transformer | Transformer | 0.07125 | 0.0062439 | 0.0045606 | 8.7634 | FALSE | 2024-01-20 20:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_142 | line_3087_22 | ACLineSegment | Line | 0.034884 | 0.0058283 | 0.0042315 | 16.7079 | FALSE | 2024-01-20 14:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_3089_22 | ACLineSegment | Line | 0.034884 | 0.025846 | 0.017716 | 74.0928 | FALSE | 2024-07-10 08:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | tr_636_22 | Transformer | Transformer | 0.0475 | 0.028639 | 0.021418 | 60.2934 | FALSE | 2024-07-10 08:00 |  |  | 50 | 1 | Transformer_kVA_x_PF
GSO_142 | line_3088_22 | ACLineSegment | Line | 0.034884 | 0.0058283 | 0.0042315 | 16.7079 | FALSE | 2024-01-20 14:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_3090_22 | ACLineSegment | Line | 0.034884 | 0.025846 | 0.017716 | 74.0928 | FALSE | 2024-07-10 08:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_3093_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_5113_22 | ACLineSegment | Line | 0.029092 | 0.0061018 | 0.0046097 | 20.9745 | FALSE | 2024-07-15 07:00 | 221 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | tr_614_22 | Transformer | Transformer | 0.0475 | 0.0061018 | 0.0046097 | 12.8459 | FALSE | 2024-07-15 07:00 |  |  | 50 | 1 | Transformer_kVA_x_PF
GSO_142 | line_3096_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_5727_22 | ACLineSegment | Line | 0.034884 | 0.0048604 | 0.0027694 | 13.9331 | FALSE | 2024-07-15 11:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | tr_933_22 | Transformer | Transformer | 0.02375 | 0.0048604 | 0.0027694 | 20.4647 | FALSE | 2024-07-15 11:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_142 | line_3134_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_5726_22 | ACLineSegment | Line | 0.51338 | 0.0052786 | 0.0036654 | 1.0282 | FALSE | 2024-01-17 16:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_932_22 | Transformer | Transformer | 0.07125 | 0.0052786 | 0.0036654 | 7.4085 | FALSE | 2024-01-17 16:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_142 | line_3190_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_5543_22 | ACLineSegment | Line | 0.51338 | 0.0063415 | 0.0046688 | 1.2353 | FALSE | 2024-01-18 03:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_844_22 | Transformer | Transformer | 0.07125 | 0.0063415 | 0.0046688 | 8.9004 | FALSE | 2024-01-18 03:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_142 | line_3203_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_5557_22 | ACLineSegment | Line | 0.034884 | 0.0060145 | 0.0044572 | 17.2418 | FALSE | 2024-01-20 12:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | tr_853_22 | Transformer | Transformer | 0.02375 | 0.0060145 | 0.0044572 | 25.3243 | FALSE | 2024-01-20 12:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_142 | line_3205_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_5519_22 | ACLineSegment | Line | 0.034884 | 0.00283 | 0.0015425 | 8.1126 | FALSE | 2024-07-15 14:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | tr_833_22 | Transformer | Transformer | 0.02375 | 0.00283 | 0.0015425 | 11.9157 | FALSE | 2024-07-15 14:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_142 | line_3206_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_5567_22 | ACLineSegment | Line | 0.51338 | 0.0064449 | 0.0050086 | 1.2554 | FALSE | 2024-07-15 20:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_858_22 | Transformer | Transformer | 0.07125 | 0.0064449 | 0.0050086 | 9.0454 | FALSE | 2024-07-15 20:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_142 | line_3207_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_5568_22 | ACLineSegment | Line | 0.51338 | 0.0047945 | 0.0035176 | 0.9339 | FALSE | 2024-01-17 17:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_859_22 | Transformer | Transformer | 0.07125 | 0.0047945 | 0.0035176 | 6.7291 | FALSE | 2024-01-17 17:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_142 | line_3422_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_5749_22 | ACLineSegment | Line | 0.025406 | 0.0060102 | 0.0033108 | 23.6569 | FALSE | 2024-01-20 23:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | tr_946_22 | Transformer | Transformer | 0.02375 | 0.0060102 | 0.0033108 | 25.3061 | FALSE | 2024-01-20 23:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_142 | line_3423_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_5782_22 | ACLineSegment | Line | 0.025406 | 0.0052099 | 0.0026021 | 20.5068 | FALSE | 2024-01-20 09:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | tr_962_22 | Transformer | Transformer | 0.02375 | 0.0052099 | 0.0026021 | 21.9364 | FALSE | 2024-01-20 09:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_142 | line_3430_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_5778_22 | ACLineSegment | Line | 0.034884 | 0.0037564 | 0.0015335 | 10.7685 | FALSE | 2024-01-20 22:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | tr_959_22 | Transformer | Transformer | 0.02375 | 0.0037564 | 0.0015335 | 15.8165 | FALSE | 2024-01-20 22:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_142 | line_3435_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_5750_22 | ACLineSegment | Line | 0.51338 | 0.0050365 | 0.0035141 | 0.98104 | FALSE | 2024-01-17 19:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_947_22 | Transformer | Transformer | 0.07125 | 0.0050365 | 0.0035141 | 7.0687 | FALSE | 2024-01-17 19:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_142 | line_3565_22 | ACLineSegment | Line | 13.5424 | 0.0058725 | 0.0043942 | 0.043364 | FALSE | 2024-07-05 09:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_3566_22 | ACLineSegment | Line | 13.5424 | 0.03547 | 0.023049 | 0.26192 | FALSE | 2024-01-20 19:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_4608_22 | ACLineSegment | Line | 13.5424 | 0.56579 | 0.45022 | 4.1779 | FALSE | 2024-01-21 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_4889_22 | ACLineSegment | Line | 13.5424 | 0.5921 | 0.47655 | 4.3722 | FALSE | 2024-01-21 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_4464_22 | ACLineSegment | Line | 13.5424 | 0.15803 | 0.13094 | 1.1669 | FALSE | 2024-01-17 16:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_4919_22 | ACLineSegment | Line | 13.5424 | 0.18053 | 0.15095 | 1.3331 | FALSE | 2024-07-15 12:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_3662_22 | ACLineSegment | Line | 12.3112 | 0.27636 | 0.22776 | 2.2448 | FALSE | 2024-01-21 04:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_3663_22 | ACLineSegment | Line | 12.3112 | 0.28621 | 0.23453 | 2.3248 | FALSE | 2024-01-21 04:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_6503_22 | ACLineSegment | Line | 12.3112 | 0.28988 | 0.23683 | 2.3546 | FALSE | 2024-01-21 04:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_4823_22 | ACLineSegment | Line | 13.5424 | 0.077711 | 0.060015 | 0.57384 | FALSE | 2024-01-17 08:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_3782_22 | ACLineSegment | Line | 12.3112 | 0.0096797 | 0.0073138 | 0.078625 | FALSE | 2024-07-15 05:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_3857_22 | ACLineSegment | Line | 0.94778 | 0.0064529 | 0.0047752 | 0.68084 | FALSE | 2024-01-17 12:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_4921_22 | ACLineSegment | Line | 13.5424 | 0.0047945 | 0.0035176 | 0.035403 | FALSE | 2024-01-17 17:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_4549_22 | ACLineSegment | Line | 13.5424 | 0.022507 | 0.017865 | 0.1662 | FALSE | 2024-01-20 20:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_3885_22 | ACLineSegment | Line | 12.3112 | 0.029951 | 0.019835 | 0.24328 | FALSE | 2024-01-21 04:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_3886_22 | ACLineSegment | Line | 13.5424 | 0.1176 | 0.09005 | 0.86836 | FALSE | 2024-01-21 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_3983_22 | ACLineSegment | Line | 13.5424 | 0.12719 | 0.098561 | 0.93919 | FALSE | 2024-01-21 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_3887_22 | ACLineSegment | Line | 12.3112 | 0.090329 | 0.069988 | 0.73371 | FALSE | 2024-01-20 22:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_4582_22 | ACLineSegment | Line | 12.3112 | 0.086695 | 0.067216 | 0.7042 | FALSE | 2024-01-20 22:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_3912_22 | ACLineSegment | Line | 13.5424 | 0.29797 | 0.24413 | 2.2003 | FALSE | 2024-01-21 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_3913_22 | ACLineSegment | Line | 13.5424 | 0.30071 | 0.24623 | 2.2205 | FALSE | 2024-01-21 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_5156_22 | ACLineSegment | Line | 13.5424 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_5157_22 | ACLineSegment | Line | 12.3112 | 0.29336 | 0.24032 | 2.3828 | FALSE | 2024-01-21 04:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_5463_22 | ACLineSegment | Line | 13.5424 | 0.3043 | 0.24959 | 2.247 | FALSE | 2024-01-21 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_3966_22 | ACLineSegment | Line | 13.5424 | 0.011155 | 0.0085053 | 0.082372 | FALSE | 2024-01-20 23:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_4904_22 | ACLineSegment | Line | 13.5424 | 0.17958 | 0.12295 | 1.326 | FALSE | 2024-10-02 08:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_4905_22 | ACLineSegment | Line | 13.5424 | 0.16755 | 0.11184 | 1.2372 | FALSE | 2024-10-02 08:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_3982_22 | ACLineSegment | Line | 2.3694 | 0.0076636 | 0.0054446 | 0.32343 | FALSE | 2024-01-18 | 600 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | tr_436_22 | Transformer | Transformer | 0.0475 | 0.0076636 | 0.0054446 | 16.1339 | FALSE | 2024-01-18 |  |  | 50 | 1 | Transformer_kVA_x_PF
GSO_142 | line_3984_22 | ACLineSegment | Line | 12.3112 | 0.13544 | 0.10551 | 1.1002 | FALSE | 2024-01-21 04:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_3988_22 | ACLineSegment | Line | 13.5424 | 0.1372 | 0.083894 | 1.0131 | FALSE | 2024-10-02 08:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_4440_22 | ACLineSegment | Line | 13.5424 | 0.13994 | 0.087819 | 1.0334 | FALSE | 2024-10-02 08:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_3989_22 | ACLineSegment | Line | 13.5424 | 0.042492 | 0.031788 | 0.31377 | FALSE | 2024-07-15 08:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_4560_22 | ACLineSegment | Line | 13.5424 | 0.03844 | 0.02866 | 0.28385 | FALSE | 2024-07-15 08:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_40_22 | ACLineSegment | Line | 0.029092 | 0.0041536 | 0.0030492 | 14.2777 | FALSE | 2024-01-20 20:00 | 221 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_42_22 | ACLineSegment | Line | 0.025406 | 0.0047205 | 0.002715 | 18.5803 | FALSE | 2024-07-15 22:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_41_22 | ACLineSegment | Line | 0.029092 | 0.0041536 | 0.0030492 | 14.2777 | FALSE | 2024-01-20 20:00 | 221 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_4122_22 | ACLineSegment | Line | 2.3694 | 0.004537 | 0.0025116 | 0.19148 | FALSE | 2024-01-20 05:00 | 600 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_4891_22 | ACLineSegment | Line | 12.3112 | 0.0090491 | 0.0062694 | 0.073503 | FALSE | 2024-01-20 05:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_43_22 | ACLineSegment | Line | 0.025406 | 0.0047205 | 0.002715 | 18.5803 | FALSE | 2024-07-15 22:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_4262_22 | ACLineSegment | Line | 12.3112 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_5168_22 | ACLineSegment | Line | 12.3112 | 0.0078929 | 0.0053708 | 0.064111 | FALSE | 2024-07-16 03:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_4684_22 | ACLineSegment | Line | 13.5424 | 0.62682 | 0.51275 | 4.6286 | FALSE | 2024-01-21 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_4685_22 | ACLineSegment | Line | 13.5424 | 0.60837 | 0.4933 | 4.4923 | FALSE | 2024-01-21 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_4387_22 | ACLineSegment | Line | 13.5424 | 0.072901 | 0.058953 | 0.53832 | FALSE | 2024-01-20 20:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_4792_22 | ACLineSegment | Line | 13.5424 | 0.068266 | 0.054151 | 0.50409 | FALSE | 2024-01-17 16:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_4391_22 | ACLineSegment | Line | 12.3112 | 0.25372 | 0.21346 | 2.0609 | FALSE | 2024-01-20 10:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_4392_22 | ACLineSegment | Line | 12.3112 | 0.24345 | 0.20336 | 1.9774 | FALSE | 2024-01-20 10:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_4830_22 | ACLineSegment | Line | 12.3112 | 0.23934 | 0.20005 | 1.9441 | FALSE | 2024-01-20 10:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_4393_22 | ACLineSegment | Line | 12.3112 | 0.0093246 | 0.0068662 | 0.07574 | FALSE | 2024-01-20 05:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_4419_22 | ACLineSegment | Line | 13.5424 | 0.0054587 | 0.0038787 | 0.040309 | FALSE | 2024-01-20 20:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_4439_22 | ACLineSegment | Line | 13.5424 | 0.1468 | 0.093964 | 1.084 | FALSE | 2024-10-02 08:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_44_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_4581_22 | ACLineSegment | Line | 0.51338 | 0.0046097 | 0.0035105 | 0.89791 | FALSE | 2024-01-20 23:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_381_22 | Transformer | Transformer | 0.07125 | 0.0046097 | 0.0035105 | 6.4698 | FALSE | 2024-01-20 23:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_142 | line_4434_22 | ACLineSegment | Line | 12.3112 | 0.20378 | 0.16858 | 1.6553 | FALSE | 2024-01-20 10:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_4435_22 | ACLineSegment | Line | 13.5424 | 0.18252 | 0.15337 | 1.3478 | FALSE | 2024-07-15 12:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_4436_22 | ACLineSegment | Line | 12.3112 | 0.020984 | 0.014814 | 0.17044 | FALSE | 2024-01-20 23:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_337_22 | Transformer | Transformer | 0.02375 | 0.0041937 | 0.0021415 | 17.6579 | FALSE | 2024-01-20 12:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_142 | line_4457_22 | ACLineSegment | Line | 13.5424 | 0.030939 | 0.02335 | 0.22846 | FALSE | 2024-01-17 16:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_4458_22 | ACLineSegment | Line | 13.5424 | 0.034873 | 0.027185 | 0.25751 | FALSE | 2024-01-17 16:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_4678_22 | ACLineSegment | Line | 13.5424 | 0.010004 | 0.0075593 | 0.073871 | FALSE | 2024-01-21 02:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_4548_22 | ACLineSegment | Line | 13.5424 | 0.031459 | 0.024975 | 0.2323 | FALSE | 2024-01-20 07:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_4462_22 | ACLineSegment | Line | 0.025406 | 0.0041937 | 0.0021415 | 16.5071 | FALSE | 2024-01-20 12:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_98_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_4463_22 | ACLineSegment | Line | 13.5424 | 0.15489 | 0.12732 | 1.1438 | FALSE | 2024-01-17 16:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_4770_22 | ACLineSegment | Line | 13.5424 | 0.13493 | 0.11119 | 0.99637 | FALSE | 2024-01-20 07:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_4476_22 | ACLineSegment | Line | 12.3112 | 0.014119 | 0.010801 | 0.11468 | FALSE | 2024-07-15 23:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_4477_22 | ACLineSegment | Line | 12.3112 | 0.22244 | 0.18573 | 1.8068 | FALSE | 2024-01-20 10:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_5109_22 | ACLineSegment | Line | 12.3112 | 0.22539 | 0.18788 | 1.8308 | FALSE | 2024-01-20 10:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_45_22 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_4744_22 | ACLineSegment | Line | 0.51338 | 0.0090436 | 0.0067754 | 1.7616 | FALSE | 2024-01-20 13:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_448_22 | Transformer | Transformer | 0.095 | 0.0090436 | 0.0067754 | 9.5196 | FALSE | 2024-01-20 13:00 |  |  | 100 | 3 | Transformer_kVA_x_PF
GSO_142 | line_4924_22 | ACLineSegment | Line | 13.5424 | 0.16351 | 0.10801 | 1.2074 | FALSE | 2024-10-02 08:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_4545_22 | ACLineSegment | Line | 12.3112 | 0.1848 | 0.14239 | 1.5011 | FALSE | 2024-01-21 04:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_4553_22 | ACLineSegment | Line | 12.3112 | 0.0098187 | 0.0071861 | 0.079754 | FALSE | 2024-01-21 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_4554_22 | ACLineSegment | Line | 12.3112 | 0.19637 | 0.15134 | 1.5951 | FALSE | 2024-01-21 04:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_4546_22 | ACLineSegment | Line | 12.3112 | 0.18265 | 0.14086 | 1.4836 | FALSE | 2024-01-21 04:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_4561_22 | ACLineSegment | Line | 13.5424 | 0.00283 | 0.0015425 | 0.020897 | FALSE | 2024-07-15 14:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_4562_22 | ACLineSegment | Line | 13.5424 | 0.031339 | 0.023584 | 0.23141 | FALSE | 2024-07-15 08:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_4717_22 | ACLineSegment | Line | 13.5424 | 0.028163 | 0.02057 | 0.20796 | FALSE | 2024-07-15 08:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_4570_22 | ACLineSegment | Line | 13.5424 | 0.0059015 | 0.0041549 | 0.043578 | FALSE | 2024-01-20 19:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_4929_22 | ACLineSegment | Line | 13.5424 | 0.011099 | 0.0077339 | 0.081961 | FALSE | 2024-01-20 08:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_4583_22 | ACLineSegment | Line | 12.3112 | 0.080989 | 0.06208 | 0.65784 | FALSE | 2024-01-17 08:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_4584_22 | ACLineSegment | Line | 12.3112 | 0.17425 | 0.13424 | 1.4154 | FALSE | 2024-01-21 04:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_4609_22 | ACLineSegment | Line | 13.5424 | 0.55412 | 0.43984 | 4.0918 | FALSE | 2024-01-21 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_4610_22 | ACLineSegment | Line | 13.5424 | 0.0061532 | 0.0045566 | 0.045437 | FALSE | 2024-06-25 01:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_4938_22 | ACLineSegment | Line | 13.5424 | 0.23343 | 0.18077 | 1.7237 | FALSE | 2024-01-21 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_5129_22 | ACLineSegment | Line | 13.5424 | 0.31487 | 0.25811 | 2.325 | FALSE | 2024-01-21 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_4658_22 | ACLineSegment | Line | 12.3112 | 0.25767 | 0.21672 | 2.0929 | FALSE | 2024-01-21 04:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_4910_22 | ACLineSegment | Line | 13.5424 | 0.0063554 | 0.0047708 | 0.04693 | FALSE | 2024-07-15 11:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_4682_22 | ACLineSegment | Line | 12.3112 | 0.016597 | 0.012243 | 0.13481 | FALSE | 2024-07-15 05:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_5565_22 | ACLineSegment | Line | 13.5424 | 0.63136 | 0.51592 | 4.6621 | FALSE | 2024-01-21 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_5427_22 | ACLineSegment | Line | 13.5424 | 0.60644 | 0.49064 | 4.4781 | FALSE | 2024-01-21 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_1404_22 | Transformer | Transformer | 0.07125 | 0.0054713 | 0.0032959 | 7.679 | FALSE | 2024-01-21 14:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_142 | line_480_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_6601_22 | ACLineSegment | Line | 0.51338 | 0.0054713 | 0.0032959 | 1.0657 | FALSE | 2024-01-21 14:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_4864_22 | ACLineSegment | Line | 12.3112 | 0.26917 | 0.22196 | 2.1864 | FALSE | 2024-01-21 04:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_4875_22 | ACLineSegment | Line | 13.5424 | 0.20924 | 0.16118 | 1.5451 | FALSE | 2024-01-21 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_5117_22 | ACLineSegment | Line | 13.5424 | 0.21194 | 0.16485 | 1.565 | FALSE | 2024-01-21 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_4876_22 | ACLineSegment | Line | 13.5424 | 0.20315 | 0.15775 | 1.5001 | FALSE | 2024-01-21 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_5777_22 | ACLineSegment | Line | 13.5424 | 0.20162 | 0.15642 | 1.4888 | FALSE | 2024-01-21 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_4913_22 | ACLineSegment | Line | 13.5424 | 0.18125 | 0.12498 | 1.3384 | FALSE | 2024-10-02 08:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_4907_22 | ACLineSegment | Line | 12.3112 | 0.13811 | 0.10895 | 1.1218 | FALSE | 2024-01-21 04:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_4908_22 | ACLineSegment | Line | 12.3112 | 0.1438 | 0.1139 | 1.168 | FALSE | 2024-01-21 04:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_5428_22 | ACLineSegment | Line | 13.5424 | 0.74528 | 0.61979 | 5.5033 | FALSE | 2024-01-21 02:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_5566_22 | ACLineSegment | Line | 13.5424 | 0.0087372 | 0.0061663 | 0.064518 | FALSE | 2024-01-20 22:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_4939_22 | ACLineSegment | Line | 13.5424 | 0.21733 | 0.16908 | 1.6048 | FALSE | 2024-01-21 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_547_22 | Transformer | Transformer | 0.02375 | 0.014211 | 0.0080577 | 59.8368 | FALSE | 2024-01-17 19:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_142 | line_4935_22 | ACLineSegment | Line | 12.3112 | 0.0053577 | 0.0037786 | 0.043519 | FALSE | 2024-07-16 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_4965_22 | ACLineSegment | Line | 0.034884 | 0.010907 | 0.006482 | 31.2676 | FALSE | 2024-07-10 21:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_4966_22 | ACLineSegment | Line | 0.034884 | 0.0042869 | 0.0026027 | 12.2892 | FALSE | 2024-01-20 17:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_5099_22 | ACLineSegment | Line | 12.3112 | 0.025693 | 0.019222 | 0.20869 | FALSE | 2024-01-21 04:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_5111_22 | ACLineSegment | Line | 12.3112 | 0.23022 | 0.19216 | 1.87 | FALSE | 2024-01-20 10:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_5442_22 | ACLineSegment | Line | 13.5424 | 0.30987 | 0.25433 | 2.2882 | FALSE | 2024-01-21 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_5345_22 | ACLineSegment | Line | 12.3112 | 0.0057022 | 0.0037529 | 0.046317 | FALSE | 2024-01-20 05:00 | 600 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_5429_22 | ACLineSegment | Line | 13.5424 | 0.74905 | 0.62297 | 5.5312 | FALSE | 2024-01-21 02:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | tr_1237_22 | Transformer | Transformer | 0.02375 | 0.0072565 | 0.0048002 | 30.5538 | FALSE | 2024-01-18 04:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_142 | line_6359_22 | ACLineSegment | Line | 0.034884 | 0.0072565 | 0.0048002 | 20.8022 | FALSE | 2024-01-18 04:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_912_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_142 | line_6639_22 | ACLineSegment | Line | 0.51338 | 0.0068903 | 0.0050917 | 1.3421 | FALSE | 2024-01-21 04:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_142 | line_667_22 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_116127_21 | ACLineSegment | Line | 13.5424 | 0.49088 | 0.38032 | 3.6247 | FALSE | 2024-01-21 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | line_128625_21 | ACLineSegment | Line | 13.5424 | 0.45393 | 0.35758 | 3.3519 | FALSE | 2024-01-21 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | tr_10640_21 | Transformer | Transformer | 0.07125 | 0.0047718 | 0.0030133 | 6.6973 | FALSE | 2024-01-17 07:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_18 | line_126656_21 | ACLineSegment | Line | 0.94778 | 0.034738 | 0.022834 | 3.6653 | FALSE | 2024-01-21 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_107809_21 | ACLineSegment | Line | 13.5424 | 1.8109 | 1.3719 | 13.3725 | FALSE | 2024-01-21 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | line_107810_21 | ACLineSegment | Line | 13.5424 | 1.8686 | 1.4115 | 13.7983 | FALSE | 2024-01-21 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | tr_660_21 | Transformer | Transformer | 0.02375 | 0.0093544 | 0.0053866 | 39.387 | FALSE | 2024-01-20 07:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_18 | line_107808_21 | ACLineSegment | Line | 0.94778 | 0.049844 | 0.03449 | 5.259 | FALSE | 2024-01-21 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_106465_21 | ACLineSegment | Line | 13.5424 | 0.034143 | 0.023197 | 0.25212 | FALSE | 2024-01-17 20:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | line_127115_21 | ACLineSegment | Line | 13.5424 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | tr_9246_21 | Transformer | Transformer | 0.1425 | 0.0073881 | 0.0044113 | 5.1847 | FALSE | 2024-01-20 13:00 |  |  | 150 | 3 | Transformer_kVA_x_PF
GSO_18 | line_108159_21 | ACLineSegment | Line | 0.94778 | 0.028885 | 0.019652 | 3.0476 | FALSE | 2024-01-20 21:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_108322_21 | ACLineSegment | Line | 13.5424 | 1.9213 | 1.4591 | 14.1874 | FALSE | 2024-01-21 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | line_108323_21 | ACLineSegment | Line | 13.5424 | 2.2568 | 1.7138 | 16.6645 | FALSE | 2024-01-21 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | tr_833_21 | Transformer | Transformer | 0.02375 | 0.024982 | 0.014506 | 105.1864 | TRUE | 2024-01-20 10:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_18 | line_108321_21 | ACLineSegment | Line | 0.94778 | 0.33113 | 0.23954 | 34.9378 | FALSE | 2024-01-20 20:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_109743_21 | ACLineSegment | Line | 13.5424 | 0.20511 | 0.15367 | 1.5146 | FALSE | 2024-01-20 05:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | line_110125_21 | ACLineSegment | Line | 13.5424 | 0.08374 | 0.063452 | 0.61835 | FALSE | 2024-01-17 23:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | tr_1495_21 | Transformer | Transformer | 0.02375 | 0.0053439 | 0.002885 | 22.5006 | FALSE | 2024-01-20 19:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_18 | line_110213_21 | ACLineSegment | Line | 0.94778 | 0.062477 | 0.045879 | 6.5919 | FALSE | 2024-01-20 11:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_108303_21 | ACLineSegment | Line | 13.5424 | 0.94782 | 0.72909 | 6.9989 | FALSE | 2024-01-21 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | line_110281_21 | ACLineSegment | Line | 13.5424 | 1.31 | 0.99852 | 9.6731 | FALSE | 2024-01-21 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | tr_1520_21 | Transformer | Transformer | 0.02375 | 0.019702 | 0.013955 | 82.9568 | FALSE | 2024-07-15 07:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_18 | line_110282_21 | ACLineSegment | Line | 0.94778 | 0.34624 | 0.25588 | 36.5323 | FALSE | 2024-01-21 03:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_111504_21 | ACLineSegment | Line | 0.94778 | 0.0086606 | 0.0045082 | 0.91377 | FALSE | 2024-01-20 23:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_111505_21 | ACLineSegment | Line | 0.94778 | 0.0029534 | 0.0015139 | 0.31161 | FALSE | 2024-01-17 22:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | tr_1985_21 | Transformer | Transformer | 0.02375 | 0.0065989 | 0.0031599 | 27.7847 | FALSE | 2024-01-20 23:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_18 | line_116128_21 | ACLineSegment | Line | 13.5424 | 0.010261 | 0.0068073 | 0.075773 | FALSE | 2024-01-21 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | tr_11870_21 | Transformer | Transformer | 0.475 | 0.0068239 | 0.0050312 | 1.4366 | FALSE | 2024-01-21 04:00 |  |  | 500 | 3 | Transformer_kVA_x_PF
GSO_18 | tr_2009_21 | Transformer | Transformer | 0.02375 | 0.0037026 | 0.0022685 | 15.59 | FALSE | 2024-01-21 01:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_18 | line_110794_21 | ACLineSegment | Line | 13.5424 | 1.7903 | 1.3567 | 13.2201 | FALSE | 2024-01-21 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | line_111728_21 | ACLineSegment | Line | 13.5424 | 1.7144 | 1.2998 | 12.6599 | FALSE | 2024-01-21 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | tr_2082_21 | Transformer | Transformer | 0.02375 | 0.0046593 | 0.0026971 | 19.6179 | FALSE | 2024-01-17 09:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_18 | line_111729_21 | ACLineSegment | Line | 0.94778 | 0.077793 | 0.053976 | 8.2079 | FALSE | 2024-01-20 07:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_108372_21 | ACLineSegment | Line | 13.5424 | 0.015456 | 0.010029 | 0.11413 | FALSE | 2024-01-20 23:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | line_115816_21 | ACLineSegment | Line | 13.5424 | 0.045756 | 0.029607 | 0.33788 | FALSE | 2024-01-21 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | tr_3781_21 | Transformer | Transformer | 0.02375 | 0.0084229 | 0.0051069 | 35.4647 | FALSE | 2024-01-17 17:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_18 | line_112325_21 | ACLineSegment | Line | 0.94778 | 0.024663 | 0.014993 | 2.6022 | FALSE | 2024-01-21 04:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_112973_21 | ACLineSegment | Line | 13.5424 | 0.019439 | 0.014852 | 0.14354 | FALSE | 2024-01-21 03:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | tr_12327_21 | Transformer | Transformer | 0.07125 | 0.0044636 | 0.0034683 | 6.2648 | FALSE | 2024-01-20 21:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_18 | line_112861_21 | ACLineSegment | Line | 0.94778 | 0.015937 | 0.011906 | 1.6816 | FALSE | 2024-01-21 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | tr_2431_21 | Transformer | Transformer | 0.02375 | 0.01032 | 0.0056026 | 43.4517 | FALSE | 2024-01-20 07:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_18 | line_106667_21 | ACLineSegment | Line | 0.94778 | 0.40253 | 0.29394 | 42.4706 | FALSE | 2024-01-20 23:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_112222_21 | ACLineSegment | Line | 13.5424 | 0.35613 | 0.26865 | 2.6298 | FALSE | 2024-07-15 23:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | line_113499_21 | ACLineSegment | Line | 13.5424 | 0.36186 | 0.2757 | 2.672 | FALSE | 2024-07-15 23:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | tr_10639_21 | Transformer | Transformer | 0.07125 | 0.0076195 | 0.005785 | 10.694 | FALSE | 2024-06-26 11:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_18 | line_106670_21 | ACLineSegment | Line | 0.94778 | 0.0052362 | 0.0036397 | 0.55247 | FALSE | 2024-01-20 14:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_129230_21 | ACLineSegment | Line | 13.5424 | 0.027707 | 0.018181 | 0.20459 | FALSE | 2024-01-21 01:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | tr_10624_21 | Transformer | Transformer | 0.285 | 0.0051941 | 0.0041106 | 1.8225 | FALSE | 2024-07-05 08:00 |  |  | 300 | 3 | Transformer_kVA_x_PF
GSO_18 | line_106690_21 | ACLineSegment | Line | 0.94778 | 0.023532 | 0.014625 | 2.4828 | FALSE | 2024-01-21 01:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_106801_21 | ACLineSegment | Line | 0.94778 | 0.071386 | 0.04963 | 7.5319 | FALSE | 2024-01-21 03:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_108246_21 | ACLineSegment | Line | 13.5424 | 0.04227 | 0.031572 | 0.31213 | FALSE | 2024-01-20 05:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | tr_10002_21 | Transformer | Transformer | 0.07125 | 0.0066831 | 0.0045068 | 9.3799 | FALSE | 2024-01-20 05:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_18 | line_106886_21 | ACLineSegment | Line | 0.94778 | 0.036238 | 0.027878 | 3.8235 | FALSE | 2024-01-20 15:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_106064_21 | ACLineSegment | Line | 0.94778 | 0.0046671 | 0.0022823 | 0.49243 | FALSE | 2024-01-20 23:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_106666_21 | ACLineSegment | Line | 0.94778 | 0.38129 | 0.27826 | 40.2303 | FALSE | 2024-01-20 23:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_112184_21 | ACLineSegment | Line | 0.94778 | 0.36889 | 0.26906 | 38.9213 | FALSE | 2024-01-20 23:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | tr_2273_21 | Transformer | Transformer | 0.02375 | 0.011039 | 0.0067688 | 46.481 | FALSE | 2024-01-20 09:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_18 | tr_74_21 | Transformer | Transformer | 0.02375 | 0.0046671 | 0.0022823 | 19.6511 | FALSE | 2024-01-20 23:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_18 | line_106065_21 | ACLineSegment | Line | 0.034884 | 0.0046671 | 0.0022823 | 13.3792 | FALSE | 2024-01-20 23:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_90187_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_106073_21 | ACLineSegment | Line | 0.94778 | 0.15117 | 0.10131 | 15.9502 | FALSE | 2024-01-20 15:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_109986_21 | ACLineSegment | Line | 0.94778 | 0.34284 | 0.25205 | 36.1727 | FALSE | 2024-01-21 03:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_109987_21 | ACLineSegment | Line | 0.94778 | 0.064184 | 0.045131 | 6.7721 | FALSE | 2024-01-20 17:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_109988_21 | ACLineSegment | Line | 0.94778 | 0.14544 | 0.10128 | 15.3452 | FALSE | 2024-01-21 01:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | tr_1411_21 | Transformer | Transformer | 0.02375 | 0.0060046 | 0.0036965 | 25.2826 | FALSE | 2024-07-15 05:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_18 | line_106074_21 | ACLineSegment | Line | 0.94778 | 0.13462 | 0.086349 | 14.2033 | FALSE | 2024-01-20 15:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | tr_77_21 | Transformer | Transformer | 0.02375 | 0.023975 | 0.014942 | 100.9476 | TRUE | 2024-01-20 12:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_18 | line_115874_21 | ACLineSegment | Line | 0.94778 | 0.078337 | 0.051352 | 8.2653 | FALSE | 2024-01-21 03:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | tr_3798_21 | Transformer | Transformer | 0.0475 | 0.056915 | 0.034978 | 119.8211 | TRUE | 2024-01-20 15:00 |  |  | 50 | 1 | Transformer_kVA_x_PF
GSO_18 | line_106075_21 | ACLineSegment | Line | 0.034884 | 0.0063612 | 0.0033936 | 18.2356 | FALSE | 2024-01-20 18:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_106076_21 | ACLineSegment | Line | 0.034884 | 0.0091973 | 0.0037224 | 26.3657 | FALSE | 2024-01-20 12:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_90310_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_90311_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_90313_21 | ACLineSegment | Line | 0.034884 | 0.010758 | 0.005953 | 30.8405 | FALSE | 2024-01-20 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_90316_21 | ACLineSegment | Line | 0.034884 | 0.0047679 | 0.0026383 | 13.668 | FALSE | 2024-07-15 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_106218_21 | ACLineSegment | Line | 13.5424 | 0.031574 | 0.025455 | 0.23315 | FALSE | 2024-07-15 23:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | line_106219_21 | ACLineSegment | Line | 13.5424 | 0.035876 | 0.028828 | 0.26492 | FALSE | 2024-07-15 23:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | tr_125_21 | Transformer | Transformer | 0.07125 | 0.0058504 | 0.0042878 | 8.2111 | FALSE | 2024-01-17 14:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_18 | line_107862_21 | ACLineSegment | Line | 13.5424 | 0.0081087 | 0.0064384 | 0.059877 | FALSE | 2024-01-20 12:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | line_107863_21 | ACLineSegment | Line | 13.5424 | 0.022325 | 0.01724 | 0.16485 | FALSE | 2024-07-15 23:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | tr_679_21 | Transformer | Transformer | 0.285 | 0.0052391 | 0.0034498 | 1.8383 | FALSE | 2024-01-20 09:00 |  |  | 300 | 3 | Transformer_kVA_x_PF
GSO_18 | line_112666_21 | ACLineSegment | Line | 13.5424 | 0.041165 | 0.033061 | 0.30397 | FALSE | 2024-07-15 23:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | tr_2496_21 | Transformer | Transformer | 0.1425 | 0.0075747 | 0.0050433 | 5.3156 | FALSE | 2024-01-20 05:00 |  |  | 150 | 3 | Transformer_kVA_x_PF
GSO_18 | line_106220_21 | ACLineSegment | Line | 0.51338 | 0.0058504 | 0.0042878 | 1.1396 | FALSE | 2024-01-17 14:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | line_91425_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_106466_21 | ACLineSegment | Line | 13.5424 | 0.039312 | 0.027527 | 0.29029 | FALSE | 2024-01-17 20:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | tr_208_21 | Transformer | Transformer | 0.02375 | 0.0076292 | 0.0045029 | 32.1229 | FALSE | 2024-01-20 23:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_18 | line_111484_21 | ACLineSegment | Line | 13.5424 | 0.045781 | 0.030921 | 0.33805 | FALSE | 2024-01-20 09:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | tr_9257_21 | Transformer | Transformer | 0.02375 | 0.0068273 | 0.0042375 | 28.7466 | FALSE | 2024-01-20 09:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_18 | line_106467_21 | ACLineSegment | Line | 0.034884 | 0.0035476 | 0.0021582 | 10.1699 | FALSE | 2024-07-15 12:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_90823_21 | ACLineSegment | Line | 0.034884 | 0.0043188 | 0.0025116 | 12.3807 | FALSE | 2024-01-20 23:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_106608_21 | ACLineSegment | Line | 0.94778 | 0.051176 | 0.035531 | 5.3996 | FALSE | 2024-01-20 06:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_109050_21 | ACLineSegment | Line | 0.94778 | 0.12577 | 0.090922 | 13.2697 | FALSE | 2024-01-20 20:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_109051_21 | ACLineSegment | Line | 0.94778 | 0.18058 | 0.12849 | 19.0534 | FALSE | 2024-01-20 20:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | tr_1088_21 | Transformer | Transformer | 0.02375 | 0.0043535 | 0.002382 | 18.3307 | FALSE | 2024-01-20 18:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_18 | tr_256_21 | Transformer | Transformer | 0.0475 | 0.051176 | 0.035531 | 107.7385 | TRUE | 2024-01-20 06:00 |  |  | 50 | 1 | Transformer_kVA_x_PF
GSO_18 | line_106609_21 | ACLineSegment | Line | 0.034884 | 0.0031382 | 0.0018215 | 8.9961 | FALSE | 2024-01-20 06:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_90897_21 | ACLineSegment | Line | 0.034884 | 0.02792 | 0.017319 | 80.0368 | FALSE | 2024-01-20 05:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_90898_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_90903_21 | ACLineSegment | Line | 0.034884 | 0.025578 | 0.016601 | 73.3255 | FALSE | 2024-01-21 03:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_106648_21 | ACLineSegment | Line | 13.5424 | 0.0091022 | 0.0060637 | 0.067213 | FALSE | 2024-01-20 13:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | line_106649_21 | ACLineSegment | Line | 13.5424 | 0.01572 | 0.0106 | 0.11608 | FALSE | 2024-01-20 13:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | tr_269_21 | Transformer | Transformer | 0.07125 | 0.0066858 | 0.0053905 | 9.3836 | FALSE | 2024-01-20 08:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_18 | tr_1655_21 | Transformer | Transformer | 0.07125 | 0.0091022 | 0.0060637 | 12.775 | FALSE | 2024-01-20 13:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_18 | line_111342_21 | ACLineSegment | Line | 13.5424 | 0.056723 | 0.04145 | 0.41886 | FALSE | 2024-01-20 09:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | line_111343_21 | ACLineSegment | Line | 13.5424 | 0.083989 | 0.065655 | 0.6202 | FALSE | 2024-01-20 12:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | tr_1922_21 | Transformer | Transformer | 0.0475 | 0.023988 | 0.018126 | 50.5008 | FALSE | 2024-01-17 17:00 |  |  | 50 | 1 | Transformer_kVA_x_PF
GSO_18 | line_106650_21 | ACLineSegment | Line | 0.51338 | 0.0066858 | 0.0053905 | 1.3023 | FALSE | 2024-01-20 08:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | line_90966_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | tr_274_21 | Transformer | Transformer | 0.02375 | 0.024009 | 0.016695 | 101.0909 | TRUE | 2024-01-20 09:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_18 | line_106668_21 | ACLineSegment | Line | 0.94778 | 0.041312 | 0.026915 | 4.3588 | FALSE | 2024-01-20 21:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_116237_21 | ACLineSegment | Line | 0.94778 | 0.10001 | 0.068597 | 10.5517 | FALSE | 2024-01-20 21:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | tr_3954_21 | Transformer | Transformer | 0.0475 | 0.060329 | 0.041864 | 127.0079 | TRUE | 2024-01-21 01:00 |  |  | 50 | 1 | Transformer_kVA_x_PF
GSO_18 | line_106669_21 | ACLineSegment | Line | 0.94778 | 0.036215 | 0.022685 | 3.821 | FALSE | 2024-01-20 21:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | tr_275_21 | Transformer | Transformer | 0.02375 | 0.0065548 | 0.0041921 | 27.5992 | FALSE | 2024-01-21 01:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_18 | tr_3974_21 | Transformer | Transformer | 0.0475 | 0.036215 | 0.022685 | 76.2412 | FALSE | 2024-01-20 21:00 |  |  | 50 | 1 | Transformer_kVA_x_PF
GSO_18 | tr_276_21 | Transformer | Transformer | 0.02375 | 0.0052362 | 0.0036397 | 22.0472 | FALSE | 2024-01-20 14:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_18 | line_106671_21 | ACLineSegment | Line | 0.034884 | 0.0052362 | 0.0036397 | 15.0106 | FALSE | 2024-01-20 14:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_90951_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | tr_284_21 | Transformer | Transformer | 0.02375 | 0.023532 | 0.014625 | 99.08 | FALSE | 2024-01-21 01:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_18 | line_106691_21 | ACLineSegment | Line | 0.034884 | 0.0073987 | 0.004368 | 21.2096 | FALSE | 2024-01-17 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_106692_21 | ACLineSegment | Line | 0.034884 | 0.0056437 | 0.0035161 | 16.1788 | FALSE | 2024-01-18 04:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_106693_21 | ACLineSegment | Line | 0.034884 | 0.0048648 | 0.0027238 | 13.9459 | FALSE | 2024-01-20 13:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_106694_21 | ACLineSegment | Line | 0.034884 | 0.0037491 | 0.0021968 | 10.7476 | FALSE | 2024-07-15 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_106695_21 | ACLineSegment | Line | 0.034884 | 0.0049853 | 0.0027766 | 14.2914 | FALSE | 2024-01-18 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_106802_21 | ACLineSegment | Line | 0.94778 | 0.041725 | 0.026945 | 4.4024 | FALSE | 2024-01-17 08:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | tr_316_21 | Transformer | Transformer | 0.02375 | 0.032986 | 0.022944 | 138.8866 | TRUE | 2024-01-21 03:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_18 | tr_9936_21 | Transformer | Transformer | 0.02375 | 0.041725 | 0.026945 | 175.6829 | TRUE | 2024-01-17 08:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_18 | line_106839_21 | ACLineSegment | Line | 2.3694 | 0.0086395 | 0.0046458 | 0.36462 | FALSE | 2024-01-20 19:00 | 600 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_107001_21 | ACLineSegment | Line | 0.94778 | 0.022665 | 0.015371 | 2.3914 | FALSE | 2024-01-20 19:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | tr_384_21 | Transformer | Transformer | 0.02375 | 0.016476 | 0.010978 | 69.3727 | FALSE | 2024-07-15 20:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_18 | line_106840_21 | ACLineSegment | Line | 0.025406 | 0.0026415 | 0.0014993 | 10.3973 | FALSE | 2024-01-21 22:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_91338_21 | ACLineSegment | Line | 0.038174 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 290 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_91339_21 | ACLineSegment | Line | 0.025406 | 0.0064007 | 0.0033203 | 25.1938 | FALSE | 2024-01-20 19:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | tr_329_21 | Transformer | Transformer | 0.02375 | 0.0086395 | 0.0046458 | 36.3766 | FALSE | 2024-01-20 19:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_18 | line_106885_21 | ACLineSegment | Line | 0.94778 | 0.02572 | 0.019442 | 2.7137 | FALSE | 2024-07-15 21:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | tr_345_21 | Transformer | Transformer | 0.0475 | 0.013665 | 0.010051 | 28.7687 | FALSE | 2024-01-17 19:00 |  |  | 50 | 1 | Transformer_kVA_x_PF
GSO_18 | line_110709_21 | ACLineSegment | Line | 0.94778 | 0.0067783 | 0.005023 | 0.71518 | FALSE | 2024-07-15 21:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | tr_1677_21 | Transformer | Transformer | 0.02375 | 0.019869 | 0.015474 | 83.6593 | FALSE | 2024-07-15 14:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_18 | line_106887_21 | ACLineSegment | Line | 0.034884 | 0.0034022 | 0.0016672 | 9.7531 | FALSE | 2024-01-20 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_106888_21 | ACLineSegment | Line | 0.034884 | 0.0075037 | 0.0055249 | 21.5108 | FALSE | 2024-01-20 22:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_106889_21 | ACLineSegment | Line | 0.034884 | 0.005112 | 0.0039446 | 14.6545 | FALSE | 2024-01-21 15:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | tr_783_21 | Transformer | Transformer | 0.02375 | 0.007994 | 0.0046061 | 33.6588 | FALSE | 2024-01-18 04:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_18 | line_107002_21 | ACLineSegment | Line | 0.025406 | 0.0061029 | 0.0035508 | 24.0218 | FALSE | 2024-01-20 07:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_91901_21 | ACLineSegment | Line | 0.025406 | 0.011588 | 0.0076311 | 45.6098 | FALSE | 2024-01-20 22:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | tr_9123_21 | Transformer | Transformer | 0.0475 | 0.049844 | 0.03449 | 104.9341 | TRUE | 2024-01-21 |  |  | 50 | 1 | Transformer_kVA_x_PF
GSO_18 | line_110795_21 | ACLineSegment | Line | 13.5424 | 1.804 | 1.3669 | 13.3215 | FALSE | 2024-01-21 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | tr_10613_21 | Transformer | Transformer | 0.02375 | 0.0089003 | 0.0066234 | 37.4751 | FALSE | 2024-01-17 13:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_18 | line_129223_21 | ACLineSegment | Line | 13.5424 | 1.8717 | 1.4196 | 13.8212 | FALSE | 2024-01-21 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | tr_10616_21 | Transformer | Transformer | 0.285 | 0.029193 | 0.020934 | 10.2433 | FALSE | 2024-02-14 22:00 |  |  | 300 | 3 | Transformer_kVA_x_PF
GSO_18 | line_107811_21 | ACLineSegment | Line | 0.034884 | 0.0036923 | 0.002081 | 10.5848 | FALSE | 2024-01-17 13:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_92843_21 | ACLineSegment | Line | 0.034884 | 0.0061757 | 0.0035436 | 17.7037 | FALSE | 2024-01-20 07:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_92845_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | tr_1034_21 | Transformer | Transformer | 0.285 | 0.0081087 | 0.0064384 | 2.8452 | FALSE | 2024-01-20 12:00 |  |  | 300 | 3 | Transformer_kVA_x_PF
GSO_18 | line_113658_21 | ACLineSegment | Line | 13.5424 | 0.01913 | 0.013935 | 0.14126 | FALSE | 2024-07-15 23:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | tr_8914_21 | Transformer | Transformer | 0.0475 | 0.0053037 | 0.0040995 | 11.1658 | FALSE | 2024-01-18 |  |  | 50 | 1 | Transformer_kVA_x_PF
GSO_18 | line_107864_21 | ACLineSegment | Line | 0.51338 | 0.0052391 | 0.0034498 | 1.0205 | FALSE | 2024-01-20 09:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | line_92855_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_108116_21 | ACLineSegment | Line | 13.5424 | 0.57971 | 0.44098 | 4.2807 | FALSE | 2024-01-21 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | line_108117_21 | ACLineSegment | Line | 13.5424 | 0.61215 | 0.46469 | 4.5202 | FALSE | 2024-01-21 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | tr_767_21 | Transformer | Transformer | 0.02375 | 0.036247 | 0.024018 | 152.6173 | TRUE | 2024-01-21 01:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_18 | tr_3910_21 | Transformer | Transformer | 0.0475 | 0.083254 | 0.058142 | 175.2707 | TRUE | 2024-01-21 03:00 |  |  | 50 | 1 | Transformer_kVA_x_PF
GSO_18 | line_108304_21 | ACLineSegment | Line | 13.5424 | 0.62574 | 0.47218 | 4.6206 | FALSE | 2024-01-21 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | tr_9073_21 | Transformer | Transformer | 0.02375 | 0.013592 | 0.0083714 | 57.228 | FALSE | 2024-01-21 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_18 | line_108160_21 | ACLineSegment | Line | 0.034884 | 0.007994 | 0.0046061 | 22.9162 | FALSE | 2024-01-18 04:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_93090_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_108245_21 | ACLineSegment | Line | 13.5424 | 0.050119 | 0.038698 | 0.37009 | FALSE | 2024-01-20 15:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | line_110779_21 | ACLineSegment | Line | 13.5424 | 0.16811 | 0.13379 | 1.2414 | FALSE | 2024-01-20 15:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | line_110780_21 | ACLineSegment | Line | 13.5424 | 0.12069 | 0.093121 | 0.89118 | FALSE | 2024-01-20 08:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | tr_1702_21 | Transformer | Transformer | 0.07125 | 0.0068304 | 0.0054003 | 9.5865 | FALSE | 2024-07-16 02:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_18 | tr_812_21 | Transformer | Transformer | 0.0475 | 0.010152 | 0.007818 | 21.3729 | FALSE | 2024-01-22 03:00 |  |  | 50 | 1 | Transformer_kVA_x_PF
GSO_18 | line_108247_21 | ACLineSegment | Line | 0.034884 | 0.007406 | 0.004701 | 21.2307 | FALSE | 2024-01-21 03:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_108248_21 | ACLineSegment | Line | 0.034884 | 0.0053949 | 0.0041756 | 15.4655 | FALSE | 2024-01-17 23:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_108305_21 | ACLineSegment | Line | 13.5424 | 0.29386 | 0.21768 | 2.1699 | FALSE | 2024-01-20 13:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | tr_828_21 | Transformer | Transformer | 0.0475 | 0.059845 | 0.039948 | 125.9898 | TRUE | 2024-01-20 23:00 |  |  | 50 | 1 | Transformer_kVA_x_PF
GSO_18 | line_109744_21 | ACLineSegment | Line | 13.5424 | 0.20849 | 0.15661 | 1.5395 | FALSE | 2024-01-20 05:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | tr_9205_21 | Transformer | Transformer | 0.0475 | 0.087605 | 0.062266 | 184.4321 | TRUE | 2024-01-20 13:00 |  |  | 50 | 1 | Transformer_kVA_x_PF
GSO_18 | line_108642_21 | ACLineSegment | Line | 0.94778 | 0.3042 | 0.21947 | 32.0962 | FALSE | 2024-01-20 20:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | tr_946_21 | Transformer | Transformer | 0.0475 | 0.031286 | 0.020208 | 65.8652 | FALSE | 2024-01-21 |  |  | 50 | 1 | Transformer_kVA_x_PF
GSO_18 | line_122867_21 | ACLineSegment | Line | 13.5424 | 1.8985 | 1.4425 | 14.0188 | FALSE | 2024-01-21 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | tr_6998_21 | Transformer | Transformer | 0.02375 | 0.023886 | 0.016282 | 100.5706 | TRUE | 2024-01-17 20:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_18 | line_108324_21 | ACLineSegment | Line | 0.034884 | 0.0031643 | 0.0020178 | 9.0709 | FALSE | 2024-07-15 03:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_93258_21 | ACLineSegment | Line | 0.034884 | 0.013409 | 0.0071101 | 38.4404 | FALSE | 2024-01-20 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_93260_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_93261_21 | ACLineSegment | Line | 0.034884 | 0.0089642 | 0.0057073 | 25.6976 | FALSE | 2024-01-18 04:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_108371_21 | ACLineSegment | Line | 13.5424 | 0.013465 | 0.0090945 | 0.099428 | FALSE | 2024-01-20 23:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | line_108373_21 | ACLineSegment | Line | 13.5424 | 0.015456 | 0.010029 | 0.11413 | FALSE | 2024-01-20 23:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | tr_850_21 | Transformer | Transformer | 0.0095 | 0.0021668 | 0.0011974 | 22.8085 | FALSE | 2024-01-21 03:00 |  |  | 10 | 1 | Transformer_kVA_x_PF
GSO_18 | line_111503_21 | ACLineSegment | Line | 0.94778 | 0.0086606 | 0.0045082 | 0.91377 | FALSE | 2024-01-20 23:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | tr_2617_21 | Transformer | Transformer | 0.095 | 0.0073095 | 0.0053054 | 7.6942 | FALSE | 2024-01-21 01:00 |  |  | 100 | 3 | Transformer_kVA_x_PF
GSO_18 | line_108374_21 | ACLineSegment | Line | 0.034884 | 0.0021668 | 0.0011974 | 6.2115 | FALSE | 2024-01-21 03:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_108379_21 | ACLineSegment | Line | 0.94778 | 0.037686 | 0.023325 | 3.9762 | FALSE | 2024-01-20 07:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_108380_21 | ACLineSegment | Line | 0.94778 | 0.11445 | 0.077794 | 12.0759 | FALSE | 2024-01-20 21:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_108381_21 | ACLineSegment | Line | 0.94778 | 0.075512 | 0.048594 | 7.9672 | FALSE | 2024-01-20 21:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | tr_853_21 | Transformer | Transformer | 0.02375 | 0.011311 | 0.0062968 | 47.6264 | FALSE | 2024-01-20 14:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_18 | line_111444_21 | ACLineSegment | Line | 0.94778 | 0.023973 | 0.015955 | 2.5294 | FALSE | 2024-01-20 07:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | tr_2699_21 | Transformer | Transformer | 0.02375 | 0.013713 | 0.0075542 | 57.7372 | FALSE | 2024-01-20 07:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_18 | line_112251_21 | ACLineSegment | Line | 0.94778 | 0.20706 | 0.14925 | 21.8465 | FALSE | 2024-01-20 15:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | tr_3877_21 | Transformer | Transformer | 0.0475 | 0.060695 | 0.041878 | 127.7793 | TRUE | 2024-01-21 01:00 |  |  | 50 | 1 | Transformer_kVA_x_PF
GSO_18 | tr_10625_21 | Transformer | Transformer | 0.0475 | 0.075512 | 0.048594 | 158.972 | TRUE | 2024-01-20 21:00 |  |  | 50 | 1 | Transformer_kVA_x_PF
GSO_18 | line_108382_21 | ACLineSegment | Line | 0.034884 | 0.0066064 | 0.0030278 | 18.9384 | FALSE | 2024-01-21 04:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_93306_21 | ACLineSegment | Line | 0.034884 | 0.0073682 | 0.0035898 | 21.1224 | FALSE | 2024-01-20 14:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_115810_21 | ACLineSegment | Line | 0.94778 | 0.25416 | 0.17925 | 26.8159 | FALSE | 2024-01-20 20:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | tr_3780_21 | Transformer | Transformer | 0.0475 | 0.057416 | 0.039537 | 120.8762 | TRUE | 2024-01-21 03:00 |  |  | 50 | 1 | Transformer_kVA_x_PF
GSO_18 | line_108643_21 | ACLineSegment | Line | 0.034884 | 0.005235 | 0.0032597 | 15.0071 | FALSE | 2024-01-20 18:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_92924_21 | ACLineSegment | Line | 0.034884 | 0.014096 | 0.00847 | 40.4086 | FALSE | 2024-01-20 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_92929_21 | ACLineSegment | Line | 0.034884 | 0.015077 | 0.0089692 | 43.2216 | FALSE | 2024-01-21 04:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_108895_21 | ACLineSegment | Line | 0.51338 | 0.0052261 | 0.0038817 | 1.018 | FALSE | 2024-06-23 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | line_108896_21 | ACLineSegment | Line | 0.51338 | 0.0045948 | 0.0033489 | 0.89501 | FALSE | 2024-01-17 09:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | line_93738_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_93739_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_108953_21 | ACLineSegment | Line | 0.94778 | 0.0088335 | 0.0041167 | 0.93203 | FALSE | 2024-01-20 05:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_108954_21 | ACLineSegment | Line | 0.94778 | 0.10413 | 0.075263 | 10.987 | FALSE | 2024-01-20 09:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_108955_21 | ACLineSegment | Line | 0.94778 | 0.090327 | 0.066732 | 9.5304 | FALSE | 2024-01-20 20:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | tr_1056_21 | Transformer | Transformer | 0.02375 | 0.0097196 | 0.0056272 | 40.9245 | FALSE | 2024-01-20 09:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_18 | tr_1314_21 | Transformer | Transformer | 0.02375 | 0.0088335 | 0.0041167 | 37.1938 | FALSE | 2024-01-20 05:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_18 | line_109719_21 | ACLineSegment | Line | 0.94778 | 0.11784 | 0.085427 | 12.4329 | FALSE | 2024-01-20 20:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | tr_1323_21 | Transformer | Transformer | 0.02375 | 0.01573 | 0.010412 | 66.233 | FALSE | 2024-07-15 12:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_18 | line_126719_21 | ACLineSegment | Line | 0.94778 | 0.008912 | 0.0056259 | 0.9403 | FALSE | 2024-01-20 09:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_127045_21 | ACLineSegment | Line | 0.94778 | 0.041246 | 0.029162 | 4.3519 | FALSE | 2024-01-17 07:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | tr_12661_21 | Transformer | Transformer | 0.0475 | 0.04635 | 0.032484 | 97.5786 | FALSE | 2024-01-20 20:00 |  |  | 50 | 1 | Transformer_kVA_x_PF
GSO_18 | tr_1317_21 | Transformer | Transformer | 0.02375 | 0.0098724 | 0.0056418 | 41.568 | FALSE | 2024-01-20 10:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_18 | line_116051_21 | ACLineSegment | Line | 0.94778 | 0.23505 | 0.16661 | 24.8005 | FALSE | 2024-01-20 20:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | tr_3871_21 | Transformer | Transformer | 0.0475 | 0.056178 | 0.038141 | 118.2687 | TRUE | 2024-01-20 13:00 |  |  | 50 | 1 | Transformer_kVA_x_PF
GSO_18 | line_109052_21 | ACLineSegment | Line | 0.034884 | 0.0043535 | 0.002382 | 12.4802 | FALSE | 2024-01-20 18:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_93837_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_109710_21 | ACLineSegment | Line | 0.034884 | 0.0088335 | 0.0041167 | 25.323 | FALSE | 2024-01-20 05:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_94631_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_109720_21 | ACLineSegment | Line | 0.034884 | 0.0042587 | 0.0020311 | 12.2083 | FALSE | 2024-01-17 11:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_94634_21 | ACLineSegment | Line | 0.034884 | 0.0076216 | 0.0039692 | 21.8487 | FALSE | 2024-01-20 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_109738_21 | ACLineSegment | Line | 0.034884 | 0.0088631 | 0.0049926 | 25.4078 | FALSE | 2024-01-20 17:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_94647_21 | ACLineSegment | Line | 0.034884 | 0.003132 | 0.0019067 | 8.9783 | FALSE | 2024-07-15 13:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_94649_21 | ACLineSegment | Line | 0.034884 | 0.0070665 | 0.0039619 | 20.2574 | FALSE | 2024-01-21 04:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | tr_1325_21 | Transformer | Transformer | 0.02375 | 0.0042823 | 0.0027633 | 18.0306 | FALSE | 2024-01-20 20:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_18 | line_109745_21 | ACLineSegment | Line | 0.034884 | 0.0024244 | 0.0014816 | 6.95 | FALSE | 2024-01-18 02:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_94101_21 | ACLineSegment | Line | 0.034884 | 0.0024523 | 0.0014109 | 7.03 | FALSE | 2024-01-20 21:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | tr_2800_21 | Transformer | Transformer | 0.02375 | 0.0063226 | 0.0039789 | 26.6216 | FALSE | 2024-07-05 10:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_18 | tr_3794_21 | Transformer | Transformer | 0.0475 | 0.064184 | 0.045131 | 135.1246 | TRUE | 2024-01-20 17:00 |  |  | 50 | 1 | Transformer_kVA_x_PF
GSO_18 | tr_9252_21 | Transformer | Transformer | 0.0475 | 0.048069 | 0.032605 | 101.197 | TRUE | 2024-01-21 01:00 |  |  | 50 | 1 | Transformer_kVA_x_PF
GSO_18 | line_110126_21 | ACLineSegment | Line | 13.5424 | 0.081843 | 0.061928 | 0.60435 | FALSE | 2024-01-17 23:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | tr_1463_21 | Transformer | Transformer | 0.02375 | 0.0046616 | 0.0024844 | 19.6279 | FALSE | 2024-01-17 14:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_18 | line_113231_21 | ACLineSegment | Line | 13.5424 | 0.047938 | 0.03783 | 0.35399 | FALSE | 2024-07-15 23:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | tr_8968_21 | Transformer | Transformer | 0.095 | 0.038989 | 0.028965 | 41.041 | FALSE | 2024-07-18 20:00 |  |  | 100 | 3 | Transformer_kVA_x_PF
GSO_18 | line_110127_21 | ACLineSegment | Line | 0.034884 | 0.0046616 | 0.0024844 | 13.3634 | FALSE | 2024-01-17 14:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_94673_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | tr_3831_21 | Transformer | Transformer | 0.0475 | 0.062477 | 0.045879 | 131.5295 | TRUE | 2024-01-20 11:00 |  |  | 50 | 1 | Transformer_kVA_x_PF
GSO_18 | line_110214_21 | ACLineSegment | Line | 0.034884 | 0.0053439 | 0.002885 | 15.3193 | FALSE | 2024-01-20 19:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_94851_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_110283_21 | ACLineSegment | Line | 0.034884 | 0.0078533 | 0.0045182 | 22.513 | FALSE | 2024-01-17 08:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_110284_21 | ACLineSegment | Line | 0.034884 | 0.0038286 | 0.0022445 | 10.9754 | FALSE | 2024-01-20 19:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_94888_21 | ACLineSegment | Line | 0.034884 | 0.010209 | 0.0060568 | 29.2651 | FALSE | 2024-07-05 07:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_94889_21 | ACLineSegment | Line | 0.034884 | 0.0026897 | 0.0015787 | 7.7104 | FALSE | 2024-01-20 15:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_94892_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_110659_21 | ACLineSegment | Line | 0.51338 | 0.0091022 | 0.0060637 | 1.773 | FALSE | 2024-01-20 13:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | line_95746_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | tr_12321_21 | Transformer | Transformer | 0.02375 | 0.0067783 | 0.005023 | 28.5404 | FALSE | 2024-07-15 21:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_18 | line_110710_21 | ACLineSegment | Line | 0.034884 | 0.019869 | 0.015474 | 56.9584 | FALSE | 2024-07-15 14:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_112965_21 | ACLineSegment | Line | 13.5424 | 0.17197 | 0.13756 | 1.2699 | FALSE | 2024-01-20 15:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | tr_2627_21 | Transformer | Transformer | 0.02375 | 0.0077652 | 0.0039367 | 32.6954 | FALSE | 2024-01-21 02:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_18 | line_112972_21 | ACLineSegment | Line | 13.5424 | 0.024781 | 0.019003 | 0.18299 | FALSE | 2024-01-21 03:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | line_131950_21 | ACLineSegment | Line | 13.5424 | 0.074802 | 0.056225 | 0.55235 | FALSE | 2024-01-21 02:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | tr_12320_21 | Transformer | Transformer | 0.02375 | 0.030006 | 0.020502 | 126.3406 | TRUE | 2024-01-20 09:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_18 | line_110781_21 | ACLineSegment | Line | 0.51338 | 0.0068304 | 0.0054003 | 1.3305 | FALSE | 2024-07-16 02:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | tr_1709_21 | Transformer | Transformer | 0.02375 | 0.017419 | 0.011192 | 73.3414 | FALSE | 2024-07-15 07:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_18 | line_110796_21 | ACLineSegment | Line | 0.034884 | 0.0054537 | 0.0032423 | 15.6341 | FALSE | 2024-01-20 21:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_95209_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_95210_21 | ACLineSegment | Line | 0.034884 | 0.0067958 | 0.0041238 | 19.4816 | FALSE | 2024-07-15 07:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_95214_21 | ACLineSegment | Line | 0.034884 | 0.0071736 | 0.0042236 | 20.5645 | FALSE | 2024-01-20 18:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_129249_21 | ACLineSegment | Line | 13.5424 | 0.052162 | 0.037756 | 0.38518 | FALSE | 2024-01-20 09:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | tr_10636_21 | Transformer | Transformer | 0.07125 | 0.0058887 | 0.0043173 | 8.2648 | FALSE | 2024-01-21 05:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_18 | line_112168_21 | ACLineSegment | Line | 13.5424 | 0.089101 | 0.070406 | 0.65794 | FALSE | 2024-01-20 12:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | tr_10647_21 | Transformer | Transformer | 0.07125 | 0.0075997 | 0.0056761 | 10.6662 | FALSE | 2024-01-20 05:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_18 | line_111344_21 | ACLineSegment | Line | 0.034884 | 0.023988 | 0.018126 | 68.7658 | FALSE | 2024-01-17 17:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_95859_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | tr_1963_21 | Transformer | Transformer | 0.02375 | 0.023973 | 0.015955 | 100.9395 | TRUE | 2024-01-20 07:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_18 | line_111445_21 | ACLineSegment | Line | 0.034884 | 0.0040799 | 0.0025237 | 11.6957 | FALSE | 2024-07-15 08:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_111446_21 | ACLineSegment | Line | 0.034884 | 0.0038392 | 0.0020957 | 11.0058 | FALSE | 2024-01-20 16:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_95939_21 | ACLineSegment | Line | 0.034884 | 0.0087954 | 0.0052008 | 25.2135 | FALSE | 2024-01-17 17:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_95944_21 | ACLineSegment | Line | 0.034884 | 0.010928 | 0.0066673 | 31.3267 | FALSE | 2024-01-18 01:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_111485_21 | ACLineSegment | Line | 13.5424 | 0.048963 | 0.033491 | 0.36156 | FALSE | 2024-01-20 09:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | tr_1980_21 | Transformer | Transformer | 0.02375 | 0.0046411 | 0.0027385 | 19.5416 | FALSE | 2024-01-20 23:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_18 | tr_10644_21 | Transformer | Transformer | 0.07125 | 0.0070896 | 0.0053597 | 9.9503 | FALSE | 2024-07-10 13:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_18 | line_111486_21 | ACLineSegment | Line | 0.034884 | 0.0046411 | 0.0027385 | 13.3047 | FALSE | 2024-01-20 23:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_95991_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | tr_2654_21 | Transformer | Transformer | 0.02375 | 0.0029534 | 0.0015139 | 12.4354 | FALSE | 2024-01-17 22:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_18 | line_111506_21 | ACLineSegment | Line | 0.034884 | 0.0065989 | 0.0031599 | 18.9169 | FALSE | 2024-01-20 23:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_95999_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_111568_21 | ACLineSegment | Line | 0.034884 | 0.0037026 | 0.0022685 | 10.6143 | FALSE | 2024-01-21 01:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_96030_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_111623_21 | ACLineSegment | Line | 13.5424 | 0.0063272 | 0.0043012 | 0.046721 | FALSE | 2024-01-20 19:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | line_112166_21 | ACLineSegment | Line | 13.5424 | 0.32257 | 0.24744 | 2.3819 | FALSE | 2024-07-15 23:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | line_112221_21 | ACLineSegment | Line | 13.5424 | 0.3331 | 0.25484 | 2.4597 | FALSE | 2024-07-15 23:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | tr_5957_21 | Transformer | Transformer | 0.02375 | 0.0066424 | 0.0049398 | 27.9679 | FALSE | 2024-01-21 23:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_18 | tr_2035_21 | Transformer | Transformer | 0.285 | 0.0063272 | 0.0043012 | 2.2201 | FALSE | 2024-01-20 19:00 |  |  | 300 | 3 | Transformer_kVA_x_PF
GSO_18 | line_111624_21 | ACLineSegment | Line | 0.51338 | 0.0063272 | 0.0043012 | 1.2325 | FALSE | 2024-01-20 19:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | line_96107_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | tr_9993_21 | Transformer | Transformer | 0.0475 | 0.077793 | 0.053976 | 163.7741 | TRUE | 2024-01-20 07:00 |  |  | 50 | 1 | Transformer_kVA_x_PF
GSO_18 | line_111730_21 | ACLineSegment | Line | 0.034884 | 0.0046593 | 0.0026971 | 13.3566 | FALSE | 2024-01-17 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_96209_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_111905_21 | ACLineSegment | Line | 13.5424 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | tr_2964_21 | Transformer | Transformer | 0.07125 | 0.01913 | 0.013935 | 26.8495 | FALSE | 2024-07-15 23:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_18 | line_111906_21 | ACLineSegment | Line | 13.5424 | 0.3863 | 0.30049 | 2.8525 | FALSE | 2024-01-21 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | line_112561_21 | ACLineSegment | Line | 13.5424 | 0.39057 | 0.30419 | 2.884 | FALSE | 2024-01-21 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | tr_9136_21 | Transformer | Transformer | 0.095 | 0.0066718 | 0.0050735 | 7.023 | FALSE | 2024-01-17 16:00 |  |  | 100 | 3 | Transformer_kVA_x_PF
GSO_18 | line_111907_21 | ACLineSegment | Line | 13.5424 | 0.38127 | 0.29686 | 2.8154 | FALSE | 2024-01-21 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | tr_2156_21 | Transformer | Transformer | 0.095 | 0.007274 | 0.0052758 | 7.6569 | FALSE | 2024-01-18 03:00 |  |  | 100 | 3 | Transformer_kVA_x_PF
GSO_18 | line_113500_21 | ACLineSegment | Line | 13.5424 | 0.37346 | 0.29182 | 2.7577 | FALSE | 2024-07-15 23:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | tr_11868_21 | Transformer | Transformer | 0.285 | 0.0081564 | 0.0057705 | 2.8619 | FALSE | 2024-01-21 |  |  | 300 | 3 | Transformer_kVA_x_PF
GSO_18 | line_111908_21 | ACLineSegment | Line | 0.51338 | 0.007274 | 0.0052758 | 1.4169 | FALSE | 2024-01-18 03:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | line_96567_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_112167_21 | ACLineSegment | Line | 13.5424 | 0.24069 | 0.18284 | 1.7773 | FALSE | 2024-12-23 13:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | tr_2265_21 | Transformer | Transformer | 0.285 | 0.0053132 | 0.0039727 | 1.8643 | FALSE | 2024-08-02 04:00 |  |  | 300 | 3 | Transformer_kVA_x_PF
GSO_18 | line_120823_21 | ACLineSegment | Line | 13.5424 | 0.18555 | 0.14716 | 1.3702 | FALSE | 2024-01-20 15:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | tr_5959_21 | Transformer | Transformer | 0.285 | 0.10553 | 0.05808 | 37.0269 | FALSE | 2024-10-03 02:00 |  |  | 300 | 3 | Transformer_kVA_x_PF
GSO_18 | line_112169_21 | ACLineSegment | Line | 0.51338 | 0.0053132 | 0.0039727 | 1.035 | FALSE | 2024-08-02 04:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | line_96363_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_112171_21 | ACLineSegment | Line | 0.94778 | 0.19987 | 0.14306 | 21.088 | FALSE | 2024-01-20 15:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_112250_21 | ACLineSegment | Line | 0.94778 | 0.20195 | 0.14554 | 21.3082 | FALSE | 2024-01-20 15:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | tr_2403_21 | Transformer | Transformer | 0.02375 | 0.007963 | 0.0049504 | 33.5286 | FALSE | 2024-01-17 21:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_18 | line_112172_21 | ACLineSegment | Line | 0.94778 | 0.19713 | 0.14146 | 20.7989 | FALSE | 2024-01-20 15:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | tr_2267_21 | Transformer | Transformer | 0.02375 | 0.0028049 | 0.0017221 | 11.81 | FALSE | 2024-01-20 18:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_18 | line_113593_21 | ACLineSegment | Line | 0.94778 | 0.0062601 | 0.0032186 | 0.6605 | FALSE | 2024-01-21 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_120790_21 | ACLineSegment | Line | 0.94778 | 0.12689 | 0.087724 | 13.3881 | FALSE | 2024-01-21 03:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | tr_5945_21 | Transformer | Transformer | 0.0475 | 0.079086 | 0.050939 | 166.4973 | TRUE | 2024-01-20 15:00 |  |  | 50 | 1 | Transformer_kVA_x_PF
GSO_18 | line_112173_21 | ACLineSegment | Line | 0.034884 | 0.0028049 | 0.0017221 | 8.0407 | FALSE | 2024-01-20 18:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_96371_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_112185_21 | ACLineSegment | Line | 0.034884 | 0.003775 | 0.0020796 | 10.8217 | FALSE | 2024-01-17 23:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_112186_21 | ACLineSegment | Line | 0.034884 | 0.0045364 | 0.0025583 | 13.0043 | FALSE | 2024-01-20 22:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_96377_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_96378_21 | ACLineSegment | Line | 0.034884 | 0.005134 | 0.0025172 | 14.7176 | FALSE | 2024-01-20 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_96380_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | tr_2288_21 | Transformer | Transformer | 0.07125 | 0.025978 | 0.018364 | 36.4602 | FALSE | 2024-01-20 14:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_18 | line_112223_21 | ACLineSegment | Line | 0.51338 | 0.025978 | 0.018364 | 5.0602 | FALSE | 2024-01-20 14:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | line_96406_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | tr_2300_21 | Transformer | Transformer | 0.02375 | 0.0071284 | 0.0038935 | 30.0144 | FALSE | 2024-01-21 03:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_18 | line_112252_21 | ACLineSegment | Line | 0.034884 | 0.0071284 | 0.0038935 | 20.4349 | FALSE | 2024-01-21 03:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_96419_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_112326_21 | ACLineSegment | Line | 0.94778 | 0.015804 | 0.0090592 | 1.6675 | FALSE | 2024-01-21 04:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | tr_2333_21 | Transformer | Transformer | 0.02375 | 0.010078 | 0.0061838 | 42.4336 | FALSE | 2024-01-20 15:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_18 | tr_10028_21 | Transformer | Transformer | 0.02375 | 0.015804 | 0.0090592 | 66.5425 | FALSE | 2024-01-21 04:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_18 | line_112479_21 | ACLineSegment | Line | 0.034884 | 0.007963 | 0.0049504 | 22.8275 | FALSE | 2024-01-17 21:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_96820_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_112529_21 | ACLineSegment | Line | 0.034884 | 0.0059202 | 0.0033575 | 16.9715 | FALSE | 2024-07-15 07:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_96862_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_96863_21 | ACLineSegment | Line | 0.034884 | 0.0049312 | 0.0025997 | 14.1362 | FALSE | 2024-01-17 19:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_112560_21 | ACLineSegment | Line | 13.5424 | 0.39615 | 0.3081 | 2.9252 | FALSE | 2024-01-21 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | line_116037_21 | ACLineSegment | Line | 13.5424 | 0.40392 | 0.31549 | 2.9826 | FALSE | 2024-01-21 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | tr_3986_21 | Transformer | Transformer | 0.07125 | 0.011583 | 0.0089374 | 16.2563 | FALSE | 2024-01-17 09:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_18 | tr_2444_21 | Transformer | Transformer | 0.07125 | 0.008191 | 0.0057916 | 11.4961 | FALSE | 2024-07-15 12:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_18 | line_112562_21 | ACLineSegment | Line | 0.22905 | 0.008191 | 0.0057916 | 3.5761 | FALSE | 2024-07-15 12:00 | 290 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | line_96873_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | tr_2754_21 | Transformer | Transformer | 0.095 | 0.0077536 | 0.005675 | 8.1617 | FALSE | 2024-01-21 15:00 |  |  | 100 | 3 | Transformer_kVA_x_PF
GSO_18 | line_112667_21 | ACLineSegment | Line | 0.51338 | 0.0075747 | 0.0050433 | 1.4755 | FALSE | 2024-01-20 05:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | line_96958_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | tr_2581_21 | Transformer | Transformer | 0.0475 | 0.015937 | 0.011906 | 33.5524 | FALSE | 2024-01-21 |  |  | 50 | 1 | Transformer_kVA_x_PF
GSO_18 | line_112862_21 | ACLineSegment | Line | 0.034884 | 0.0049644 | 0.0038691 | 14.2315 | FALSE | 2024-07-10 01:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_112863_21 | ACLineSegment | Line | 0.034884 | 0.0089673 | 0.0065371 | 25.7064 | FALSE | 2024-01-17 23:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_112864_21 | ACLineSegment | Line | 0.034884 | 0.0048477 | 0.0029189 | 13.8968 | FALSE | 2024-01-17 16:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_112945_21 | ACLineSegment | Line | 0.51338 | 0.0073095 | 0.0053054 | 1.4238 | FALSE | 2024-01-21 01:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | tr_9112_21 | Transformer | Transformer | 0.07125 | 0.016167 | 0.012073 | 22.6908 | FALSE | 2024-07-15 20:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_18 | line_112966_21 | ACLineSegment | Line | 0.034884 | 0.0077652 | 0.0039367 | 22.2603 | FALSE | 2024-01-21 02:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | tr_2630_21 | Transformer | Transformer | 0.07125 | 0.0059687 | 0.0047958 | 8.3771 | FALSE | 2024-01-21 23:00 |  |  | 75 | 3 | Transformer_kVA_x_PF
GSO_18 | line_112974_21 | ACLineSegment | Line | 0.51338 | 0.0059687 | 0.0047958 | 1.1626 | FALSE | 2024-01-21 23:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | line_113029_21 | ACLineSegment | Line | 0.034884 | 0.0029534 | 0.0015139 | 8.4665 | FALSE | 2024-01-17 22:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_97019_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_113115_21 | ACLineSegment | Line | 0.034884 | 0.0055562 | 0.0029053 | 15.9279 | FALSE | 2024-01-20 16:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_113116_21 | ACLineSegment | Line | 0.034884 | 0.0092559 | 0.0048397 | 26.5338 | FALSE | 2024-01-20 05:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_97056_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_97057_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_113232_21 | ACLineSegment | Line | 0.51338 | 0.0077536 | 0.005675 | 1.5103 | FALSE | 2024-01-21 15:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | line_97421_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_113332_21 | ACLineSegment | Line | 0.034884 | 0.0063226 | 0.0039789 | 18.125 | FALSE | 2024-07-05 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_97465_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_113501_21 | ACLineSegment | Line | 13.5424 | 0.041591 | 0.028008 | 0.30712 | FALSE | 2024-06-20 16:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | tr_2887_21 | Transformer | Transformer | 0.02375 | 0.0040052 | 0.0022224 | 16.864 | FALSE | 2024-01-20 18:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_18 | line_113502_21 | ACLineSegment | Line | 0.034884 | 0.0040052 | 0.0022224 | 11.4817 | FALSE | 2024-01-20 18:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_97326_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | tr_2932_21 | Transformer | Transformer | 0.02375 | 0.0062601 | 0.0032186 | 26.3583 | FALSE | 2024-01-21 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_18 | line_113594_21 | ACLineSegment | Line | 0.034884 | 0.0062601 | 0.0032186 | 17.9457 | FALSE | 2024-01-21 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_97397_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_113659_21 | ACLineSegment | Line | 0.51338 | 0.01913 | 0.013935 | 3.7263 | FALSE | 2024-07-15 23:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | line_97377_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | tr_9245_21 | Transformer | Transformer | 0.02375 | 0.019638 | 0.01276 | 82.687 | FALSE | 2024-01-20 21:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_18 | line_115811_21 | ACLineSegment | Line | 0.034884 | 0.0037366 | 0.0019812 | 10.7118 | FALSE | 2024-01-21 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_115812_21 | ACLineSegment | Line | 0.034884 | 0.0044251 | 0.0025 | 12.6854 | FALSE | 2024-01-21 03:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_115813_21 | ACLineSegment | Line | 0.034884 | 0.0029976 | 0.0017671 | 8.5933 | FALSE | 2024-07-15 05:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_115814_21 | ACLineSegment | Line | 0.034884 | 0.0050533 | 0.0028289 | 14.4862 | FALSE | 2024-01-17 15:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_115815_21 | ACLineSegment | Line | 0.034884 | 0.0036156 | 0.0019946 | 10.3647 | FALSE | 2024-01-20 22:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_24868_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_24870_21 | ACLineSegment | Line | 0.034884 | 0.017703 | 0.011842 | 50.7481 | FALSE | 2024-07-15 13:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_24883_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_24885_21 | ACLineSegment | Line | 0.034884 | 0.02751 | 0.017733 | 78.8625 | FALSE | 2024-01-21 01:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_24887_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_24889_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_128347_21 | ACLineSegment | Line | 13.5424 | 0.050395 | 0.033316 | 0.37213 | FALSE | 2024-01-21 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | tr_10069_21 | Transformer | Transformer | 0.02375 | 0.0063402 | 0.0044336 | 26.6956 | FALSE | 2024-01-21 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_18 | line_115861_21 | ACLineSegment | Line | 0.034884 | 0.004737 | 0.0023591 | 13.5796 | FALSE | 2024-01-21 03:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25057_21 | ACLineSegment | Line | 0.034884 | 0.035918 | 0.024792 | 102.9653 | TRUE | 2024-01-20 23:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25071_21 | ACLineSegment | Line | 0.034884 | 0.029003 | 0.01853 | 83.1414 | FALSE | 2024-01-20 07:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_127903_21 | ACLineSegment | Line | 0.94778 | 0.074493 | 0.048823 | 7.8597 | FALSE | 2024-01-21 03:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | tr_10035_21 | Transformer | Transformer | 0.02375 | 0.0048322 | 0.002692 | 20.3461 | FALSE | 2024-01-20 09:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_18 | line_115875_21 | ACLineSegment | Line | 0.034884 | 0.0064622 | 0.0030595 | 18.5251 | FALSE | 2024-01-20 15:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25135_21 | ACLineSegment | Line | 0.034884 | 0.029344 | 0.01859 | 84.1193 | FALSE | 2024-01-20 11:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25140_21 | ACLineSegment | Line | 0.034884 | 0.022656 | 0.013839 | 64.9472 | FALSE | 2024-01-20 15:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_115957_21 | ACLineSegment | Line | 0.034884 | 0.0057233 | 0.0034584 | 16.407 | FALSE | 2024-07-15 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25835_21 | ACLineSegment | Line | 0.034884 | 0.035725 | 0.022965 | 102.4113 | TRUE | 2024-01-20 11:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25856_21 | ACLineSegment | Line | 0.034884 | 0.029699 | 0.019821 | 85.1384 | FALSE | 2024-01-20 08:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_116038_21 | ACLineSegment | Line | 13.5424 | 0.42866 | 0.33351 | 3.1653 | FALSE | 2024-01-21 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | tr_3864_21 | Transformer | Transformer | 0.0475 | 0.031092 | 0.020452 | 65.4566 | FALSE | 2024-01-20 06:00 |  |  | 50 | 1 | Transformer_kVA_x_PF
GSO_18 | line_131276_21 | ACLineSegment | Line | 13.5424 | 0.44822 | 0.35217 | 3.3098 | FALSE | 2024-01-21 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | line_116039_21 | ACLineSegment | Line | 0.034884 | 0.0080992 | 0.0042566 | 23.2178 | FALSE | 2024-01-20 17:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_15467_21 | ACLineSegment | Line | 0.034884 | 0.0099914 | 0.0055441 | 28.6422 | FALSE | 2024-01-21 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_15469_21 | ACLineSegment | Line | 0.034884 | 0.0172 | 0.012525 | 49.3076 | FALSE | 2024-01-20 06:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_116059_21 | ACLineSegment | Line | 0.034884 | 0.0071379 | 0.0037063 | 20.4621 | FALSE | 2024-01-20 07:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_116060_21 | ACLineSegment | Line | 0.034884 | 0.00271 | 0.0015571 | 7.7688 | FALSE | 2024-01-20 08:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_116061_21 | ACLineSegment | Line | 0.034884 | 0.0085284 | 0.0044696 | 24.4483 | FALSE | 2024-01-21 01:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_15592_21 | ACLineSegment | Line | 0.034884 | 0.030721 | 0.021098 | 88.0671 | FALSE | 2024-01-20 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_15602_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_15610_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_15611_21 | ACLineSegment | Line | 0.034884 | 0.017813 | 0.011906 | 51.0642 | FALSE | 2024-01-20 19:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_116129_21 | ACLineSegment | Line | 0.034884 | 0.0091008 | 0.0049947 | 26.0892 | FALSE | 2024-01-20 22:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_116130_21 | ACLineSegment | Line | 0.034884 | 0.0031733 | 0.0016296 | 9.097 | FALSE | 2024-01-20 15:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_16390_21 | ACLineSegment | Line | 0.034884 | 0.03597 | 0.024389 | 103.1135 | TRUE | 2024-01-21 03:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_16421_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_16422_21 | ACLineSegment | Line | 0.034884 | 0.041165 | 0.027842 | 118.0079 | TRUE | 2024-01-20 11:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_116238_21 | ACLineSegment | Line | 0.034884 | 0.0063894 | 0.0035595 | 18.3163 | FALSE | 2024-01-20 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_17635_21 | ACLineSegment | Line | 0.034884 | 0.029768 | 0.020844 | 85.3353 | FALSE | 2024-01-20 18:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_17638_21 | ACLineSegment | Line | 0.034884 | 0.028318 | 0.017864 | 81.1795 | FALSE | 2024-01-20 11:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_116286_21 | ACLineSegment | Line | 0.034884 | 0.0040654 | 0.0023384 | 11.6542 | FALSE | 2024-07-16 03:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_116287_21 | ACLineSegment | Line | 0.034884 | 0.0082529 | 0.0043513 | 23.6583 | FALSE | 2024-01-20 22:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_17899_21 | ACLineSegment | Line | 0.034884 | 0.013672 | 0.0082809 | 39.1927 | FALSE | 2024-01-20 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_17902_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_17907_21 | ACLineSegment | Line | 0.034884 | 0.014175 | 0.0086002 | 40.6355 | FALSE | 2024-01-20 21:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_122817_21 | ACLineSegment | Line | 0.94778 | 0.10745 | 0.074193 | 11.3369 | FALSE | 2024-01-21 04:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | tr_12338_21 | Transformer | Transformer | 0.02375 | 0.023224 | 0.013575 | 97.7833 | FALSE | 2024-01-20 05:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_18 | line_122816_21 | ACLineSegment | Line | 0.94778 | 0.029415 | 0.019015 | 3.1035 | FALSE | 2024-01-18 01:00 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | tr_6973_21 | Transformer | Transformer | 0.0475 | 0.081585 | 0.055082 | 171.7576 | TRUE | 2024-01-20 11:00 |  |  | 50 | 1 | Transformer_kVA_x_PF
GSO_18 | line_122824_21 | ACLineSegment | Line | 0.94778 | 0.0084675 | 0.0050452 | 0.8934 | FALSE | 2024-01-21 | 240 | 7.2 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | tr_6975_21 | Transformer | Transformer | 0.02375 | 0.023378 | 0.014237 | 98.4324 | FALSE | 2024-01-18 01:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_18 | line_122818_21 | ACLineSegment | Line | 0.034884 | 0.0042937 | 0.0026636 | 12.3086 | FALSE | 2024-01-17 08:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_122819_21 | ACLineSegment | Line | 0.034884 | 0.0040147 | 0.0021568 | 11.5089 | FALSE | 2024-01-20 11:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_122820_21 | ACLineSegment | Line | 0.034884 | 0.0040559 | 0.0021686 | 11.6269 | FALSE | 2024-01-21 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_55496_21 | ACLineSegment | Line | 0.034884 | 0.048088 | 0.03053 | 137.8533 | TRUE | 2024-01-20 11:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_55503_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_55508_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_55523_21 | ACLineSegment | Line | 0.034884 | 0.028528 | 0.018307 | 81.7818 | FALSE | 2024-01-21 04:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_55531_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | tr_6981_21 | Transformer | Transformer | 0.02375 | 0.0084675 | 0.0050452 | 35.6525 | FALSE | 2024-01-21 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_18 | line_122825_21 | ACLineSegment | Line | 0.034884 | 0.003913 | 0.0022606 | 11.2174 | FALSE | 2024-07-15 05:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_122826_21 | ACLineSegment | Line | 0.034884 | 0.0038456 | 0.0020218 | 11.0241 | FALSE | 2024-01-20 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_122827_21 | ACLineSegment | Line | 0.034884 | 0.0035376 | 0.0019993 | 10.1411 | FALSE | 2024-07-15 11:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_55342_21 | ACLineSegment | Line | 0.034884 | 0.014669 | 0.008535 | 42.0524 | FALSE | 2024-01-18 01:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_55343_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_55344_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_122834_21 | ACLineSegment | Line | 0.034884 | 0.0052883 | 0.0030289 | 15.1599 | FALSE | 2024-07-16 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_122835_21 | ACLineSegment | Line | 0.034884 | 0.004508 | 0.002233 | 12.9229 | FALSE | 2024-01-20 17:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_55651_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_55652_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | tr_10620_21 | Transformer | Transformer | 0.02375 | 0.0078583 | 0.005676 | 33.0876 | FALSE | 2024-01-21 03:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_18 | line_122868_21 | ACLineSegment | Line | 0.034884 | 0.0062684 | 0.0038476 | 17.9697 | FALSE | 2024-01-20 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_122869_21 | ACLineSegment | Line | 0.034884 | 0.0037868 | 0.0020725 | 10.8555 | FALSE | 2024-01-20 08:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_53932_21 | ACLineSegment | Line | 0.034884 | 0.010224 | 0.0059715 | 29.3088 | FALSE | 2024-01-21 04:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_53936_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_53937_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_53938_21 | ACLineSegment | Line | 0.034884 | 0.0083556 | 0.0050383 | 23.9527 | FALSE | 2024-01-17 20:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_126507_21 | ACLineSegment | Line | 0.034884 | 0.0053037 | 0.0040995 | 15.2042 | FALSE | 2024-01-18 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_65044_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_126596_21 | ACLineSegment | Line | 0.51338 | 0.038989 | 0.028965 | 7.5946 | FALSE | 2024-07-18 20:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | line_65796_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | tr_8999_21 | Transformer | Transformer | 0.02375 | 0.034738 | 0.022834 | 146.2673 | TRUE | 2024-01-21 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_18 | line_126657_21 | ACLineSegment | Line | 0.034884 | 0.0053288 | 0.0029493 | 15.2758 | FALSE | 2024-01-20 07:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_65976_21 | ACLineSegment | Line | 0.034884 | 0.015877 | 0.010189 | 45.5157 | FALSE | 2024-01-20 14:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_65983_21 | ACLineSegment | Line | 0.034884 | 0.018512 | 0.010352 | 53.0679 | FALSE | 2024-01-21 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_65985_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | tr_9028_21 | Transformer | Transformer | 0.02375 | 0.008912 | 0.0056259 | 37.524 | FALSE | 2024-01-20 09:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_18 | line_126883_21 | ACLineSegment | Line | 0.51338 | 0.016167 | 0.012073 | 3.1492 | FALSE | 2024-07-15 20:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | line_126895_21 | ACLineSegment | Line | 0.034884 | 0.0060156 | 0.0034032 | 17.2448 | FALSE | 2024-01-20 06:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_126896_21 | ACLineSegment | Line | 0.034884 | 0.0030678 | 0.0015686 | 8.7946 | FALSE | 2024-01-20 12:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_67991_21 | ACLineSegment | Line | 0.034884 | 0.030574 | 0.020284 | 87.6473 | FALSE | 2024-01-21 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_68005_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_68006_21 | ACLineSegment | Line | 0.034884 | 0.016153 | 0.0098727 | 46.3051 | FALSE | 2024-01-20 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_126916_21 | ACLineSegment | Line | 0.51338 | 0.0066718 | 0.0050735 | 1.2996 | FALSE | 2024-01-17 16:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | line_67900_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_127035_21 | ACLineSegment | Line | 0.034884 | 0.0042619 | 0.002626 | 12.2175 | FALSE | 2024-01-20 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_127036_21 | ACLineSegment | Line | 0.034884 | 0.0057692 | 0.0032363 | 16.5384 | FALSE | 2024-01-20 15:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69062_21 | ACLineSegment | Line | 0.034884 | 0.043725 | 0.02977 | 125.3465 | TRUE | 2024-01-20 07:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69078_21 | ACLineSegment | Line | 0.034884 | 0.038918 | 0.026999 | 111.5658 | TRUE | 2024-01-20 22:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69084_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | tr_9210_21 | Transformer | Transformer | 0.0475 | 0.041246 | 0.029162 | 86.8336 | FALSE | 2024-01-17 07:00 |  |  | 50 | 1 | Transformer_kVA_x_PF
GSO_18 | line_127046_21 | ACLineSegment | Line | 0.034884 | 0.0047073 | 0.0024911 | 13.4945 | FALSE | 2024-01-20 19:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69146_21 | ACLineSegment | Line | 0.034884 | 0.026091 | 0.017232 | 74.7949 | FALSE | 2024-01-21 03:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69154_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69155_21 | ACLineSegment | Line | 0.034884 | 0.015082 | 0.0096291 | 43.235 | FALSE | 2024-07-16 02:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_127113_21 | ACLineSegment | Line | 0.034884 | 0.0050899 | 0.0029667 | 14.5911 | FALSE | 2024-07-15 19:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_127114_21 | ACLineSegment | Line | 0.034884 | 0.0077748 | 0.0040465 | 22.2879 | FALSE | 2024-01-21 01:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69299_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69302_21 | ACLineSegment | Line | 0.034884 | 0.007836 | 0.0045548 | 22.4632 | FALSE | 2024-01-20 11:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69308_21 | ACLineSegment | Line | 0.034884 | 0.0040034 | 0.002323 | 11.4766 | FALSE | 2024-01-20 17:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_127116_21 | ACLineSegment | Line | 0.51338 | 0.0073881 | 0.0044113 | 1.4391 | FALSE | 2024-01-20 13:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | line_69708_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_127126_21 | ACLineSegment | Line | 0.034884 | 0.0065963 | 0.0034653 | 18.9095 | FALSE | 2024-01-20 06:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69753_21 | ACLineSegment | Line | 0.034884 | 0.023571 | 0.015176 | 67.5709 | FALSE | 2024-01-20 06:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69760_21 | ACLineSegment | Line | 0.034884 | 0.021078 | 0.014445 | 60.424 | FALSE | 2024-01-21 01:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_127131_21 | ACLineSegment | Line | 0.034884 | 0.0043808 | 0.00284 | 12.5584 | FALSE | 2024-08-08 18:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_127132_21 | ACLineSegment | Line | 0.034884 | 0.0039437 | 0.0021517 | 11.3054 | FALSE | 2024-01-21 03:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | tr_9773_21 | Transformer | Transformer | 0.0475 | 0.074493 | 0.048823 | 156.8269 | TRUE | 2024-01-21 03:00 |  |  | 50 | 1 | Transformer_kVA_x_PF
GSO_18 | line_127904_21 | ACLineSegment | Line | 0.034884 | 0.0051901 | 0.0030199 | 14.8784 | FALSE | 2024-01-20 23:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_73276_21 | ACLineSegment | Line | 0.046073 | 0.071159 | 0.04596 | 154.4508 | TRUE | 2024-01-21 03:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_128131_21 | ACLineSegment | Line | 0.034884 | 0.0068367 | 0.0039251 | 19.5987 | FALSE | 2024-01-17 14:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_72176_21 | ACLineSegment | Line | 0.034884 | 0.036853 | 0.023247 | 105.6465 | TRUE | 2024-01-17 08:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_128234_21 | ACLineSegment | Line | 0.034884 | 0.0033099 | 0.0018729 | 9.4883 | FALSE | 2024-07-15 13:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_128235_21 | ACLineSegment | Line | 0.034884 | 0.0034687 | 0.0021965 | 9.9438 | FALSE | 2024-07-15 16:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_75359_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_75360_21 | ACLineSegment | Line | 0.034884 | 0.033638 | 0.02244 | 96.4303 | FALSE | 2024-01-20 07:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_75394_21 | ACLineSegment | Line | 0.034884 | 0.042075 | 0.02773 | 120.6144 | TRUE | 2024-01-20 13:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_128249_21 | ACLineSegment | Line | 0.51338 | 0.0066831 | 0.0045068 | 1.3018 | FALSE | 2024-01-20 05:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | line_128297_21 | ACLineSegment | Line | 0.034884 | 0.0048322 | 0.002692 | 13.8524 | FALSE | 2024-01-20 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_75880_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | tr_12314_21 | Transformer | Transformer | 0.0475 | 0.03244 | 0.024511 | 68.2955 | FALSE | 2024-01-21 02:00 |  |  | 50 | 1 | Transformer_kVA_x_PF
GSO_18 | line_128348_21 | ACLineSegment | Line | 0.034884 | 0.0063402 | 0.0044336 | 18.1754 | FALSE | 2024-01-21 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_76172_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_128626_21 | ACLineSegment | Line | 13.5424 | 0.45154 | 0.35585 | 3.3343 | FALSE | 2024-01-21 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | tr_10235_21 | Transformer | Transformer | 0.02375 | 0.0033518 | 0.0018022 | 14.1127 | FALSE | 2024-01-20 15:00 |  |  | 25 | 1 | Transformer_kVA_x_PF
GSO_18 | tr_11876_21 | Transformer | Transformer | 0.475 | 0.0071411 | 0.0053999 | 1.5034 | FALSE | 2024-01-17 13:00 |  |  | 500 | 3 | Transformer_kVA_x_PF
GSO_18 | line_128627_21 | ACLineSegment | Line | 0.034884 | 0.0033518 | 0.0018022 | 9.6085 | FALSE | 2024-01-20 15:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_78640_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_129218_21 | ACLineSegment | Line | 0.034884 | 0.0089003 | 0.0066234 | 25.5145 | FALSE | 2024-01-17 13:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_79128_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_129224_21 | ACLineSegment | Line | 0.51338 | 0.029193 | 0.020934 | 5.6865 | FALSE | 2024-02-14 22:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | line_79132_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_129231_21 | ACLineSegment | Line | 0.034884 | 0.0078583 | 0.005676 | 22.5273 | FALSE | 2024-01-21 03:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_79131_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_129234_21 | ACLineSegment | Line | 0.51338 | 0.0051941 | 0.0041106 | 1.0117 | FALSE | 2024-07-05 08:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | line_129250_21 | ACLineSegment | Line | 0.51338 | 0.0058887 | 0.0043173 | 1.147 | FALSE | 2024-01-21 05:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | line_79219_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_129253_21 | ACLineSegment | Line | 0.51338 | 0.0076195 | 0.005785 | 1.4842 | FALSE | 2024-06-26 11:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | line_79129_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_129254_21 | ACLineSegment | Line | 0.51338 | 0.0047718 | 0.0030133 | 0.92949 | FALSE | 2024-01-17 07:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | line_79247_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_129258_21 | ACLineSegment | Line | 0.22905 | 0.0070896 | 0.0053597 | 3.0953 | FALSE | 2024-07-10 13:00 | 290 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | line_79222_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_129262_21 | ACLineSegment | Line | 0.51338 | 0.0075997 | 0.0056761 | 1.4803 | FALSE | 2024-01-20 05:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | line_79227_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_131266_21 | ACLineSegment | Line | 0.51338 | 0.0081564 | 0.0057705 | 1.5888 | FALSE | 2024-01-21 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | line_86356_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_131268_21 | ACLineSegment | Line | 0.51338 | 0.0068239 | 0.0050312 | 1.3292 | FALSE | 2024-01-21 04:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | line_86355_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_131277_21 | ACLineSegment | Line | 0.51338 | 0.0071411 | 0.0053999 | 1.391 | FALSE | 2024-01-17 13:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | line_86361_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_131951_21 | ACLineSegment | Line | 0.034884 | 0.0038095 | 0.002021 | 10.9207 | FALSE | 2024-01-20 07:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_131952_21 | ACLineSegment | Line | 0.034884 | 0.0026042 | 0.0016128 | 7.4653 | FALSE | 2024-07-15 17:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_131953_21 | ACLineSegment | Line | 0.034884 | 0.0091793 | 0.0065443 | 26.3141 | FALSE | 2024-01-20 18:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_88164_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_88166_21 | ACLineSegment | Line | 0.034884 | 0.022399 | 0.016546 | 64.2103 | FALSE | 2024-01-20 08:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_88173_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_131971_21 | ACLineSegment | Line | 0.034884 | 0.0055848 | 0.0027604 | 16.0099 | FALSE | 2024-01-17 13:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_131972_21 | ACLineSegment | Line | 0.034884 | 0.0071177 | 0.0029114 | 20.4043 | FALSE | 2024-01-20 20:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_131973_21 | ACLineSegment | Line | 0.034884 | 0.021292 | 0.016248 | 61.0363 | FALSE | 2024-07-15 20:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_131974_21 | ACLineSegment | Line | 0.034884 | 0.0067783 | 0.005023 | 19.4314 | FALSE | 2024-07-15 21:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_131984_21 | ACLineSegment | Line | 0.51338 | 0.0044636 | 0.0034683 | 0.86946 | FALSE | 2024-01-20 21:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | line_131998_21 | ACLineSegment | Line | 0.034884 | 0.0094824 | 0.0046116 | 27.183 | FALSE | 2024-01-21 03:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_131999_21 | ACLineSegment | Line | 0.034884 | 0.0028505 | 0.0015416 | 8.1716 | FALSE | 2024-01-20 05:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_132000_21 | ACLineSegment | Line | 0.034884 | 0.003851 | 0.002289 | 11.0396 | FALSE | 2024-01-20 23:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_132001_21 | ACLineSegment | Line | 0.034884 | 0.0063201 | 0.00293 | 18.1176 | FALSE | 2024-01-20 05:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_132002_21 | ACLineSegment | Line | 0.034884 | 0.0054579 | 0.0032221 | 15.6461 | FALSE | 2024-01-20 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_88589_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_88590_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_88591_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_88593_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_88594_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_15464_21 | ACLineSegment | Line | 0.034884 | 0.0064869 | 0.0038401 | 18.5958 | FALSE | 2024-01-21 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_15466_21 | ACLineSegment | Line | 0.034884 | 0.0099914 | 0.0055441 | 28.6422 | FALSE | 2024-01-21 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_15468_21 | ACLineSegment | Line | 0.034884 | 0.0035045 | 0.0019277 | 10.0464 | FALSE | 2024-01-21 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_15465_21 | ACLineSegment | Line | 0.034884 | 0.0064869 | 0.0038401 | 18.5958 | FALSE | 2024-01-21 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_15470_21 | ACLineSegment | Line | 0.034884 | 0.0172 | 0.012525 | 49.3076 | FALSE | 2024-01-20 06:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_15479_21 | ACLineSegment | Line | 0.034884 | 0.014468 | 0.0088563 | 41.476 | FALSE | 2024-01-20 15:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_15497_21 | ACLineSegment | Line | 0.034884 | 0.016265 | 0.010252 | 46.6267 | FALSE | 2024-01-21 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_15498_21 | ACLineSegment | Line | 0.034884 | 0.0030458 | 0.0015606 | 8.7313 | FALSE | 2024-01-21 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_15480_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_15481_21 | ACLineSegment | Line | 0.034884 | 0.009019 | 0.0050056 | 25.8547 | FALSE | 2024-01-20 17:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_15482_21 | ACLineSegment | Line | 0.034884 | 0.0066233 | 0.0029628 | 18.987 | FALSE | 2024-01-20 20:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_15483_21 | ACLineSegment | Line | 0.034884 | 0.0026561 | 0.0013887 | 7.6143 | FALSE | 2024-01-20 21:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_15508_21 | ACLineSegment | Line | 0.034884 | 0.009019 | 0.0050056 | 25.8547 | FALSE | 2024-01-20 17:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_15484_21 | ACLineSegment | Line | 0.034884 | 0.0097368 | 0.0060525 | 27.9125 | FALSE | 2024-01-17 06:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_15489_21 | ACLineSegment | Line | 0.034884 | 0.01824 | 0.011582 | 52.2875 | FALSE | 2024-01-20 13:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_15495_21 | ACLineSegment | Line | 0.034884 | 0.0098187 | 0.0059147 | 28.1472 | FALSE | 2024-01-21 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_15485_21 | ACLineSegment | Line | 0.034884 | 0.0035143 | 0.0019594 | 10.0744 | FALSE | 2024-01-17 06:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_15486_21 | ACLineSegment | Line | 0.034884 | 0.0071886 | 0.0043179 | 20.6076 | FALSE | 2024-01-17 05:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_15487_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_15488_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_15490_21 | ACLineSegment | Line | 0.034884 | 0.028376 | 0.018174 | 81.3441 | FALSE | 2024-07-15 06:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_15491_21 | ACLineSegment | Line | 0.034884 | 0.0050013 | 0.0028579 | 14.3371 | FALSE | 2024-01-20 19:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_15492_21 | ACLineSegment | Line | 0.034884 | 0.0039904 | 0.0022482 | 11.4394 | FALSE | 2024-01-20 21:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_15493_21 | ACLineSegment | Line | 0.034884 | 0.0038856 | 0.0020584 | 11.1387 | FALSE | 2024-01-17 06:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_15503_21 | ACLineSegment | Line | 0.034884 | 0.030088 | 0.02022 | 86.2529 | FALSE | 2024-01-20 20:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_15494_21 | ACLineSegment | Line | 0.034884 | 0.0078974 | 0.0040755 | 22.6394 | FALSE | 2024-01-21 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_15496_21 | ACLineSegment | Line | 0.034884 | 0.0031564 | 0.0020327 | 9.0484 | FALSE | 2024-07-15 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_15499_21 | ACLineSegment | Line | 0.034884 | 0.0078974 | 0.0040755 | 22.6394 | FALSE | 2024-01-21 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_15505_21 | ACLineSegment | Line | 0.034884 | 0.02047 | 0.012995 | 58.682 | FALSE | 2024-01-20 20:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_15506_21 | ACLineSegment | Line | 0.034884 | 0.0053502 | 0.0029359 | 15.3373 | FALSE | 2024-01-20 23:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_15502_21 | ACLineSegment | Line | 0.034884 | 0.025157 | 0.01599 | 72.1166 | FALSE | 2024-01-20 15:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_15504_21 | ACLineSegment | Line | 0.034884 | 0.0088384 | 0.0046339 | 25.3369 | FALSE | 2024-01-17 14:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_15507_21 | ACLineSegment | Line | 0.034884 | 0.0054788 | 0.0033579 | 15.7059 | FALSE | 2024-07-05 08:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_15585_21 | ACLineSegment | Line | 0.034884 | 0.0086062 | 0.0059584 | 24.6714 | FALSE | 2024-07-14 13:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_15596_21 | ACLineSegment | Line | 0.034884 | 0.012362 | 0.0086706 | 35.4367 | FALSE | 2024-06-23 13:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_15599_21 | ACLineSegment | Line | 0.034884 | 0.005563 | 0.0030259 | 15.9475 | FALSE | 2024-01-17 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_15586_21 | ACLineSegment | Line | 0.034884 | 0.0036519 | 0.0020901 | 10.4689 | FALSE | 2024-01-21 04:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_15587_21 | ACLineSegment | Line | 0.034884 | 0.0063131 | 0.0040657 | 18.0976 | FALSE | 2024-07-14 13:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_15603_21 | ACLineSegment | Line | 0.034884 | 0.0036519 | 0.0020901 | 10.4689 | FALSE | 2024-01-21 04:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_15606_21 | ACLineSegment | Line | 0.034884 | 0.004354 | 0.0025146 | 12.4817 | FALSE | 2024-07-16 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_15607_21 | ACLineSegment | Line | 0.034884 | 0.0031362 | 0.0017557 | 8.9906 | FALSE | 2024-01-20 16:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_15588_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_15589_21 | ACLineSegment | Line | 0.034884 | 0.0092026 | 0.0058048 | 26.381 | FALSE | 2024-01-20 06:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_15590_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_15591_21 | ACLineSegment | Line | 0.034884 | 0.016049 | 0.0095819 | 46.0086 | FALSE | 2024-01-20 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_15593_21 | ACLineSegment | Line | 0.034884 | 0.0043158 | 0.0024593 | 12.3721 | FALSE | 2024-01-20 12:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_15594_21 | ACLineSegment | Line | 0.034884 | 0.0047038 | 0.0026726 | 13.4844 | FALSE | 2024-01-20 16:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_15595_21 | ACLineSegment | Line | 0.034884 | 0.0023926 | 0.0012187 | 6.8587 | FALSE | 2024-01-20 18:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_15604_21 | ACLineSegment | Line | 0.034884 | 0.0036586 | 0.0021732 | 10.4881 | FALSE | 2024-01-20 06:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_15605_21 | ACLineSegment | Line | 0.034884 | 0.0065337 | 0.0038515 | 18.73 | FALSE | 2024-01-18 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_15612_21 | ACLineSegment | Line | 0.034884 | 0.0106 | 0.0058866 | 30.387 | FALSE | 2024-01-20 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_15614_21 | ACLineSegment | Line | 0.034884 | 0.0070626 | 0.0040155 | 20.2461 | FALSE | 2024-01-20 23:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_15597_21 | ACLineSegment | Line | 0.034884 | 0.017813 | 0.011906 | 51.0642 | FALSE | 2024-01-20 19:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_15598_21 | ACLineSegment | Line | 0.034884 | 0.006586 | 0.0035167 | 18.8801 | FALSE | 2024-01-21 01:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_15600_21 | ACLineSegment | Line | 0.034884 | 0.0067545 | 0.0037395 | 19.3629 | FALSE | 2024-01-20 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_15613_21 | ACLineSegment | Line | 0.034884 | 0.0041474 | 0.0024136 | 11.8893 | FALSE | 2024-01-20 19:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_15601_21 | ACLineSegment | Line | 0.034884 | 0.0067545 | 0.0037395 | 19.3629 | FALSE | 2024-01-20 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_15609_21 | ACLineSegment | Line | 0.034884 | 0.0036586 | 0.0021732 | 10.4881 | FALSE | 2024-01-20 06:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_16381_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_16382_21 | ACLineSegment | Line | 0.034884 | 0.0095845 | 0.0060826 | 27.4756 | FALSE | 2024-01-20 20:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_16383_21 | ACLineSegment | Line | 0.034884 | 0.0048163 | 0.0023254 | 13.8067 | FALSE | 2024-01-20 14:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_16384_21 | ACLineSegment | Line | 0.034884 | 0.0040376 | 0.0022853 | 11.5745 | FALSE | 2024-01-20 15:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_16385_21 | ACLineSegment | Line | 0.034884 | 0.0034342 | 0.0020017 | 9.8448 | FALSE | 2024-01-17 06:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_16407_21 | ACLineSegment | Line | 0.034884 | 0.024523 | 0.015505 | 70.2997 | FALSE | 2024-01-20 21:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_16413_21 | ACLineSegment | Line | 0.034884 | 0.017129 | 0.0097759 | 49.1025 | FALSE | 2024-01-20 21:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_16388_21 | ACLineSegment | Line | 0.034884 | 0.028907 | 0.01966 | 82.8676 | FALSE | 2024-01-20 20:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_16389_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_16391_21 | ACLineSegment | Line | 0.034884 | 0.0033253 | 0.0019177 | 9.5325 | FALSE | 2024-01-20 07:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_16392_21 | ACLineSegment | Line | 0.034884 | 0.0056329 | 0.0033095 | 16.1478 | FALSE | 2024-01-20 17:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_16403_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_16404_21 | ACLineSegment | Line | 0.034884 | 0.020362 | 0.013325 | 58.3725 | FALSE | 2024-07-15 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_16405_21 | ACLineSegment | Line | 0.034884 | 0.0063529 | 0.0037787 | 18.2117 | FALSE | 2024-01-17 16:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_16406_21 | ACLineSegment | Line | 0.034884 | 0.0056403 | 0.0030133 | 16.1691 | FALSE | 2024-01-20 11:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_16393_21 | ACLineSegment | Line | 0.034884 | 0.0070743 | 0.0044717 | 20.2797 | FALSE | 2024-01-20 12:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_16394_21 | ACLineSegment | Line | 0.034884 | 0.010631 | 0.0063756 | 30.477 | FALSE | 2024-01-20 08:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_16395_21 | ACLineSegment | Line | 0.034884 | 0.0041242 | 0.0020915 | 11.8229 | FALSE | 2024-01-20 08:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_16401_21 | ACLineSegment | Line | 0.034884 | 0.0048574 | 0.0030186 | 13.9248 | FALSE | 2024-07-15 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_16402_21 | ACLineSegment | Line | 0.034884 | 0.0029158 | 0.0016223 | 8.3588 | FALSE | 2024-01-20 07:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_16418_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_16420_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_16425_21 | ACLineSegment | Line | 0.034884 | 0.0069014 | 0.0037408 | 19.7842 | FALSE | 2024-01-21 01:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_16426_21 | ACLineSegment | Line | 0.034884 | 0.0034834 | 0.0015754 | 9.9858 | FALSE | 2024-01-20 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_16427_21 | ACLineSegment | Line | 0.034884 | 0.0043439 | 0.0022562 | 12.4527 | FALSE | 2024-01-20 12:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_16396_21 | ACLineSegment | Line | 0.034884 | 0.031898 | 0.022084 | 91.4403 | FALSE | 2024-01-20 21:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_16397_21 | ACLineSegment | Line | 0.034884 | 0.041165 | 0.027842 | 118.0079 | TRUE | 2024-01-20 11:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_16398_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_16399_21 | ACLineSegment | Line | 0.034884 | 0.011159 | 0.0072718 | 31.9882 | FALSE | 2024-05-14 18:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_16400_21 | ACLineSegment | Line | 0.034884 | 0.0035407 | 0.0018858 | 10.15 | FALSE | 2024-01-20 20:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_16408_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_16409_21 | ACLineSegment | Line | 0.034884 | 0.0073794 | 0.0038047 | 21.1544 | FALSE | 2024-01-21 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_16410_21 | ACLineSegment | Line | 0.034884 | 0.0059805 | 0.0035872 | 17.1441 | FALSE | 2024-06-27 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_16419_21 | ACLineSegment | Line | 0.034884 | 0.0048574 | 0.0030186 | 13.9248 | FALSE | 2024-07-15 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_16411_21 | ACLineSegment | Line | 0.034884 | 0.010263 | 0.0054513 | 29.4214 | FALSE | 2024-01-21 03:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_16415_21 | ACLineSegment | Line | 0.034884 | 0.008505 | 0.0046304 | 24.3813 | FALSE | 2024-01-20 21:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_16412_21 | ACLineSegment | Line | 0.034884 | 0.010263 | 0.0054513 | 29.4214 | FALSE | 2024-01-21 03:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_16416_21 | ACLineSegment | Line | 0.034884 | 0.0046466 | 0.0023208 | 13.3203 | FALSE | 2024-01-21 03:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_16417_21 | ACLineSegment | Line | 0.034884 | 0.0057039 | 0.0033565 | 16.3512 | FALSE | 2024-01-20 07:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_17429_21 | ACLineSegment | Line | 0.22905 | 0.0070658 | 0.0053107 | 3.0849 | FALSE | 2024-01-17 09:00 | 290 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | line_17431_21 | ACLineSegment | Line | 0.22905 | 0.0062018 | 0.0046636 | 2.7077 | FALSE | 2024-01-20 13:00 | 290 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | line_17430_21 | ACLineSegment | Line | 0.22905 | 0.0070658 | 0.0053107 | 3.0849 | FALSE | 2024-01-17 09:00 | 290 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | line_17432_21 | ACLineSegment | Line | 0.22905 | 0.0062018 | 0.0046636 | 2.7077 | FALSE | 2024-01-20 13:00 | 290 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | line_17634_21 | ACLineSegment | Line | 0.034884 | 0.029768 | 0.020844 | 85.3353 | FALSE | 2024-01-20 18:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_17653_21 | ACLineSegment | Line | 0.034884 | 0.026841 | 0.019062 | 76.9451 | FALSE | 2024-01-20 21:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_17654_21 | ACLineSegment | Line | 0.034884 | 0.0036452 | 0.0019177 | 10.4498 | FALSE | 2024-01-20 13:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_17636_21 | ACLineSegment | Line | 0.034884 | 0.021351 | 0.012527 | 61.2059 | FALSE | 2024-01-20 11:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_17637_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_17639_21 | ACLineSegment | Line | 0.034884 | 0.005674 | 0.0033405 | 16.2656 | FALSE | 2024-01-20 20:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_17640_21 | ACLineSegment | Line | 0.034884 | 0.0039949 | 0.0023334 | 11.452 | FALSE | 2024-01-17 08:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_17644_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_17645_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_17646_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_17647_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_17648_21 | ACLineSegment | Line | 0.034884 | 0.0031774 | 0.0017251 | 9.1086 | FALSE | 2024-01-20 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_17649_21 | ACLineSegment | Line | 0.034884 | 0.0070528 | 0.003527 | 20.2181 | FALSE | 2024-01-20 11:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_17650_21 | ACLineSegment | Line | 0.034884 | 0.0063679 | 0.0035377 | 18.2547 | FALSE | 2024-07-15 12:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_17651_21 | ACLineSegment | Line | 0.034884 | 0.0035612 | 0.0020823 | 10.2089 | FALSE | 2024-01-20 11:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_17652_21 | ACLineSegment | Line | 0.034884 | 0.0050459 | 0.0026625 | 14.4649 | FALSE | 2024-01-21 04:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_17641_21 | ACLineSegment | Line | 0.034884 | 0.0109 | 0.0068017 | 31.2456 | FALSE | 2024-01-20 18:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_17655_21 | ACLineSegment | Line | 0.034884 | 0.016965 | 0.010467 | 48.6341 | FALSE | 2024-01-20 18:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_17656_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_17657_21 | ACLineSegment | Line | 0.034884 | 0.0034908 | 0.0019545 | 10.0071 | FALSE | 2024-01-17 11:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_17658_21 | ACLineSegment | Line | 0.034884 | 0.0033493 | 0.0020517 | 9.6014 | FALSE | 2024-01-17 11:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_17642_21 | ACLineSegment | Line | 0.034884 | 0.0089699 | 0.0054162 | 25.7138 | FALSE | 2024-07-15 21:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_17643_21 | ACLineSegment | Line | 0.034884 | 0.0024558 | 0.0014647 | 7.04 | FALSE | 2024-01-17 19:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_17667_21 | ACLineSegment | Line | 0.034884 | 0.0048958 | 0.0026824 | 14.0348 | FALSE | 2024-01-20 18:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_17669_21 | ACLineSegment | Line | 0.034884 | 0.005112 | 0.0029138 | 14.6546 | FALSE | 2024-01-17 21:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_17663_21 | ACLineSegment | Line | 0.034884 | 0.025125 | 0.01734 | 72.0259 | FALSE | 2024-01-20 21:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_17671_21 | ACLineSegment | Line | 0.034884 | 0.00381 | 0.0018077 | 10.922 | FALSE | 2024-01-20 19:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_17661_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_17662_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_17664_21 | ACLineSegment | Line | 0.034884 | 0.0031429 | 0.0017809 | 9.0096 | FALSE | 2024-01-21 04:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_17665_21 | ACLineSegment | Line | 0.034884 | 0.0049025 | 0.0029773 | 14.054 | FALSE | 2024-01-20 21:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_17666_21 | ACLineSegment | Line | 0.034884 | 0.005281 | 0.0026407 | 15.1388 | FALSE | 2024-01-20 16:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_17668_21 | ACLineSegment | Line | 0.034884 | 0.0048958 | 0.0026824 | 14.0348 | FALSE | 2024-01-20 18:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_17889_21 | ACLineSegment | Line | 0.034884 | 0.0073434 | 0.004462 | 21.0511 | FALSE | 2024-01-20 21:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_17892_21 | ACLineSegment | Line | 0.034884 | 0.014175 | 0.0086002 | 40.6355 | FALSE | 2024-01-20 21:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_17893_21 | ACLineSegment | Line | 0.034884 | 0.0050209 | 0.0028848 | 14.3933 | FALSE | 2024-01-21 03:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_17894_21 | ACLineSegment | Line | 0.034884 | 0.003275 | 0.0017249 | 9.3885 | FALSE | 2024-07-15 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_17890_21 | ACLineSegment | Line | 0.034884 | 0.0047632 | 0.0028734 | 13.6545 | FALSE | 2024-01-20 21:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_17891_21 | ACLineSegment | Line | 0.034884 | 0.0030803 | 0.0017738 | 8.8301 | FALSE | 2024-01-20 14:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_17900_21 | ACLineSegment | Line | 0.034884 | 0.0047632 | 0.0028734 | 13.6545 | FALSE | 2024-01-20 21:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_17895_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_17897_21 | ACLineSegment | Line | 0.034884 | 0.011414 | 0.0068312 | 32.7195 | FALSE | 2024-01-20 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_17903_21 | ACLineSegment | Line | 0.034884 | 0.0042418 | 0.002116 | 12.1598 | FALSE | 2024-01-20 20:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_17904_21 | ACLineSegment | Line | 0.034884 | 0.0054668 | 0.0028944 | 15.6716 | FALSE | 2024-01-20 08:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_17905_21 | ACLineSegment | Line | 0.034884 | 0.003927 | 0.0023271 | 11.2575 | FALSE | 2024-01-20 18:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_17896_21 | ACLineSegment | Line | 0.034884 | 0.013672 | 0.0082809 | 39.1927 | FALSE | 2024-01-20 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_17898_21 | ACLineSegment | Line | 0.034884 | 0.0027522 | 0.0015824 | 7.8896 | FALSE | 2024-07-16 01:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_17906_21 | ACLineSegment | Line | 0.034884 | 0.0042418 | 0.002116 | 12.1598 | FALSE | 2024-01-20 20:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_24661_21 | ACLineSegment | Line | 0.034884 | 0.0027033 | 0.0014657 | 7.7496 | FALSE | 2024-01-21 01:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_24663_21 | ACLineSegment | Line | 0.034884 | 0.0060791 | 0.0037687 | 17.4268 | FALSE | 2024-01-17 17:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_24662_21 | ACLineSegment | Line | 0.034884 | 0.0027033 | 0.0014657 | 7.7496 | FALSE | 2024-01-21 01:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_24664_21 | ACLineSegment | Line | 0.034884 | 0.0060791 | 0.0037687 | 17.4268 | FALSE | 2024-01-17 17:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_24864_21 | ACLineSegment | Line | 0.034884 | 0.0049018 | 0.0029183 | 14.052 | FALSE | 2024-01-20 15:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_24865_21 | ACLineSegment | Line | 0.034884 | 0.0091327 | 0.0056425 | 26.1806 | FALSE | 2024-01-20 12:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_24866_21 | ACLineSegment | Line | 0.034884 | 0.0059293 | 0.0029223 | 16.9973 | FALSE | 2024-01-20 17:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_24867_21 | ACLineSegment | Line | 0.034884 | 0.0049018 | 0.0029183 | 14.052 | FALSE | 2024-01-20 15:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_24873_21 | ACLineSegment | Line | 0.034884 | 0.017447 | 0.010427 | 50.0143 | FALSE | 2024-01-21 03:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_24886_21 | ACLineSegment | Line | 0.034884 | 0.004151 | 0.0022825 | 11.8996 | FALSE | 2024-01-20 06:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_24869_21 | ACLineSegment | Line | 0.034884 | 0.017703 | 0.011842 | 50.7481 | FALSE | 2024-07-15 13:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_24876_21 | ACLineSegment | Line | 0.034884 | 0.013895 | 0.0088404 | 39.8323 | FALSE | 2024-07-15 13:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_24882_21 | ACLineSegment | Line | 0.034884 | 0.0056052 | 0.0032962 | 16.0684 | FALSE | 2024-01-21 03:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_24872_21 | ACLineSegment | Line | 0.034884 | 0.015534 | 0.008733 | 44.53 | FALSE | 2024-01-21 03:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_24874_21 | ACLineSegment | Line | 0.034884 | 0.0030227 | 0.0018703 | 8.665 | FALSE | 2024-01-20 16:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_24880_21 | ACLineSegment | Line | 0.034884 | 0.015534 | 0.008733 | 44.53 | FALSE | 2024-01-21 03:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_24875_21 | ACLineSegment | Line | 0.034884 | 0.0083989 | 0.0050953 | 24.077 | FALSE | 2024-07-15 13:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_24877_21 | ACLineSegment | Line | 0.034884 | 0.0067378 | 0.0040578 | 19.3152 | FALSE | 2024-01-20 07:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_24878_21 | ACLineSegment | Line | 0.034884 | 0.0054419 | 0.0030811 | 15.6003 | FALSE | 2024-01-20 12:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_24879_21 | ACLineSegment | Line | 0.034884 | 0.0034683 | 0.0022768 | 9.9426 | FALSE | 2024-07-15 05:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_24884_21 | ACLineSegment | Line | 0.034884 | 0.0054419 | 0.0030811 | 15.6003 | FALSE | 2024-01-20 12:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_24881_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_24890_21 | ACLineSegment | Line | 0.034884 | 0.0048316 | 0.0024849 | 13.8508 | FALSE | 2024-01-21 03:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_24891_21 | ACLineSegment | Line | 0.034884 | 0.0046147 | 0.0028683 | 13.2288 | FALSE | 2024-01-20 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_24892_21 | ACLineSegment | Line | 0.034884 | 0.0076285 | 0.0038206 | 21.8686 | FALSE | 2024-01-21 03:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25042_21 | ACLineSegment | Line | 0.034884 | 0.017844 | 0.011537 | 51.1517 | FALSE | 2024-01-20 12:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25056_21 | ACLineSegment | Line | 0.034884 | 0.025852 | 0.017624 | 74.109 | FALSE | 2024-01-21 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25063_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25064_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25065_21 | ACLineSegment | Line | 0.034884 | 0.0045728 | 0.0020415 | 13.1087 | FALSE | 2024-01-20 22:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25066_21 | ACLineSegment | Line | 0.034884 | 0.0043003 | 0.0021367 | 12.3276 | FALSE | 2024-01-21 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25067_21 | ACLineSegment | Line | 0.034884 | 0.0043069 | 0.0024172 | 12.3466 | FALSE | 2024-01-17 20:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25043_21 | ACLineSegment | Line | 0.034884 | 0.012852 | 0.0080384 | 36.8423 | FALSE | 2024-01-21 02:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25044_21 | ACLineSegment | Line | 0.034884 | 0.0072203 | 0.003844 | 20.6984 | FALSE | 2024-01-20 17:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25069_21 | ACLineSegment | Line | 0.034884 | 0.0099428 | 0.005832 | 28.5029 | FALSE | 2024-01-21 02:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25072_21 | ACLineSegment | Line | 0.034884 | 0.0050481 | 0.0025062 | 14.4714 | FALSE | 2024-01-20 12:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25045_21 | ACLineSegment | Line | 0.034884 | 0.0036109 | 0.0019557 | 10.3512 | FALSE | 2024-07-15 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25070_21 | ACLineSegment | Line | 0.034884 | 0.0070712 | 0.0041158 | 20.2709 | FALSE | 2024-01-20 05:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25046_21 | ACLineSegment | Line | 0.034884 | 0.0036109 | 0.0019557 | 10.3512 | FALSE | 2024-07-15 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25047_21 | ACLineSegment | Line | 0.034884 | 0.0034759 | 0.0021564 | 9.9644 | FALSE | 2024-01-20 11:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25061_21 | ACLineSegment | Line | 0.034884 | 0.0084902 | 0.004835 | 24.3386 | FALSE | 2024-01-20 11:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25062_21 | ACLineSegment | Line | 0.034884 | 0.0050142 | 0.0028813 | 14.3742 | FALSE | 2024-01-20 11:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25048_21 | ACLineSegment | Line | 0.034884 | 0.0034759 | 0.0021564 | 9.9644 | FALSE | 2024-01-20 11:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25049_21 | ACLineSegment | Line | 0.034884 | 0.025916 | 0.016482 | 74.294 | FALSE | 2024-01-20 07:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25050_21 | ACLineSegment | Line | 0.034884 | 0.029003 | 0.01853 | 83.1414 | FALSE | 2024-01-20 07:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25051_21 | ACLineSegment | Line | 0.034884 | 0.004251 | 0.0023274 | 12.1864 | FALSE | 2024-01-17 12:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25052_21 | ACLineSegment | Line | 0.034884 | 0.0067552 | 0.0037431 | 19.3651 | FALSE | 2024-01-20 20:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25053_21 | ACLineSegment | Line | 0.034884 | 0.018325 | 0.011588 | 52.5331 | FALSE | 2024-01-20 07:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25054_21 | ACLineSegment | Line | 0.034884 | 0.0035503 | 0.0018143 | 10.1776 | FALSE | 2024-01-21 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25060_21 | ACLineSegment | Line | 0.034884 | 0.0067552 | 0.0037431 | 19.3651 | FALSE | 2024-01-20 20:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25073_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25074_21 | ACLineSegment | Line | 0.034884 | 0.006162 | 0.0036239 | 17.6644 | FALSE | 2024-01-20 16:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25075_21 | ACLineSegment | Line | 0.034884 | 0.0071015 | 0.0036375 | 20.3579 | FALSE | 2024-01-20 07:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25055_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25058_21 | ACLineSegment | Line | 0.034884 | 0.0065688 | 0.0035104 | 18.8306 | FALSE | 2024-06-27 02:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25059_21 | ACLineSegment | Line | 0.034884 | 0.008383 | 0.0043496 | 24.0313 | FALSE | 2024-01-20 23:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25120_21 | ACLineSegment | Line | 0.034884 | 0.0041338 | 0.002249 | 11.8503 | FALSE | 2024-07-15 21:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25122_21 | ACLineSegment | Line | 0.034884 | 0.029344 | 0.01859 | 84.1193 | FALSE | 2024-01-20 11:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25123_21 | ACLineSegment | Line | 0.034884 | 0.020939 | 0.013965 | 60.0259 | FALSE | 2024-01-21 02:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25124_21 | ACLineSegment | Line | 0.034884 | 0.0049383 | 0.0026423 | 14.1565 | FALSE | 2024-01-20 11:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25121_21 | ACLineSegment | Line | 0.034884 | 0.0041338 | 0.002249 | 11.8503 | FALSE | 2024-07-15 21:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25132_21 | ACLineSegment | Line | 0.034884 | 0.020939 | 0.013965 | 60.0259 | FALSE | 2024-01-21 02:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25125_21 | ACLineSegment | Line | 0.034884 | 0.0048028 | 0.0022533 | 13.7682 | FALSE | 2024-01-20 15:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25143_21 | ACLineSegment | Line | 0.034884 | 0.0072687 | 0.004216 | 20.837 | FALSE | 2024-01-20 15:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25150_21 | ACLineSegment | Line | 0.034884 | 0.0035064 | 0.0021281 | 10.0516 | FALSE | 2024-01-17 15:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25126_21 | ACLineSegment | Line | 0.034884 | 0.0048028 | 0.0022533 | 13.7682 | FALSE | 2024-01-20 15:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25127_21 | ACLineSegment | Line | 0.034884 | 0.0034624 | 0.0018754 | 9.9256 | FALSE | 2024-01-20 13:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25129_21 | ACLineSegment | Line | 0.034884 | 0.0076655 | 0.0046446 | 21.9746 | FALSE | 2024-01-20 13:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25130_21 | ACLineSegment | Line | 0.034884 | 0.0047287 | 0.0029215 | 13.5557 | FALSE | 2024-07-05 21:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25128_21 | ACLineSegment | Line | 0.034884 | 0.0034624 | 0.0018754 | 9.9256 | FALSE | 2024-01-20 13:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25136_21 | ACLineSegment | Line | 0.034884 | 0.0076655 | 0.0046446 | 21.9746 | FALSE | 2024-01-20 13:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25131_21 | ACLineSegment | Line | 0.034884 | 0.01456 | 0.0089303 | 41.7395 | FALSE | 2024-01-20 13:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25133_21 | ACLineSegment | Line | 0.034884 | 0.0065205 | 0.0035967 | 18.6922 | FALSE | 2024-01-20 22:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25134_21 | ACLineSegment | Line | 0.034884 | 0.0031896 | 0.001834 | 9.1436 | FALSE | 2024-01-21 02:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25137_21 | ACLineSegment | Line | 0.034884 | 0.0030641 | 0.0016431 | 8.7837 | FALSE | 2024-01-20 11:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25138_21 | ACLineSegment | Line | 0.034884 | 0.0061053 | 0.0029924 | 17.502 | FALSE | 2024-01-20 18:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25139_21 | ACLineSegment | Line | 0.034884 | 0.022656 | 0.013839 | 64.9472 | FALSE | 2024-01-20 15:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25142_21 | ACLineSegment | Line | 0.034884 | 0.0092292 | 0.0058367 | 26.4572 | FALSE | 2024-01-20 15:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25145_21 | ACLineSegment | Line | 0.034884 | 0.006675 | 0.0039383 | 19.135 | FALSE | 2024-01-20 19:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25146_21 | ACLineSegment | Line | 0.034884 | 0.0033011 | 0.0019609 | 9.4632 | FALSE | 2024-07-15 20:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25147_21 | ACLineSegment | Line | 0.034884 | 0.0051844 | 0.00276 | 14.8621 | FALSE | 2024-01-20 15:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25144_21 | ACLineSegment | Line | 0.034884 | 0.0035304 | 0.0017961 | 10.1205 | FALSE | 2024-01-17 16:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25148_21 | ACLineSegment | Line | 0.034884 | 0.0041587 | 0.0021134 | 11.9216 | FALSE | 2024-01-20 20:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25151_21 | ACLineSegment | Line | 0.034884 | 0.003792 | 0.0021377 | 10.8705 | FALSE | 2024-01-17 15:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25149_21 | ACLineSegment | Line | 0.034884 | 0.0041587 | 0.0021134 | 11.9216 | FALSE | 2024-01-20 20:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25818_21 | ACLineSegment | Line | 0.034884 | 0.014903 | 0.0095343 | 42.7225 | FALSE | 2024-01-20 08:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25819_21 | ACLineSegment | Line | 0.034884 | 0.015848 | 0.01079 | 45.4312 | FALSE | 2024-01-20 08:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25820_21 | ACLineSegment | Line | 0.034884 | 0.0023492 | 0.0013968 | 6.7344 | FALSE | 2024-07-14 13:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25821_21 | ACLineSegment | Line | 0.034884 | 0.011256 | 0.0072239 | 32.2688 | FALSE | 2024-01-20 05:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25822_21 | ACLineSegment | Line | 0.034884 | 0.0045101 | 0.0024921 | 12.9291 | FALSE | 2024-01-20 23:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25849_21 | ACLineSegment | Line | 0.034884 | 0.006474 | 0.0036876 | 18.5588 | FALSE | 2024-01-20 08:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25854_21 | ACLineSegment | Line | 0.034884 | 0.022322 | 0.014338 | 63.99 | FALSE | 2024-01-20 08:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25836_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25837_21 | ACLineSegment | Line | 0.034884 | 0.0038874 | 0.0022489 | 11.144 | FALSE | 2024-01-20 18:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25838_21 | ACLineSegment | Line | 0.034884 | 0.0054937 | 0.0030784 | 15.7488 | FALSE | 2024-01-17 07:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25839_21 | ACLineSegment | Line | 0.034884 | 0.0045166 | 0.0024382 | 12.9478 | FALSE | 2024-01-20 06:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25859_21 | ACLineSegment | Line | 0.034884 | 0.0045101 | 0.0024921 | 12.9291 | FALSE | 2024-01-20 23:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25823_21 | ACLineSegment | Line | 0.034884 | 0.014375 | 0.0090956 | 41.2077 | FALSE | 2024-01-17 17:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25833_21 | ACLineSegment | Line | 0.034884 | 0.020163 | 0.012606 | 57.8009 | FALSE | 2024-01-20 11:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25834_21 | ACLineSegment | Line | 0.034884 | 0.0068222 | 0.0037517 | 19.5571 | FALSE | 2024-01-20 14:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25824_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25825_21 | ACLineSegment | Line | 0.034884 | 0.0083839 | 0.005265 | 24.0339 | FALSE | 2024-01-17 17:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25826_21 | ACLineSegment | Line | 0.034884 | 0.0049845 | 0.0027688 | 14.2891 | FALSE | 2024-07-16 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25827_21 | ACLineSegment | Line | 0.034884 | 0.0022923 | 0.0013295 | 6.5714 | FALSE | 2024-01-21 04:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25852_21 | ACLineSegment | Line | 0.034884 | 0.0046821 | 0.0029461 | 13.4221 | FALSE | 2024-07-15 20:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25860_21 | ACLineSegment | Line | 0.034884 | 0.0043489 | 0.0024364 | 12.467 | FALSE | 2024-01-17 17:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25828_21 | ACLineSegment | Line | 0.034884 | 0.035725 | 0.022965 | 102.4113 | TRUE | 2024-01-20 11:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25829_21 | ACLineSegment | Line | 0.034884 | 0.026837 | 0.017218 | 76.9337 | FALSE | 2024-01-20 11:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25830_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25831_21 | ACLineSegment | Line | 0.034884 | 0.0057153 | 0.0027946 | 16.384 | FALSE | 2024-01-21 02:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25832_21 | ACLineSegment | Line | 0.034884 | 0.0058404 | 0.0034743 | 16.7425 | FALSE | 2024-07-15 06:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25846_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25847_21 | ACLineSegment | Line | 0.034884 | 0.0050509 | 0.0030862 | 14.4793 | FALSE | 2024-01-18 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25848_21 | ACLineSegment | Line | 0.034884 | 0.0035978 | 0.0019083 | 10.3137 | FALSE | 2024-01-20 19:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25850_21 | ACLineSegment | Line | 0.034884 | 0.0030668 | 0.0018365 | 8.7914 | FALSE | 2024-07-15 22:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25851_21 | ACLineSegment | Line | 0.034884 | 0.0036508 | 0.0019773 | 10.4656 | FALSE | 2024-01-20 08:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25853_21 | ACLineSegment | Line | 0.034884 | 0.0046821 | 0.0029461 | 13.4221 | FALSE | 2024-07-15 20:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25855_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25857_21 | ACLineSegment | Line | 0.034884 | 0.0070484 | 0.0036592 | 20.2056 | FALSE | 2024-01-20 13:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_25858_21 | ACLineSegment | Line | 0.034884 | 0.00436 | 0.0023204 | 12.4988 | FALSE | 2024-07-15 16:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_45221_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_45231_21 | ACLineSegment | Line | 0.034884 | 0.02495 | 0.015498 | 71.5251 | FALSE | 2024-01-20 11:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_45232_21 | ACLineSegment | Line | 0.034884 | 0.013173 | 0.0087865 | 37.7627 | FALSE | 2024-01-20 15:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_45233_21 | ACLineSegment | Line | 0.034884 | 0.0089668 | 0.0044432 | 25.705 | FALSE | 2024-01-20 21:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_45234_21 | ACLineSegment | Line | 0.034884 | 0.0052333 | 0.0028077 | 15.0024 | FALSE | 2024-01-17 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_45222_21 | ACLineSegment | Line | 0.034884 | 0.0078406 | 0.004361 | 22.4766 | FALSE | 2024-07-15 13:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_45235_21 | ACLineSegment | Line | 0.034884 | 0.0078406 | 0.004361 | 22.4766 | FALSE | 2024-07-15 13:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_45223_21 | ACLineSegment | Line | 0.034884 | 0.0043958 | 0.0023023 | 12.6013 | FALSE | 2024-07-15 13:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_45224_21 | ACLineSegment | Line | 0.034884 | 0.0048301 | 0.0024184 | 13.8465 | FALSE | 2024-01-20 11:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_45225_21 | ACLineSegment | Line | 0.046073 | 0.066549 | 0.044094 | 144.4429 | TRUE | 2024-01-20 15:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_45226_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_45227_21 | ACLineSegment | Line | 0.046073 | 0.079086 | 0.050939 | 171.6558 | TRUE | 2024-01-20 15:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_45228_21 | ACLineSegment | Line | 0.034884 | 0.0065478 | 0.0034516 | 18.7705 | FALSE | 2024-01-20 15:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_45229_21 | ACLineSegment | Line | 0.034884 | 0.004776 | 0.0026241 | 13.6913 | FALSE | 2024-01-20 15:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_45230_21 | ACLineSegment | Line | 0.034884 | 0.0021477 | 0.0012962 | 6.1568 | FALSE | 2024-07-15 05:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_45240_21 | ACLineSegment | Line | 0.034884 | 0.039519 | 0.025191 | 113.2881 | TRUE | 2024-01-20 15:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_45258_21 | ACLineSegment | Line | 0.034884 | 0.029745 | 0.018997 | 85.2703 | FALSE | 2024-01-20 20:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_45242_21 | ACLineSegment | Line | 0.034884 | 0.030303 | 0.019204 | 86.8705 | FALSE | 2024-01-20 12:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_45243_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_45244_21 | ACLineSegment | Line | 0.034884 | 0.0038722 | 0.0021467 | 11.1002 | FALSE | 2024-07-15 21:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_45245_21 | ACLineSegment | Line | 0.034884 | 0.0033137 | 0.0019969 | 9.4992 | FALSE | 2024-07-16 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_45236_21 | ACLineSegment | Line | 0.034884 | 0.013173 | 0.0087865 | 37.7627 | FALSE | 2024-01-20 15:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_45237_21 | ACLineSegment | Line | 0.034884 | 0.0038352 | 0.0020088 | 10.9942 | FALSE | 2024-01-20 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_45238_21 | ACLineSegment | Line | 0.034884 | 0.0052426 | 0.0027866 | 15.0288 | FALSE | 2024-01-21 02:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_45239_21 | ACLineSegment | Line | 0.034884 | 0.036414 | 0.022902 | 104.3863 | TRUE | 2024-01-20 15:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_45241_21 | ACLineSegment | Line | 0.034884 | 0.0037825 | 0.0023668 | 10.8431 | FALSE | 2024-01-20 12:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_45257_21 | ACLineSegment | Line | 0.034884 | 0.0086252 | 0.004375 | 24.7258 | FALSE | 2024-01-21 01:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_45246_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_45247_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_45248_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_45249_21 | ACLineSegment | Line | 0.034884 | 0.023356 | 0.014879 | 66.954 | FALSE | 2024-01-20 07:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_45250_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_45251_21 | ACLineSegment | Line | 0.034884 | 0.0040521 | 0.0024544 | 11.6162 | FALSE | 2024-01-20 05:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_45252_21 | ACLineSegment | Line | 0.034884 | 0.0032566 | 0.0019732 | 9.3357 | FALSE | 2024-01-20 22:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_45253_21 | ACLineSegment | Line | 0.034884 | 0.0082675 | 0.0043469 | 23.7002 | FALSE | 2024-01-20 07:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_45254_21 | ACLineSegment | Line | 0.034884 | 0.0061258 | 0.0032516 | 17.5608 | FALSE | 2024-01-20 20:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_45255_21 | ACLineSegment | Line | 0.034884 | 0.0030583 | 0.0017945 | 8.7672 | FALSE | 2024-01-20 13:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_45256_21 | ACLineSegment | Line | 0.034884 | 0.0037425 | 0.0021548 | 10.7286 | FALSE | 2024-01-21 04:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_45259_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_45260_21 | ACLineSegment | Line | 0.034884 | 0.0037588 | 0.0021365 | 10.7753 | FALSE | 2024-01-20 20:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_45261_21 | ACLineSegment | Line | 0.034884 | 0.003523 | 0.0022151 | 10.0992 | FALSE | 2024-01-20 22:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_45267_21 | ACLineSegment | Line | 0.034884 | 0.0040521 | 0.0024544 | 11.6162 | FALSE | 2024-01-20 05:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_45289_21 | ACLineSegment | Line | 0.034884 | 0.0066424 | 0.0049398 | 19.0416 | FALSE | 2024-01-21 23:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_45290_21 | ACLineSegment | Line | 0.034884 | 0.0066424 | 0.0049398 | 19.0416 | FALSE | 2024-01-21 23:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_45310_21 | ACLineSegment | Line | 0.51338 | 0.10553 | 0.05808 | 20.5553 | FALSE | 2024-10-03 02:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | line_45311_21 | ACLineSegment | Line | 0.51338 | 0.10553 | 0.05808 | 20.5553 | FALSE | 2024-10-03 02:00 | 650 | 0.48 |  | 3 | 3Phase_sqrt3_VLL_I
GSO_18 | line_53930_21 | ACLineSegment | Line | 0.034884 | 0.0047658 | 0.0025217 | 13.6621 | FALSE | 2024-01-21 04:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_53933_21 | ACLineSegment | Line | 0.034884 | 0.0062154 | 0.0036878 | 17.8175 | FALSE | 2024-01-20 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_53931_21 | ACLineSegment | Line | 0.034884 | 0.0047658 | 0.0025217 | 13.6621 | FALSE | 2024-01-21 04:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_53934_21 | ACLineSegment | Line | 0.034884 | 0.0039257 | 0.0023467 | 11.2538 | FALSE | 2024-01-20 13:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_53939_21 | ACLineSegment | Line | 0.034884 | 0.0051792 | 0.0028882 | 14.8471 | FALSE | 2024-01-20 08:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_53935_21 | ACLineSegment | Line | 0.034884 | 0.0039257 | 0.0023467 | 11.2538 | FALSE | 2024-01-20 13:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_55339_21 | ACLineSegment | Line | 0.034884 | 0.0033075 | 0.0019957 | 9.4816 | FALSE | 2024-01-20 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_55341_21 | ACLineSegment | Line | 0.034884 | 0.011998 | 0.0066627 | 34.3946 | FALSE | 2024-01-18 01:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_55340_21 | ACLineSegment | Line | 0.034884 | 0.0033075 | 0.0019957 | 9.4816 | FALSE | 2024-01-20 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_55345_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_55346_21 | ACLineSegment | Line | 0.034884 | 0.0059225 | 0.0033436 | 16.9779 | FALSE | 2024-01-18 01:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_55347_21 | ACLineSegment | Line | 0.034884 | 0.0062323 | 0.0035505 | 17.8661 | FALSE | 2024-07-16 01:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_55488_21 | ACLineSegment | Line | 0.034884 | 0.048088 | 0.03053 | 137.8533 | TRUE | 2024-01-20 11:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_55489_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_55490_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_55491_21 | ACLineSegment | Line | 0.034884 | 0.029945 | 0.018907 | 85.844 | FALSE | 2024-01-21 03:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_55492_21 | ACLineSegment | Line | 0.034884 | 0.0027981 | 0.0015913 | 8.0212 | FALSE | 2024-01-20 20:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_55493_21 | ACLineSegment | Line | 0.034884 | 0.0060314 | 0.0034754 | 17.2902 | FALSE | 2024-01-20 11:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_55494_21 | ACLineSegment | Line | 0.034884 | 0.0082853 | 0.0043521 | 23.7513 | FALSE | 2024-01-20 11:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_55495_21 | ACLineSegment | Line | 0.034884 | 0.0056405 | 0.0031327 | 16.1695 | FALSE | 2024-01-20 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_55513_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_55514_21 | ACLineSegment | Line | 0.034884 | 0.012038 | 0.0071779 | 34.5093 | FALSE | 2024-01-21 03:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_55515_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_55516_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_55517_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_55518_21 | ACLineSegment | Line | 0.034884 | 0.0034864 | 0.0020656 | 9.9943 | FALSE | 2024-01-17 19:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_55519_21 | ACLineSegment | Line | 0.034884 | 0.0052523 | 0.003088 | 15.0566 | FALSE | 2024-01-20 18:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_55520_21 | ACLineSegment | Line | 0.034884 | 0.0055262 | 0.0033221 | 15.8419 | FALSE | 2024-01-18 04:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_55521_21 | ACLineSegment | Line | 0.034884 | 0.0033836 | 0.0019445 | 9.6997 | FALSE | 2024-07-16 01:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_55522_21 | ACLineSegment | Line | 0.034884 | 0.0047936 | 0.0025592 | 13.7417 | FALSE | 2024-01-20 07:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_55497_21 | ACLineSegment | Line | 0.034884 | 0.010974 | 0.0059728 | 31.4604 | FALSE | 2024-01-20 19:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_55498_21 | ACLineSegment | Line | 0.034884 | 0.018189 | 0.010421 | 52.1413 | FALSE | 2024-01-20 19:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_55499_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_55500_21 | ACLineSegment | Line | 0.034884 | 0.0039043 | 0.002202 | 11.1924 | FALSE | 2024-01-17 06:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_55501_21 | ACLineSegment | Line | 0.034884 | 0.0055143 | 0.0027252 | 15.8076 | FALSE | 2024-01-20 16:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_55502_21 | ACLineSegment | Line | 0.034884 | 0.010974 | 0.0059728 | 31.4604 | FALSE | 2024-01-20 19:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_55506_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_55509_21 | ACLineSegment | Line | 0.034884 | 0.028528 | 0.018307 | 81.7818 | FALSE | 2024-01-21 04:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_55510_21 | ACLineSegment | Line | 0.034884 | 0.0041928 | 0.0024504 | 12.0193 | FALSE | 2024-01-20 08:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_55511_21 | ACLineSegment | Line | 0.034884 | 0.0030928 | 0.0017064 | 8.8662 | FALSE | 2024-01-20 12:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_55512_21 | ACLineSegment | Line | 0.034884 | 0.008305 | 0.0044324 | 23.8078 | FALSE | 2024-01-20 23:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_55504_21 | ACLineSegment | Line | 0.034884 | 0.0071252 | 0.0029458 | 20.4257 | FALSE | 2024-01-20 19:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_55505_21 | ACLineSegment | Line | 0.034884 | 0.0053277 | 0.0031957 | 15.2727 | FALSE | 2024-01-20 08:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_55524_21 | ACLineSegment | Line | 0.034884 | 0.012038 | 0.0071779 | 34.5093 | FALSE | 2024-01-21 03:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_55525_21 | ACLineSegment | Line | 0.034884 | 0.012038 | 0.0071779 | 34.5093 | FALSE | 2024-01-21 03:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_55526_21 | ACLineSegment | Line | 0.034884 | 0.0040701 | 0.0021318 | 11.6676 | FALSE | 2024-01-21 01:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_55527_21 | ACLineSegment | Line | 0.034884 | 0.0068364 | 0.0037428 | 19.5979 | FALSE | 2024-01-20 11:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_55528_21 | ACLineSegment | Line | 0.034884 | 0.0032229 | 0.0018348 | 9.2389 | FALSE | 2024-01-20 15:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_65974_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_65975_21 | ACLineSegment | Line | 0.034884 | 0.0066245 | 0.0039721 | 18.9905 | FALSE | 2024-01-20 17:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_65977_21 | ACLineSegment | Line | 0.034884 | 0.0059045 | 0.0032547 | 16.9262 | FALSE | 2024-01-20 06:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_65978_21 | ACLineSegment | Line | 0.034884 | 0.0067106 | 0.0034373 | 19.2372 | FALSE | 2024-01-17 22:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_65988_21 | ACLineSegment | Line | 0.034884 | 0.0066245 | 0.0039721 | 18.9905 | FALSE | 2024-01-20 17:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_65979_21 | ACLineSegment | Line | 0.034884 | 0.0081361 | 0.0044806 | 23.3238 | FALSE | 2024-01-22 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_65981_21 | ACLineSegment | Line | 0.034884 | 0.014471 | 0.0067905 | 41.4828 | FALSE | 2024-01-21 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_65984_21 | ACLineSegment | Line | 0.034884 | 0.006335 | 0.0026381 | 18.1605 | FALSE | 2024-01-21 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_65980_21 | ACLineSegment | Line | 0.034884 | 0.0081361 | 0.0044806 | 23.3238 | FALSE | 2024-01-22 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_65982_21 | ACLineSegment | Line | 0.034884 | 0.0059329 | 0.0037668 | 17.0076 | FALSE | 2024-07-05 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_65989_21 | ACLineSegment | Line | 0.034884 | 0.0030382 | 0.0017561 | 8.7094 | FALSE | 2024-01-17 15:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_65990_21 | ACLineSegment | Line | 0.034884 | 0.0039694 | 0.0022187 | 11.3792 | FALSE | 2024-07-05 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_66567_21 | ACLineSegment | Line | 0.034884 | 0.0068731 | 0.0040051 | 19.7031 | FALSE | 2024-01-20 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_66569_21 | ACLineSegment | Line | 0.034884 | 0.0034294 | 0.0018948 | 9.831 | FALSE | 2024-01-20 18:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_66568_21 | ACLineSegment | Line | 0.034884 | 0.0068731 | 0.0040051 | 19.7031 | FALSE | 2024-01-20 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_66570_21 | ACLineSegment | Line | 0.034884 | 0.0034294 | 0.0018948 | 9.831 | FALSE | 2024-01-20 18:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_67374_21 | ACLineSegment | Line | 0.034884 | 0.0084513 | 0.0044696 | 24.2271 | FALSE | 2024-07-16 03:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_67377_21 | ACLineSegment | Line | 0.034884 | 0.006326 | 0.0042828 | 18.1345 | FALSE | 2024-01-17 08:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_67375_21 | ACLineSegment | Line | 0.034884 | 0.0084513 | 0.0044696 | 24.2271 | FALSE | 2024-07-16 03:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_67376_21 | ACLineSegment | Line | 0.034884 | 0.006326 | 0.0042828 | 18.1345 | FALSE | 2024-01-17 08:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_67378_21 | ACLineSegment | Line | 0.034884 | 0.003381 | 0.0019961 | 9.6922 | FALSE | 2024-07-15 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_67379_21 | ACLineSegment | Line | 0.034884 | 0.0042152 | 0.002536 | 12.0836 | FALSE | 2024-01-18 01:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_67979_21 | ACLineSegment | Line | 0.034884 | 0.0044307 | 0.0020443 | 12.7015 | FALSE | 2024-01-20 18:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_67984_21 | ACLineSegment | Line | 0.034884 | 0.0076875 | 0.0046522 | 22.0376 | FALSE | 2024-01-20 18:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_67985_21 | ACLineSegment | Line | 0.034884 | 0.0054334 | 0.0027755 | 15.5758 | FALSE | 2024-01-20 11:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_67980_21 | ACLineSegment | Line | 0.034884 | 0.0044307 | 0.0020443 | 12.7015 | FALSE | 2024-01-20 18:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_67981_21 | ACLineSegment | Line | 0.034884 | 0.023554 | 0.015115 | 67.5232 | FALSE | 2024-01-20 08:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_67982_21 | ACLineSegment | Line | 0.034884 | 0.026018 | 0.01701 | 74.5866 | FALSE | 2024-01-20 08:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_67983_21 | ACLineSegment | Line | 0.034884 | 0.0039539 | 0.0020862 | 11.3346 | FALSE | 2024-01-21 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_67990_21 | ACLineSegment | Line | 0.034884 | 0.023554 | 0.015115 | 67.5232 | FALSE | 2024-01-20 08:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_67992_21 | ACLineSegment | Line | 0.034884 | 0.0063351 | 0.0035248 | 18.1606 | FALSE | 2024-01-20 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_67998_21 | ACLineSegment | Line | 0.034884 | 0.0076875 | 0.0046522 | 22.0376 | FALSE | 2024-01-20 18:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_67986_21 | ACLineSegment | Line | 0.034884 | 0.0044383 | 0.0024104 | 12.7233 | FALSE | 2024-01-20 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_67993_21 | ACLineSegment | Line | 0.034884 | 0.0084846 | 0.0045648 | 24.3226 | FALSE | 2024-01-20 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_67994_21 | ACLineSegment | Line | 0.034884 | 0.0043137 | 0.0023471 | 12.3661 | FALSE | 2024-01-20 12:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_67987_21 | ACLineSegment | Line | 0.034884 | 0.0044383 | 0.0024104 | 12.7233 | FALSE | 2024-01-20 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_67997_21 | ACLineSegment | Line | 0.034884 | 0.017546 | 0.010791 | 50.2979 | FALSE | 2024-01-20 08:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_68001_21 | ACLineSegment | Line | 0.034884 | 0.0037696 | 0.0019913 | 10.8063 | FALSE | 2024-01-20 18:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_68002_21 | ACLineSegment | Line | 0.034884 | 0.0044908 | 0.0026853 | 12.8738 | FALSE | 2024-07-15 12:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_67995_21 | ACLineSegment | Line | 0.034884 | 0.013285 | 0.0077934 | 38.0836 | FALSE | 2024-01-20 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_67996_21 | ACLineSegment | Line | 0.034884 | 0.0053352 | 0.0034005 | 15.2942 | FALSE | 2024-01-20 21:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_68003_21 | ACLineSegment | Line | 0.034884 | 0.016153 | 0.0098727 | 46.3051 | FALSE | 2024-01-20 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_68004_21 | ACLineSegment | Line | 0.034884 | 0.0045993 | 0.0023105 | 13.1849 | FALSE | 2024-01-20 05:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_67999_21 | ACLineSegment | Line | 0.034884 | 0.0073073 | 0.0040088 | 20.9478 | FALSE | 2024-01-17 11:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_68000_21 | ACLineSegment | Line | 0.034884 | 0.0048345 | 0.0026442 | 13.8588 | FALSE | 2024-01-20 08:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69053_21 | ACLineSegment | Line | 0.034884 | 0.022415 | 0.014884 | 64.2581 | FALSE | 2024-01-20 22:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69054_21 | ACLineSegment | Line | 0.034884 | 0.024718 | 0.016589 | 70.8587 | FALSE | 2024-01-20 22:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69055_21 | ACLineSegment | Line | 0.034884 | 0.0036051 | 0.0019189 | 10.3346 | FALSE | 2024-01-20 08:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69074_21 | ACLineSegment | Line | 0.034884 | 0.0072416 | 0.0045212 | 20.7594 | FALSE | 2024-01-17 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69079_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69080_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69081_21 | ACLineSegment | Line | 0.034884 | 0.0068806 | 0.0035722 | 19.7245 | FALSE | 2024-01-20 21:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69082_21 | ACLineSegment | Line | 0.034884 | 0.0064321 | 0.0035115 | 18.4387 | FALSE | 2024-01-20 22:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69083_21 | ACLineSegment | Line | 0.034884 | 0.0065425 | 0.0039964 | 18.7552 | FALSE | 2024-01-20 19:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69091_21 | ACLineSegment | Line | 0.034884 | 0.030012 | 0.020515 | 86.0344 | FALSE | 2024-01-20 22:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69092_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69093_21 | ACLineSegment | Line | 0.034884 | 0.0045161 | 0.0024097 | 12.9463 | FALSE | 2024-01-20 07:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69094_21 | ACLineSegment | Line | 0.034884 | 0.0034322 | 0.001908 | 9.8392 | FALSE | 2024-01-20 17:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69056_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69057_21 | ACLineSegment | Line | 0.034884 | 0.038474 | 0.02548 | 110.2941 | TRUE | 2024-01-20 07:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69063_21 | ACLineSegment | Line | 0.034884 | 0.0047502 | 0.0025215 | 13.6174 | FALSE | 2024-01-20 12:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69064_21 | ACLineSegment | Line | 0.034884 | 0.003727 | 0.0021651 | 10.6842 | FALSE | 2024-01-17 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69058_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69059_21 | ACLineSegment | Line | 0.034884 | 0.029666 | 0.018904 | 85.0419 | FALSE | 2024-01-20 07:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69060_21 | ACLineSegment | Line | 0.034884 | 0.0065439 | 0.0038549 | 18.7593 | FALSE | 2024-01-20 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69061_21 | ACLineSegment | Line | 0.034884 | 0.0053923 | 0.0033095 | 15.4581 | FALSE | 2024-01-20 06:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69072_21 | ACLineSegment | Line | 0.034884 | 0.027058 | 0.016663 | 77.5678 | FALSE | 2024-01-20 07:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69100_21 | ACLineSegment | Line | 0.034884 | 0.0038378 | 0.002316 | 11.0018 | FALSE | 2024-01-20 14:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69071_21 | ACLineSegment | Line | 0.034884 | 0.023198 | 0.014317 | 66.5012 | FALSE | 2024-01-20 07:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69073_21 | ACLineSegment | Line | 0.034884 | 0.0043444 | 0.0025627 | 12.454 | FALSE | 2024-01-20 18:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69085_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69086_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69087_21 | ACLineSegment | Line | 0.034884 | 0.0074827 | 0.0039291 | 21.4506 | FALSE | 2024-01-20 21:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69088_21 | ACLineSegment | Line | 0.034884 | 0.0084343 | 0.0045558 | 24.1785 | FALSE | 2024-01-21 03:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69089_21 | ACLineSegment | Line | 0.034884 | 0.0047406 | 0.0023677 | 13.5899 | FALSE | 2024-01-20 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69090_21 | ACLineSegment | Line | 0.034884 | 0.0095933 | 0.0044764 | 27.501 | FALSE | 2024-01-17 06:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69075_21 | ACLineSegment | Line | 0.034884 | 0.0054594 | 0.0033179 | 15.6504 | FALSE | 2024-01-17 11:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69076_21 | ACLineSegment | Line | 0.034884 | 0.0027551 | 0.0013568 | 7.898 | FALSE | 2024-01-20 22:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69096_21 | ACLineSegment | Line | 0.034884 | 0.0054594 | 0.0033179 | 15.6504 | FALSE | 2024-01-17 11:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69077_21 | ACLineSegment | Line | 0.034884 | 0.038918 | 0.026999 | 111.5658 | TRUE | 2024-01-20 22:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69097_21 | ACLineSegment | Line | 0.034884 | 0.036327 | 0.024747 | 104.1391 | TRUE | 2024-01-20 22:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69099_21 | ACLineSegment | Line | 0.034884 | 0.0048454 | 0.0024337 | 13.8902 | FALSE | 2024-01-21 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69095_21 | ACLineSegment | Line | 0.034884 | 0.0074827 | 0.0039291 | 21.4506 | FALSE | 2024-01-20 21:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69098_21 | ACLineSegment | Line | 0.034884 | 0.0080317 | 0.0045703 | 23.0244 | FALSE | 2024-01-20 20:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69130_21 | ACLineSegment | Line | 0.034884 | 0.013263 | 0.0083325 | 38.0198 | FALSE | 2024-01-20 22:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69131_21 | ACLineSegment | Line | 0.034884 | 0.013263 | 0.0083325 | 38.0198 | FALSE | 2024-01-20 22:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69132_21 | ACLineSegment | Line | 0.034884 | 0.0094553 | 0.005775 | 27.1055 | FALSE | 2024-01-21 03:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69133_21 | ACLineSegment | Line | 0.034884 | 0.0046904 | 0.00271 | 13.4458 | FALSE | 2024-01-20 22:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69134_21 | ACLineSegment | Line | 0.034884 | 0.020779 | 0.013647 | 59.5674 | FALSE | 2024-01-20 14:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69135_21 | ACLineSegment | Line | 0.034884 | 0.0072338 | 0.0036933 | 20.7369 | FALSE | 2024-01-21 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69136_21 | ACLineSegment | Line | 0.034884 | 0.0048934 | 0.0021243 | 14.0278 | FALSE | 2024-01-20 14:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69138_21 | ACLineSegment | Line | 0.034884 | 0.0062941 | 0.0036524 | 18.0433 | FALSE | 2024-01-20 07:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69148_21 | ACLineSegment | Line | 0.034884 | 0.0040312 | 0.0022976 | 11.5562 | FALSE | 2024-01-17 06:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69143_21 | ACLineSegment | Line | 0.034884 | 0.023951 | 0.015766 | 68.6609 | FALSE | 2024-01-21 03:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69144_21 | ACLineSegment | Line | 0.034884 | 0.0051735 | 0.0024564 | 14.8308 | FALSE | 2024-01-20 16:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69137_21 | ACLineSegment | Line | 0.034884 | 0.0034978 | 0.0019622 | 10.0271 | FALSE | 2024-01-20 11:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69139_21 | ACLineSegment | Line | 0.034884 | 0.003481 | 0.0018473 | 9.979 | FALSE | 2024-01-21 03:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69141_21 | ACLineSegment | Line | 0.034884 | 0.0034978 | 0.0019622 | 10.0271 | FALSE | 2024-01-20 11:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69140_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69145_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69149_21 | ACLineSegment | Line | 0.034884 | 0.015082 | 0.0096291 | 43.235 | FALSE | 2024-07-16 02:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69150_21 | ACLineSegment | Line | 0.034884 | 0.0051417 | 0.0031157 | 14.7397 | FALSE | 2024-01-20 17:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69151_21 | ACLineSegment | Line | 0.034884 | 0.0059272 | 0.0029635 | 16.9913 | FALSE | 2024-07-15 21:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69152_21 | ACLineSegment | Line | 0.034884 | 0.0042875 | 0.0021089 | 12.2909 | FALSE | 2024-01-20 17:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69153_21 | ACLineSegment | Line | 0.034884 | 0.0033638 | 0.0020478 | 9.643 | FALSE | 2024-01-17 17:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69147_21 | ACLineSegment | Line | 0.034884 | 0.0030556 | 0.0016125 | 8.7594 | FALSE | 2024-01-21 02:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69300_21 | ACLineSegment | Line | 0.034884 | 0.0040034 | 0.002323 | 11.4766 | FALSE | 2024-01-20 17:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69301_21 | ACLineSegment | Line | 0.034884 | 0.0040034 | 0.002323 | 11.4766 | FALSE | 2024-01-20 17:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69303_21 | ACLineSegment | Line | 0.034884 | 0.007836 | 0.0045548 | 22.4632 | FALSE | 2024-01-20 11:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69742_21 | ACLineSegment | Line | 0.034884 | 0.0053312 | 0.0031525 | 15.2828 | FALSE | 2024-01-18 01:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69743_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69744_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69745_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69746_21 | ACLineSegment | Line | 0.034884 | 0.019747 | 0.012661 | 56.6074 | FALSE | 2024-01-21 01:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69747_21 | ACLineSegment | Line | 0.034884 | 0.005868 | 0.0028096 | 16.8218 | FALSE | 2024-07-15 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69748_21 | ACLineSegment | Line | 0.034884 | 0.0047911 | 0.002597 | 13.7347 | FALSE | 2024-07-16 02:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69749_21 | ACLineSegment | Line | 0.034884 | 0.0060132 | 0.0034668 | 17.2381 | FALSE | 2024-07-15 08:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69750_21 | ACLineSegment | Line | 0.034884 | 0.0035874 | 0.0018633 | 10.284 | FALSE | 2024-01-20 08:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69751_21 | ACLineSegment | Line | 0.034884 | 0.0053312 | 0.0031525 | 15.2828 | FALSE | 2024-01-18 01:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69752_21 | ACLineSegment | Line | 0.034884 | 0.023571 | 0.015176 | 67.5709 | FALSE | 2024-01-20 06:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69766_21 | ACLineSegment | Line | 0.034884 | 0.0052241 | 0.0027345 | 14.9757 | FALSE | 2024-01-20 06:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69754_21 | ACLineSegment | Line | 0.034884 | 0.015818 | 0.010486 | 45.3456 | FALSE | 2024-01-21 01:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69757_21 | ACLineSegment | Line | 0.034884 | 0.021078 | 0.014445 | 60.424 | FALSE | 2024-01-21 01:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69758_21 | ACLineSegment | Line | 0.034884 | 0.003097 | 0.0017056 | 8.8782 | FALSE | 2024-01-20 12:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69759_21 | ACLineSegment | Line | 0.034884 | 0.0049609 | 0.0026655 | 14.2214 | FALSE | 2024-01-20 19:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69755_21 | ACLineSegment | Line | 0.034884 | 0.011014 | 0.0069317 | 31.5735 | FALSE | 2024-01-21 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69756_21 | ACLineSegment | Line | 0.034884 | 0.0068308 | 0.0037935 | 19.5819 | FALSE | 2024-01-18 02:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69761_21 | ACLineSegment | Line | 0.034884 | 0.0071587 | 0.0043258 | 20.5217 | FALSE | 2024-01-20 07:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69762_21 | ACLineSegment | Line | 0.034884 | 0.0049775 | 0.0027531 | 14.2689 | FALSE | 2024-01-21 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69763_21 | ACLineSegment | Line | 0.034884 | 0.0071587 | 0.0043258 | 20.5217 | FALSE | 2024-01-20 07:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69764_21 | ACLineSegment | Line | 0.034884 | 0.0048861 | 0.0028214 | 14.0068 | FALSE | 2024-01-20 07:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_69765_21 | ACLineSegment | Line | 0.034884 | 0.0031512 | 0.0017025 | 9.0335 | FALSE | 2024-01-20 20:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_72162_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_72163_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_72164_21 | ACLineSegment | Line | 0.034884 | 0.016283 | 0.010607 | 46.6794 | FALSE | 2024-01-17 08:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_72165_21 | ACLineSegment | Line | 0.034884 | 0.0045067 | 0.0027428 | 12.9193 | FALSE | 2024-01-21 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_72166_21 | ACLineSegment | Line | 0.034884 | 0.0065011 | 0.0037446 | 18.6365 | FALSE | 2024-01-20 19:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_72167_21 | ACLineSegment | Line | 0.034884 | 0.0081436 | 0.0045964 | 23.3452 | FALSE | 2024-01-20 22:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_72175_21 | ACLineSegment | Line | 0.034884 | 0.02057 | 0.012933 | 58.9671 | FALSE | 2024-01-17 08:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_72173_21 | ACLineSegment | Line | 0.034884 | 0.005815 | 0.0034929 | 16.6699 | FALSE | 2024-01-21 02:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_72179_21 | ACLineSegment | Line | 0.034884 | 0.010936 | 0.0067748 | 31.3502 | FALSE | 2024-07-15 19:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_72180_21 | ACLineSegment | Line | 0.034884 | 0.006072 | 0.0035036 | 17.4064 | FALSE | 2024-01-20 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_72174_21 | ACLineSegment | Line | 0.034884 | 0.005815 | 0.0034929 | 16.6699 | FALSE | 2024-01-21 02:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_72177_21 | ACLineSegment | Line | 0.034884 | 0.014989 | 0.0093042 | 42.9696 | FALSE | 2024-01-20 08:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_72178_21 | ACLineSegment | Line | 0.034884 | 0.0079961 | 0.0039418 | 22.9224 | FALSE | 2024-01-20 11:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_72181_21 | ACLineSegment | Line | 0.034884 | 0.0049041 | 0.002789 | 14.0586 | FALSE | 2024-07-15 08:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_73244_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_73245_21 | ACLineSegment | Line | 0.034884 | 0.029617 | 0.019738 | 84.9021 | FALSE | 2024-01-21 03:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_73246_21 | ACLineSegment | Line | 0.034884 | 0.0096541 | 0.0056778 | 27.6753 | FALSE | 2024-01-20 15:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_73247_21 | ACLineSegment | Line | 0.034884 | 0.049738 | 0.032171 | 142.5825 | TRUE | 2024-01-21 03:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_73248_21 | ACLineSegment | Line | 0.034884 | 0.0053353 | 0.0028758 | 15.2945 | FALSE | 2024-01-21 04:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_73249_21 | ACLineSegment | Line | 0.034884 | 0.0089536 | 0.0046463 | 25.6673 | FALSE | 2024-01-20 13:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_73255_21 | ACLineSegment | Line | 0.034884 | 0.022408 | 0.014562 | 64.2373 | FALSE | 2024-01-21 02:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_73256_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_73257_21 | ACLineSegment | Line | 0.034884 | 0.0071299 | 0.0035204 | 20.4393 | FALSE | 2024-01-20 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_73258_21 | ACLineSegment | Line | 0.034884 | 0.0032411 | 0.0019192 | 9.2913 | FALSE | 2024-01-20 13:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_73262_21 | ACLineSegment | Line | 0.034884 | 0.0047387 | 0.0029029 | 13.5844 | FALSE | 2024-06-26 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_73271_21 | ACLineSegment | Line | 0.034884 | 0.0056495 | 0.0031356 | 16.1954 | FALSE | 2024-01-20 15:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_73275_21 | ACLineSegment | Line | 0.034884 | 0.02305 | 0.01419 | 66.0766 | FALSE | 2024-01-20 08:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_73250_21 | ACLineSegment | Line | 0.034884 | 0.015571 | 0.0090542 | 44.6381 | FALSE | 2024-01-20 23:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_73253_21 | ACLineSegment | Line | 0.034884 | 0.018651 | 0.011554 | 53.4671 | FALSE | 2024-01-20 21:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_73254_21 | ACLineSegment | Line | 0.034884 | 0.0048974 | 0.002779 | 14.0393 | FALSE | 2024-01-21 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_73251_21 | ACLineSegment | Line | 0.034884 | 0.012161 | 0.0072711 | 34.8629 | FALSE | 2024-01-17 16:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_73252_21 | ACLineSegment | Line | 0.034884 | 0.0041369 | 0.0020093 | 11.8592 | FALSE | 2024-01-20 23:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_73272_21 | ACLineSegment | Line | 0.034884 | 0.0081628 | 0.0043336 | 23.4001 | FALSE | 2024-01-17 16:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_73282_21 | ACLineSegment | Line | 0.034884 | 0.0067689 | 0.003437 | 19.4042 | FALSE | 2024-01-18 01:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_73281_21 | ACLineSegment | Line | 0.034884 | 0.0049657 | 0.0029051 | 14.2351 | FALSE | 2024-01-21 08:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_73264_21 | ACLineSegment | Line | 0.034884 | 0.019543 | 0.012081 | 56.0232 | FALSE | 2024-01-21 03:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_73265_21 | ACLineSegment | Line | 0.034884 | 0.005295 | 0.0027184 | 15.1792 | FALSE | 2024-01-20 12:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_73263_21 | ACLineSegment | Line | 0.034884 | 0.0047387 | 0.0029029 | 13.5844 | FALSE | 2024-06-26 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_73268_21 | ACLineSegment | Line | 0.034884 | 0.013485 | 0.007563 | 38.6582 | FALSE | 2024-01-21 03:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_73277_21 | ACLineSegment | Line | 0.034884 | 0.0093422 | 0.0050171 | 26.7811 | FALSE | 2024-01-21 04:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_73266_21 | ACLineSegment | Line | 0.034884 | 0.0048098 | 0.0024538 | 13.7882 | FALSE | 2024-01-21 03:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_73273_21 | ACLineSegment | Line | 0.034884 | 0.0048072 | 0.0022322 | 13.7806 | FALSE | 2024-07-15 16:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_73267_21 | ACLineSegment | Line | 0.034884 | 0.0048098 | 0.0024538 | 13.7882 | FALSE | 2024-01-21 03:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_73269_21 | ACLineSegment | Line | 0.034884 | 0.0084541 | 0.0043946 | 24.2352 | FALSE | 2024-01-21 03:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_73270_21 | ACLineSegment | Line | 0.034884 | 0.0068507 | 0.0035107 | 19.6388 | FALSE | 2024-01-20 18:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_73274_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_73278_21 | ACLineSegment | Line | 0.034884 | 0.0028949 | 0.0016588 | 8.2987 | FALSE | 2024-01-20 15:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_73279_21 | ACLineSegment | Line | 0.034884 | 0.0066961 | 0.0035773 | 19.1955 | FALSE | 2024-01-21 02:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_75356_21 | ACLineSegment | Line | 0.034884 | 0.033638 | 0.02244 | 96.4303 | FALSE | 2024-01-20 07:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_75357_21 | ACLineSegment | Line | 0.034884 | 0.032173 | 0.020695 | 92.23 | FALSE | 2024-01-20 07:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_75358_21 | ACLineSegment | Line | 0.034884 | 0.0031202 | 0.0018632 | 8.9447 | FALSE | 2024-01-20 11:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_75376_21 | ACLineSegment | Line | 0.034884 | 0.024618 | 0.015956 | 70.5734 | FALSE | 2024-01-20 17:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_75377_21 | ACLineSegment | Line | 0.034884 | 0.0051848 | 0.0026869 | 14.8631 | FALSE | 2024-07-15 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_75378_21 | ACLineSegment | Line | 0.034884 | 0.004473 | 0.0025978 | 12.8228 | FALSE | 2024-07-16 01:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_75361_21 | ACLineSegment | Line | 0.034884 | 0.0055989 | 0.0031674 | 16.0504 | FALSE | 2024-01-20 07:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_75362_21 | ACLineSegment | Line | 0.034884 | 0.011552 | 0.0064596 | 33.1157 | FALSE | 2024-01-20 17:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_75363_21 | ACLineSegment | Line | 0.034884 | 0.0063907 | 0.0035837 | 18.3202 | FALSE | 2024-01-20 17:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_75373_21 | ACLineSegment | Line | 0.034884 | 0.0055989 | 0.0031674 | 16.0504 | FALSE | 2024-01-20 07:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_75382_21 | ACLineSegment | Line | 0.034884 | 0.015944 | 0.0093967 | 45.7065 | FALSE | 2024-01-20 17:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_75391_21 | ACLineSegment | Line | 0.034884 | 0.0055853 | 0.0031519 | 16.0112 | FALSE | 2024-01-18 03:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_75364_21 | ACLineSegment | Line | 0.034884 | 0.02017 | 0.01171 | 57.8206 | FALSE | 2024-01-20 13:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_75365_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_75366_21 | ACLineSegment | Line | 0.034884 | 0.028464 | 0.01756 | 81.5968 | FALSE | 2024-01-20 13:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_75367_21 | ACLineSegment | Line | 0.034884 | 0.0037558 | 0.0021035 | 10.7668 | FALSE | 2024-01-20 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_75368_21 | ACLineSegment | Line | 0.034884 | 0.0080879 | 0.0043524 | 23.1854 | FALSE | 2024-01-20 17:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_75369_21 | ACLineSegment | Line | 0.034884 | 0.02017 | 0.01171 | 57.8206 | FALSE | 2024-01-20 13:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_75384_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_75385_21 | ACLineSegment | Line | 0.034884 | 0.035094 | 0.022033 | 100.6023 | TRUE | 2024-01-20 13:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_75386_21 | ACLineSegment | Line | 0.034884 | 0.0045707 | 0.0026799 | 13.1028 | FALSE | 2024-07-15 12:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_75387_21 | ACLineSegment | Line | 0.034884 | 0.0037315 | 0.0022547 | 10.6969 | FALSE | 2024-01-20 13:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_75379_21 | ACLineSegment | Line | 0.034884 | 0.010664 | 0.0062991 | 30.5704 | FALSE | 2024-01-20 23:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_75380_21 | ACLineSegment | Line | 0.034884 | 0.0078068 | 0.0037693 | 22.3796 | FALSE | 2024-01-20 13:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_75381_21 | ACLineSegment | Line | 0.034884 | 0.003905 | 0.0021854 | 11.1945 | FALSE | 2024-01-20 23:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_75370_21 | ACLineSegment | Line | 0.034884 | 0.019878 | 0.01284 | 56.9832 | FALSE | 2024-01-20 17:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_75371_21 | ACLineSegment | Line | 0.034884 | 0.024618 | 0.015956 | 70.5734 | FALSE | 2024-01-20 17:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_75372_21 | ACLineSegment | Line | 0.034884 | 0.0056436 | 0.0032795 | 16.1785 | FALSE | 2024-01-20 07:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_75383_21 | ACLineSegment | Line | 0.034884 | 0.0061261 | 0.0036988 | 17.5616 | FALSE | 2024-01-18 02:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_75374_21 | ACLineSegment | Line | 0.034884 | 0.0068153 | 0.0036775 | 19.5372 | FALSE | 2024-01-20 17:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_75390_21 | ACLineSegment | Line | 0.034884 | 0.0050202 | 0.0029303 | 14.3912 | FALSE | 2024-01-21 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_75375_21 | ACLineSegment | Line | 0.034884 | 0.0068153 | 0.0036775 | 19.5372 | FALSE | 2024-01-20 17:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_75392_21 | ACLineSegment | Line | 0.034884 | 0.039821 | 0.025543 | 114.1552 | TRUE | 2024-01-20 13:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_75393_21 | ACLineSegment | Line | 0.034884 | 0.0062851 | 0.0035205 | 18.0173 | FALSE | 2024-01-20 18:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_75395_21 | ACLineSegment | Line | 0.034884 | 0.0052787 | 0.0025447 | 15.1323 | FALSE | 2024-01-20 19:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_75872_21 | ACLineSegment | Line | 0.034884 | 0.010578 | 0.0055991 | 30.3235 | FALSE | 2024-01-21 04:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_75873_21 | ACLineSegment | Line | 0.034884 | 0.010578 | 0.0055991 | 30.3235 | FALSE | 2024-01-21 04:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_75874_21 | ACLineSegment | Line | 0.034884 | 0.0066498 | 0.0035384 | 19.063 | FALSE | 2024-01-17 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_75875_21 | ACLineSegment | Line | 0.034884 | 0.0047356 | 0.002411 | 13.5756 | FALSE | 2024-01-21 04:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_75876_21 | ACLineSegment | Line | 0.034884 | 0.0073501 | 0.0037958 | 21.0704 | FALSE | 2024-01-21 01:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_75877_21 | ACLineSegment | Line | 0.034884 | 0.0073501 | 0.0037958 | 21.0704 | FALSE | 2024-01-21 01:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_79141_21 | ACLineSegment | Line | 0.034884 | 0.0084736 | 0.0040736 | 24.2912 | FALSE | 2024-07-06 02:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_79166_21 | ACLineSegment | Line | 0.034884 | 0.013061 | 0.0072078 | 37.4427 | FALSE | 2024-07-16 02:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_79167_21 | ACLineSegment | Line | 0.034884 | 0.0059445 | 0.0034478 | 17.041 | FALSE | 2024-01-17 05:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_79142_21 | ACLineSegment | Line | 0.034884 | 0.0084736 | 0.0040736 | 24.2912 | FALSE | 2024-07-06 02:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_79145_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_79146_21 | ACLineSegment | Line | 0.034884 | 0.018298 | 0.010416 | 52.4549 | FALSE | 2024-01-21 02:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_79147_21 | ACLineSegment | Line | 0.034884 | 0.0075168 | 0.0038299 | 21.5484 | FALSE | 2024-01-21 02:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_79148_21 | ACLineSegment | Line | 0.034884 | 0.0082757 | 0.0038364 | 23.724 | FALSE | 2024-01-20 22:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_79149_21 | ACLineSegment | Line | 0.034884 | 0.0064261 | 0.0035422 | 18.4217 | FALSE | 2024-07-15 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_79155_21 | ACLineSegment | Line | 0.034884 | 0.021755 | 0.012711 | 62.3655 | FALSE | 2024-01-20 06:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_79177_21 | ACLineSegment | Line | 0.034884 | 0.036446 | 0.022821 | 104.4806 | TRUE | 2024-01-20 21:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_79150_21 | ACLineSegment | Line | 0.034884 | 0.012097 | 0.0065084 | 34.6773 | FALSE | 2024-01-20 06:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_79153_21 | ACLineSegment | Line | 0.034884 | 0.012097 | 0.0065084 | 34.6773 | FALSE | 2024-01-20 06:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_79151_21 | ACLineSegment | Line | 0.034884 | 0.0072871 | 0.003989 | 20.8898 | FALSE | 2024-01-20 06:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_79152_21 | ACLineSegment | Line | 0.034884 | 0.005305 | 0.002714 | 15.2077 | FALSE | 2024-01-20 21:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_79168_21 | ACLineSegment | Line | 0.034884 | 0.01578 | 0.0083979 | 45.2368 | FALSE | 2024-01-20 06:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_79178_21 | ACLineSegment | Line | 0.034884 | 0.0036835 | 0.0021343 | 10.5595 | FALSE | 2024-01-20 06:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_79154_21 | ACLineSegment | Line | 0.034884 | 0.019168 | 0.010715 | 54.9477 | FALSE | 2024-01-20 06:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_79156_21 | ACLineSegment | Line | 0.034884 | 0.0038907 | 0.0021778 | 11.1533 | FALSE | 2024-01-20 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_79169_21 | ACLineSegment | Line | 0.034884 | 0.0052041 | 0.0025679 | 14.9185 | FALSE | 2024-01-21 04:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_79157_21 | ACLineSegment | Line | 0.034884 | 0.0050092 | 0.0030262 | 14.3597 | FALSE | 2024-01-17 13:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_79160_21 | ACLineSegment | Line | 0.034884 | 0.029364 | 0.019287 | 84.1769 | FALSE | 2024-07-16 02:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_79171_21 | ACLineSegment | Line | 0.034884 | 0.020653 | 0.01362 | 59.2062 | FALSE | 2024-07-16 02:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_79176_21 | ACLineSegment | Line | 0.034884 | 0.005733 | 0.0031978 | 16.4346 | FALSE | 2024-01-21 02:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_79158_21 | ACLineSegment | Line | 0.034884 | 0.0050092 | 0.0030262 | 14.3597 | FALSE | 2024-01-17 13:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_79159_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_79161_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_79162_21 | ACLineSegment | Line | 0.034884 | 0.039387 | 0.026112 | 112.9089 | TRUE | 2024-07-16 02:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_79163_21 | ACLineSegment | Line | 0.034884 | 0.0029667 | 0.0016035 | 8.5045 | FALSE | 2024-01-20 14:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_79164_21 | ACLineSegment | Line | 0.034884 | 0.0039093 | 0.0023327 | 11.2068 | FALSE | 2024-01-20 21:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_79165_21 | ACLineSegment | Line | 0.034884 | 0.0061052 | 0.0036213 | 17.5016 | FALSE | 2024-01-20 13:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_79173_21 | ACLineSegment | Line | 0.034884 | 0.013061 | 0.0072078 | 37.4427 | FALSE | 2024-07-16 02:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_79170_21 | ACLineSegment | Line | 0.034884 | 0.018677 | 0.012016 | 53.5413 | FALSE | 2024-01-18 02:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_79172_21 | ACLineSegment | Line | 0.034884 | 0.0041624 | 0.0017554 | 11.9323 | FALSE | 2024-01-20 05:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_79174_21 | ACLineSegment | Line | 0.034884 | 0.0038719 | 0.0023161 | 11.0995 | FALSE | 2024-01-20 21:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_79175_21 | ACLineSegment | Line | 0.034884 | 0.0055829 | 0.0030429 | 16.0045 | FALSE | 2024-01-21 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_88165_21 | ACLineSegment | Line | 0.034884 | 0.022399 | 0.016546 | 64.2103 | FALSE | 2024-01-20 08:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_88172_21 | ACLineSegment | Line | 0.034884 | 0.022399 | 0.016546 | 64.2103 | FALSE | 2024-01-20 08:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_89679_21 | ACLineSegment | Line | 0.034884 | 0.018443 | 0.011473 | 52.8715 | FALSE | 2024-01-17 15:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_89682_21 | ACLineSegment | Line | 0.034884 | 0.012372 | 0.0074826 | 35.4666 | FALSE | 2024-01-20 22:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_89683_21 | ACLineSegment | Line | 0.034884 | 0.02818 | 0.018704 | 80.782 | FALSE | 2024-01-20 21:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_89680_21 | ACLineSegment | Line | 0.034884 | 0.013019 | 0.0082893 | 37.3201 | FALSE | 2024-01-20 13:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_89681_21 | ACLineSegment | Line | 0.034884 | 0.0061988 | 0.0034783 | 17.77 | FALSE | 2024-07-15 15:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_89693_21 | ACLineSegment | Line | 0.034884 | 0.0082106 | 0.0048978 | 23.5372 | FALSE | 2024-01-21 04:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_89694_21 | ACLineSegment | Line | 0.034884 | 0.0065559 | 0.0037601 | 18.7936 | FALSE | 2024-01-17 15:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_89684_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_89696_21 | ACLineSegment | Line | 0.034884 | 0.0058339 | 0.0029423 | 16.724 | FALSE | 2024-01-20 17:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_89697_21 | ACLineSegment | Line | 0.034884 | 0.0054011 | 0.0025242 | 15.4834 | FALSE | 2024-01-20 23:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_89698_21 | ACLineSegment | Line | 0.034884 | 0.0046115 | 0.0025156 | 13.2198 | FALSE | 2024-01-17 13:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_89687_21 | ACLineSegment | Line | 0.034884 | 0.01981 | 0.013685 | 56.7898 | FALSE | 2024-01-20 12:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_89685_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_89686_21 | ACLineSegment | Line | 0.034884 | 0.013217 | 0.0084205 | 37.8897 | FALSE | 2024-01-20 12:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_89688_21 | ACLineSegment | Line | 0.034884 | 0.0053147 | 0.0031181 | 15.2355 | FALSE | 2024-01-17 14:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_89689_21 | ACLineSegment | Line | 0.034884 | 0.0044778 | 0.0026909 | 12.8365 | FALSE | 2024-07-15 01:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_89691_21 | ACLineSegment | Line | 0.034884 | 0.0080463 | 0.0046605 | 23.0661 | FALSE | 2024-01-20 20:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_89702_21 | ACLineSegment | Line | 0.034884 | 0.0063579 | 0.0039466 | 18.2262 | FALSE | 2024-01-20 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_89690_21 | ACLineSegment | Line | 0.034884 | 0.0059889 | 0.0029137 | 17.1682 | FALSE | 2024-01-21 03:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_89692_21 | ACLineSegment | Line | 0.034884 | 0.0037387 | 0.0019833 | 10.7177 | FALSE | 2024-01-20 23:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_89695_21 | ACLineSegment | Line | 0.034884 | 0.0059889 | 0.0029137 | 17.1682 | FALSE | 2024-01-21 03:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_89699_21 | ACLineSegment | Line | 0.034884 | 0.0060912 | 0.0030667 | 17.4615 | FALSE | 2024-01-20 19:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_89700_21 | ACLineSegment | Line | 0.034884 | 0.0035968 | 0.0021616 | 10.3108 | FALSE | 2024-01-21 04:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_89701_21 | ACLineSegment | Line | 0.034884 | 0.0065559 | 0.0037601 | 18.7936 | FALSE | 2024-01-17 15:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_90312_21 | ACLineSegment | Line | 0.034884 | 0.0066482 | 0.0033973 | 19.0583 | FALSE | 2024-01-20 12:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_90314_21 | ACLineSegment | Line | 0.034884 | 0.0049456 | 0.0028076 | 14.1776 | FALSE | 2024-01-20 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_90315_21 | ACLineSegment | Line | 0.034884 | 0.0066482 | 0.0033973 | 19.0583 | FALSE | 2024-01-20 12:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_90317_21 | ACLineSegment | Line | 0.034884 | 0.0047679 | 0.0026383 | 13.668 | FALSE | 2024-07-15 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_90820_21 | ACLineSegment | Line | 0.034884 | 0.0043188 | 0.0025116 | 12.3807 | FALSE | 2024-01-20 23:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_90821_21 | ACLineSegment | Line | 0.034884 | 0.0043188 | 0.0025116 | 12.3807 | FALSE | 2024-01-20 23:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_90886_21 | ACLineSegment | Line | 0.034884 | 0.010107 | 0.006346 | 28.9728 | FALSE | 2024-01-20 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_90887_21 | ACLineSegment | Line | 0.034884 | 0.016807 | 0.010129 | 48.1806 | FALSE | 2024-01-20 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_90888_21 | ACLineSegment | Line | 0.034884 | 0.0047142 | 0.0022997 | 13.5141 | FALSE | 2024-01-20 13:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_90889_21 | ACLineSegment | Line | 0.034884 | 0.0035165 | 0.0019671 | 10.0806 | FALSE | 2024-07-16 02:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_90899_21 | ACLineSegment | Line | 0.034884 | 0.010107 | 0.006346 | 28.9728 | FALSE | 2024-01-20 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_90902_21 | ACLineSegment | Line | 0.034884 | 0.018899 | 0.012308 | 54.1775 | FALSE | 2024-01-20 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_90911_21 | ACLineSegment | Line | 0.034884 | 0.0041163 | 0.0023545 | 11.8002 | FALSE | 2024-01-21 03:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_90890_21 | ACLineSegment | Line | 0.034884 | 0.0099134 | 0.0051774 | 28.4186 | FALSE | 2024-01-20 05:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_90891_21 | ACLineSegment | Line | 0.034884 | 0.016525 | 0.0097252 | 47.3713 | FALSE | 2024-01-20 05:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_90892_21 | ACLineSegment | Line | 0.034884 | 0.0083647 | 0.0050208 | 23.9788 | FALSE | 2024-01-20 21:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_90901_21 | ACLineSegment | Line | 0.034884 | 0.0099134 | 0.0051774 | 28.4186 | FALSE | 2024-01-20 05:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_90906_21 | ACLineSegment | Line | 0.034884 | 0.021718 | 0.012521 | 62.2591 | FALSE | 2024-01-20 05:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_90907_21 | ACLineSegment | Line | 0.034884 | 0.0055555 | 0.0030668 | 15.9259 | FALSE | 2024-01-21 01:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_90896_21 | ACLineSegment | Line | 0.034884 | 0.02792 | 0.017319 | 80.0368 | FALSE | 2024-01-20 05:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_90913_21 | ACLineSegment | Line | 0.034884 | 0.0077887 | 0.0036699 | 22.3277 | FALSE | 2024-01-20 20:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_90914_21 | ACLineSegment | Line | 0.034884 | 0.003805 | 0.0019991 | 10.9076 | FALSE | 2024-01-21 04:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_90908_21 | ACLineSegment | Line | 0.034884 | 0.010107 | 0.006346 | 28.9728 | FALSE | 2024-01-20 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_90900_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_90904_21 | ACLineSegment | Line | 0.034884 | 0.0053652 | 0.0028431 | 15.3803 | FALSE | 2024-01-21 02:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_90905_21 | ACLineSegment | Line | 0.034884 | 0.0027804 | 0.001706 | 7.9706 | FALSE | 2024-01-20 20:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_90909_21 | ACLineSegment | Line | 0.034884 | 0.0061301 | 0.0036763 | 17.5729 | FALSE | 2024-01-20 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_90910_21 | ACLineSegment | Line | 0.034884 | 0.0049647 | 0.0029849 | 14.2323 | FALSE | 2024-01-18 01:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_90946_21 | ACLineSegment | Line | 0.034884 | 0.0036041 | 0.0020028 | 10.3319 | FALSE | 2024-01-20 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_90948_21 | ACLineSegment | Line | 0.034884 | 0.0037823 | 0.0023418 | 10.8425 | FALSE | 2024-01-17 14:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_90947_21 | ACLineSegment | Line | 0.034884 | 0.0036041 | 0.0020028 | 10.3319 | FALSE | 2024-01-20 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_90949_21 | ACLineSegment | Line | 0.034884 | 0.0037823 | 0.0023418 | 10.8425 | FALSE | 2024-01-17 14:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_91037_21 | ACLineSegment | Line | 0.034884 | 0.005839 | 0.0032953 | 16.7387 | FALSE | 2024-01-20 17:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_91043_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_91046_21 | ACLineSegment | Line | 0.034884 | 0.012445 | 0.008138 | 35.6746 | FALSE | 2024-01-20 05:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_91047_21 | ACLineSegment | Line | 0.034884 | 0.0034018 | 0.0019776 | 9.7519 | FALSE | 2024-01-21 01:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_91048_21 | ACLineSegment | Line | 0.034884 | 0.0058247 | 0.0032857 | 16.6975 | FALSE | 2024-01-18 04:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_91038_21 | ACLineSegment | Line | 0.034884 | 0.005839 | 0.0032953 | 16.7387 | FALSE | 2024-01-20 17:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_91039_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_91040_21 | ACLineSegment | Line | 0.034884 | 0.010493 | 0.0075726 | 30.0797 | FALSE | 2024-06-29 17:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_91041_21 | ACLineSegment | Line | 0.034884 | 0.005512 | 0.0031131 | 15.8012 | FALSE | 2024-01-20 20:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_91042_21 | ACLineSegment | Line | 0.034884 | 0.0089762 | 0.0056233 | 25.7319 | FALSE | 2024-07-07 17:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_91044_21 | ACLineSegment | Line | 0.034884 | 0.013853 | 0.0093606 | 39.7134 | FALSE | 2024-01-20 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_91045_21 | ACLineSegment | Line | 0.034884 | 0.0048365 | 0.0025293 | 13.8648 | FALSE | 2024-01-20 05:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_91229_21 | ACLineSegment | Line | 0.034884 | 0.0045802 | 0.0027081 | 13.13 | FALSE | 2024-01-21 12:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_91231_21 | ACLineSegment | Line | 0.034884 | 0.0092443 | 0.006022 | 26.5006 | FALSE | 2024-01-21 04:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_91232_21 | ACLineSegment | Line | 0.034884 | 0.0065458 | 0.0036005 | 18.7649 | FALSE | 2024-01-20 23:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_91230_21 | ACLineSegment | Line | 0.034884 | 0.0045802 | 0.0027081 | 13.13 | FALSE | 2024-01-21 12:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_91233_21 | ACLineSegment | Line | 0.034884 | 0.012548 | 0.0087795 | 35.971 | FALSE | 2024-07-14 21:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_91234_21 | ACLineSegment | Line | 0.034884 | 0.0045358 | 0.002892 | 13.0028 | FALSE | 2024-07-14 21:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_91247_21 | ACLineSegment | Line | 0.034884 | 0.017551 | 0.012592 | 50.3123 | FALSE | 2024-01-21 04:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_91248_21 | ACLineSegment | Line | 0.034884 | 0.0072325 | 0.0040295 | 20.7332 | FALSE | 2024-01-21 01:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_91235_21 | ACLineSegment | Line | 0.034884 | 0.0063053 | 0.003469 | 18.0754 | FALSE | 2024-01-20 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_91236_21 | ACLineSegment | Line | 0.034884 | 0.015569 | 0.0084402 | 44.6314 | FALSE | 2024-01-21 03:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_91237_21 | ACLineSegment | Line | 0.034884 | 0.008163 | 0.0035345 | 23.4006 | FALSE | 2024-01-21 03:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_91238_21 | ACLineSegment | Line | 0.034884 | 0.0042687 | 0.0021916 | 12.2371 | FALSE | 2024-07-16 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_91246_21 | ACLineSegment | Line | 0.034884 | 0.0063053 | 0.003469 | 18.0754 | FALSE | 2024-01-20 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_91239_21 | ACLineSegment | Line | 0.034884 | 0.015569 | 0.0084402 | 44.6314 | FALSE | 2024-01-21 03:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_91240_21 | ACLineSegment | Line | 0.034884 | 0.018393 | 0.010816 | 52.7262 | FALSE | 2024-01-20 11:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_91241_21 | ACLineSegment | Line | 0.034884 | 0.0047183 | 0.0027409 | 13.5257 | FALSE | 2024-01-20 15:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_91340_21 | ACLineSegment | Line | 0.025406 | 0.0064007 | 0.0033203 | 25.1938 | FALSE | 2024-01-20 19:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_91895_21 | ACLineSegment | Line | 0.025406 | 0.0042275 | 0.0025942 | 16.6401 | FALSE | 2024-07-15 20:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_91896_21 | ACLineSegment | Line | 0.025406 | 0.0070765 | 0.0045136 | 27.8539 | FALSE | 2024-01-17 20:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_91897_21 | ACLineSegment | Line | 0.025406 | 0.003819 | 0.0020782 | 15.0322 | FALSE | 2024-01-20 20:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_91898_21 | ACLineSegment | Line | 0.025406 | 0.0042275 | 0.0025942 | 16.6401 | FALSE | 2024-07-15 20:00 | 193 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_91899_21 | ACLineSegment | Line | 0.034884 | 0.0063593 | 0.0034381 | 18.2301 | FALSE | 2024-01-17 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_91900_21 | ACLineSegment | Line | 0.034884 | 0.0063593 | 0.0034381 | 18.2301 | FALSE | 2024-01-17 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_92680_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_92682_21 | ACLineSegment | Line | 0.034884 | 0.015141 | 0.009308 | 43.4051 | FALSE | 2024-01-20 21:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_92689_21 | ACLineSegment | Line | 0.034884 | 0.0058285 | 0.003246 | 16.7086 | FALSE | 2024-01-21 02:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_92694_21 | ACLineSegment | Line | 0.034884 | 0.0037253 | 0.0021054 | 10.6794 | FALSE | 2024-01-20 07:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_92695_21 | ACLineSegment | Line | 0.034884 | 0.0057709 | 0.00302 | 16.5434 | FALSE | 2024-01-20 21:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_92696_21 | ACLineSegment | Line | 0.034884 | 0.0032314 | 0.0015888 | 9.2634 | FALSE | 2024-07-15 05:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_92681_21 | ACLineSegment | Line | 0.034884 | 0.015141 | 0.009308 | 43.4051 | FALSE | 2024-01-20 21:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_92692_21 | ACLineSegment | Line | 0.034884 | 0.020932 | 0.013508 | 60.0051 | FALSE | 2024-01-20 18:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_92693_21 | ACLineSegment | Line | 0.034884 | 0.0086773 | 0.0046965 | 24.8752 | FALSE | 2024-01-17 17:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_92683_21 | ACLineSegment | Line | 0.034884 | 0.0072273 | 0.0040902 | 20.7183 | FALSE | 2024-01-21 01:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_92684_21 | ACLineSegment | Line | 0.034884 | 0.017222 | 0.010775 | 49.371 | FALSE | 2024-01-18 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_92685_21 | ACLineSegment | Line | 0.034884 | 0.0063473 | 0.0035443 | 18.1957 | FALSE | 2024-07-16 03:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_92686_21 | ACLineSegment | Line | 0.034884 | 0.0085874 | 0.0037688 | 24.6173 | FALSE | 2024-01-20 20:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_92687_21 | ACLineSegment | Line | 0.034884 | 0.0040545 | 0.0021229 | 11.6229 | FALSE | 2024-01-21 01:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_92688_21 | ACLineSegment | Line | 0.034884 | 0.0038177 | 0.0021754 | 10.9442 | FALSE | 2024-01-20 16:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_92691_21 | ACLineSegment | Line | 0.034884 | 0.017222 | 0.010775 | 49.371 | FALSE | 2024-01-18 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_92697_21 | ACLineSegment | Line | 0.034884 | 0.0040545 | 0.0021229 | 11.6229 | FALSE | 2024-01-21 01:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_92690_21 | ACLineSegment | Line | 0.034884 | 0.0058285 | 0.003246 | 16.7086 | FALSE | 2024-01-21 02:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_92844_21 | ACLineSegment | Line | 0.034884 | 0.0061757 | 0.0035436 | 17.7037 | FALSE | 2024-01-20 07:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_92916_21 | ACLineSegment | Line | 0.034884 | 0.0082627 | 0.0052629 | 23.6865 | FALSE | 2024-01-20 19:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_92925_21 | ACLineSegment | Line | 0.034884 | 0.00738 | 0.003429 | 21.156 | FALSE | 2024-01-20 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_92917_21 | ACLineSegment | Line | 0.034884 | 0.0054029 | 0.0033268 | 15.4884 | FALSE | 2024-01-20 19:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_92918_21 | ACLineSegment | Line | 0.034884 | 0.0040064 | 0.0020752 | 11.485 | FALSE | 2024-01-20 11:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_92927_21 | ACLineSegment | Line | 0.034884 | 0.0025837 | 0.0012836 | 7.4066 | FALSE | 2024-01-20 16:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_92935_21 | ACLineSegment | Line | 0.034884 | 0.0038611 | 0.0022006 | 11.0686 | FALSE | 2024-01-17 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_92919_21 | ACLineSegment | Line | 0.034884 | 0.0094509 | 0.0053048 | 27.0926 | FALSE | 2024-01-20 08:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_92920_21 | ACLineSegment | Line | 0.034884 | 0.015077 | 0.0089692 | 43.2216 | FALSE | 2024-01-21 04:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_92921_21 | ACLineSegment | Line | 0.034884 | 0.0066643 | 0.0039651 | 19.1043 | FALSE | 2024-01-20 21:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_92922_21 | ACLineSegment | Line | 0.034884 | 0.0033402 | 0.0021341 | 9.5753 | FALSE | 2024-01-18 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_92926_21 | ACLineSegment | Line | 0.034884 | 0.0072789 | 0.0034018 | 20.8662 | FALSE | 2024-01-21 04:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_92923_21 | ACLineSegment | Line | 0.034884 | 0.0033402 | 0.0021341 | 9.5753 | FALSE | 2024-01-18 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_92928_21 | ACLineSegment | Line | 0.034884 | 0.0025837 | 0.0012836 | 7.4066 | FALSE | 2024-01-20 16:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_93145_21 | ACLineSegment | Line | 0.034884 | 0.019891 | 0.011574 | 57.0213 | FALSE | 2024-01-20 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_93146_21 | ACLineSegment | Line | 0.034884 | 0.016515 | 0.0099105 | 47.3434 | FALSE | 2024-01-17 14:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_93147_21 | ACLineSegment | Line | 0.034884 | 0.037584 | 0.023968 | 107.7419 | TRUE | 2024-01-20 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_93148_21 | ACLineSegment | Line | 0.034884 | 0.0055036 | 0.0031196 | 15.777 | FALSE | 2024-01-20 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_93161_21 | ACLineSegment | Line | 0.034884 | 0.01266 | 0.0077676 | 36.2936 | FALSE | 2024-01-20 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_93171_21 | ACLineSegment | Line | 0.034884 | 0.0072306 | 0.004057 | 20.7277 | FALSE | 2024-01-20 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_93158_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_93164_21 | ACLineSegment | Line | 0.034884 | 0.005947 | 0.0033291 | 17.048 | FALSE | 2024-01-17 14:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_93172_21 | ACLineSegment | Line | 0.034884 | 0.0042723 | 0.0022701 | 12.2473 | FALSE | 2024-01-20 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_93173_21 | ACLineSegment | Line | 0.034884 | 0.0083035 | 0.0047479 | 23.8036 | FALSE | 2024-07-16 03:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_93155_21 | ACLineSegment | Line | 0.034884 | 0.025159 | 0.016057 | 72.124 | FALSE | 2024-01-21 02:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_93149_21 | ACLineSegment | Line | 0.034884 | 0.020729 | 0.012584 | 59.4242 | FALSE | 2024-01-21 02:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_93156_21 | ACLineSegment | Line | 0.034884 | 0.0058625 | 0.0036015 | 16.806 | FALSE | 2024-01-18 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_93150_21 | ACLineSegment | Line | 0.034884 | 0.015598 | 0.0098118 | 44.7141 | FALSE | 2024-01-21 02:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_93151_21 | ACLineSegment | Line | 0.034884 | 0.0053068 | 0.0030558 | 15.2128 | FALSE | 2024-01-17 16:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_93167_21 | ACLineSegment | Line | 0.034884 | 0.0069166 | 0.0041551 | 19.8277 | FALSE | 2024-01-21 04:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_93168_21 | ACLineSegment | Line | 0.046073 | 0 | 0 | 0 | FALSE | 2024-01-01 05:00 | 350 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_93169_21 | ACLineSegment | Line | 0.034884 | 0.0060301 | 0.0027008 | 17.2864 | FALSE | 2024-01-20 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_93170_21 | ACLineSegment | Line | 0.034884 | 0.0065386 | 0.0033596 | 18.744 | FALSE | 2024-01-20 23:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_93152_21 | ACLineSegment | Line | 0.034884 | 0.0069166 | 0.0041551 | 19.8277 | FALSE | 2024-01-21 04:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_93153_21 | ACLineSegment | Line | 0.034884 | 0.0053832 | 0.0026339 | 15.4318 | FALSE | 2024-01-21 04:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_93154_21 | ACLineSegment | Line | 0.034884 | 0.0028943 | 0.0016936 | 8.2971 | FALSE | 2024-01-20 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_93159_21 | ACLineSegment | Line | 0.034884 | 0.0048449 | 0.0026328 | 13.8889 | FALSE | 2024-01-20 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_93162_21 | ACLineSegment | Line | 0.034884 | 0.0060843 | 0.0032981 | 17.4418 | FALSE | 2024-01-21 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_93163_21 | ACLineSegment | Line | 0.034884 | 0.0039382 | 0.0022268 | 11.2895 | FALSE | 2024-07-15 18:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_93160_21 | ACLineSegment | Line | 0.034884 | 0.0048449 | 0.0026328 | 13.8889 | FALSE | 2024-01-20 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_93166_21 | ACLineSegment | Line | 0.034884 | 0.0048449 | 0.0026328 | 13.8889 | FALSE | 2024-01-20 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_93165_21 | ACLineSegment | Line | 0.034884 | 0.005947 | 0.0033291 | 17.048 | FALSE | 2024-01-17 14:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_93250_21 | ACLineSegment | Line | 0.034884 | 0.0030887 | 0.0017804 | 8.8543 | FALSE | 2024-01-20 12:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_93251_21 | ACLineSegment | Line | 0.034884 | 0.0060565 | 0.0037594 | 17.3621 | FALSE | 2024-01-20 12:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_93252_21 | ACLineSegment | Line | 0.034884 | 0.0037354 | 0.0021423 | 10.7083 | FALSE | 2024-07-15 12:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_93257_21 | ACLineSegment | Line | 0.034884 | 0.0030887 | 0.0017804 | 8.8543 | FALSE | 2024-01-20 12:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_93262_21 | ACLineSegment | Line | 0.034884 | 0.0041961 | 0.0021082 | 12.029 | FALSE | 2024-01-18 04:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_93253_21 | ACLineSegment | Line | 0.034884 | 0.0062452 | 0.0033655 | 17.903 | FALSE | 2024-01-20 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_93255_21 | ACLineSegment | Line | 0.034884 | 0.0080645 | 0.0043208 | 23.1184 | FALSE | 2024-01-20 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_93256_21 | ACLineSegment | Line | 0.034884 | 0.0022041 | 0.0011847 | 6.3185 | FALSE | 2024-01-20 23:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_93254_21 | ACLineSegment | Line | 0.034884 | 0.0062452 | 0.0033655 | 17.903 | FALSE | 2024-01-20 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_93259_21 | ACLineSegment | Line | 0.034884 | 0.0055755 | 0.0031796 | 15.9832 | FALSE | 2024-01-20 17:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_93304_21 | ACLineSegment | Line | 0.034884 | 0.0073682 | 0.0035898 | 21.1224 | FALSE | 2024-01-20 14:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_93305_21 | ACLineSegment | Line | 0.034884 | 0.0073682 | 0.0035898 | 21.1224 | FALSE | 2024-01-20 14:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_93815_21 | ACLineSegment | Line | 0.034884 | 0.0042229 | 0.002254 | 12.1059 | FALSE | 2024-01-20 19:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_93818_21 | ACLineSegment | Line | 0.034884 | 0.0064079 | 0.0036282 | 18.3694 | FALSE | 2024-01-20 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_93816_21 | ACLineSegment | Line | 0.034884 | 0.0042229 | 0.002254 | 12.1059 | FALSE | 2024-01-20 19:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_93819_21 | ACLineSegment | Line | 0.034884 | 0.0064079 | 0.0036282 | 18.3694 | FALSE | 2024-01-20 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_94099_21 | ACLineSegment | Line | 0.034884 | 0.0024523 | 0.0014109 | 7.03 | FALSE | 2024-01-20 21:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_94100_21 | ACLineSegment | Line | 0.034884 | 0.0024523 | 0.0014109 | 7.03 | FALSE | 2024-01-20 21:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_94246_21 | ACLineSegment | Line | 0.034884 | 0.0039565 | 0.0021233 | 11.3419 | FALSE | 2024-01-20 11:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_94250_21 | ACLineSegment | Line | 0.034884 | 0.0028161 | 0.0017585 | 8.0729 | FALSE | 2024-07-14 14:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_94247_21 | ACLineSegment | Line | 0.034884 | 0.0039565 | 0.0021233 | 11.3419 | FALSE | 2024-01-20 11:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_94251_21 | ACLineSegment | Line | 0.034884 | 0.0028161 | 0.0017585 | 8.0729 | FALSE | 2024-07-14 14:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_94633_21 | ACLineSegment | Line | 0.034884 | 0.0076216 | 0.0039692 | 21.8487 | FALSE | 2024-01-20 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_94636_21 | ACLineSegment | Line | 0.034884 | 0.0034229 | 0.0018063 | 9.8123 | FALSE | 2024-01-20 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_94637_21 | ACLineSegment | Line | 0.034884 | 0.0041987 | 0.0022645 | 12.0364 | FALSE | 2024-01-20 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_94638_21 | ACLineSegment | Line | 0.034884 | 0.0034229 | 0.0018063 | 9.8123 | FALSE | 2024-01-20 10:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_94645_21 | ACLineSegment | Line | 0.034884 | 0.0070665 | 0.0039619 | 20.2574 | FALSE | 2024-01-21 04:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_94646_21 | ACLineSegment | Line | 0.034884 | 0.0070665 | 0.0039619 | 20.2574 | FALSE | 2024-01-21 04:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_94648_21 | ACLineSegment | Line | 0.034884 | 0.003132 | 0.0019067 | 8.9783 | FALSE | 2024-07-15 13:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_94885_21 | ACLineSegment | Line | 0.034884 | 0.010209 | 0.0060568 | 29.2651 | FALSE | 2024-07-05 07:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_94886_21 | ACLineSegment | Line | 0.034884 | 0.0044519 | 0.0026442 | 12.7623 | FALSE | 2024-07-05 07:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_94887_21 | ACLineSegment | Line | 0.034884 | 0.0057567 | 0.0036578 | 16.5028 | FALSE | 2024-07-05 07:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_94891_21 | ACLineSegment | Line | 0.034884 | 0.0044519 | 0.0026442 | 12.7623 | FALSE | 2024-07-05 07:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_94890_21 | ACLineSegment | Line | 0.034884 | 0.0026897 | 0.0015787 | 7.7104 | FALSE | 2024-01-20 15:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_95211_21 | ACLineSegment | Line | 0.034884 | 0.0067958 | 0.0041238 | 19.4816 | FALSE | 2024-07-15 07:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_95212_21 | ACLineSegment | Line | 0.034884 | 0.0032688 | 0.0018953 | 9.3705 | FALSE | 2024-01-20 05:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_95215_21 | ACLineSegment | Line | 0.034884 | 0.0043312 | 0.0024351 | 12.4162 | FALSE | 2024-01-20 18:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_95213_21 | ACLineSegment | Line | 0.034884 | 0.0032688 | 0.0018953 | 9.3705 | FALSE | 2024-01-20 05:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_95935_21 | ACLineSegment | Line | 0.034884 | 0.010928 | 0.0066673 | 31.3267 | FALSE | 2024-01-18 01:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_95936_21 | ACLineSegment | Line | 0.034884 | 0.010928 | 0.0066673 | 31.3267 | FALSE | 2024-01-18 01:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_95941_21 | ACLineSegment | Line | 0.034884 | 0.0060782 | 0.0037348 | 17.4242 | FALSE | 2024-01-21 19:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_95942_21 | ACLineSegment | Line | 0.034884 | 0.0059094 | 0.003298 | 16.9404 | FALSE | 2024-01-20 15:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_95937_21 | ACLineSegment | Line | 0.034884 | 0.004145 | 0.0022522 | 11.8824 | FALSE | 2024-01-20 08:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_95940_21 | ACLineSegment | Line | 0.034884 | 0.0057707 | 0.0031858 | 16.5427 | FALSE | 2024-01-20 13:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_95938_21 | ACLineSegment | Line | 0.034884 | 0.004145 | 0.0022522 | 11.8824 | FALSE | 2024-01-20 08:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_95943_21 | ACLineSegment | Line | 0.034884 | 0.0060782 | 0.0037348 | 17.4242 | FALSE | 2024-01-21 19:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_96379_21 | ACLineSegment | Line | 0.034884 | 0.005134 | 0.0025172 | 14.7176 | FALSE | 2024-01-20 09:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_96700_21 | ACLineSegment | Line | 0.034884 | 0.0061632 | 0.0034156 | 17.668 | FALSE | 2024-01-17 17:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_96702_21 | ACLineSegment | Line | 0.034884 | 0.0056516 | 0.0030395 | 16.2013 | FALSE | 2024-01-21 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_96701_21 | ACLineSegment | Line | 0.034884 | 0.0061632 | 0.0034156 | 17.668 | FALSE | 2024-01-17 17:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_96703_21 | ACLineSegment | Line | 0.034884 | 0.0056516 | 0.0030395 | 16.2013 | FALSE | 2024-01-21 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_18 | line_96864_21 | ACLineSegment | Line | 0.034884 | 0.0049312 | 0.0025997 | 14.1362 | FALSE | 2024-01-17 19:00 | 265 | 0.24 |  | 1 | 1Phase_VLN_I_from_VLL
GSO_127 | line_6871_22 | ACLineSegment | Line | 13.5424 | 0.02104 | 0.016376 | 0.15536 | FALSE | 2024-01-22 04:00 | 660 | 12.47 |  | 3 | 3Phase_sqrt3_VLL_I

## Meter_Mapping
MeterID | LoadNode | MappingMethod | Resolved | Depth | GridID
m_1106_22 | UCLV3658 | DirectTerminal | TRUE | 4 | GSO_122
m_1367_22 | UCLV41356 | DirectTerminal | TRUE | 5 | GSO_122
m_2721_22 | UCMV107 | DirectTerminal | TRUE | 4 | GSO_122
m_1116_22 | UCLV3664 | DirectTerminal | TRUE | 8 | GSO_124
m_1211_22 | UCLV38205 | DirectTerminal | TRUE | 8 | GSO_124
m_1381_22 | UCLV41634 | DirectTerminal | TRUE | 10 | GSO_124
m_1526_22 | UCLV45022 | DirectTerminal | TRUE | 10 | GSO_124
m_2747_22 | UCMV3 | DirectTerminal | TRUE | 5 | GSO_124
m_2752_22 | UCMV4 | DirectTerminal | TRUE | 7 | GSO_124
m_366_22 | UCLV15395 | DirectTerminal | TRUE | 7 | GSO_124
m_398_22 | UCLV16891 | DirectTerminal | TRUE | 8 | GSO_124
m_402_22 | UCLV17000 | DirectTerminal | TRUE | 7 | GSO_124
m_424_22 | UCLV18505 | DirectTerminal | TRUE | 5 | GSO_124
m_601_22 | UCLV22029 | DirectTerminal | TRUE | 9 | GSO_124
m_604_22 | UCLV22140 | DirectTerminal | TRUE | 6 | GSO_124
m_665_22 | UCLV25683 | DirectTerminal | TRUE | 4 | GSO_124
m_703_22 | UCLV27473 | DirectTerminal | TRUE | 6 | GSO_124
m_750_22 | UCLV28844 | DirectTerminal | TRUE | 10 | GSO_124
m_876_22 | UCLV31459 | DirectTerminal | TRUE | 11 | GSO_124
m_1012_22 | UCLV34590 | DirectTerminal | TRUE | 33 | GSO_123
m_1015_22 | UCLV34767 | DirectTerminal | TRUE | 16 | GSO_123
m_1084_22 | UCLV36123 | DirectTerminal | TRUE | 29 | GSO_123
m_1208_22 | UCLV38132 | DirectTerminal | TRUE | 30 | GSO_123
m_1267_22 | UCLV39302 | DirectTerminal | TRUE | 11 | GSO_123
m_1277_22 | UCLV39521 | DirectTerminal | TRUE | 30 | GSO_123
m_1356_22 | UCLV41172 | DirectTerminal | TRUE | 6 | GSO_123
m_1426_22 | UCLV42881 | DirectTerminal | TRUE | 13 | GSO_123
m_1480_22 | UCLV43729 | DirectTerminal | TRUE | 18 | GSO_123
m_15_22 | UCLV10014 | DirectTerminal | TRUE | 19 | GSO_123
m_1522_22 | UCLV44974 | DirectTerminal | TRUE | 10 | GSO_123
m_1546_22 | UCLV45381 | DirectTerminal | TRUE | 7 | GSO_123
m_1607_22 | UCLV46893 | DirectTerminal | TRUE | 8 | GSO_123
m_1617_22 | UCLV47101 | DirectTerminal | TRUE | 15 | GSO_123
m_1656_22 | UCLV48193 | DirectTerminal | TRUE | 17 | GSO_123
m_17_22 | UCLV10016 | DirectTerminal | TRUE | 32 | GSO_123
m_1740_22 | UCLV50250 | DirectTerminal | TRUE | 8 | GSO_123
m_1794_22 | UCLV51732 | DirectTerminal | TRUE | 5 | GSO_123
m_2_22 | UCLV10001 | DirectTerminal | TRUE | 5 | GSO_123
m_2746_22 | UCMV29 | DirectTerminal | TRUE | 32 | GSO_123
m_2756_22 | UCMV44 | DirectTerminal | TRUE | 18 | GSO_123
m_3_22 | UCLV10002 | DirectTerminal | TRUE | 20 | GSO_123
m_333_22 | UCLV14278 | DirectTerminal | TRUE | 25 | GSO_123
m_352_22 | UCLV14935 | DirectTerminal | TRUE | 22 | GSO_123
m_356_22 | UCLV15061 | DirectTerminal | TRUE | 14 | GSO_123
m_378_22 | UCLV16140 | DirectTerminal | TRUE | 13 | GSO_123
m_387_22 | UCLV16433 | DirectTerminal | TRUE | 25 | GSO_123
m_400_22 | UCLV16952 | DirectTerminal | TRUE | 30 | GSO_123
m_413_22 | UCLV17927 | DirectTerminal | TRUE | 28 | GSO_123
m_490_22 | UCLV19534 | DirectTerminal | TRUE | 24 | GSO_123
m_492_22 | UCLV19668 | DirectTerminal | TRUE | 18 | GSO_123
m_513_22 | UCLV20406 | DirectTerminal | TRUE | 34 | GSO_123
m_591_22 | UCLV21679 | DirectTerminal | TRUE | 21 | GSO_123
m_607_22 | UCLV22235 | DirectTerminal | TRUE | 22 | GSO_123
m_613_22 | UCLV23074 | DirectTerminal | TRUE | 27 | GSO_123
m_617_22 | UCLV23193 | DirectTerminal | TRUE | 26 | GSO_123
m_651_22 | UCLV25207 | DirectTerminal | TRUE | 24 | GSO_123
m_680_22 | UCLV26611 | DirectTerminal | TRUE | 23 | GSO_123
m_687_22 | UCLV26786 | DirectTerminal | TRUE | 31 | GSO_123
m_698_22 | UCLV27349 | DirectTerminal | TRUE | 33 | GSO_123
m_777_22 | UCLV29355 | DirectTerminal | TRUE | 32 | GSO_123
m_786_22 | UCLV29520 | DirectTerminal | TRUE | 19 | GSO_123
m_845_22 | UCLV30689 | DirectTerminal | TRUE | 9 | GSO_123
m_855_22 | UCLV30966 | DirectTerminal | TRUE | 30 | GSO_123
m_862_22 | UCLV31179 | DirectTerminal | TRUE | 4 | GSO_123
m_933_22 | UCLV33018 | DirectTerminal | TRUE | 28 | GSO_123
m_941_22 | UCLV33278 | DirectTerminal | TRUE | 18 | GSO_123
m_1021_22 | UCLV34991 | DirectTerminal | TRUE | 16 | GSO_121
m_1040_22 | UCLV35370 | DirectTerminal | TRUE | 10 | GSO_121
m_1064_22 | UCLV35751 | DirectTerminal | TRUE | 8 | GSO_121
m_1075_22 | UCLV35980 | DirectTerminal | TRUE | 21 | GSO_121
m_1096_22 | UCLV36504 | DirectTerminal | TRUE | 14 | GSO_121
m_1103_22 | UCLV3657 | DirectTerminal | TRUE | 4 | GSO_121
m_1107_22 | UCLV3659 | DirectTerminal | TRUE | 25 | GSO_121
m_1108_22 | UCLV3660 | DirectTerminal | TRUE | 10 | GSO_121
m_1110_22 | UCLV3661 | DirectTerminal | TRUE | 10 | GSO_121
m_1111_22 | UCLV3662 | DirectTerminal | TRUE | 14 | GSO_121
m_1114_22 | UCLV3663 | DirectTerminal | TRUE | 18 | GSO_121
m_1118_22 | UCLV3665 | DirectTerminal | TRUE | 22 | GSO_121
m_1119_22 | UCLV3666 | DirectTerminal | TRUE | 22 | GSO_121
m_1120_22 | UCLV3667 | DirectTerminal | TRUE | 25 | GSO_121
m_1121_22 | UCLV3668 | DirectTerminal | TRUE | 22 | GSO_121
m_1122_22 | UCLV3669 | DirectTerminal | TRUE | 23 | GSO_121
m_1170_22 | UCLV37219 | DirectTerminal | TRUE | 39 | GSO_121
m_1174_22 | UCLV37292 | DirectTerminal | TRUE | 16 | GSO_121
m_1195_22 | UCLV37615 | DirectTerminal | TRUE | 5 | GSO_121
m_1199_22 | UCLV37686 | DirectTerminal | TRUE | 12 | GSO_121
m_1215_22 | UCLV38319 | DirectTerminal | TRUE | 30 | GSO_121
m_1_22 | UCLV10000 | DirectTerminal | TRUE | 10 | GSO_121
m_1234_22 | UCLV38703 | DirectTerminal | TRUE | 10 | GSO_121
m_1256_22 | UCLV39080 | DirectTerminal | TRUE | 8 | GSO_121
m_1258_22 | UCLV39144 | DirectTerminal | TRUE | 13 | GSO_121
m_1297_22 | UCLV39995 | DirectTerminal | TRUE | 13 | GSO_121
m_1317_22 | UCLV40371 | DirectTerminal | TRUE | 27 | GSO_121
m_1335_22 | UCLV40839 | DirectTerminal | TRUE | 18 | GSO_121
m_1347_22 | UCLV41019 | DirectTerminal | TRUE | 23 | GSO_121
m_1449_22 | UCLV43242 | DirectTerminal | TRUE | 38 | GSO_121
m_1464_22 | UCLV43504 | DirectTerminal | TRUE | 20 | GSO_121
m_1466_22 | UCLV43514 | DirectTerminal | TRUE | 12 | GSO_121
m_1544_22 | UCLV45368 | DirectTerminal | TRUE | 27 | GSO_121
m_1582_22 | UCLV46490 | DirectTerminal | TRUE | 27 | GSO_121
m_1590_22 | UCLV46632 | DirectTerminal | TRUE | 35 | GSO_121
m_1605_22 | UCLV46875 | DirectTerminal | TRUE | 25 | GSO_121
m_1652_22 | UCLV48119 | DirectTerminal | TRUE | 29 | GSO_121
m_1665_22 | UCLV48349 | DirectTerminal | TRUE | 16 | GSO_121
m_1686_22 | UCLV48743 | DirectTerminal | TRUE | 26 | GSO_121
m_1715_22 | UCLV49838 | DirectTerminal | TRUE | 17 | GSO_121
m_1724_22 | UCLV49986 | DirectTerminal | TRUE | 33 | GSO_121
m_1731_22 | UCLV50132 | DirectTerminal | TRUE | 25 | GSO_121
m_1738_22 | UCLV50231 | DirectTerminal | TRUE | 27 | GSO_121
m_1784_22 | UCLV51585 | DirectTerminal | TRUE | 15 | GSO_121
m_1813_22 | UCLV52061 | DirectTerminal | TRUE | 20 | GSO_121
m_1818_22 | UCLV52142 | DirectTerminal | TRUE | 29 | GSO_121
m_1820_22 | UCLV52158 | DirectTerminal | TRUE | 15 | GSO_121
m_1867_22 | UCLV53393 | DirectTerminal | TRUE | 27 | GSO_121
m_1869_22 | UCLV53413 | DirectTerminal | TRUE | 25 | GSO_121
m_1881_22 | UCLV53727 | DirectTerminal | TRUE | 20 | GSO_121
m_2785_22 | UCMV81 | DirectTerminal | TRUE | 9 | GSO_121
m_2793_22 | UCMV95 | DirectTerminal | TRUE | 5 | GSO_121
m_708_22 | UCLV27653 | DirectTerminal | TRUE | 18 | GSO_121
m_716_22 | UCLV27775 | DirectTerminal | TRUE | 29 | GSO_121
m_719_22 | UCLV27999 | DirectTerminal | TRUE | 24 | GSO_121
m_727_22 | UCLV28153 | DirectTerminal | TRUE | 11 | GSO_121
m_730_22 | UCLV28224 | DirectTerminal | TRUE | 11 | GSO_121
m_761_22 | UCLV28962 | DirectTerminal | TRUE | 10 | GSO_121
m_766_22 | UCLV29029 | DirectTerminal | TRUE | 15 | GSO_121
m_794_22 | UCLV29668 | DirectTerminal | TRUE | 31 | GSO_121
m_798_22 | UCLV29740 | DirectTerminal | TRUE | 17 | GSO_121
m_805_22 | UCLV29897 | DirectTerminal | TRUE | 23 | GSO_121
m_815_22 | UCLV30065 | DirectTerminal | TRUE | 27 | GSO_121
m_832_22 | UCLV30508 | DirectTerminal | TRUE | 13 | GSO_121
m_860_22 | UCLV31162 | DirectTerminal | TRUE | 30 | GSO_121
m_865_22 | UCLV31246 | DirectTerminal | TRUE | 15 | GSO_121
m_878_22 | UCLV31546 | DirectTerminal | TRUE | 9 | GSO_121
m_894_22 | UCLV32007 | DirectTerminal | TRUE | 13 | GSO_121
m_912_22 | UCLV32424 | DirectTerminal | TRUE | 12 | GSO_121
m_971_22 | UCLV33842 | DirectTerminal | TRUE | 39 | GSO_121
m_973_22 | UCLV33864 | DirectTerminal | TRUE | 12 | GSO_121
m_998_22 | UCLV34244 | DirectTerminal | TRUE | 6 | GSO_121
m_2321_22 | UCLV7876 | DirectTerminal | TRUE | 10 | GSO_144
m_2324_22 | UCLV7879 | DirectTerminal | TRUE | 11 | GSO_144
m_2333_22 | UCLV7888 | DirectTerminal | TRUE | 4 | GSO_144
m_2334_22 | UCLV7889 | DirectTerminal | TRUE | 4 | GSO_144
m_2335_22 | UCLV7890 | DirectTerminal | TRUE | 4 | GSO_144
m_2336_22 | UCLV7891 | DirectTerminal | TRUE | 6 | GSO_144
m_2337_22 | UCLV7892 | DirectTerminal | TRUE | 8 | GSO_144
m_2338_22 | UCLV7893 | DirectTerminal | TRUE | 6 | GSO_144
m_2340_22 | UCLV7895 | DirectTerminal | TRUE | 9 | GSO_144
m_2341_22 | UCLV7896 | DirectTerminal | TRUE | 8 | GSO_144
m_2342_22 | UCLV7898 | DirectTerminal | TRUE | 8 | GSO_144
m_2343_22 | UCLV7899 | DirectTerminal | TRUE | 9 | GSO_144
m_2344_22 | UCLV7901 | DirectTerminal | TRUE | 8 | GSO_144
m_2345_22 | UCLV7902 | DirectTerminal | TRUE | 9 | GSO_144
m_2346_22 | UCLV7904 | DirectTerminal | TRUE | 10 | GSO_144
m_2347_22 | UCLV7905 | DirectTerminal | TRUE | 10 | GSO_144
m_2348_22 | UCLV7906 | DirectTerminal | TRUE | 8 | GSO_144
m_2349_22 | UCLV7907 | DirectTerminal | TRUE | 8 | GSO_144
m_2350_22 | UCLV7908 | DirectTerminal | TRUE | 14 | GSO_144
m_2351_22 | UCLV7909 | DirectTerminal | TRUE | 10 | GSO_144
m_2352_22 | UCLV7910 | DirectTerminal | TRUE | 10 | GSO_144
m_2353_22 | UCLV7912 | DirectTerminal | TRUE | 12 | GSO_144
m_2354_22 | UCLV7913 | DirectTerminal | TRUE | 12 | GSO_144
m_2355_22 | UCLV7914 | DirectTerminal | TRUE | 12 | GSO_144
m_2356_22 | UCLV7916 | DirectTerminal | TRUE | 14 | GSO_144
m_2357_22 | UCLV7917 | DirectTerminal | TRUE | 14 | GSO_144
m_2358_22 | UCLV7918 | DirectTerminal | TRUE | 14 | GSO_144
m_2359_22 | UCLV7919 | DirectTerminal | TRUE | 14 | GSO_144
m_2360_22 | UCLV7920 | DirectTerminal | TRUE | 14 | GSO_144
m_2361_22 | UCLV7921 | DirectTerminal | TRUE | 12 | GSO_144
m_2362_22 | UCLV7922 | DirectTerminal | TRUE | 14 | GSO_144
m_2363_22 | UCLV7923 | DirectTerminal | TRUE | 10 | GSO_144
m_1030_22 | UCLV35176 | DirectTerminal | TRUE | 40 | GSO_141
m_1065_22 | UCLV35764 | DirectTerminal | TRUE | 6 | GSO_141
m_1172_22 | UCLV37231 | DirectTerminal | TRUE | 10 | GSO_141
m_1188_22 | UCLV37468 | DirectTerminal | TRUE | 32 | GSO_141
m_1226_22 | UCLV38560 | DirectTerminal | TRUE | 46 | GSO_141
m_1247_22 | UCLV38938 | DirectTerminal | TRUE | 38 | GSO_141
m_1325_22 | UCLV40616 | DirectTerminal | TRUE | 40 | GSO_141
m_1407_22 | UCLV42234 | DirectTerminal | TRUE | 21 | GSO_141
m_1410_22 | UCLV42348 | DirectTerminal | TRUE | 7 | GSO_141
m_1429_22 | UCLV42899 | DirectTerminal | TRUE | 52 | GSO_141
m_1552_22 | UCLV45525 | DirectTerminal | TRUE | 15 | GSO_141
m_1596_22 | UCLV46722 | DirectTerminal | TRUE | 51 | GSO_141
m_1609_22 | UCLV46905 | DirectTerminal | TRUE | 32 | GSO_141
m_1624_22 | UCLV47256 | DirectTerminal | TRUE | 22 | GSO_141
m_1681_22 | UCLV48620 | DirectTerminal | TRUE | 48 | GSO_141
m_1705_22 | UCLV49486 | DirectTerminal | TRUE | 4 | GSO_141
m_1757_22 | UCLV50662 | DirectTerminal | TRUE | 28 | GSO_141
m_1766_22 | UCLV50980 | DirectTerminal | TRUE | 22 | GSO_141
m_1810_22 | UCLV52000 | DirectTerminal | TRUE | 48 | GSO_141
m_1831_22 | UCLV52337 | DirectTerminal | TRUE | 16 | GSO_141
m_1843_22 | UCLV52800 | DirectTerminal | TRUE | 19 | GSO_141
m_1859_22 | UCLV53264 | DirectTerminal | TRUE | 52 | GSO_141
m_1879_22 | UCLV53673 | DirectTerminal | TRUE | 46 | GSO_141
m_1890_22 | UCLV53872 | DirectTerminal | TRUE | 24 | GSO_141
m_1901_22 | UCLV54181 | DirectTerminal | TRUE | 12 | GSO_141
m_1949_22 | UCLV55799 | DirectTerminal | TRUE | 26 | GSO_141
m_1977_22 | UCLV56776 | DirectTerminal | TRUE | 28 | GSO_141
m_2025_22 | UCLV58897 | DirectTerminal | TRUE | 30 | GSO_141
m_2033_22 | UCLV59245 | DirectTerminal | TRUE | 17 | GSO_141
m_2059_22 | UCLV60252 | DirectTerminal | TRUE | 26 | GSO_141
m_2070_22 | UCLV60571 | DirectTerminal | TRUE | 27 | GSO_141
m_2096_22 | UCLV61808 | DirectTerminal | TRUE | 18 | GSO_141
m_2124_22 | UCLV63121 | DirectTerminal | TRUE | 29 | GSO_141
m_2149_22 | UCLV6874 | DirectTerminal | TRUE | 28 | GSO_141
m_2150_22 | UCLV6875 | DirectTerminal | TRUE | 28 | GSO_141
m_2151_22 | UCLV6876 | DirectTerminal | TRUE | 27 | GSO_141
m_2152_22 | UCLV6877 | DirectTerminal | TRUE | 27 | GSO_141
m_2153_22 | UCLV6878 | DirectTerminal | TRUE | 27 | GSO_141
m_2154_22 | UCLV6879 | DirectTerminal | TRUE | 27 | GSO_141
m_2155_22 | UCLV6880 | DirectTerminal | TRUE | 25 | GSO_141
m_2156_22 | UCLV6881 | DirectTerminal | TRUE | 25 | GSO_141
m_2157_22 | UCLV6882 | DirectTerminal | TRUE | 23 | GSO_141
m_2158_22 | UCLV6884 | DirectTerminal | TRUE | 21 | GSO_141
m_2159_22 | UCLV6885 | DirectTerminal | TRUE | 23 | GSO_141
m_2160_22 | UCLV6886 | DirectTerminal | TRUE | 23 | GSO_141
m_2161_22 | UCLV6889 | DirectTerminal | TRUE | 23 | GSO_141
m_2162_22 | UCLV6890 | DirectTerminal | TRUE | 26 | GSO_141
m_2163_22 | UCLV6891 | DirectTerminal | TRUE | 24 | GSO_141
m_2164_22 | UCLV6892 | DirectTerminal | TRUE | 26 | GSO_141
m_2165_22 | UCLV6893 | DirectTerminal | TRUE | 26 | GSO_141
m_2166_22 | UCLV6894 | DirectTerminal | TRUE | 27 | GSO_141
m_2167_22 | UCLV6895 | DirectTerminal | TRUE | 27 | GSO_141
m_2385_22 | UCLV8160 | DirectTerminal | TRUE | 28 | GSO_141
m_2386_22 | UCLV8161 | DirectTerminal | TRUE | 20 | GSO_141
m_2389_22 | UCLV8164 | DirectTerminal | TRUE | 50 | GSO_141
m_2390_22 | UCLV8165 | DirectTerminal | TRUE | 52 | GSO_141
m_2734_22 | UCMV128 | DirectTerminal | TRUE | 5 | GSO_141
m_2781_22 | UCMV77 | DirectTerminal | TRUE | 11 | GSO_141
m_2786_22 | UCMV84 | DirectTerminal | TRUE | 6 | GSO_141
m_2791_22 | UCMV93 | DirectTerminal | TRUE | 8 | GSO_141
m_2794_22 | UCMV96 | DirectTerminal | TRUE | 3 | GSO_141
m_738_22 | UCLV28401 | DirectTerminal | TRUE | 36 | GSO_141
m_808_22 | UCLV29912 | DirectTerminal | TRUE | 44 | GSO_141
m_826_22 | UCLV30309 | DirectTerminal | TRUE | 34 | GSO_141
m_880_22 | UCLV31560 | DirectTerminal | TRUE | 30 | GSO_141
m_886_22 | UCLV31806 | DirectTerminal | TRUE | 38 | GSO_141
m_944_22 | UCLV33291 | DirectTerminal | TRUE | 42 | GSO_141
m_962_22 | UCLV33648 | DirectTerminal | TRUE | 28 | GSO_141
m_1025_22 | UCLV35123 | DirectTerminal | TRUE | 44 | GSO_145
m_1027_22 | UCLV35140 | DirectTerminal | TRUE | 51 | GSO_145
m_1034_22 | UCLV35294 | DirectTerminal | TRUE | 8 | GSO_145
m_1039_22 | UCLV35360 | DirectTerminal | TRUE | 36 | GSO_145
m_1043_22 | UCLV35432 | DirectTerminal | TRUE | 11 | GSO_145
m_1050_22 | UCLV35498 | DirectTerminal | TRUE | 50 | GSO_145
m_1052_22 | UCLV35513 | DirectTerminal | TRUE | 50 | GSO_145
m_1063_22 | UCLV35740 | DirectTerminal | TRUE | 45 | GSO_145
m_1066_22 | UCLV35835 | DirectTerminal | TRUE | 7 | GSO_145
m_1071_22 | UCLV35903 | DirectTerminal | TRUE | 9 | GSO_145
m_1102_22 | S_nSSEE4_12.47 | RootFallback | FALSE | 0 | GSO_145
m_1113_22 | UCLV36627 | DirectTerminal | TRUE | 16 | GSO_145
m_1162_22 | UCLV36999 | DirectTerminal | TRUE | 16 | GSO_145
m_1165_22 | UCLV37149 | DirectTerminal | TRUE | 9 | GSO_145
m_1169_22 | UCLV37208 | DirectTerminal | TRUE | 40 | GSO_145
m_1173_22 | UCLV37284 | DirectTerminal | TRUE | 52 | GSO_145
m_1175_22 | UCLV37306 | DirectTerminal | TRUE | 10 | GSO_145
m_1182_22 | UCLV37378 | DirectTerminal | TRUE | 44 | GSO_145
m_1183_22 | UCLV37392 | DirectTerminal | TRUE | 49 | GSO_145
m_1190_22 | UCLV37536 | DirectTerminal | TRUE | 8 | GSO_145
m_1221_22 | UCLV38475 | DirectTerminal | TRUE | 52 | GSO_145
m_1233_22 | UCLV38694 | DirectTerminal | TRUE | 30 | GSO_145
m_1241_22 | UCLV38847 | DirectTerminal | TRUE | 18 | GSO_145
m_1255_22 | UCLV39070 | DirectTerminal | TRUE | 33 | GSO_145
m_1261_22 | UCLV39218 | DirectTerminal | TRUE | 11 | GSO_145
m_1263_22 | UCLV39236 | DirectTerminal | TRUE | 50 | GSO_145
m_1287_22 | UCLV39769 | DirectTerminal | TRUE | 20 | GSO_145
m_1293_22 | UCLV39921 | DirectTerminal | TRUE | 8 | GSO_145
m_1299_22 | UCLV40054 | DirectTerminal | TRUE | 47 | GSO_145
m_1306_22 | UCLV40125 | DirectTerminal | TRUE | 44 | GSO_145
m_1311_22 | UCLV40292 | DirectTerminal | TRUE | 7 | GSO_145
m_1316_22 | UCLV40360 | DirectTerminal | TRUE | 28 | GSO_145
m_1319_22 | UCLV40432 | DirectTerminal | TRUE | 50 | GSO_145
m_1327_22 | UCLV40679 | DirectTerminal | TRUE | 40 | GSO_145
m_1332_22 | UCLV40761 | DirectTerminal | TRUE | 26 | GSO_145
m_1341_22 | UCLV40938 | DirectTerminal | TRUE | 18 | GSO_145
m_1352_22 | UCLV41088 | DirectTerminal | TRUE | 37 | GSO_145
m_1361_22 | UCLV41246 | DirectTerminal | TRUE | 34 | GSO_145
m_1363_22 | UCLV41296 | DirectTerminal | TRUE | 8 | GSO_145
m_1374_22 | UCLV41529 | DirectTerminal | TRUE | 8 | GSO_145
m_1376_22 | UCLV41541 | DirectTerminal | TRUE | 48 | GSO_145
m_1380_22 | UCLV41625 | DirectTerminal | TRUE | 47 | GSO_145
m_1388_22 | UCLV41767 | DirectTerminal | TRUE | 18 | GSO_145
m_1439_22 | UCLV43026 | DirectTerminal | TRUE | 52 | GSO_145
m_1441_22 | UCLV43098 | DirectTerminal | TRUE | 45 | GSO_145
m_1442_22 | UCLV43107 | DirectTerminal | TRUE | 31 | GSO_145
m_1448_22 | UCLV43231 | DirectTerminal | TRUE | 25 | GSO_145
m_1455_22 | UCLV43348 | DirectTerminal | TRUE | 47 | GSO_145
m_1460_22 | UCLV43425 | DirectTerminal | TRUE | 8 | GSO_145
m_1476_22 | UCLV43647 | DirectTerminal | TRUE | 49 | GSO_145
m_1504_22 | UCLV44609 | DirectTerminal | TRUE | 46 | GSO_145
m_1506_22 | UCLV44622 | DirectTerminal | TRUE | 49 | GSO_145
m_1525_22 | UCLV45013 | DirectTerminal | TRUE | 47 | GSO_145
m_1540_22 | UCLV45302 | DirectTerminal | TRUE | 12 | GSO_145
m_1548_22 | UCLV45439 | DirectTerminal | TRUE | 48 | GSO_145
m_1579_22 | UCLV46426 | DirectTerminal | TRUE | 49 | GSO_145
m_1589_22 | UCLV46622 | DirectTerminal | TRUE | 20 | GSO_145
m_1597_22 | UCLV46749 | DirectTerminal | TRUE | 42 | GSO_145
m_1601_22 | UCLV46813 | DirectTerminal | TRUE | 10 | GSO_145
m_1615_22 | UCLV47020 | DirectTerminal | TRUE | 52 | GSO_145
m_1633_22 | S_nSSEE4_12.47 | RootFallback | FALSE | 0 | GSO_145
m_1651_22 | UCLV48110 | DirectTerminal | TRUE | 24 | GSO_145
m_1668_22 | UCLV48415 | DirectTerminal | TRUE | 47 | GSO_145
m_1670_22 | UCLV48431 | DirectTerminal | TRUE | 35 | GSO_145
m_1684_22 | UCLV48697 | DirectTerminal | TRUE | 50 | GSO_145
m_1713_22 | UCLV49773 | DirectTerminal | TRUE | 51 | GSO_145
m_1719_22 | UCLV49905 | DirectTerminal | TRUE | 51 | GSO_145
m_1730_22 | UCLV50122 | DirectTerminal | TRUE | 12 | GSO_145
m_1747_22 | UCLV50402 | DirectTerminal | TRUE | 11 | GSO_145
m_1755_22 | S_nSSEE4_12.47 | RootFallback | FALSE | 0 | GSO_145
m_1765_22 | S_nSSEE4_12.47 | RootFallback | FALSE | 0 | GSO_145
m_1781_22 | UCLV51504 | DirectTerminal | TRUE | 42 | GSO_145
m_1792_22 | UCLV51671 | DirectTerminal | TRUE | 49 | GSO_145
m_1804_22 | UCLV51904 | DirectTerminal | TRUE | 14 | GSO_145
m_1812_22 | UCLV52052 | DirectTerminal | TRUE | 47 | GSO_145
m_1822_22 | UCLV52215 | DirectTerminal | TRUE | 46 | GSO_145
m_1825_22 | UCLV52280 | DirectTerminal | TRUE | 10 | GSO_145
m_1854_22 | UCLV53175 | DirectTerminal | TRUE | 41 | GSO_145
m_1871_22 | UCLV53479 | DirectTerminal | TRUE | 46 | GSO_145
m_1880_22 | UCLV53717 | DirectTerminal | TRUE | 46 | GSO_145
m_1885_22 | UCLV53789 | DirectTerminal | TRUE | 9 | GSO_145
m_1888_22 | S_nSSEE4_12.47 | RootFallback | FALSE | 0 | GSO_145
m_1975_22 | S_nSSEE4_12.47 | RootFallback | FALSE | 0 | GSO_145
m_1991_22 | S_nSSEE4_12.47 | RootFallback | FALSE | 0 | GSO_145
m_2030_22 | UCLV59161 | DirectTerminal | TRUE | 5 | GSO_145
m_2089_22 | S_nSSEE4_12.47 | RootFallback | FALSE | 0 | GSO_145
m_2094_22 | UCLV61724 | DirectTerminal | TRUE | 5 | GSO_145
m_2123_22 | S_nSSEE4_12.47 | RootFallback | FALSE | 0 | GSO_145
m_2138_22 | UCLV63744 | DirectTerminal | TRUE | 6 | GSO_145
m_2240_22 | UCLV7769 | DirectTerminal | TRUE | 6 | GSO_145
m_2241_22 | UCLV7771 | DirectTerminal | TRUE | 8 | GSO_145
m_2242_22 | UCLV7773 | DirectTerminal | TRUE | 8 | GSO_145
m_2243_22 | UCLV7774 | DirectTerminal | TRUE | 7 | GSO_145
m_2244_22 | UCLV7775 | DirectTerminal | TRUE | 6 | GSO_145
m_2245_22 | UCLV7777 | DirectTerminal | TRUE | 5 | GSO_145
m_2252_22 | UCLV7786 | DirectTerminal | TRUE | 8 | GSO_145
m_2391_22 | UCLV8166 | DirectTerminal | TRUE | 9 | GSO_145
m_2392_22 | S_nSSEE4_12.47 | RootFallback | FALSE | 0 | GSO_145
m_2393_22 | UCLV8168 | DirectTerminal | TRUE | 10 | GSO_145
m_2394_22 | UCLV8169 | DirectTerminal | TRUE | 19 | GSO_145
m_2395_22 | UCLV8170 | DirectTerminal | TRUE | 8 | GSO_145
m_2396_22 | UCLV8171 | DirectTerminal | TRUE | 17 | GSO_145
m_2397_22 | UCLV8172 | DirectTerminal | TRUE | 9 | GSO_145
m_2398_22 | UCLV8173 | DirectTerminal | TRUE | 8 | GSO_145
m_2399_22 | UCLV8174 | DirectTerminal | TRUE | 14 | GSO_145
m_2400_22 | UCLV8175 | DirectTerminal | TRUE | 15 | GSO_145
m_2401_22 | UCLV8176 | DirectTerminal | TRUE | 41 | GSO_145
m_2402_22 | UCLV8177 | DirectTerminal | TRUE | 49 | GSO_145
m_2403_22 | UCLV8178 | DirectTerminal | TRUE | 50 | GSO_145
m_2407_22 | UCLV8182 | DirectTerminal | TRUE | 48 | GSO_145
m_2411_22 | UCLV8186 | DirectTerminal | TRUE | 49 | GSO_145
m_2418_22 | UCLV8197 | DirectTerminal | TRUE | 37 | GSO_145
m_2419_22 | UCLV8198 | DirectTerminal | TRUE | 33 | GSO_145
m_2420_22 | UCLV8199 | DirectTerminal | TRUE | 39 | GSO_145
m_2421_22 | UCLV8200 | DirectTerminal | TRUE | 52 | GSO_145
m_2422_22 | UCLV8201 | DirectTerminal | TRUE | 39 | GSO_145
m_2423_22 | S_nSSEE4_12.47 | RootFallback | FALSE | 0 | GSO_145
m_2424_22 | S_nSSEE4_12.47 | RootFallback | FALSE | 0 | GSO_145
m_2425_22 | UCLV8204 | DirectTerminal | TRUE | 51 | GSO_145
m_2426_22 | UCLV8205 | DirectTerminal | TRUE | 40 | GSO_145
m_2444_22 | UCLV8223 | DirectTerminal | TRUE | 47 | GSO_145
m_2732_22 | UCMV122 | DirectTerminal | TRUE | 32 | GSO_145
m_52_22 | UCLV10074 | DirectTerminal | TRUE | 5 | GSO_145
m_53_22 | S_nSSEE4_12.47 | RootFallback | FALSE | 0 | GSO_145
m_54_22 | UCLV10076 | DirectTerminal | TRUE | 10 | GSO_145
m_712_22 | UCLV27716 | DirectTerminal | TRUE | 12 | GSO_145
m_724_22 | UCLV28089 | DirectTerminal | TRUE | 47 | GSO_145
m_729_22 | UCLV28216 | DirectTerminal | TRUE | 48 | GSO_145
m_733_22 | UCLV28315 | DirectTerminal | TRUE | 12 | GSO_145
m_744_22 | UCLV28541 | DirectTerminal | TRUE | 39 | GSO_145
m_752_22 | UCLV28850 | DirectTerminal | TRUE | 50 | GSO_145
m_755_22 | UCLV28908 | DirectTerminal | TRUE | 7 | GSO_145
m_760_22 | UCLV28951 | DirectTerminal | TRUE | 44 | GSO_145
m_779_22 | UCLV29375 | DirectTerminal | TRUE | 9 | GSO_145
m_797_22 | UCLV29732 | DirectTerminal | TRUE | 51 | GSO_145
m_801_22 | UCLV29804 | DirectTerminal | TRUE | 10 | GSO_145
m_803_22 | UCLV29817 | DirectTerminal | TRUE | 51 | GSO_145
m_804_22 | UCLV29831 | DirectTerminal | TRUE | 51 | GSO_145
m_814_22 | UCLV30056 | DirectTerminal | TRUE | 39 | GSO_145
m_835_22 | S_nSSEE4_12.47 | RootFallback | FALSE | 0 | GSO_145
m_841_22 | UCLV30634 | DirectTerminal | TRUE | 10 | GSO_145
m_849_22 | UCLV30761 | DirectTerminal | TRUE | 38 | GSO_145
m_864_22 | UCLV31237 | DirectTerminal | TRUE | 49 | GSO_145
m_868_22 | UCLV31305 | DirectTerminal | TRUE | 49 | GSO_145
m_875_22 | UCLV31451 | DirectTerminal | TRUE | 43 | GSO_145
m_888_22 | UCLV31848 | DirectTerminal | TRUE | 43 | GSO_145
m_900_22 | UCLV32144 | DirectTerminal | TRUE | 12 | GSO_145
m_903_22 | UCLV32231 | DirectTerminal | TRUE | 45 | GSO_145
m_910_22 | UCLV32370 | DirectTerminal | TRUE | 44 | GSO_145
m_919_22 | UCLV32553 | DirectTerminal | TRUE | 18 | GSO_145
m_948_22 | UCLV33406 | DirectTerminal | TRUE | 9 | GSO_145
m_952_22 | UCLV33500 | DirectTerminal | TRUE | 49 | GSO_145
m_959_22 | UCLV33626 | DirectTerminal | TRUE | 45 | GSO_145
m_990_22 | UCLV34160 | DirectTerminal | TRUE | 9 | GSO_145
m_997_22 | UCLV34233 | DirectTerminal | TRUE | 22 | GSO_145
m_1399_22 | UCLV41975 | DirectTerminal | TRUE | 14 | GSO_142
m_1400_22 | UCLV41992 | DirectTerminal | TRUE | 51 | GSO_142
m_1402_22 | UCLV42030 | DirectTerminal | TRUE | 26 | GSO_142
m_1405_22 | UCLV42093 | DirectTerminal | TRUE | 5 | GSO_142
m_1413_22 | UCLV42416 | DirectTerminal | TRUE | 10 | GSO_142
m_1416_22 | UCLV42483 | DirectTerminal | TRUE | 33 | GSO_142
m_1417_22 | UCLV42489 | DirectTerminal | TRUE | 17 | GSO_142
m_1422_22 | UCLV42788 | DirectTerminal | TRUE | 46 | GSO_142
m_1423_22 | UCLV42795 | DirectTerminal | TRUE | 16 | GSO_142
m_1483_22 | UCLV43791 | DirectTerminal | TRUE | 15 | GSO_142
m_1489_22 | UCLV44096 | DirectTerminal | TRUE | 35 | GSO_142
m_1490_22 | UCLV44102 | DirectTerminal | TRUE | 18 | GSO_142
m_1494_22 | UCLV44238 | DirectTerminal | TRUE | 10 | GSO_142
m_1497_22 | UCLV44447 | DirectTerminal | TRUE | 57 | GSO_142
m_1502_22 | UCLV44555 | DirectTerminal | TRUE | 5 | GSO_142
m_1549_22 | UCLV45457 | DirectTerminal | TRUE | 37 | GSO_142
m_1556_22 | UCLV45734 | DirectTerminal | TRUE | 54 | GSO_142
m_1558_22 | UCLV45773 | DirectTerminal | TRUE | 41 | GSO_142
m_1561_22 | UCLV45837 | DirectTerminal | TRUE | 13 | GSO_142
m_1563_22 | UCLV45894 | DirectTerminal | TRUE | 45 | GSO_142
m_1564_22 | UCLV45901 | DirectTerminal | TRUE | 17 | GSO_142
m_1567_22 | UCLV46061 | DirectTerminal | TRUE | 55 | GSO_142
m_1571_22 | UCLV46234 | DirectTerminal | TRUE | 19 | GSO_142
m_1622_22 | UCLV47171 | DirectTerminal | TRUE | 37 | GSO_142
m_1626_22 | UCLV47328 | DirectTerminal | TRUE | 50 | GSO_142
m_1629_22 | UCLV47425 | DirectTerminal | TRUE | 13 | GSO_142
m_1631_22 | UCLV47486 | DirectTerminal | TRUE | 31 | GSO_142
m_1632_22 | UCLV47495 | DirectTerminal | TRUE | 12 | GSO_142
m_1634_22 | UCLV47622 | DirectTerminal | TRUE | 11 | GSO_142
m_1638_22 | UCLV47848 | DirectTerminal | TRUE | 53 | GSO_142
m_1642_22 | UCLV47952 | DirectTerminal | TRUE | 8 | GSO_142
m_1693_22 | UCLV48912 | DirectTerminal | TRUE | 15 | GSO_142
m_1695_22 | UCLV49042 | DirectTerminal | TRUE | 11 | GSO_142
m_1696_22 | UCLV49116 | DirectTerminal | TRUE | 53 | GSO_142
m_1698_22 | UCLV49161 | DirectTerminal | TRUE | 10 | GSO_142
m_1701_22 | UCLV49288 | DirectTerminal | TRUE | 22 | GSO_142
m_1703_22 | UCLV49444 | DirectTerminal | TRUE | 53 | GSO_142
m_1709_22 | UCLV49603 | DirectTerminal | TRUE | 41 | GSO_142
m_1710_22 | UCLV49609 | DirectTerminal | TRUE | 17 | GSO_142
m_1754_22 | UCLV50585 | DirectTerminal | TRUE | 24 | GSO_142
m_1759_22 | UCLV50785 | DirectTerminal | TRUE | 29 | GSO_142
m_1763_22 | UCLV50888 | DirectTerminal | TRUE | 47 | GSO_142
m_1764_22 | UCLV50897 | DirectTerminal | TRUE | 25 | GSO_142
m_1767_22 | UCLV51036 | DirectTerminal | TRUE | 13 | GSO_142
m_1769_22 | UCLV51253 | DirectTerminal | TRUE | 54 | GSO_142
m_1773_22 | UCLV51366 | DirectTerminal | TRUE | 7 | GSO_142
m_1835_22 | UCLV52543 | DirectTerminal | TRUE | 52 | GSO_142
m_1837_22 | UCLV52584 | DirectTerminal | TRUE | 28 | GSO_142
m_1840_22 | UCLV52651 | DirectTerminal | TRUE | 12 | GSO_142
m_1844_22 | UCLV52869 | DirectTerminal | TRUE | 56 | GSO_142
m_1846_22 | UCLV52911 | DirectTerminal | TRUE | 11 | GSO_142
m_1851_22 | UCLV53047 | DirectTerminal | TRUE | 33 | GSO_142
m_1852_22 | UCLV53055 | DirectTerminal | TRUE | 25 | GSO_142
m_1892_22 | UCLV53943 | DirectTerminal | TRUE | 49 | GSO_142
m_1894_22 | UCLV53987 | DirectTerminal | TRUE | 28 | GSO_142
m_1899_22 | UCLV54104 | DirectTerminal | TRUE | 16 | GSO_142
m_1904_22 | UCLV54426 | DirectTerminal | TRUE | 22 | GSO_142
m_1905_22 | UCLV54462 | DirectTerminal | TRUE | 56 | GSO_142
m_1910_22 | UCLV54567 | DirectTerminal | TRUE | 13 | GSO_142
m_1916_22 | UCLV54878 | DirectTerminal | TRUE | 13 | GSO_142
m_1918_22 | UCLV54948 | DirectTerminal | TRUE | 6 | GSO_142
m_1922_22 | UCLV55260 | DirectTerminal | TRUE | 10 | GSO_142
m_1923_22 | UCLV55363 | DirectTerminal | TRUE | 45 | GSO_142
m_1927_22 | UCLV55556 | DirectTerminal | TRUE | 47 | GSO_142
m_1929_22 | UCLV55599 | DirectTerminal | TRUE | 20 | GSO_142
m_1934_22 | UCLV55661 | DirectTerminal | TRUE | 45 | GSO_142
m_1953_22 | UCLV55873 | DirectTerminal | TRUE | 48 | GSO_142
m_1955_22 | UCLV55914 | DirectTerminal | TRUE | 22 | GSO_142
m_1956_22 | UCLV55975 | DirectTerminal | TRUE | 44 | GSO_142
m_1957_22 | UCLV55982 | DirectTerminal | TRUE | 28 | GSO_142
m_1963_22 | UCLV56279 | DirectTerminal | TRUE | 45 | GSO_142
m_1964_22 | UCLV56393 | DirectTerminal | TRUE | 7 | GSO_142
m_1968_22 | UCLV56578 | DirectTerminal | TRUE | 56 | GSO_142
m_1969_22 | UCLV56586 | DirectTerminal | TRUE | 35 | GSO_142
m_1974_22 | UCLV56696 | DirectTerminal | TRUE | 9 | GSO_142
m_1978_22 | UCLV56946 | DirectTerminal | TRUE | 9 | GSO_142
m_1981_22 | UCLV57009 | DirectTerminal | TRUE | 14 | GSO_142
m_1985_22 | UCLV57080 | DirectTerminal | TRUE | 30 | GSO_142
m_1990_22 | UCLV57389 | DirectTerminal | TRUE | 14 | GSO_142
m_1993_22 | UCLV57510 | DirectTerminal | TRUE | 45 | GSO_142
m_1997_22 | UCLV57742 | DirectTerminal | TRUE | 19 | GSO_142
m_1999_22 | UCLV57810 | DirectTerminal | TRUE | 45 | GSO_142
m_2003_22 | UCLV58006 | DirectTerminal | TRUE | 46 | GSO_142
m_2006_22 | UCLV58050 | DirectTerminal | TRUE | 21 | GSO_142
m_2009_22 | UCLV58116 | DirectTerminal | TRUE | 35 | GSO_142
m_2010_22 | UCLV58124 | DirectTerminal | TRUE | 18 | GSO_142
m_2016_22 | UCLV58398 | DirectTerminal | TRUE | 50 | GSO_142
m_2017_22 | UCLV58403 | DirectTerminal | TRUE | 18 | GSO_142
m_2020_22 | UCLV58709 | DirectTerminal | TRUE | 37 | GSO_142
m_2024_22 | UCLV58815 | DirectTerminal | TRUE | 8 | GSO_142
m_2026_22 | UCLV59060 | DirectTerminal | TRUE | 8 | GSO_142
m_2029_22 | UCLV59126 | DirectTerminal | TRUE | 12 | GSO_142
m_2031_22 | UCLV59180 | DirectTerminal | TRUE | 24 | GSO_142
m_2037_22 | UCLV59401 | DirectTerminal | TRUE | 14 | GSO_142
m_2045_22 | UCLV59704 | DirectTerminal | TRUE | 6 | GSO_142
m_2047_22 | UCLV59824 | DirectTerminal | TRUE | 47 | GSO_142
m_2051_22 | UCLV60017 | DirectTerminal | TRUE | 6 | GSO_142
m_2053_22 | UCLV60053 | DirectTerminal | TRUE | 35 | GSO_142
m_2056_22 | UCLV60122 | DirectTerminal | TRUE | 43 | GSO_142
m_2061_22 | UCLV60326 | DirectTerminal | TRUE | 49 | GSO_142
m_2063_22 | UCLV60367 | DirectTerminal | TRUE | 35 | GSO_142
m_2065_22 | UCLV60434 | DirectTerminal | TRUE | 47 | GSO_142
m_2068_22 | UCLV60482 | DirectTerminal | TRUE | 39 | GSO_142
m_2072_22 | UCLV60644 | DirectTerminal | TRUE | 48 | GSO_142
m_2080_22 | UCLV60948 | DirectTerminal | TRUE | 46 | GSO_142
m_2081_22 | UCLV60957 | DirectTerminal | TRUE | 16 | GSO_142
m_2085_22 | UCLV61262 | DirectTerminal | TRUE | 47 | GSO_142
m_2086_22 | UCLV61270 | DirectTerminal | TRUE | 35 | GSO_142
m_2088_22 | UCLV61374 | DirectTerminal | TRUE | 9 | GSO_142
m_2093_22 | UCLV61685 | DirectTerminal | TRUE | 11 | GSO_142
m_2100_22 | UCLV62151 | DirectTerminal | TRUE | 43 | GSO_142
m_2101_22 | UCLV62160 | DirectTerminal | TRUE | 20 | GSO_142
m_2104_22 | UCLV62266 | DirectTerminal | TRUE | 14 | GSO_142
m_2110_22 | UCLV62581 | DirectTerminal | TRUE | 13 | GSO_142
m_2111_22 | UCLV62621 | DirectTerminal | TRUE | 19 | GSO_142
m_2113_22 | UCLV62689 | DirectTerminal | TRUE | 45 | GSO_142
m_2117_22 | UCLV62873 | DirectTerminal | TRUE | 47 | GSO_142
m_2119_22 | UCLV62919 | DirectTerminal | TRUE | 34 | GSO_142
m_2120_22 | UCLV62984 | DirectTerminal | TRUE | 42 | GSO_142
m_2122_22 | UCLV63036 | DirectTerminal | TRUE | 14 | GSO_142
m_2126_22 | UCLV63192 | DirectTerminal | TRUE | 47 | GSO_142
m_2128_22 | UCLV63236 | DirectTerminal | TRUE | 23 | GSO_142
m_2129_22 | UCLV63281 | DirectTerminal | TRUE | 43 | GSO_142
m_2130_22 | UCLV63289 | DirectTerminal | TRUE | 30 | GSO_142
m_2134_22 | UCLV63606 | DirectTerminal | TRUE | 17 | GSO_142
m_2137_22 | UCLV63707 | DirectTerminal | TRUE | 13 | GSO_142
m_2383_22 | UCLV8158 | DirectTerminal | TRUE | 39 | GSO_142
m_2744_22 | UCMV27 | DirectTerminal | TRUE | 26 | GSO_142
m_327_22 | UCLV13216 | DirectTerminal | TRUE | 55 | GSO_142
m_328_22 | UCLV13217 | DirectTerminal | TRUE | 51 | GSO_142
m_370_22 | UCLV15913 | DirectTerminal | TRUE | 32 | GSO_142
m_38_22 | UCLV10060 | DirectTerminal | TRUE | 13 | GSO_142
m_39_22 | UCLV10061 | DirectTerminal | TRUE | 26 | GSO_142
m_40_22 | UCLV10062 | DirectTerminal | TRUE | 15 | GSO_142
m_41_22 | UCLV10063 | DirectTerminal | TRUE | 12 | GSO_142
m_55_22 | UCLV10077 | DirectTerminal | TRUE | 39 | GSO_142
m_56_22 | UCLV10078 | DirectTerminal | TRUE | 37 | GSO_142
m_57_22 | UCLV10079 | DirectTerminal | TRUE | 52 | GSO_142
m_58_22 | UCLV10080 | DirectTerminal | TRUE | 41 | GSO_142
m_59_22 | UCLV10081 | DirectTerminal | TRUE | 37 | GSO_142
m_2027_21 | UCLV12119 | DirectTerminal | TRUE | 33 | GSO_18
m_2029_21 | UCLV12120 | DirectTerminal | TRUE | 35 | GSO_18
m_2049_21 | UCLV12139 | DirectTerminal | TRUE | 30 | GSO_18
m_2051_21 | UCLV12140 | DirectTerminal | TRUE | 28 | GSO_18
m_2052_21 | UCLV12141 | DirectTerminal | TRUE | 28 | GSO_18
m_2053_21 | UCLV12142 | DirectTerminal | TRUE | 30 | GSO_18
m_2056_21 | UCLV12145 | DirectTerminal | TRUE | 26 | GSO_18
m_2057_21 | UCLV12147 | DirectTerminal | TRUE | 26 | GSO_18
m_2058_21 | UCLV12148 | DirectTerminal | TRUE | 25 | GSO_18
m_2059_21 | UCLV12149 | DirectTerminal | TRUE | 25 | GSO_18
m_2061_21 | UCLV12150 | DirectTerminal | TRUE | 24 | GSO_18
m_2062_21 | UCLV12151 | DirectTerminal | TRUE | 21 | GSO_18
m_2063_21 | UCLV12152 | DirectTerminal | TRUE | 21 | GSO_18
m_2064_21 | UCLV12153 | DirectTerminal | TRUE | 21 | GSO_18
m_2065_21 | UCLV12155 | DirectTerminal | TRUE | 23 | GSO_18
m_2066_21 | UCLV12157 | DirectTerminal | TRUE | 24 | GSO_18
m_2067_21 | UCLV12158 | DirectTerminal | TRUE | 24 | GSO_18
m_2068_21 | UCLV12159 | DirectTerminal | TRUE | 24 | GSO_18
m_2070_21 | UCLV12160 | DirectTerminal | TRUE | 24 | GSO_18
m_2071_21 | UCLV12161 | DirectTerminal | TRUE | 23 | GSO_18
m_2072_21 | UCLV12162 | DirectTerminal | TRUE | 23 | GSO_18
m_2073_21 | UCLV12163 | DirectTerminal | TRUE | 28 | GSO_18
m_2074_21 | UCLV12164 | DirectTerminal | TRUE | 28 | GSO_18
m_2075_21 | UCLV12165 | DirectTerminal | TRUE | 28 | GSO_18
m_2076_21 | UCLV12166 | DirectTerminal | TRUE | 25 | GSO_18
m_2077_21 | UCLV12167 | DirectTerminal | TRUE | 25 | GSO_18
m_2078_21 | UCLV12168 | DirectTerminal | TRUE | 25 | GSO_18
m_2079_21 | UCLV12169 | DirectTerminal | TRUE | 21 | GSO_18
m_2081_21 | UCLV12170 | DirectTerminal | TRUE | 21 | GSO_18
m_2082_21 | UCLV12171 | DirectTerminal | TRUE | 21 | GSO_18
m_2083_21 | UCLV12172 | DirectTerminal | TRUE | 21 | GSO_18
m_2084_21 | UCLV12173 | DirectTerminal | TRUE | 21 | GSO_18
m_2085_21 | UCLV12174 | DirectTerminal | TRUE | 22 | GSO_18
m_2086_21 | UCLV12175 | DirectTerminal | TRUE | 25 | GSO_18
m_2087_21 | UCLV12176 | DirectTerminal | TRUE | 25 | GSO_18
m_2088_21 | UCLV12177 | DirectTerminal | TRUE | 23 | GSO_18
m_2089_21 | UCLV12178 | DirectTerminal | TRUE | 23 | GSO_18
m_2090_21 | UCLV12179 | DirectTerminal | TRUE | 23 | GSO_18
m_2092_21 | UCLV12180 | DirectTerminal | TRUE | 25 | GSO_18
m_2093_21 | UCLV12181 | DirectTerminal | TRUE | 24 | GSO_18
m_2094_21 | UCLV12182 | DirectTerminal | TRUE | 24 | GSO_18
m_2095_21 | UCLV12183 | DirectTerminal | TRUE | 27 | GSO_18
m_2096_21 | UCLV12184 | DirectTerminal | TRUE | 27 | GSO_18
m_2097_21 | UCLV12185 | DirectTerminal | TRUE | 25 | GSO_18
m_2098_21 | UCLV12186 | DirectTerminal | TRUE | 25 | GSO_18
m_2099_21 | UCLV12187 | DirectTerminal | TRUE | 24 | GSO_18
m_2100_21 | UCLV12188 | DirectTerminal | TRUE | 24 | GSO_18
m_2101_21 | UCLV12189 | DirectTerminal | TRUE | 24 | GSO_18
m_2103_21 | UCLV12190 | DirectTerminal | TRUE | 22 | GSO_18
m_2104_21 | UCLV12191 | DirectTerminal | TRUE | 22 | GSO_18
m_2105_21 | UCLV12192 | DirectTerminal | TRUE | 25 | GSO_18
m_2106_21 | UCLV12193 | DirectTerminal | TRUE | 25 | GSO_18
m_2107_21 | UCLV12194 | DirectTerminal | TRUE | 24 | GSO_18
m_2108_21 | UCLV12195 | DirectTerminal | TRUE | 24 | GSO_18
m_2109_21 | UCLV12196 | DirectTerminal | TRUE | 24 | GSO_18
m_2110_21 | UCLV12197 | DirectTerminal | TRUE | 24 | GSO_18
m_2111_21 | UCLV12198 | DirectTerminal | TRUE | 7 | GSO_18
m_2931_21 | UCLV13122 | DirectTerminal | TRUE | 39 | GSO_18
m_2932_21 | UCLV13123 | DirectTerminal | TRUE | 39 | GSO_18
m_2933_21 | UCLV13124 | DirectTerminal | TRUE | 38 | GSO_18
m_2934_21 | UCLV13125 | DirectTerminal | TRUE | 38 | GSO_18
m_2935_21 | UCLV13126 | DirectTerminal | TRUE | 40 | GSO_18
m_2936_21 | UCLV13127 | DirectTerminal | TRUE | 38 | GSO_18
m_2937_21 | UCLV13128 | DirectTerminal | TRUE | 43 | GSO_18
m_33157_21 | UCLV41945 | DirectTerminal | TRUE | 24 | GSO_18
m_33160_21 | UCLV41948 | DirectTerminal | TRUE | 10 | GSO_18
m_33218_21 | UCLV42002 | DirectTerminal | TRUE | 20 | GSO_18
m_33220_21 | UCLV42004 | DirectTerminal | TRUE | 18 | GSO_18
m_33282_21 | UCLV42063 | DirectTerminal | TRUE | 20 | GSO_18
m_33284_21 | UCLV42065 | DirectTerminal | TRUE | 39 | GSO_18
m_33350_21 | UCLV42126 | DirectTerminal | TRUE | 19 | GSO_18
m_33352_21 | UCLV42128 | DirectTerminal | TRUE | 21 | GSO_18
m_33426_21 | UCLV42195 | DirectTerminal | TRUE | 16 | GSO_18
m_33433_21 | UCLV42200 | DirectTerminal | TRUE | 18 | GSO_18
m_33478_21 | UCLV42243 | DirectTerminal | TRUE | 35 | GSO_18
m_33489_21 | UCLV42253 | DirectTerminal | TRUE | 22 | GSO_18
m_33491_21 | UCLV42255 | DirectTerminal | TRUE | 25 | GSO_18
m_33559_21 | UCLV42317 | DirectTerminal | TRUE | 23 | GSO_18
m_33628_21 | UCLV42382 | DirectTerminal | TRUE | 21 | GSO_18
m_33631_21 | UCLV42385 | DirectTerminal | TRUE | 41 | GSO_18
m_33633_21 | UCLV42387 | DirectTerminal | TRUE | 8 | GSO_18
m_33675_21 | UCLV42426 | DirectTerminal | TRUE | 6 | GSO_18
m_33716_21 | UCLV42463 | DirectTerminal | TRUE | 16 | GSO_18
m_33776_21 | UCLV42520 | DirectTerminal | TRUE | 22 | GSO_18
m_33779_21 | UCLV42523 | DirectTerminal | TRUE | 21 | GSO_18
m_33782_21 | UCLV42526 | DirectTerminal | TRUE | 14 | GSO_18
m_33844_21 | UCLV42583 | DirectTerminal | TRUE | 23 | GSO_18
m_33846_21 | UCLV42585 | DirectTerminal | TRUE | 22 | GSO_18
m_33897_21 | UCLV42630 | DirectTerminal | TRUE | 18 | GSO_18
m_33898_21 | UCLV42631 | DirectTerminal | TRUE | 24 | GSO_18
m_33969_21 | UCLV42697 | DirectTerminal | TRUE | 18 | GSO_18
m_34045_21 | UCLV42766 | DirectTerminal | TRUE | 20 | GSO_18
m_34048_21 | UCLV42769 | DirectTerminal | TRUE | 9 | GSO_18
m_34099_21 | UCLV42817 | DirectTerminal | TRUE | 42 | GSO_18
m_34111_21 | UCLV42828 | DirectTerminal | TRUE | 21 | GSO_18
m_34115_21 | UCLV42831 | DirectTerminal | TRUE | 25 | GSO_18
m_35086_21 | UCLV43763 | DirectTerminal | TRUE | 17 | GSO_18
m_35149_21 | UCLV43822 | DirectTerminal | TRUE | 22 | GSO_18
m_35153_21 | UCLV43826 | DirectTerminal | TRUE | 12 | GSO_18
m_35206_21 | UCLV43877 | DirectTerminal | TRUE | 39 | GSO_18
m_35216_21 | UCLV43886 | DirectTerminal | TRUE | 15 | GSO_18
m_35276_21 | UCLV43940 | DirectTerminal | TRUE | 23 | GSO_18
m_35353_21 | UCLV44009 | DirectTerminal | TRUE | 12 | GSO_18
m_35419_21 | UCLV44070 | DirectTerminal | TRUE | 16 | GSO_18
m_35475_21 | UCLV44125 | DirectTerminal | TRUE | 46 | GSO_18
m_35487_21 | UCLV44136 | DirectTerminal | TRUE | 19 | GSO_18
m_35489_21 | UCLV44138 | DirectTerminal | TRUE | 17 | GSO_18
m_35562_21 | UCLV44205 | DirectTerminal | TRUE | 20 | GSO_18
m_35564_21 | UCLV44207 | DirectTerminal | TRUE | 40 | GSO_18
m_35566_21 | UCLV44209 | DirectTerminal | TRUE | 7 | GSO_18
m_35629_21 | UCLV44268 | DirectTerminal | TRUE | 19 | GSO_18
m_35632_21 | UCLV44270 | DirectTerminal | TRUE | 19 | GSO_18
m_35715_21 | UCLV44346 | DirectTerminal | TRUE | 17 | GSO_18
m_35766_21 | UCLV44393 | DirectTerminal | TRUE | 13 | GSO_18
m_35835_21 | UCLV44458 | DirectTerminal | TRUE | 21 | GSO_18
m_35906_21 | UCLV44524 | DirectTerminal | TRUE | 19 | GSO_18
m_36913_21 | UCLV45492 | DirectTerminal | TRUE | 19 | GSO_18
m_36915_21 | UCLV45494 | DirectTerminal | TRUE | 39 | GSO_18
m_36917_21 | UCLV45496 | DirectTerminal | TRUE | 14 | GSO_18
m_36982_21 | UCLV45556 | DirectTerminal | TRUE | 22 | GSO_18
m_37021_21 | UCLV45592 | DirectTerminal | TRUE | 9 | GSO_18
m_37056_21 | UCLV45623 | DirectTerminal | TRUE | 19 | GSO_18
m_37094_21 | UCLV45659 | DirectTerminal | TRUE | 14 | GSO_18
m_37113_21 | UCLV45676 | DirectTerminal | TRUE | 19 | GSO_18
m_37183_21 | UCLV45743 | DirectTerminal | TRUE | 15 | GSO_18
m_37186_21 | UCLV45746 | DirectTerminal | TRUE | 6 | GSO_18
m_37250_21 | UCLV45806 | DirectTerminal | TRUE | 20 | GSO_18
m_37252_21 | UCLV45808 | DirectTerminal | TRUE | 43 | GSO_18
m_37317_21 | UCLV45869 | DirectTerminal | TRUE | 24 | GSO_18
m_37374_21 | UCLV45922 | DirectTerminal | TRUE | 47 | GSO_18
m_37386_21 | UCLV45933 | DirectTerminal | TRUE | 22 | GSO_18
m_37388_21 | UCLV45935 | DirectTerminal | TRUE | 19 | GSO_18
m_37391_21 | UCLV45938 | DirectTerminal | TRUE | 12 | GSO_18
m_37451_21 | UCLV45993 | DirectTerminal | TRUE | 38 | GSO_18
m_37462_21 | UCLV46001 | DirectTerminal | TRUE | 22 | GSO_18
m_37465_21 | UCLV46004 | DirectTerminal | TRUE | 19 | GSO_18
m_37538_21 | UCLV46072 | DirectTerminal | TRUE | 16 | GSO_18
m_37541_21 | UCLV46075 | DirectTerminal | TRUE | 23 | GSO_18
m_37542_21 | UCLV46076 | DirectTerminal | TRUE | 8 | GSO_18
m_37608_21 | UCLV46136 | DirectTerminal | TRUE | 18 | GSO_18
m_37610_21 | UCLV46138 | DirectTerminal | TRUE | 17 | GSO_18
m_37646_21 | UCLV46171 | DirectTerminal | TRUE | 5 | GSO_18
m_37682_21 | UCLV46203 | DirectTerminal | TRUE | 19 | GSO_18
m_37739_21 | UCLV46257 | DirectTerminal | TRUE | 43 | GSO_18
m_37750_21 | UCLV46267 | DirectTerminal | TRUE | 24 | GSO_18
m_37752_21 | UCLV46269 | DirectTerminal | TRUE | 19 | GSO_18
m_38662_21 | UCLV47149 | DirectTerminal | TRUE | 23 | GSO_18
m_38666_21 | UCLV47152 | DirectTerminal | TRUE | 15 | GSO_18
m_38723_21 | UCLV47206 | DirectTerminal | TRUE | 23 | GSO_18
m_38725_21 | UCLV47208 | DirectTerminal | TRUE | 21 | GSO_18
m_38728_21 | UCLV47210 | DirectTerminal | TRUE | 11 | GSO_18
m_38783_21 | UCLV47262 | DirectTerminal | TRUE | 41 | GSO_18
m_38795_21 | UCLV47273 | DirectTerminal | TRUE | 16 | GSO_18
m_38864_21 | UCLV47338 | DirectTerminal | TRUE | 22 | GSO_18
m_38867_21 | UCLV47340 | DirectTerminal | TRUE | 22 | GSO_18
m_38868_21 | UCLV47341 | DirectTerminal | TRUE | 10 | GSO_18
m_38924_21 | UCLV47393 | DirectTerminal | TRUE | 16 | GSO_18
m_38960_21 | UCLV47427 | DirectTerminal | TRUE | 9 | GSO_18
m_39057_21 | UCLV47517 | DirectTerminal | TRUE | 46 | GSO_18
m_39069_21 | UCLV47528 | DirectTerminal | TRUE | 24 | GSO_18
m_39072_21 | UCLV47530 | DirectTerminal | TRUE | 13 | GSO_18
m_39137_21 | UCLV47590 | DirectTerminal | TRUE | 23 | GSO_18
m_39139_21 | UCLV47592 | DirectTerminal | TRUE | 46 | GSO_18
m_39207_21 | UCLV47656 | DirectTerminal | TRUE | 23 | GSO_18
m_39209_21 | UCLV47658 | DirectTerminal | TRUE | 19 | GSO_18
m_39287_21 | UCLV47729 | DirectTerminal | TRUE | 18 | GSO_18
m_39356_21 | UCLV47792 | DirectTerminal | TRUE | 24 | GSO_18
m_39427_21 | UCLV47858 | DirectTerminal | TRUE | 23 | GSO_18
m_39494_21 | UCLV47920 | DirectTerminal | TRUE | 21 | GSO_18
m_39559_21 | UCLV47981 | DirectTerminal | TRUE | 24 | GSO_18
m_39563_21 | UCLV47985 | DirectTerminal | TRUE | 10 | GSO_18
m_40495_21 | UCLV48882 | DirectTerminal | TRUE | 20 | GSO_18
m_40498_21 | UCLV48885 | DirectTerminal | TRUE | 36 | GSO_18
m_40500_21 | UCLV48887 | DirectTerminal | TRUE | 14 | GSO_18
m_40548_21 | UCLV48931 | DirectTerminal | TRUE | 32 | GSO_18
m_40559_21 | UCLV48941 | DirectTerminal | TRUE | 20 | GSO_18
m_40562_21 | UCLV48944 | DirectTerminal | TRUE | 16 | GSO_18
m_40564_21 | UCLV48946 | DirectTerminal | TRUE | 15 | GSO_18
m_40599_21 | UCLV48978 | DirectTerminal | TRUE | 9 | GSO_18
m_40637_21 | UCLV49010 | DirectTerminal | TRUE | 24 | GSO_18
m_40763_21 | UCLV49127 | DirectTerminal | TRUE | 21 | GSO_18
m_40765_21 | UCLV49129 | DirectTerminal | TRUE | 20 | GSO_18
m_40767_21 | UCLV49130 | DirectTerminal | TRUE | 9 | GSO_18
m_40834_21 | UCLV49194 | DirectTerminal | TRUE | 17 | GSO_18
m_40836_21 | UCLV49196 | DirectTerminal | TRUE | 42 | GSO_18
m_40899_21 | UCLV49253 | DirectTerminal | TRUE | 23 | GSO_18
m_40901_21 | UCLV49255 | DirectTerminal | TRUE | 17 | GSO_18
m_40963_21 | UCLV49311 | DirectTerminal | TRUE | 46 | GSO_18
m_40976_21 | UCLV49323 | DirectTerminal | TRUE | 23 | GSO_18
m_40978_21 | UCLV49325 | DirectTerminal | TRUE | 18 | GSO_18
m_41035_21 | UCLV49378 | DirectTerminal | TRUE | 41 | GSO_18
m_41049_21 | UCLV49390 | DirectTerminal | TRUE | 20 | GSO_18
m_41120_21 | UCLV49455 | DirectTerminal | TRUE | 22 | GSO_18
m_41122_21 | UCLV49457 | DirectTerminal | TRUE | 18 | GSO_18
m_41184_21 | UCLV49514 | DirectTerminal | TRUE | 24 | GSO_18
m_41186_21 | UCLV49516 | DirectTerminal | TRUE | 16 | GSO_18
m_41257_21 | UCLV49581 | DirectTerminal | TRUE | 17 | GSO_18
m_41260_21 | UCLV49584 | DirectTerminal | TRUE | 7 | GSO_18
m_41323_21 | UCLV49644 | DirectTerminal | TRUE | 24 | GSO_18
m_41325_21 | UCLV49646 | DirectTerminal | TRUE | 16 | GSO_18
m_41392_21 | UCLV49707 | DirectTerminal | TRUE | 22 | GSO_18
m_421_21 | UCLV10440 | DirectTerminal | TRUE | 7 | GSO_18
m_423_21 | UCLV10442 | DirectTerminal | TRUE | 9 | GSO_18
m_42346_21 | UCLV50618 | DirectTerminal | TRUE | 22 | GSO_18
m_42413_21 | UCLV50681 | DirectTerminal | TRUE | 19 | GSO_18
m_424_21 | UCLV10443 | DirectTerminal | TRUE | 7 | GSO_18
m_42494_21 | UCLV50755 | DirectTerminal | TRUE | 14 | GSO_18
m_425_21 | UCLV10444 | DirectTerminal | TRUE | 6 | GSO_18
m_42542_21 | UCLV50800 | DirectTerminal | TRUE | 19 | GSO_18
m_42544_21 | UCLV50802 | DirectTerminal | TRUE | 11 | GSO_18
m_42610_21 | UCLV50864 | DirectTerminal | TRUE | 20 | GSO_18
m_426_21 | UCLV10445 | DirectTerminal | TRUE | 7 | GSO_18
m_42676_21 | UCLV50928 | DirectTerminal | TRUE | 24 | GSO_18
m_42680_21 | UCLV50931 | DirectTerminal | TRUE | 20 | GSO_18
m_42682_21 | UCLV50933 | DirectTerminal | TRUE | 10 | GSO_18
m_42740_21 | UCLV50989 | DirectTerminal | TRUE | 41 | GSO_18
m_42751_21 | UCLV50999 | DirectTerminal | TRUE | 20 | GSO_18
m_42825_21 | UCLV51066 | DirectTerminal | TRUE | 22 | GSO_18
m_42827_21 | UCLV51068 | DirectTerminal | TRUE | 24 | GSO_18
m_42830_21 | UCLV51070 | DirectTerminal | TRUE | 10 | GSO_18
m_42906_21 | UCLV51139 | DirectTerminal | TRUE | 17 | GSO_18
m_42937_21 | UCLV51167 | DirectTerminal | TRUE | 5 | GSO_18
m_42975_21 | UCLV51200 | DirectTerminal | TRUE | 15 | GSO_18
m_43042_21 | UCLV51264 | DirectTerminal | TRUE | 24 | GSO_18
m_43115_21 | UCLV51333 | DirectTerminal | TRUE | 27 | GSO_18
m_43117_21 | UCLV51335 | DirectTerminal | TRUE | 47 | GSO_18
m_43183_21 | UCLV51397 | DirectTerminal | TRUE | 23 | GSO_18
m_43185_21 | UCLV51399 | DirectTerminal | TRUE | 17 | GSO_18
m_43189_21 | UCLV51401 | DirectTerminal | TRUE | 12 | GSO_18
m_44154_21 | UCLV52359 | DirectTerminal | TRUE | 41 | GSO_18
m_44165_21 | UCLV52369 | DirectTerminal | TRUE | 26 | GSO_18
m_44169_21 | UCLV52372 | DirectTerminal | TRUE | 19 | GSO_18
m_44203_21 | UCLV52404 | DirectTerminal | TRUE | 9 | GSO_18
m_44239_21 | UCLV52438 | DirectTerminal | TRUE | 19 | GSO_18
m_44242_21 | UCLV52440 | DirectTerminal | TRUE | 16 | GSO_18
m_44244_21 | UCLV52442 | DirectTerminal | TRUE | 15 | GSO_18
m_44310_21 | UCLV52503 | DirectTerminal | TRUE | 17 | GSO_18
m_44363_21 | UCLV52555 | DirectTerminal | TRUE | 15 | GSO_18
m_44364_21 | UCLV52556 | DirectTerminal | TRUE | 15 | GSO_18
m_44427_21 | UCLV52616 | DirectTerminal | TRUE | 20 | GSO_18
m_44430_21 | UCLV52619 | DirectTerminal | TRUE | 40 | GSO_18
m_44493_21 | UCLV52679 | DirectTerminal | TRUE | 20 | GSO_18
m_44495_21 | UCLV52680 | DirectTerminal | TRUE | 22 | GSO_18
m_44497_21 | UCLV52682 | DirectTerminal | TRUE | 13 | GSO_18
m_44569_21 | UCLV52751 | DirectTerminal | TRUE | 18 | GSO_18
m_44571_21 | UCLV52753 | DirectTerminal | TRUE | 16 | GSO_18
m_44628_21 | UCLV52808 | DirectTerminal | TRUE | 38 | GSO_18
m_44638_21 | UCLV52817 | DirectTerminal | TRUE | 20 | GSO_18
m_44705_21 | UCLV52880 | DirectTerminal | TRUE | 15 | GSO_18
m_44708_21 | UCLV52883 | DirectTerminal | TRUE | 11 | GSO_18
m_44776_21 | UCLV52948 | DirectTerminal | TRUE | 25 | GSO_18
m_44779_21 | UCLV52950 | DirectTerminal | TRUE | 46 | GSO_18
m_44861_21 | UCLV53026 | DirectTerminal | TRUE | 21 | GSO_18
m_44863_21 | UCLV53028 | DirectTerminal | TRUE | 16 | GSO_18
m_44925_21 | UCLV53088 | DirectTerminal | TRUE | 17 | GSO_18
m_44928_21 | UCLV53090 | DirectTerminal | TRUE | 21 | GSO_18
m_44989_21 | UCLV53146 | DirectTerminal | TRUE | 16 | GSO_18
m_45680_21 | UCLV53824 | DirectTerminal | TRUE | 20 | GSO_18
m_45683_21 | UCLV53827 | DirectTerminal | TRUE | 21 | GSO_18
m_45818_21 | UCLV53954 | DirectTerminal | TRUE | 16 | GSO_18
m_45821_21 | UCLV53957 | DirectTerminal | TRUE | 7 | GSO_18
m_45886_21 | UCLV54019 | DirectTerminal | TRUE | 20 | GSO_18
m_45890_21 | UCLV54022 | DirectTerminal | TRUE | 37 | GSO_18
m_45911_21 | UCLV54042 | DirectTerminal | TRUE | 14 | GSO_18
m_45945_21 | UCLV54074 | DirectTerminal | TRUE | 24 | GSO_18
m_45948_21 | UCLV54077 | DirectTerminal | TRUE | 9 | GSO_18
m_46009_21 | UCLV54134 | DirectTerminal | TRUE | 22 | GSO_18
m_46011_21 | UCLV54136 | DirectTerminal | TRUE | 17 | GSO_18
m_46013_21 | UCLV54138 | DirectTerminal | TRUE | 10 | GSO_18
m_46066_21 | UCLV54189 | DirectTerminal | TRUE | 42 | GSO_18
m_46076_21 | UCLV54198 | DirectTerminal | TRUE | 22 | GSO_18
m_46146_21 | UCLV54260 | DirectTerminal | TRUE | 23 | GSO_18
m_46219_21 | UCLV54328 | DirectTerminal | TRUE | 10 | GSO_18
m_46291_21 | UCLV54397 | DirectTerminal | TRUE | 17 | GSO_18
m_46350_21 | UCLV54451 | DirectTerminal | TRUE | 45 | GSO_18
m_46440_21 | UCLV54536 | DirectTerminal | TRUE | 22 | GSO_18
m_46443_21 | UCLV54539 | DirectTerminal | TRUE | 44 | GSO_18
m_46506_21 | UCLV54599 | DirectTerminal | TRUE | 21 | GSO_18
m_46510_21 | UCLV54601 | DirectTerminal | TRUE | 24 | GSO_18
m_46513_21 | UCLV54604 | DirectTerminal | TRUE | 12 | GSO_18
m_46579_21 | UCLV54667 | DirectTerminal | TRUE | 19 | GSO_18
m_46622_21 | UCLV54705 | DirectTerminal | TRUE | 37 | GSO_18
m_46632_21 | UCLV54714 | DirectTerminal | TRUE | 24 | GSO_18
m_46635_21 | UCLV54717 | DirectTerminal | TRUE | 22 | GSO_18
m_46702_21 | UCLV54779 | DirectTerminal | TRUE | 13 | GSO_18
m_46705_21 | UCLV54781 | DirectTerminal | TRUE | 15 | GSO_18
m_46775_21 | UCLV54847 | DirectTerminal | TRUE | 22 | GSO_18
m_46848_21 | UCLV54916 | DirectTerminal | TRUE | 18 | GSO_18
m_46912_21 | UCLV54977 | DirectTerminal | TRUE | 23 | GSO_18
m_46989_21 | UCLV55046 | DirectTerminal | TRUE | 11 | GSO_18
m_47052_21 | UCLV55102 | DirectTerminal | TRUE | 20 | GSO_18
m_47054_21 | UCLV55104 | DirectTerminal | TRUE | 20 | GSO_18
m_47119_21 | UCLV55163 | DirectTerminal | TRUE | 17 | GSO_18
m_47122_21 | UCLV55166 | DirectTerminal | TRUE | 11 | GSO_18
m_47189_21 | UCLV55227 | DirectTerminal | TRUE | 22 | GSO_18
m_47257_21 | UCLV55291 | DirectTerminal | TRUE | 24 | GSO_18
m_47304_21 | UCLV55333 | DirectTerminal | TRUE | 22 | GSO_18
m_47306_21 | UCLV55335 | DirectTerminal | TRUE | 18 | GSO_18
m_47309_21 | UCLV55338 | DirectTerminal | TRUE | 10 | GSO_18
m_47366_21 | UCLV55390 | DirectTerminal | TRUE | 23 | GSO_18
m_47368_21 | UCLV55392 | DirectTerminal | TRUE | 24 | GSO_18
m_47440_21 | UCLV55459 | DirectTerminal | TRUE | 17 | GSO_18
m_47558_21 | UCLV55569 | DirectTerminal | TRUE | 19 | GSO_18
m_47561_21 | UCLV55571 | DirectTerminal | TRUE | 17 | GSO_18
m_47562_21 | UCLV55572 | DirectTerminal | TRUE | 7 | GSO_18
m_47625_21 | UCLV55631 | DirectTerminal | TRUE | 21 | GSO_18
m_47627_21 | UCLV55633 | DirectTerminal | TRUE | 35 | GSO_18
m_47683_21 | UCLV55691 | DirectTerminal | TRUE | 20 | GSO_18
m_47741_21 | UCLV55749 | DirectTerminal | TRUE | 20 | GSO_18
m_47809_21 | UCLV55817 | DirectTerminal | TRUE | 21 | GSO_18
m_47811_21 | UCLV55819 | DirectTerminal | TRUE | 18 | GSO_18
m_47880_21 | UCLV55885 | DirectTerminal | TRUE | 26 | GSO_18
m_47950_21 | UCLV55950 | DirectTerminal | TRUE | 26 | GSO_18
m_47953_21 | UCLV55953 | DirectTerminal | TRUE | 38 | GSO_18
m_48006_21 | UCLV56002 | DirectTerminal | TRUE | 47 | GSO_18
m_48017_21 | UCLV56012 | DirectTerminal | TRUE | 20 | GSO_18
m_48019_21 | UCLV56014 | DirectTerminal | TRUE | 21 | GSO_18
m_48085_21 | UCLV56075 | DirectTerminal | TRUE | 20 | GSO_18
m_481_21 | UCLV10495 | DirectTerminal | TRUE | 34 | GSO_18
m_48156_21 | UCLV56140 | DirectTerminal | TRUE | 19 | GSO_18
m_48159_21 | UCLV56143 | DirectTerminal | TRUE | 11 | GSO_18
m_48203_21 | UCLV56184 | DirectTerminal | TRUE | 16 | GSO_18
m_482_21 | UCLV10496 | DirectTerminal | TRUE | 25 | GSO_18
m_48278_21 | UCLV56254 | DirectTerminal | TRUE | 18 | GSO_18
m_48280_21 | UCLV56256 | DirectTerminal | TRUE | 18 | GSO_18
m_48281_21 | UCLV56257 | DirectTerminal | TRUE | 9 | GSO_18
m_483_21 | UCLV10497 | DirectTerminal | TRUE | 20 | GSO_18
m_48353_21 | UCLV56323 | DirectTerminal | TRUE | 19 | GSO_18
m_48355_21 | UCLV56325 | DirectTerminal | TRUE | 19 | GSO_18
m_48390_21 | UCLV56357 | DirectTerminal | TRUE | 24 | GSO_18
m_484_21 | UCLV10498 | DirectTerminal | TRUE | 36 | GSO_18
m_48464_21 | UCLV56424 | DirectTerminal | TRUE | 19 | GSO_18
m_485_21 | UCLV10499 | DirectTerminal | TRUE | 37 | GSO_18
m_48525_21 | UCLV56481 | DirectTerminal | TRUE | 33 | GSO_18
m_48537_21 | UCLV56492 | DirectTerminal | TRUE | 17 | GSO_18
m_48606_21 | UCLV56555 | DirectTerminal | TRUE | 17 | GSO_18
m_48648_21 | UCLV56596 | DirectTerminal | TRUE | 23 | GSO_18
m_48719_21 | UCLV56661 | DirectTerminal | TRUE | 18 | GSO_18
m_48787_21 | UCLV56725 | DirectTerminal | TRUE | 22 | GSO_18
m_48790_21 | UCLV56728 | DirectTerminal | TRUE | 21 | GSO_18
m_488_21 | UCLV10500 | DirectTerminal | TRUE | 13 | GSO_18
m_48856_21 | UCLV56792 | DirectTerminal | TRUE | 11 | GSO_18
m_48911_21 | UCLV56841 | DirectTerminal | TRUE | 26 | GSO_18
m_48914_21 | UCLV56844 | DirectTerminal | TRUE | 17 | GSO_18
m_489_21 | UCLV10501 | DirectTerminal | TRUE | 21 | GSO_18
m_48952_21 | UCLV56879 | DirectTerminal | TRUE | 9 | GSO_18
m_48989_21 | UCLV56911 | DirectTerminal | TRUE | 19 | GSO_18
m_48994_21 | UCLV56916 | DirectTerminal | TRUE | 10 | GSO_18
m_490_21 | UCLV10502 | DirectTerminal | TRUE | 18 | GSO_18
m_49028_21 | UCLV56948 | DirectTerminal | TRUE | 8 | GSO_18
m_49065_21 | UCLV56981 | DirectTerminal | TRUE | 20 | GSO_18
m_49069_21 | UCLV56985 | DirectTerminal | TRUE | 7 | GSO_18
m_491_21 | UCLV10503 | DirectTerminal | TRUE | 22 | GSO_18
m_49136_21 | UCLV57048 | DirectTerminal | TRUE | 23 | GSO_18
m_49202_21 | UCLV57110 | DirectTerminal | TRUE | 20 | GSO_18
m_49206_21 | UCLV57114 | DirectTerminal | TRUE | 10 | GSO_18
m_492_21 | UCLV10504 | DirectTerminal | TRUE | 22 | GSO_18
m_49274_21 | UCLV57176 | DirectTerminal | TRUE | 26 | GSO_18
m_49276_21 | UCLV57178 | DirectTerminal | TRUE | 17 | GSO_18
m_493_21 | UCLV10505 | DirectTerminal | TRUE | 30 | GSO_18
m_49349_21 | UCLV57243 | DirectTerminal | TRUE | 18 | GSO_18
m_49396_21 | UCLV57286 | DirectTerminal | TRUE | 12 | GSO_18
m_49398_21 | UCLV57288 | DirectTerminal | TRUE | 16 | GSO_18
m_49399_21 | UCLV57289 | DirectTerminal | TRUE | 12 | GSO_18
m_494_21 | UCLV10506 | DirectTerminal | TRUE | 15 | GSO_18
m_49470_21 | UCLV57355 | DirectTerminal | TRUE | 19 | GSO_18
m_49537_21 | UCLV57419 | DirectTerminal | TRUE | 20 | GSO_18
m_49600_21 | UCLV57477 | DirectTerminal | TRUE | 19 | GSO_18
m_49665_21 | UCLV57539 | DirectTerminal | TRUE | 16 | GSO_18
m_49738_21 | UCLV57604 | DirectTerminal | TRUE | 20 | GSO_18
m_49740_21 | UCLV57606 | DirectTerminal | TRUE | 16 | GSO_18
m_49807_21 | UCLV57668 | DirectTerminal | TRUE | 17 | GSO_18
m_49811_21 | UCLV57671 | DirectTerminal | TRUE | 9 | GSO_18
m_49854_21 | UCLV57711 | DirectTerminal | TRUE | 19 | GSO_18
m_49925_21 | UCLV57778 | DirectTerminal | TRUE | 22 | GSO_18
m_49928_21 | UCLV57780 | DirectTerminal | TRUE | 21 | GSO_18
m_49986_21 | UCLV57835 | DirectTerminal | TRUE | 22 | GSO_18
m_49988_21 | UCLV57837 | DirectTerminal | TRUE | 15 | GSO_18
m_50087_21 | UCLV57927 | DirectTerminal | TRUE | 19 | GSO_18
m_50107_21 | UCLV57945 | DirectTerminal | TRUE | 33 | GSO_18
m_50118_21 | UCLV57955 | DirectTerminal | TRUE | 16 | GSO_18
m_50184_21 | UCLV58018 | DirectTerminal | TRUE | 22 | GSO_18
m_50252_21 | UCLV58083 | DirectTerminal | TRUE | 16 | GSO_18
m_50255_21 | UCLV58086 | DirectTerminal | TRUE | 17 | GSO_18
m_50257_21 | UCLV58088 | DirectTerminal | TRUE | 17 | GSO_18
m_50321_21 | UCLV58148 | DirectTerminal | TRUE | 42 | GSO_18
m_50333_21 | UCLV58159 | DirectTerminal | TRUE | 20 | GSO_18
m_50336_21 | UCLV58161 | DirectTerminal | TRUE | 16 | GSO_18
m_50398_21 | UCLV58219 | DirectTerminal | TRUE | 24 | GSO_18
m_50462_21 | UCLV58278 | DirectTerminal | TRUE | 21 | GSO_18
m_50466_21 | UCLV58281 | DirectTerminal | TRUE | 12 | GSO_18
m_50524_21 | UCLV58339 | DirectTerminal | TRUE | 6 | GSO_18
m_50564_21 | UCLV58376 | DirectTerminal | TRUE | 21 | GSO_18
m_50618_21 | UCLV58427 | DirectTerminal | TRUE | 44 | GSO_18
m_50629_21 | UCLV58437 | DirectTerminal | TRUE | 24 | GSO_18
m_50631_21 | UCLV58439 | DirectTerminal | TRUE | 20 | GSO_18
m_50635_21 | UCLV58442 | DirectTerminal | TRUE | 14 | GSO_18
m_50697_21 | UCLV58499 | DirectTerminal | TRUE | 22 | GSO_18
m_50702_21 | UCLV58502 | DirectTerminal | TRUE | 15 | GSO_18
m_50755_21 | UCLV58550 | DirectTerminal | TRUE | 19 | GSO_18
m_50757_21 | UCLV58552 | DirectTerminal | TRUE | 15 | GSO_18
m_50809_21 | UCLV58601 | DirectTerminal | TRUE | 31 | GSO_18
m_50821_21 | UCLV58612 | DirectTerminal | TRUE | 18 | GSO_18
m_50823_21 | UCLV58614 | DirectTerminal | TRUE | 18 | GSO_18
m_50891_21 | UCLV58679 | DirectTerminal | TRUE | 17 | GSO_18
m_50895_21 | UCLV58682 | DirectTerminal | TRUE | 6 | GSO_18
m_51002_21 | UCLV58781 | DirectTerminal | TRUE | 17 | GSO_18
m_51071_21 | UCLV58846 | DirectTerminal | TRUE | 20 | GSO_18
m_51073_21 | UCLV58848 | DirectTerminal | TRUE | 16 | GSO_18
m_51076_21 | UCLV58850 | DirectTerminal | TRUE | 12 | GSO_18
m_51148_21 | UCLV58916 | DirectTerminal | TRUE | 12 | GSO_18
m_51196_21 | UCLV58961 | DirectTerminal | TRUE | 23 | GSO_18
m_51199_21 | UCLV58964 | DirectTerminal | TRUE | 22 | GSO_18
m_51273_21 | UCLV59030 | DirectTerminal | TRUE | 14 | GSO_18
m_51403_21 | UCLV59155 | DirectTerminal | TRUE | 23 | GSO_18
m_51466_21 | UCLV59215 | DirectTerminal | TRUE | 20 | GSO_18
m_51468_21 | UCLV59217 | DirectTerminal | TRUE | 18 | GSO_18
m_51517_21 | UCLV59265 | DirectTerminal | TRUE | 39 | GSO_18
m_51529_21 | UCLV59276 | DirectTerminal | TRUE | 19 | GSO_18
m_51601_21 | UCLV59342 | DirectTerminal | TRUE | 19 | GSO_18
m_51692_21 | UCLV59430 | DirectTerminal | TRUE | 26 | GSO_18
m_51693_21 | UCLV59431 | DirectTerminal | TRUE | 24 | GSO_18
m_51763_21 | UCLV59497 | DirectTerminal | TRUE | 17 | GSO_18
m_51765_21 | UCLV59499 | DirectTerminal | TRUE | 12 | GSO_18
m_51837_21 | UCLV59566 | DirectTerminal | TRUE | 20 | GSO_18
m_51879_21 | UCLV59605 | DirectTerminal | TRUE | 17 | GSO_18
m_51948_21 | UCLV59670 | DirectTerminal | TRUE | 21 | GSO_18
m_52018_21 | UCLV59736 | DirectTerminal | TRUE | 20 | GSO_18
m_52020_21 | UCLV59738 | DirectTerminal | TRUE | 11 | GSO_18
m_52090_21 | UCLV59803 | DirectTerminal | TRUE | 18 | GSO_18
m_52113_21 | UCLV59825 | DirectTerminal | TRUE | 25 | GSO_18
m_52144_21 | UCLV59854 | DirectTerminal | TRUE | 26 | GSO_18
m_52146_21 | UCLV59856 | DirectTerminal | TRUE | 21 | GSO_18
m_52217_21 | UCLV59922 | DirectTerminal | TRUE | 20 | GSO_18
m_52219_21 | UCLV59924 | DirectTerminal | TRUE | 9 | GSO_18
m_52282_21 | UCLV59985 | DirectTerminal | TRUE | 22 | GSO_18
m_52325_21 | UCLV60024 | DirectTerminal | TRUE | 23 | GSO_18
m_52328_21 | UCLV60027 | DirectTerminal | TRUE | 8 | GSO_18
m_52390_21 | UCLV60086 | DirectTerminal | TRUE | 25 | GSO_18
m_52392_21 | UCLV60088 | DirectTerminal | TRUE | 22 | GSO_18
m_52449_21 | UCLV60142 | DirectTerminal | TRUE | 42 | GSO_18
m_52460_21 | UCLV60152 | DirectTerminal | TRUE | 20 | GSO_18
m_52533_21 | UCLV60218 | DirectTerminal | TRUE | 20 | GSO_18
m_52588_21 | UCLV60270 | DirectTerminal | TRUE | 17 | GSO_18
m_52660_21 | UCLV60337 | DirectTerminal | TRUE | 16 | GSO_18
m_52731_21 | UCLV60404 | DirectTerminal | TRUE | 21 | GSO_18
m_52733_21 | UCLV60406 | DirectTerminal | TRUE | 23 | GSO_18
m_52787_21 | UCLV60459 | DirectTerminal | TRUE | 19 | GSO_18
m_52851_21 | UCLV60520 | DirectTerminal | TRUE | 22 | GSO_18
m_52853_21 | UCLV60522 | DirectTerminal | TRUE | 20 | GSO_18
m_52926_21 | UCLV60590 | DirectTerminal | TRUE | 19 | GSO_18
m_52928_21 | UCLV60592 | DirectTerminal | TRUE | 18 | GSO_18
m_52997_21 | UCLV60658 | DirectTerminal | TRUE | 21 | GSO_18
m_53016_21 | UCLV60676 | DirectTerminal | TRUE | 44 | GSO_18
m_53029_21 | UCLV60688 | DirectTerminal | TRUE | 24 | GSO_18
m_53032_21 | UCLV60690 | DirectTerminal | TRUE | 23 | GSO_18
m_53085_21 | UCLV60740 | DirectTerminal | TRUE | 36 | GSO_18
m_53098_21 | UCLV60752 | DirectTerminal | TRUE | 22 | GSO_18
m_53166_21 | UCLV60818 | DirectTerminal | TRUE | 16 | GSO_18
m_53170_21 | UCLV60821 | DirectTerminal | TRUE | 17 | GSO_18
m_53233_21 | UCLV60884 | DirectTerminal | TRUE | 21 | GSO_18
m_53280_21 | UCLV60927 | DirectTerminal | TRUE | 22 | GSO_18
m_53334_21 | UCLV60979 | DirectTerminal | TRUE | 48 | GSO_18
m_53347_21 | UCLV60990 | DirectTerminal | TRUE | 23 | GSO_18
m_53407_21 | UCLV61045 | DirectTerminal | TRUE | 39 | GSO_18
m_53415_21 | UCLV61052 | DirectTerminal | TRUE | 22 | GSO_18
m_53476_21 | UCLV61110 | DirectTerminal | TRUE | 19 | GSO_18
m_53538_21 | UCLV61167 | DirectTerminal | TRUE | 17 | GSO_18
m_53615_21 | UCLV61238 | DirectTerminal | TRUE | 25 | GSO_18
m_53686_21 | UCLV61303 | DirectTerminal | TRUE | 23 | GSO_18
m_53688_21 | UCLV61305 | DirectTerminal | TRUE | 18 | GSO_18
m_53728_21 | UCLV61344 | DirectTerminal | TRUE | 21 | GSO_18
m_53791_21 | UCLV61403 | DirectTerminal | TRUE | 20 | GSO_18
m_53793_21 | UCLV61405 | DirectTerminal | TRUE | 17 | GSO_18
m_53860_21 | UCLV61467 | DirectTerminal | TRUE | 17 | GSO_18
m_53991_21 | UCLV61587 | DirectTerminal | TRUE | 11 | GSO_18
m_53996_21 | UCLV61592 | DirectTerminal | TRUE | 10 | GSO_18
m_54064_21 | UCLV61653 | DirectTerminal | TRUE | 17 | GSO_18
m_54069_21 | UCLV61658 | DirectTerminal | TRUE | 7 | GSO_18
m_54130_21 | UCLV61717 | DirectTerminal | TRUE | 20 | GSO_18
m_54132_21 | UCLV61719 | DirectTerminal | TRUE | 16 | GSO_18
m_54198_21 | UCLV61782 | DirectTerminal | TRUE | 20 | GSO_18
m_54201_21 | UCLV61785 | DirectTerminal | TRUE | 15 | GSO_18
m_54259_21 | UCLV61839 | DirectTerminal | TRUE | 25 | GSO_18
m_54261_21 | UCLV61840 | DirectTerminal | TRUE | 16 | GSO_18
m_54330_21 | UCLV61904 | DirectTerminal | TRUE | 19 | GSO_18
m_54334_21 | UCLV61908 | DirectTerminal | TRUE | 5 | GSO_18
m_54430_21 | UCLV61995 | DirectTerminal | TRUE | 20 | GSO_18
m_54432_21 | UCLV61997 | DirectTerminal | TRUE | 19 | GSO_18
m_54508_21 | UCLV62065 | DirectTerminal | TRUE | 13 | GSO_18
m_54577_21 | UCLV62128 | DirectTerminal | TRUE | 15 | GSO_18
m_54691_21 | UCLV62235 | DirectTerminal | TRUE | 19 | GSO_18
m_54697_21 | UCLV62240 | DirectTerminal | TRUE | 8 | GSO_18
m_54756_21 | UCLV62297 | DirectTerminal | TRUE | 22 | GSO_18
m_54758_21 | UCLV62299 | DirectTerminal | TRUE | 22 | GSO_18
m_54879_21 | UCLV62412 | DirectTerminal | TRUE | 22 | GSO_18
m_54881_21 | UCLV62414 | DirectTerminal | TRUE | 22 | GSO_18
m_54953_21 | UCLV62481 | DirectTerminal | TRUE | 13 | GSO_18
m_54955_21 | UCLV62483 | DirectTerminal | TRUE | 15 | GSO_18
m_55027_21 | UCLV62550 | DirectTerminal | TRUE | 18 | GSO_18
m_55031_21 | UCLV62554 | DirectTerminal | TRUE | 17 | GSO_18
m_55140_21 | UCLV62658 | DirectTerminal | TRUE | 22 | GSO_18
m_55144_21 | UCLV62661 | DirectTerminal | TRUE | 7 | GSO_18
m_55202_21 | UCLV62716 | DirectTerminal | TRUE | 15 | GSO_18
m_55270_21 | UCLV62779 | DirectTerminal | TRUE | 20 | GSO_18
m_55274_21 | UCLV62782 | DirectTerminal | TRUE | 4 | GSO_18
m_55310_21 | UCLV62819 | DirectTerminal | TRUE | 20 | GSO_18
m_55379_21 | UCLV62885 | DirectTerminal | TRUE | 16 | GSO_18
m_55454_21 | UCLV62955 | DirectTerminal | TRUE | 20 | GSO_18
m_55456_21 | UCLV62957 | DirectTerminal | TRUE | 19 | GSO_18
m_55507_21 | UCLV63004 | DirectTerminal | TRUE | 42 | GSO_18
m_55517_21 | UCLV63013 | DirectTerminal | TRUE | 26 | GSO_18
m_55571_21 | UCLV63067 | DirectTerminal | TRUE | 24 | GSO_18
m_55575_21 | UCLV63070 | DirectTerminal | TRUE | 28 | GSO_18
m_55644_21 | UCLV63138 | DirectTerminal | TRUE | 19 | GSO_18
m_55716_21 | UCLV63205 | DirectTerminal | TRUE | 22 | GSO_18
m_55718_21 | UCLV63207 | DirectTerminal | TRUE | 16 | GSO_18
m_55771_21 | UCLV63258 | DirectTerminal | TRUE | 19 | GSO_18
m_55827_21 | UCLV63310 | DirectTerminal | TRUE | 44 | GSO_18
m_55839_21 | UCLV63321 | DirectTerminal | TRUE | 23 | GSO_18
m_55876_21 | UCLV63355 | DirectTerminal | TRUE | 21 | GSO_18
m_55904_21 | UCLV63382 | DirectTerminal | TRUE | 21 | GSO_18
m_55907_21 | UCLV63385 | DirectTerminal | TRUE | 14 | GSO_18
m_55983_21 | UCLV63455 | DirectTerminal | TRUE | 14 | GSO_18
m_55984_21 | UCLV63456 | DirectTerminal | TRUE | 5 | GSO_18
m_56044_21 | UCLV63511 | DirectTerminal | TRUE | 22 | GSO_18
m_56114_21 | UCLV63578 | DirectTerminal | TRUE | 24 | GSO_18
m_56180_21 | UCLV63639 | DirectTerminal | TRUE | 19 | GSO_18
m_56183_21 | UCLV63641 | DirectTerminal | TRUE | 18 | GSO_18
m_56185_21 | UCLV63643 | DirectTerminal | TRUE | 13 | GSO_18
m_56220_21 | UCLV63675 | DirectTerminal | TRUE | 21 | GSO_18
m_56285_21 | UCLV63738 | DirectTerminal | TRUE | 22 | GSO_18
m_56288_21 | UCLV63740 | DirectTerminal | TRUE | 18 | GSO_18
m_56290_21 | UCLV63742 | DirectTerminal | TRUE | 13 | GSO_18
m_56358_21 | UCLV63807 | DirectTerminal | TRUE | 25 | GSO_18
m_56427_21 | UCLV63870 | DirectTerminal | TRUE | 18 | GSO_18
m_56468_21 | UCLV63908 | DirectTerminal | TRUE | 17 | GSO_18
m_56471_21 | UCLV63910 | DirectTerminal | TRUE | 17 | GSO_18
m_56473_21 | UCLV63912 | DirectTerminal | TRUE | 11 | GSO_18
m_56543_21 | UCLV63979 | DirectTerminal | TRUE | 21 | GSO_18
m_56608_21 | UCLV64039 | DirectTerminal | TRUE | 23 | GSO_18
m_56612_21 | UCLV64042 | DirectTerminal | TRUE | 15 | GSO_18
m_56730_21 | UCLV64154 | DirectTerminal | TRUE | 42 | GSO_18
m_56741_21 | UCLV64164 | DirectTerminal | TRUE | 20 | GSO_18
m_56743_21 | UCLV64166 | DirectTerminal | TRUE | 15 | GSO_18
m_56785_21 | UCLV64203 | DirectTerminal | TRUE | 9 | GSO_18
m_56818_21 | UCLV64233 | DirectTerminal | TRUE | 20 | GSO_18
m_56821_21 | UCLV64236 | DirectTerminal | TRUE | 10 | GSO_18
m_56852_21 | UCLV64267 | DirectTerminal | TRUE | 15 | GSO_18
m_56885_21 | UCLV64297 | DirectTerminal | TRUE | 21 | GSO_18
m_58172_21 | UCLV790 | DirectTerminal | TRUE | 7 | GSO_18
m_58185_21 | UCLV795 | DirectTerminal | TRUE | 6 | GSO_18
m_58252_21 | UCLV801 | DirectTerminal | TRUE | 14 | GSO_18
m_58263_21 | UCLV802 | DirectTerminal | TRUE | 8 | GSO_18
m_58274_21 | UCLV803 | DirectTerminal | TRUE | 13 | GSO_18
m_58285_21 | UCLV804 | DirectTerminal | TRUE | 14 | GSO_18
m_58295_21 | UCLV805 | DirectTerminal | TRUE | 14 | GSO_18
m_58306_21 | UCLV806 | DirectTerminal | TRUE | 13 | GSO_18
m_58316_21 | UCLV807 | DirectTerminal | TRUE | 14 | GSO_18
m_58327_21 | UCLV808 | DirectTerminal | TRUE | 12 | GSO_18
m_58338_21 | UCLV809 | DirectTerminal | TRUE | 13 | GSO_18
m_58350_21 | UCLV810 | DirectTerminal | TRUE | 16 | GSO_18
m_58361_21 | UCLV811 | DirectTerminal | TRUE | 10 | GSO_18
m_58372_21 | UCLV812 | DirectTerminal | TRUE | 11 | GSO_18
m_58382_21 | UCLV813 | DirectTerminal | TRUE | 14 | GSO_18
m_58393_21 | UCLV814 | DirectTerminal | TRUE | 13 | GSO_18
m_58624_21 | UCLV842 | DirectTerminal | TRUE | 22 | GSO_18
m_58635_21 | UCLV843 | DirectTerminal | TRUE | 26 | GSO_18
m_58646_21 | UCLV844 | DirectTerminal | TRUE | 25 | GSO_18
m_58657_21 | UCLV845 | DirectTerminal | TRUE | 19 | GSO_18
m_58690_21 | UCLV848 | DirectTerminal | TRUE | 16 | GSO_18
m_58713_21 | UCLV850 | DirectTerminal | TRUE | 18 | GSO_18
m_58724_21 | UCLV851 | DirectTerminal | TRUE | 20 | GSO_18
m_58735_21 | UCLV852 | DirectTerminal | TRUE | 18 | GSO_18
m_58768_21 | UCLV855 | DirectTerminal | TRUE | 24 | GSO_18
m_58790_21 | UCLV857 | DirectTerminal | TRUE | 20 | GSO_18
m_5880_21 | UCLV15920 | DirectTerminal | TRUE | 23 | GSO_18
m_58808_21 | UCLV8586 | DirectTerminal | TRUE | 21 | GSO_18
m_58809_21 | UCLV8587 | DirectTerminal | TRUE | 20 | GSO_18
m_58810_21 | UCLV8588 | DirectTerminal | TRUE | 18 | GSO_18
m_58811_21 | UCLV8589 | DirectTerminal | TRUE | 27 | GSO_18
m_5881_21 | UCLV15921 | DirectTerminal | TRUE | 22 | GSO_18
m_59998_21 | UCMV21 | DirectTerminal | TRUE | 19 | GSO_18
m_59999_21 | UCMV22 | DirectTerminal | TRUE | 27 | GSO_18
m_2755_22 | UCMV43 | DirectTerminal | TRUE | 2 | GSO_127

## Assumptions
Item | Assumption
Model purpose | Hourly time-series thermal hosting model used as the physical feasibility layer before optimization and Monte Carlo.
Historical period | 2024 observed meter and breaker kWh profiles are used as the baseline operating year.
Feeder load truth | Circuit-breaker SCADA is treated as the feeder-level total load truth.
Spatial load distribution | Hourly meter profiles determine the spatial distribution of feeder demand and are rescaled each hour to exactly reconcile to breaker SCADA.
Meter reconciliation | This approach is supported by the prior audit in which all 10 modeled feeders reconciled strongly to breaker SCADA.
Meter topology fallback | Meters are mapped to reachable topology terminals first, then upstream-element topology when available; unresolved meters are conservatively retained at the feeder root and flagged.
Power factor | 0.95 converts apparent equipment ratings to screening real-power capacity.
Three-phase line capacity | For three-phase lines, real-power thermal capacity = sqrt(3) x line-line kV x ampacity x power factor.
Two-phase line capacity | For two-phase line-line elements, real-power thermal capacity = line-line kV x ampacity x power factor.
Single-phase line capacity | For single-phase elements, phase-neutral voltage is approximated as line-line voltage / sqrt(3).
Transformer capacity | Transformer real-power thermal capacity = rating_kVA / 1000 x power factor.
Breaker capacity | Breaker real-power thermal capacity = rating_kVA / 1000 x power factor.
Candidate connection | The added data-center load is connected at the downstream node of the candidate primary line and therefore flows through that line and every upstream constrained element.
Open switches | Open switchable elements are excluded from the active network topology.
Parallel elements | When multiple series elements connect the same topology nodes, the lower-capacity representation is retained as a conservative screening assumption.
Thermal constraints | Rated lines, transformers, and the feeder breaker are enforced. Switches, fuses, reclosers, and regulators preserve connectivity but are not constrained unless a usable thermal rating is represented as a line/transformer rating.
Substation capacity | No explicit substation capacity is currently available, so substation capacity is NOT enforced and must be added before calling the result final upstream hosting capacity.
Voltage / AC power flow | Line R/X and transformer impedance are unavailable, so voltage drop, reactive power, losses, and full AC power flow are NOT modeled.
PV / EV baseline | Baseline net feeder behavior is captured through breaker calibration. PV, EV, battery, DR, and flexible-compute interventions should be added explicitly in later scenario models.
Interpretation | Outputs are time-series thermal hosting capacity, not utility-approved interconnection capacity.